## AQ 100 Modbus map
AQ 100 Modbus map
Reg # | Register Name | HR | Type | Data Type | Bit 1 | Bit 2 | Bit 3 | Bit 4 | Bit 5 | Bit 6 | Bit 7 | Bit 8 | Bit 9 | Bit 10 | Bit 11 | Bit 12 | Bit 13 | Bit 14 | Bit 15 | Bit 16 | Description
1 | Sensors installed to channel | 40001 | R | 1-Bit | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10 | S11 | S12 | S13 | S14 | S15 | - | Indicates if a sensor has been connected to the channel or not.
2 | Sensor channels activated | 40002 | R | 1-Bit | S1 | S2 | S3 | S4 | S5/AQD | S6 | S7 | S8 | S9 | S10 | S11 | S12 | S13 | S14 | S15 | - | Indicates sensor activation for each channel.
3 | I/O channels activated | 40003 | R | 1-Bit | BI1 | BI2 | BO1 | T1 | T2 | T3 | T4 | SF | HSO1 | AQD | HSO2 | Io | IL1 | IL2 | IL3 | - | Indicates activation of I/O: binary inputs binary outputs, trip relays, high-speed outputs, arc quenching device control, phase overcurrent (I>) detection, earth fault detection
4 | Device settings (DIP switch SW1) | 40004 | R | 1-Bit | SW1:1 | SW1:2 | SW1:3 | SW1:4 | SW1:5 | SW1:6 | SW1:7 | SW1:8 | SW2:1 | SW2:2 | SW2:3 | SW2:4 | SW2:5 | SW2:6 | SW2:7 | SW2:8 | Position of the DIP switches (ON/OFF).
5 | Serial number | 40005 | R | 32-Bit Int | SN17 | SN18 | SN19 | SN20 | SN21 | SN22 | SN23 | SN24 | SN25 | SN26 | SN27 | SN28 | SN29 | SN30 | SN31 | SN32 | Serial number of the device.
6 | Serial number, cont. | 40006 | R |  | SN1 | SN2 | SN3 | SN4 | SN5 | SN6 | SN7 | SN8 | SN9 | SN10 | SN11 | SN12 | SN13 | SN14 | SN15 | SN16 | Serial number, cont.
7 | Sensor channel activated (Latched) | 40007 | R | 1-Bit | S1 | S2 | S3 | S4 | S5/AQD | S6 | S7 | S8 | S9 | S10 | S11 | S12 | S13 | S14 | S15 | - | Same as "Sensor channel activations", but the activated status is held until reset with "Clear latched signals" (reg. number 11).
8 | I/O channels activated (Latched) | 40008 | R | 1-Bit | BI1 | BI2 | BO1 | T1 | T2 | T3 | T4 | SF | HSO1 | AQD | HSO2 | Io | IL1 | IL2 | IL3 | - | Same as "I/O channels activated", but the activated status is held until reset with "Clear latched signals" (reg. number 11).
9 | Sensor channel errors | 40009 | R | 1-Bit | S1 | S2 | S3 | S4 | S5/AQD | S6 | S7 | S8 | S9 | S10 | S11 | S12 | S13 | S14 | S15 | - | Activates if the number of sensors connected to the channel doesn't match with the loaded configuration (e.g. a sensor has been disconnected).
10 | Input channel errors | 40010 | R | 1-Bit | BI1 | BI2 | BI3 | BI4 | BI5 | BI6 | IL | - | - | - | - | - | - | - | - | - | Position of the DIP switches (ON/OFF).
11 | Clearing of latched registers (reg. no. 7 ,8 & 19) | 40011 | W | 1-Bit | [6 empty] | - | - | - | - | - | - | - | - | - | - | Writeable register. Clears signals latched in registers 7, 8 & 19. These latched signals are not reset when "SET" button is pressed. | bar: BI1 to S6 BI6
12 | Device settings (DIP switch SW2) | 40012 | R | 1-Bit | SW2:1 | SW2:2 | SW2:3 | SW2:4 | SW2:5 | SW2:6 | SW2:7 | SW2:8 | - | - | - | - | - | - | - | - | Position of the DIP switches (ON/OFF).
13 | Device settings (DIP switch SW3) | 40013 | R | 1-Bit | SW3:1 | SW3:2 | SW3:3 | SW3:4 | SW3:5 | SW3:6 | SW3:7 | SW3:8 | - | - | - | - | - | - | - | - | Position of the DIP switches (ON/OFF).
14 | (reserved) | 40014 | R | 1-Bit | [6 empty] | - | - | - | - | - | - | - | - | - | - | (reserved) | bar: BI1 to S6 BI6
15 | Sensor channels, number of sensors installed per channel | 40015 | R | 2-Bit | S1:Bit 1 | S1:Bit 2 | S2:Bit 1 | S2:Bit 2 | S3:Bit 1 | S3:Bit 2 | S4:Bit 1 | S4:Bit 2 | S5:Bit 1 | - | - | - | - | - | - | - | Number of sensors connected to the channel (0…3).
16 | I/O number of devices installed to BI1 & BI2 | 40016 | R | 8-Bit | BI1:1 | BI1:2 | BI1:3 | BI1:4 | BI1:5 | BI1:6 | BI1:7 | BI1:8 | BI2:1 | BI2:2 | BI2:3 | BI2:4 | BI2:5 | BI2:6 | BI2:7 | BI2:8 | Detected number of devices (binary output or high-speed output) connected to the binary input.
17 | I/O number of devices installed to BI3 & BI4 | 40017 | R | 8-Bit | BI3:1 | BI3:2 | BI3:3 | BI3:4 | BI3:5 | BI3:6 | BI3:7 | BI3:8 | BI4:1 | BI4:2 | BI4:3 | BI4:4 | BI4:5 | BI4:6 | BI4:7 | BI4:8 | Detected number of devices (binary output or high-speed output) connected to the binary input.
18 | I/O number of devices installed to BI5 & BI6 | 40018 | R | 8-Bit | BI5:1 | BI5:2 | BI5:3 | BI5:4 | BI5:5 | BI5:6 | BI5:7 | BI5:8 | BI6:1 | BI6:2 | BI6:3 | BI6:4 | BI6:5 | BI6:6 | BI6:7 | BI6:8 | Detected number of devices (binary output or high-speed output) connected to the binary input.
19 | I/O channels activated, extended (Latched) | 40019 | R | 1-Bit | BI3 | BI4 | BI5 | BI6 | BO2 | BO3 | BO1-CBFP | BO2-CBFP | BO3-CBFP | - | - | - | - | - | - | - | Same as "I/O channels activated", but the activated status is held until reset with "Clear latched signals" (reg. number 11).
20 | IL1: Measured current, ADC values | 40020 | R | 16-Bit Int | IL1:1 | IL1:2 | IL1:3 | IL1:4 | IL1:5 | IL1:6 | IL1:7 | IL1:8 | IL1:9 | IL1:10 | IL1:11 | IL1:12 | IL1:13 | IL1:14 | IL1:15 | IL1:16 | Raw phase current value measured by IL1 channel.
21 | IL2: Measured current, ADC values | 40021 | R | 16-Bit Int | IL2:1 | IL2:2 | IL2:3 | IL2:4 | IL2:5 | IL2:6 | IL2:7 | IL2:8 | IL2:9 | IL2:10 | IL2:11 | IL2:12 | IL2:13 | IL2:14 | IL2:15 | IL2:16 | Raw phase current value measured by IL2 channel.
22 | IL3: Measured current, ADC values | 40022 | R | 16-Bit Int | IL3:1 | IL3:2 | IL3:3 | IL3:4 | IL3:5 | IL3:6 | IL3:7 | IL3:8 | IL3:9 | IL3:10 | IL3:11 | IL3:12 | IL3:13 | IL3:14 | IL3:15 | IL3:16 | Raw phase current value measured by IL3 channel.
23 | I0: Measured current, ADC values | 40023 | R | 16-Bit Int | I0:1 | I0:2 | I0:3 | I0:4 | I0:5 | I0:6 | I0:7 | I0:8 | I0:9 | I0:10 | I0:11 | I0:12 | I0:13 | I0:14 | I0:15 | I0:16 | Raw residual current value measured by I0 channel.
24 | IL1, IL2 & IL3: Set overcurrent level, ADC values | 40024 | R | 16-Bit Int | TRIML:1 | TRIML:2 | TRIML:3 | TRIML:4 | TRIML:5 | TRIML:6 | TRIML:7 | TRIML:8 | TRIML:9 | TRIML:10 | TRIML:11 | TRIML:12 | TRIML:13 | TRIML:14 | TRIML:15 | TRIML:16 | Raw phase overcurrent setting level in use.
25 | I0: Set overcurrent level, ADC values | 40025 | R | 16-Bit Int | TRIMN:1 | TRIMN:2 | TRIMN:3 | TRIMN:4 | TRIMN:5 | TRIMN:6 | TRIMN:7 | TRIMN:8 | TRIMN:9 | TRIMN:10 | TRIMN:11 | TRIMN:12 | TRIMN:13 | TRIMN:14 | TRIMN:15 | TRIMN:16 | Raw earth fault setting level in use.
26 | IL1: Measured current, calculated, A | 40026 | R | 16-Bit Int | IL1:1 | IL1:2 | IL1:3 | IL1:4 | IL1:5 | IL1:6 | IL1:7 | IL1:8 | IL1:9 | IL1:10 | IL1:11 | IL1:12 | IL1:13 | IL1:14 | IL1:15 | IL1:16 | Phase current value measured by IL1 channel in amperes.
27 | IL2: Measured current, calculated, A | 40027 | R | 16-Bit Int | IL2:1 | IL2:2 | IL2:3 | IL2:4 | IL2:5 | IL2:6 | IL2:7 | IL2:8 | IL2:9 | IL2:10 | IL2:11 | IL2:12 | IL2:13 | IL2:14 | IL2:15 | IL2:16 | Phase current value measured by IL2 channel in amperes.
28 | IL3: Measured current, calculated, A | 40028 | R | 16-Bit Int | IL3:1 | IL3:2 | IL3:3 | IL3:4 | IL3:5 | IL3:6 | IL3:7 | IL3:8 | IL3:9 | IL3:10 | IL3:11 | IL3:12 | IL3:13 | IL3:14 | IL3:15 | IL3:16 | Phase current value measured by IL3 channel in amperes.
29 | I0: Measured current, calculated, A | 40029 | R | 16-Bit Int | I0:1 | I0:2 | I0:3 | I0:4 | I0:5 | I0:6 | I0:7 | I0:8 | I0:9 | I0:10 | I0:11 | I0:12 | I0:13 | I0:14 | I0:15 | I0:16 | Residual current value measured by I0 channel in amperes.
30 | IL1, IL2 & IL3: Set overcurrent level, calculated, A | 40030 | R | 16-Bit Int | TRIML:1 | TRIML:2 | TRIML:3 | TRIML:4 | TRIML:5 | TRIML:6 | TRIML:7 | TRIML:8 | TRIML:9 | TRIML:10 | TRIML:11 | TRIML:12 | TRIML:13 | TRIML:14 | TRIML:15 | TRIML:16 | Phase overcurrent setting level in use in amperes.
31 | I0: Set overcurrent level, calculated, A | 40031 | R | 16-Bit Int | TRIMN:1 | TRIMN:2 | TRIMN:3 | TRIMN:4 | TRIMN:5 | TRIMN:6 | TRIMN:7 | TRIMN:8 | TRIMN:9 | TRIMN:10 | TRIMN:11 | TRIMN:12 | TRIMN:13 | TRIMN:14 | TRIMN:15 | TRIMN:16 | Earth fault setting level in use in amperes.
32 | Error types (See table below for descriptions) | 40032 | R | 1-Bit | PSCE | BICE | DSSE | TLSE | DIVE | DIVE | VRSE | PRSE | ASSE | IEPE | SNE | - | - | - | - | - | Error types (See table below for descriptions)
Error types
Code | Name | Description
SCE | Sensor Connection Error | Activates, if any sensor channel is missing sensors or has too many sensors compared to installed number | bar: TRIML:1 TRIMN:1 to TRIML:13 TRIMN:13
BICE | Binary Input Connection Error | Activates, if any binary input channel is missing its self-supervision pulses or has too many self-supervision pulses compared to installed number
DSSE | DIP Switch Setting Error | Activates, if any DIP switch setting is changed, and thus, different than the settings installed | bar: TRIML:1 TRIMN:1 to TRIML:13 TRIMN:13
TLSE | Trip Level Setting Error | Activates, if any of the IL or I0 activation threshold setting trimmers are changed and not installed
DIVE | Device Internal Voltage Error | Activates, if the monitored internal voltage drops below properly funtioning level | bar: TRIML:1 TRIMN:1 to TRIML:13 TRIMN:13
CTBE | Current Transformer Balance Error | Activates, if any current input channel is at zero when at least one current channel is over 0.2x In, which means an imbalance in the transformer
VRSE | Voltage Reference Supervision Error | Activates, if internal voltage of the device is out of bounds | bar: TRIML:1 TRIMN:1 to TRIML:13 TRIMN:13
PRSE | PCB Relay Supervision Error | Activates, if internal voltage of the device is out of bounds
ASSE | Arc Scheme Selection Error | Activates, if the selected arc scheme is not available in the device | bar: TRIML:1 TRIMN:1 to TRIML:13 TRIMN:13
IEPE | Internal EEPROM Power-on Error | Activates, if the EEPROM does not load correctly when the device powers on
SNE | Serial Number Error | Activates, if the serial number is 0 | bar: TRIML:1 TRIMN:1 to TRIML:13 TRIMN:13