## New IEC104 map
AQ-200 IED IEC101/IEC104 IOA LIST
NOTE: THIS MAP CAN BE DIFFERENT FROM THE ONE USED BY YOUR DEVICE! TO MAKE SURE YOU HAVE A MAP THAT MATCHES WITH YOUR DEVICE, GET IT FROM THE AQS CONFIGURATION FILE (TOOLS -> COMMUNICATION -> IEC101 / 104 MAP)
Single points
IOA | IOA2 byte | Name | Description
65537 | 1 | Local/Remote switch | Local/Remote switch
65538 | 2 | DI1 | Digital input 1
65539 | 3 | DI2 | Digital input 2
65540 | 4 | DI3 | Digital input 3
65541 | 5 | DI4 | Digital input 4
65542 | 6 | DI5 | Digital input 5
65543 | 7 | DI6 | Digital input 6
65544 | 8 | DI7 | Digital input 7
65545 | 9 | DI8 | Digital input 8
65546 | 10 | DI9 | Digital input 9
65547 | 11 | DI10 | Digital input 10
65548 | 12 | DI11 | Digital input 11
65549 | 13 | DI12 | Digital input 12
65550 | 14 | DI13 | Digital input 13
65551 | 15 | DI14 | Digital input 14
65552 | 16 | DI15 | Digital input 15
65553 | 17 | DI16 | Digital input 16
65554 | 18 | DI17 | Digital input 17
65555 | 19 | DI18 | Digital input 18
65556 | 20 | DI19 | Digital input 19
65557 | 21 | DI20 | Digital input 20
65558 | 22 | DI21 | Digital input 21
65559 | 23 | DI22 | Digital input 22
65560 | 24 | DI23 | Digital input 23
65561 | 25 | DI24 | Digital input 24
65562 | 26 | DI25 | Digital input 25
65563 | 27 | DI26 | Digital input 26
65564 | 28 | DI27 | Digital input 27
65565 | 29 | DI28 | Digital input 28
65566 | 30 | DI29 | Digital input 29
65567 | 31 | DI30 | Digital input 30
65568 | 32 | DI31 | Digital input 31
65569 | 33 | DI32 | Digital input 32
65570 | 34 | DI33 | Digital input 33
65571 | 35 | DI34 | Digital input 34
65572 | 36 | DI35 | Digital input 35
65573 | 37 | DI36 | Digital input 36
65574 | 38 | DI37 | Digital input 37
65575 | 39 | DI38 | Digital input 38
65576 | 40 | DI39 | Digital input 39
65577 | 41 | DI40 | Digital input 40
65578 | 42 | DI41 | Digital input 41
65579 | 43 | DI42 | Digital input 42
65580 | 44 | DI43 | Digital input 43
65581 | 45 | DI44 | Digital input 44
65582 | 46 | DI45 | Digital input 45
65583 | 47 | DI46 | Digital input 46
65584 | 48 | DI47 | Digital input 47
65585 | 49 | DI48 | Digital input 48
65586 | 50 | DI49 | Digital input 49
65587 | 51 | DI50 | Digital input 50
65588 | 52 | DI51 | Digital input 51
65589 | 53 | I> START (General) | Non-directional overcurrent 1 pick-up
65590 | 54 | I> TRIP (General) | Non-directional overcurrent 1 trip
65591 | 55 | I>> START (General) | Non-directional overcurrent 2 pick-up
65592 | 56 | I>> TRIP (General) | Non-directional overcurrent 2 trip
65593 | 57 | I>>> START (General) | Non-directional overcurrent 3 pick-up
65594 | 58 | I>>> TRIP (General) | Non-directional overcurrent 3 trip
65595 | 59 | I>>>> START (General) | Non-directional overcurrent 4 pick-up
65596 | 60 | I>>>> TRIP (General) | Non-directional overcurrent 4 trip
65597 | 61 | I0> START | Non-directional residual overcurrent 1 pick-up
65598 | 62 | I0> TRIP | Non-directional residual overcurrent 1 trip
65599 | 63 | I0>> START | Non-directional residual overcurrent 2 pick-up
65600 | 64 | I0>> TRIP | Non-directional residual overcurrent 2 trip
65601 | 65 | I0>>> START | Non-directional residual overcurrent 3 pick-up
65602 | 66 | I0>>> TRIP | Non-directional residual overcurrent 3 trip
65603 | 67 | I0>>>> START | Non-directional residual overcurrent 4 pick-up
65604 | 68 | I0>>>> TRIP | Non-directional residual overcurrent 4 trip
65605 | 69 | Ih> START | Harmonic overcurrent 1 pick-up
65606 | 70 | Ih>> START | Harmonic overcurrent 2 pick-up
65607 | 71 | Ih>>> START | Harmonic overcurrent 3 pick-up
65608 | 72 | Ih>>>> START | Harmonic overcurrent 4 pick-up
65609 | 73 | I2> START | Current unbalance 1 pick-up
65610 | 74 | I2> TRIP | Current unbalance 1 trip
65611 | 75 | I2>> START | Current unbalance 2 pick-up
65612 | 76 | I2>> TRIP | Current unbalance 2 trip
65613 | 77 | I2>>> START | Current unbalance 3 pick-up
65614 | 78 | I2>>> TRIP | Current unbalance 3 trip
65615 | 79 | I2>>>> START | Current unbalance 4 pick-up
65616 | 80 | I2>>>> TRIP | Current unbalance 4 trip
65617 | 81 | CLP condition | Cold-load pick-up condition
65618 | 82 | CLP condition | Cold-load pick-up condition
65619 | 83 | CBFP condition | Circuit breaker failure protection
65620 | 84 | CBFP condition | Circuit breaker failure protection
65621 | 85 | AR1 Operate | Autorecloser Operate
65622 | 86 | AR1 Request on | Autorecloser Request 1 On
65623 | 87 | AR2 Request on | Autorecloser Request 2 On
65624 | 88 | AR3 Request on | Autorecloser Request 3 On
65625 | 89 | AR4 Request on | Autorecloser Request 4 On
65626 | 90 | AR5 Request on | Autorecloser Request 5 On
65627 | 91 | AR Shot 1 Running | Autorecloser Shot 1 Running
65628 | 92 | AR Shot 2 Running | Autorecloser Shot 1 Running
65629 | 93 | AR Shot 3 Running | Autorecloser Shot 1 Running
65630 | 94 | AR Shot 4 Running | Autorecloser Shot 1 Running
65631 | 95 | AR Shot 5 Running | Autorecloser Shot 1 Running
65632 | 96 | AR Sequence finished | Autorecloser Shot 1 Running
65633 | 97 | AR Final Trip | Autorecloser Final Trip
65634 | 98 | ARC time on | Arcing time on
65635 | 99 | Reclaim time on | Reclaim time on
65636 | 100 | NTP quality | NTP quality for events
65637 | 101 | AR Lockout after successfull sequence | Autorecloser lockout after successfull sequence
65638 | 102 | AR Operation Inhibit | Autorecloser Operation Inhibit
65639 | 103 | AR Locked | Autorecloser locked
65640 | 104 | TF> Alarm1 | Feeder thermal overload alarm 1
65641 | 105 | TF> Trip | Feeder thermal overload trip
65642 | 106 | Internal Relay Fault active | Internal Relay Fault active
65643 | 107 | I0d> TRIP | Restricted earth-fault / Cable end differential trip
65644 | 108 | CBW Alarm 1 act | Circuit breaker wear alarm 1 act
65645 | 109 | CBW Alarm 2 act | Circuit breaker wear alarm 2 act
65646 | 110 | CTS1 ALARM | Current transformer supervision 1 Alarm
65647 | 111 | Logical Output 1 | Logical Output 1
65648 | 112 | Logical Output 2 | Logical Output 2
65649 | 113 | Logical Output 3 | Logical Output 3
65650 | 114 | Logical Output 4 | Logical Output 4
65651 | 115 | Logical Output 5 | Logical Output 5
65652 | 116 | Logical Output 6 | Logical Output 6
65653 | 117 | Logical Output 7 | Logical Output 7
65654 | 118 | Logical Output 8 | Logical Output 8
65655 | 119 | Logical Output 9 | Logical Output 9
65656 | 120 | Logical Output 10 | Logical Output 10
65657 | 121 | Logical Output 11 | Logical Output 11
65658 | 122 | Logical Output 12 | Logical Output 12
65659 | 123 | Logical Output 13 | Logical Output 13
65660 | 124 | Logical Output 14 | Logical Output 14
65661 | 125 | Logical Output 15 | Logical Output 15
65662 | 126 | Logical Output 16 | Logical Output 16
65663 | 127 | Logical Output 17 | Logical Output 17
65664 | 128 | Logical Output 18 | Logical Output 18
65665 | 129 | Logical Output 19 | Logical Output 19
65666 | 130 | Logical Output 20 | Logical Output 20
65667 | 131 | Logical Output 21 | Logical Output 21
65668 | 132 | Logical Output 22 | Logical Output 22
65669 | 133 | Logical Output 23 | Logical Output 23
65670 | 134 | Logical Output 24 | Logical Output 24
65671 | 135 | Logical Output 25 | Logical Output 25
65672 | 136 | Logical Output 26 | Logical Output 26
65673 | 137 | Logical Output 27 | Logical Output 27
65674 | 138 | Logical Output 28 | Logical Output 28
65675 | 139 | Logical Output 29 | Logical Output 29
65676 | 140 | Logical Output 30 | Logical Output 30
65677 | 141 | Logical Output 31 | Logical Output 31
65678 | 142 | Logical Output 32 | Logical Output 32
65679 | 143 | Logical Input 1 | Logical Input 1
65680 | 144 | Logical Input 2 | Logical Input 2
65681 | 145 | Logical Input 3 | Logical Input 3
65682 | 146 | Logical Input 4 | Logical Input 4
65683 | 147 | Logical Input 5 | Logical Input 5
65684 | 148 | Logical Input 6 | Logical Input 6
65685 | 149 | Logical Input 7 | Logical Input 7
65686 | 150 | Logical Input 8 | Logical Input 8
65687 | 151 | Logical Input 9 | Logical Input 9
65688 | 152 | Logical Input 10 | Logical Input 10
65689 | 153 | Logical Input 11 | Logical Input 11
65690 | 154 | Logical Input 12 | Logical Input 12
65691 | 155 | Logical Input 13 | Logical Input 13
65692 | 156 | Logical Input 14 | Logical Input 14
65693 | 157 | Logical Input 15 | Logical Input 15
65694 | 158 | Logical Input 16 | Logical Input 16
65695 | 159 | Logical Input 17 | Logical Input 17
65696 | 160 | Logical Input 18 | Logical Input 18
65697 | 161 | Logical Input 19 | Logical Input 19
65698 | 162 | Logical Input 20 | Logical Input 20
65699 | 163 | Logical Input 21 | Logical Input 21
65700 | 164 | Logical Input 22 | Logical Input 22
65701 | 165 | Logical Input 23 | Logical Input 23
65702 | 166 | Logical Input 24 | Logical Input 24
65703 | 167 | Logical Input 25 | Logical Input 25
65704 | 168 | Logical Input 26 | Logical Input 26
65705 | 169 | Logical Input 27 | Logical Input 27
65706 | 170 | Logical Input 28 | Logical Input 28
65707 | 171 | Logical Input 29 | Logical Input 29
65708 | 172 | Logical Input 30 | Logical Input 30
65709 | 173 | Logical Input 31 | Logical Input 31
65710 | 174 | Logical Input 32 | Logical Input 32
65711 | 175 | Object1 Open Block Input | Object1 Open Block Input
65712 | 176 | Object1 Close Block Input | Object1 Close Block Input
65713 | 177 | Object2 Open Block Input | Object2 Open Block Input
65714 | 178 | Object2 Close Block Input | Object2 Close Block Input
65715 | 179 | Object3 Open Block Input | Object3 Open Block Input
65716 | 180 | Object3 Close Block Input | Object3 Close Block Input
65717 | 181 | Object4 Open Block Input | Object4 Open Block Input
65718 | 182 | Object4 Close Block Input | Object4 Close Block Input
65719 | 183 | Object5 Open Block Input | Object5 Open Block Input
65720 | 184 | Object5 Close Block Input | Object5 Close Block Input
65721 | 185 | Object6 Open Block Input | Object6 Open Block Input
65722 | 186 | Object6 Close Block Input | Object6 Close Block Input
65723 | 187 | Object7 Open Block Input | Object7 Open Block Input
65724 | 188 | Object7 Close Block Input | Object7 Close Block Input
65725 | 189 | Object8 Open Block Input | Object8 Open Block Input
65726 | 190 | Object8 Close Block Input | Object8 Close Block Input
65727 | 191 | Object9 Open Block Input | Object9 Open Block Input
65728 | 192 | Object9 Close Block Input | Object9 Close Block Input
65729 | 193 | Object10 Open Block Input | Object10 Open Block Input
65730 | 194 | Object10 Close Block Input | Object10 Close Block Input
65731 | 195 | Idir> START | Directional overcurrent 1 pick-up
65732 | 196 | Idir> TRIP | Directional overcurrent 1 trip
65733 | 197 | Idir>> START | Directional overcurrent 2 pick-up
65734 | 198 | Idir>> TRIP | Directional overcurrent 2 trip
65735 | 199 | Idir>>> START | Directional overcurrent 3 pick-up
65736 | 200 | Idir>>> TRIP | Directional overcurrent 3 trip
65737 | 201 | Idir>>>> START | Directional overcurrent 4 pick-up
65738 | 202 | Idir>>>> TRIP | Directional overcurrent 4 trip
65739 | 203 | N>ALARM ON | Frequent start protection FSP Alarm
65740 | 204 | N> INHIBIT ON | Frequent start protection FSP Inhibit
65741 | 205 | TM> Trip | Motor thermal protection Trip
65742 | 206 | TM> Restart Inh. | Motor thermal protection Restart inhibit
65743 | 207 | ISt> START | Motor start / locked rotor monitoring LCR pick-up
65744 | 208 | ISt> Set time TRIP | Motor start / locked rotor monitoring LCR trip
65745 | 209 | Motor stopped | Motor stopped
65746 | 210 | Motor starting | Motor starting
65747 | 211 | Motor running | Motor running
65748 | 212 | Motor stalled | Motor stalled
65749 | 213 | Missing phase | Missing phase
65750 | 214 | Load Normal | Load Normal
65751 | 215 | Overloading | Overloading
65752 | 216 | High overcurrent | High overcurrent
65753 | 217 | I< START | Under current protection pick-up
65754 | 218 | I< TRIP | Under current protection trip
65755 | 219 | Im> START | Mechanical jam protection pick-up
65756 | 220 | Im> TRIP | Mechanical jam protection trip
65757 | 221 | U> START | Overvoltage 1 pick-up
65758 | 222 | U> TRIP | Overvoltage 1 trip
65759 | 223 | U>> START | Overvoltage 2 pick-up
65760 | 224 | U>>> START | Overvoltage 2 trip
65761 | 225 | U>>> TRIP | Overvoltage 3 pick-up
65762 | 226 | U>>>> START | Overvoltage 3 trip
65763 | 227 | U>>>> TRIP | Overvoltage 4 pick-up
65764 | 228 | U>> TRIP | Overvoltage 4 trip
65765 | 229 | U0> START | Residual overvoltage 1 pick-up
65766 | 230 | U0> TRIP | Residual overvoltage 1 trip
65767 | 231 | U0>> START | Residual overvoltage 2 pick-up
65768 | 232 | U0>> TRIP | Residual overvoltage 2 trip
65769 | 233 | U0>>> START | Residual overvoltage 3 pick-up
65770 | 234 | U0>>> TRIP | Residual overvoltage 3 trip
65771 | 235 | U0>>>> START | Residual overvoltage 4 pick-up
65772 | 236 | U0>>>> TRIP | Residual overvoltage 4 trip
65773 | 237 | U< START | Undervoltage 1 pick-up
65774 | 238 | U< TRIP | Undervoltage 1 trip
65775 | 239 | U<< START | Undervoltage 2 pick-up
65776 | 240 | U<< TRIP | Undervoltage 2 trip
65777 | 241 | U<<< START | Undervoltage 3 pick-up
65778 | 242 | U<<< TRIP | Undervoltage 3 trip
65779 | 243 | U<<<< START | Undervoltage 4 pick-up
65780 | 244 | U<<<< TRIP | Undervoltage 4 trip
65781 | 245 | VTS Start | Voltage transformer supervision pick-up
65782 | 246 | VTS Fail Alarm Bus | Voltage transformer supervision Fail Alarm Bus
65783 | 247 | VTS Fail Alarm Line | Voltage transformer supervision Fail Alarm Line
65784 | 248 | SOTF Active | Switch onto fault Active
65785 | 249 | SOTF Trip | Switch onto fault Trip
65786 | 250 | I0dir> START (General) | Directional residual overcurrent 1 pick-up
65787 | 251 | I0dir> TRIP (General) | Directional residual overcurrent 1 trip
65788 | 252 | I0Dir>> START (General) | Directional residual overcurrent 2 pick-up
65789 | 253 | I0Dir>> TRIP (General) | Directional residual overcurrent 2 trip
65790 | 254 | I0Dir>>> START (General) | Directional residual overcurrent 3 pick-up
65791 | 255 | I0Dir>>> TRIP (General) | Directional residual overcurrent 3 trip
65792 | 256 | I0Dir>>>> START (General) | Directional residual overcurrent 4 pick-up
65793 | 257 | I0Dir>>>> TRIP (General) | Directional residual overcurrent 4 trip
65794 | 258 | P> START | Over power protection pick-up
65795 | 259 | P> TRIP | Over power protection trip
65796 | 260 | Prev> START | Reverse power protection pick-up
65797 | 261 | Prev> TRIP | Reverse power protection trip
65798 | 262 | P< START | Under power protection pick-up
65799 | 263 | P< TRIP | Under power protection trip
65800 | 264 | f> START | Over frequency protection 1 pick-up
65801 | 265 | f> TRIP | Over frequency protection 1 trip
65802 | 266 | f>> START | Over frequency protection 2 pick-up
65803 | 267 | f>> TRIP | Over frequency protection 2 trip
65804 | 268 | f>>> START | Over frequency protection 3 pick-up
65805 | 269 | f>>> TRIP | Over frequency protection 3 trip
65806 | 270 | f>>>> START | Over frequency protection 4 pick-up
65807 | 271 | f>>>> TRIP | Over frequency protection 4 trip
65808 | 272 | f< START | Under frequency protection 1 pick-up
65809 | 273 | f< TRIP | Under frequency protection 1 trip
65810 | 274 | f<< START | Under frequency protection 2 pick-up
65811 | 275 | f<< TRIP | Under frequency protection 2 trip
65812 | 276 | f<<< START | Under frequency protection 3 pick-up
65813 | 277 | f<<< TRIP | Under frequency protection 3 trip
65814 | 278 | f<<<< START | Under frequency protection 4 pick-up
65815 | 279 | f<<<< TRIP | Under frequency protection 4 trip
65816 | 280 | I/I0 Arc> Zone1 TRIP | Arc protection Zone 1 Trip
65817 | 281 | I/I0 Arc> Zone2 TRIP | Arc protection Zone 2 Trip
65818 | 282 | I/I0 Arc> Zone3 TRIP | Arc protection Zone 3 Trip
65819 | 283 | I/I0 Arc> Zone4 TRIP | Arc protection Zone 4 Trip
65820 | 284 | PCS1 Switch Status | Programmable control switch 1 status
65821 | 285 | PCS2 Switch Status | Programmable control switch 2 status
65822 | 286 | PCS3 Switch Status | Programmable control switch 3 status
65823 | 287 | PCS4 Switch Status | Programmable control switch 4 status
65824 | 288 | PCS5 Switch Status | Programmable control switch 5 status
65825 | 289 | GOOSE IN 1 | GOOSE Input 1
65826 | 290 | GOOSE IN 2 | GOOSE Input 2
65827 | 291 | GOOSE IN 3 | GOOSE Input 3
65828 | 292 | GOOSE IN 4 | GOOSE Input 4
65829 | 293 | GOOSE IN 5 | GOOSE Input 5
65830 | 294 | GOOSE IN 6 | GOOSE Input 6
65831 | 295 | GOOSE IN 7 | GOOSE Input 7
65832 | 296 | GOOSE IN 8 | GOOSE Input 8
65833 | 297 | GOOSE IN 9 | GOOSE Input 9
65834 | 298 | GOOSE IN 10 | GOOSE Input 10
65835 | 299 | GOOSE IN 11 | GOOSE Input 11
65836 | 300 | GOOSE IN 12 | GOOSE Input 12
65837 | 301 | GOOSE IN 13 | GOOSE Input 13
65838 | 302 | GOOSE IN 14 | GOOSE Input 14
65839 | 303 | GOOSE IN 15 | GOOSE Input 15
65840 | 304 | GOOSE IN 16 | GOOSE Input 16
65841 | 305 | GOOSE IN 17 | GOOSE Input 17
65842 | 306 | GOOSE IN 18 | GOOSE Input 18
65843 | 307 | GOOSE IN 19 | GOOSE Input 19
65844 | 308 | GOOSE IN 20 | GOOSE Input 20
65845 | 309 | GOOSE IN 21 | GOOSE Input 21
65846 | 310 | GOOSE IN 22 | GOOSE Input 22
65847 | 311 | GOOSE IN 23 | GOOSE Input 23
65848 | 312 | GOOSE IN 24 | GOOSE Input 24
65849 | 313 | GOOSE IN 25 | GOOSE Input 25
65850 | 314 | GOOSE IN 26 | GOOSE Input 26
65851 | 315 | GOOSE IN 27 | GOOSE Input 27
65852 | 316 | GOOSE IN 28 | GOOSE Input 28
65853 | 317 | GOOSE IN 29 | GOOSE Input 29
65854 | 318 | GOOSE IN 30 | GOOSE Input 30
65855 | 319 | GOOSE IN 31 | GOOSE Input 31
65856 | 320 | GOOSE IN 32 | GOOSE Input 32
65857 | 321 | GOOSE IN 33 | GOOSE Input 33
65858 | 322 | GOOSE IN 34 | GOOSE Input 34
65859 | 323 | GOOSE IN 35 | GOOSE Input 35
65860 | 324 | GOOSE IN 36 | GOOSE Input 36
65861 | 325 | GOOSE IN 37 | GOOSE Input 37
65862 | 326 | GOOSE IN 38 | GOOSE Input 38
65863 | 327 | GOOSE IN 39 | GOOSE Input 39
65864 | 328 | GOOSE IN 40 | GOOSE Input 40
65865 | 329 | GOOSE IN 41 | GOOSE Input 41
65866 | 330 | GOOSE IN 42 | GOOSE Input 42
65867 | 331 | GOOSE IN 43 | GOOSE Input 43
65868 | 332 | GOOSE IN 44 | GOOSE Input 44
65869 | 333 | GOOSE IN 45 | GOOSE Input 45
65870 | 334 | GOOSE IN 46 | GOOSE Input 46
65871 | 335 | GOOSE IN 47 | GOOSE Input 47
65872 | 336 | GOOSE IN 48 | GOOSE Input 48
65873 | 337 | GOOSE IN 49 | GOOSE Input 49
65874 | 338 | GOOSE IN 50 | GOOSE Input 50
65875 | 339 | GOOSE IN 51 | GOOSE Input 51
65876 | 340 | GOOSE IN 52 | GOOSE Input 52
65877 | 341 | GOOSE IN 53 | GOOSE Input 53
65878 | 342 | GOOSE IN 54 | GOOSE Input 54
65879 | 343 | GOOSE IN 55 | GOOSE Input 55
65880 | 344 | GOOSE IN 56 | GOOSE Input 56
65881 | 345 | GOOSE IN 57 | GOOSE Input 57
65882 | 346 | GOOSE IN 58 | GOOSE Input 58
65883 | 347 | GOOSE IN 59 | GOOSE Input 59
65884 | 348 | GOOSE IN 60 | GOOSE Input 60
65885 | 349 | GOOSE IN 61 | GOOSE Input 61
65886 | 350 | GOOSE IN 62 | GOOSE Input 62
65887 | 351 | GOOSE IN 63 | GOOSE Input 63
65888 | 352 | GOOSE IN 64 | GOOSE Input 64
65889 | 353 | SYN1 Condition | Synchrocheck 1 condition
65890 | 354 | SYN2 Condition | Synchrocheck 1 condition
65891 | 355 | SYN3 Condition | Synchrocheck 1 condition
65892 | 356 | I0Int> IEF DETECTED | Intermittent eart fault detected
65893 | 357 | I0Int> TRIP | Intermittent eart fault trip
65894 | 358 | Final Trip Object1 | Final Trip Object1
65895 | 359 | Final Trip Object2 | Final Trip Object2
65896 | 360 | Final Trip Object3 | Final Trip Object3
65897 | 361 | Final Trip Object4 | Final Trip Object4
65898 | 362 | Final Trip Object5 | Final Trip Object5
65899 | 363 | Recordings in memory | Recordings in memory
65900 | 364 | Fault locator condition | Fault locator condition
65901 | 365 | AR On | Autorecloser On
65902 | 366 | U1/2 >/< START | Sequence voltage 1 pick-up
65903 | 367 | U1/2 >/< TRIP | Sequence voltage 1 trip
65904 | 368 | U1/2 >>/<< START | Sequence voltage 2 pick-up
65905 | 369 | U1/2 >>/<< TRIP | Sequence voltage 2 trip
65906 | 370 | U1/2 >>>/<<< START | Sequence voltage 3 pick-up
65907 | 371 | U1/2 >>>/<<< TRIP | Sequence voltage 3 trip
65908 | 372 | U1/2 >>>>/<<<< START | Sequence voltage 4 pick-up
65909 | 373 | U1/2 >>>>/<<<< TRIP | Sequence voltage 4 trip
65910 | 374 | PF< START | Power factor protection pick-up
65911 | 375 | PF< TRIP | Power factor protection trip
65912 | 376 | V/Hz(1) > START | Volts-per-Hz 1 pick-up
65913 | 377 | V/Hz(1) > TRIP | Volts-per-Hz 1 trip
65914 | 378 | I> (50) Alarm | E215 Overcurrent alarm
65915 | 379 | I0> (50N) Alarm | E215 Non-directional residual current alarm
65916 | 380 | Idir> (67) Alarm | E215 Directional over current Alarm
65917 | 381 | I0dir> (67N) Alarm | E215 Residual over current Alarm
65918 | 382 | I0int> (67NT) Alarm FWD | E215 Intermittent residual overcurrent forward Alarm
65919 | 383 | I0int> (67NT) Alarm REV | E215 Intermittent residual overcurrent reverse Alarm
65920 | 384 | U< (27) Alarm | E215 Undervoltage Alarm
65921 | 385 | U< (27) No voltage | E215 Undervoltage no voltage Alarm
65922 | 386 | U0> (59N) Alarm | E215 Residual overvoltage Alarm
65923 | 387 | FL (21FL) Triggered | Fault locator triggered
65924 | 388 | AR In Progress | Autorecloser in progress
65925 | 389 | Force SG change | Force setting group change
65926 | 390 | Idb> BIAS TRIP | Differential BIAS trip
65927 | 391 | ALARM 1 | ALARM 1
65928 | 392 | ALARM 2 | ALARM 2
65929 | 393 | ALARM 3 | ALARM 3
65930 | 394 | ALARM 4 | ALARM 4
65931 | 395 | ALARM 5 | ALARM 5
65932 | 396 | ALARM 6 | ALARM 6
65933 | 397 | ALARM 7 | ALARM 7
65934 | 398 | ALARM 8 | ALARM 8
65935 | 399 | ALARM 9 | ALARM 9
65936 | 400 | ALARM 10 | ALARM 10
65937 | 401 | ALARM 11 | ALARM 11
65938 | 402 | ALARM 12 | ALARM 12
65939 | 403 | ALARM 13 | ALARM 13
65940 | 404 | ALARM 14 | ALARM 14
65941 | 405 | ALARM 15 | ALARM 15
65942 | 406 | ALARM 16 | ALARM 16
65943 | 407 | ALARM 17 | ALARM 17
65944 | 408 | ALARM 18 | ALARM 18
65945 | 409 | ALARM 19 | ALARM 19
65946 | 410 | ALARM 20 | ALARM 20
65947 | 411 | ALARM 21 | ALARM 21
65948 | 412 | ALARM 22 | ALARM 22
65949 | 413 | ALARM 23 | ALARM 23
65950 | 414 | ALARM 24 | ALARM 24
65951 | 415 | ALARM 25 | ALARM 25
65952 | 416 | ALARM 26 | ALARM 26
65953 | 417 | ALARM 27 | ALARM 27
65954 | 418 | ALARM 28 | ALARM 28
65955 | 419 | ALARM 29 | ALARM 29
65956 | 420 | ALARM 30 | ALARM 30
65957 | 421 | ALARM 31 | ALARM 31
65958 | 422 | ALARM 32 | ALARM 32
65959 | 423 | ALARM 33 | ALARM 33
65960 | 424 | ALARM 34 | ALARM 34
65961 | 425 | ALARM 35 | ALARM 35
65962 | 426 | ALARM 36 | ALARM 36
65963 | 427 | ALARM 37 | ALARM 37
65964 | 428 | ALARM 38 | ALARM 38
65965 | 429 | ALARM 39 | ALARM 39
65966 | 430 | ALARM 40 | ALARM 40
65967 | 431 | ALARM 41 | ALARM 41
65968 | 432 | ALARM 42 | ALARM 42
65969 | 433 | ALARM 43 | ALARM 43
65970 | 434 | ALARM 44 | ALARM 44
65971 | 435 | ALARM 45 | ALARM 45
65972 | 436 | ALARM 46 | ALARM 46
65973 | 437 | ALARM 47 | ALARM 47
65974 | 438 | ALARM 48 | ALARM 48
65975 | 439 | ALARM 49 | ALARM 49
65976 | 440 | ALARM 50 | ALARM 50
65977 | 441 | ALARM 51 | ALARM 51
65978 | 442 | ALARM 52 | ALARM 52
65979 | 443 | ALARM 53 | ALARM 53
65980 | 444 | ALARM 54 | ALARM 54
65981 | 445 | ALARM 55 | ALARM 55
65982 | 446 | ALARM 56 | ALARM 56
65983 | 447 | ALARM 57 | ALARM 57
65984 | 448 | ALARM 58 | ALARM 58
65985 | 449 | ALARM 59 | ALARM 59
65986 | 450 | ALARM 60 | ALARM 60
65987 | 451 | ALARM 61 | ALARM 61
65988 | 452 | ALARM 62 | ALARM 62
65989 | 453 | ALARM 63 | ALARM 63
65990 | 454 | ALARM 64 | ALARM 64
65991 | 455 | Configuration changed | Configuration changed
65992 | 456 | Control mode | Tap changer control mode
65993 | 457 | U0> RECL Blocked | U0> Recloser blocked
65994 | 458 | U0> RECL Active | Residual overvoltage recloser active
65995 | 459 | U0> RECL CLOSE | Residual overvoltage recloser close
65996 | 460 | U0> RECL BLKU0 | Residual overvoltage recloser blocked
65997 | 461 | AVR Tap in highlimit | Automatic voltage regulator / tap changer highlimit
65998 | 462 | AVR Tap in lowlimit | Automatic voltage regulator / tap changer lowlimit
65999 | 463 | Idi> NOBIAS TRIP | Differential NOBIAS TRIP
66000 | 464 | Q< START | Underexcitation START
66001 | 465 | Q< TRIP | Underexcitation TRIP
66002 | 466 | TM> Alarm1 | Motor thermal overload alarm 1
66003 | 467 | TM> Alarm2 | Motor thermal overload alarm 2
66004 | 468 | GSYN Blocked
66005 | 469 | GSYN Running
66006 | 470 | GSYN Increase Voltage
66007 | 471 | GSYN Decrease Voltage
66008 | 472 | GSYN Increase Frequency
66009 | 473 | GSYN Decrease Frequency
66010 | 474 | GSYN Breaker Close Pulse
66011 | 475 | GSYN Long Sync Time
66012 | 476 | GMAG AVR Mode
66013 | 477 | GMAG FCR Mode
66014 | 478 | GMAG MVAR Mode
66015 | 479 | GMAG PF Mode
66016 | 480 | GMAG Field Breaker is closed
66017 | 481 | GMAG Excitation Off
66018 | 482 | GMAG Field Breaker is open
66019 | 483 | GMAG Synchronised
66020 | 484 | GMAG Islandmode
66021 | 485 | GMAG Test mode on
66022 | 486 | GMAG Reset On
66023 | 487 | GMAG Excitation run order
66024 | 488 | GMAG Overriding control
66025 | 489 | GMAG Increase MVar PF
66026 | 490 | GMAG Decrease MVar PF
66027 | 491 | GMAG New reference start
66028 | 492 | GMAG GB is closed
66029 | 493 | GMAG Field breaker is open Gen breaker is Closed
66030 | 494 | GMAG Following line volt
66031 | 495 | GMAG Test square enabled
66032 | 496 | GMAG Reactive power unloaded
66033 | 497 | GMAG AVR Start Ref
66034 | 498 | GMAG FCR Start Ref
66035 | 499 | GMAG Excitation On
66036 | 500 | GMAG Field current limiter active
66037 | 501 | GMAG VHZ limit active
66038 | 502 | GMAG Under excitation limiter active
66039 | 503 | GMAG Stator current limiter overexcited active
66040 | 504 | GMAG Stator current limiter underexcited active
66041 | 505 | GMAG High active current
66042 | 506 | GMAG Instantaneous field current limiter
66043 | 507 | GMAG Overcurrent
66044 | 508 | GMAG Low measured voltage
66045 | 509 | GMAG Phase retard
66046 | 510 | GMAG Field flashing
66047 | 511 | GMAG Long field flashing
66048 | 512 | GMAG Low Q Error
66049 | 513 | GMAG Field breaker does not open
66050 | 514 | GMAG Disturbed mode
66051 | 515 | GMAG Disturbed mode pulse
66052 | 516 | GMAG AVR ref on low limit
66053 | 517 | GMAG AVR ref on high limit
66054 | 518 | GMAG FCR ref on low limit
66055 | 519 | GMAG FCR ref on high limit
66056 | 520 | GMAG Mvar ref on highlimit
66057 | 521 | GMAG Mvar ref on lowlimit
66058 | 522 | GMAG PF ref on highlimit
66059 | 523 | GMAG PF ref on lowlimit
66060 | 524 | GMAG Reset and excitation off
66061 | 525 | GMAG Low supply voltage
66062 | 526 | GMAG IGBT shorted
66063 | 527 | GMAG PWM Enabled
66064 | 528 | GMAG PWM AC1 On
66065 | 529 | GMAG PWM DC1 On
66066 | 530 | GMAG Rectifier trip
66067 | 531 | GMAG Bridge1 temperature high
66068 | 532 | GMAG Bridge2 temperature high
66069 | 533 | GMAG Diode fault
66070 | 534 | GMAG Bridge 1 DI1 Signal
66071 | 535 | GMAG Bridge 1 DI2 Signal
66072 | 536 | GMAG Bridge 1 DI3 Signal
66073 | 537 | GMAG Bridge 1 DI4 Signal
66074 | 538 | GMAG Bridge 1 DI5 Signal
66075 | 539 | GMAG Bridge 1 DI6 Signal
66076 | 540 | GMAG Bridge 1 DI7 Signal
66077 | 541 | GMAG Bridge 1 DI8 Signal
66078 | 542 | IPW> START (General)
66079 | 543 | IPW> START (Phase A)
66080 | 544 | IPW> START (Phase B)
66081 | 545 | IPW> START (Phase C)
66082 | 546 | IPW> TRIP (General)
66083 | 547 | IPW> TRIP (Phase A)
66084 | 548 | IPW> TRIP (Phase B)
66085 | 549 | IPW> TRIP (Phase C)
66086 | 550 | IPW>> START (General)
66087 | 551 | IPW>> START (Phase A)
66088 | 552 | IPW>> START (Phase B)
66089 | 553 | IPW>> START (Phase C)
66090 | 554 | IPW>> TRIP (General)
66091 | 555 | IPW>> TRIP (Phase A)
66092 | 556 | IPW>> TRIP (Phase B)
66093 | 557 | IPW>> TRIP (Phase C)
66094 | 558 | DI52 | Digital input 52
66095 | 559 | DI53 | Digital input 53
66096 | 560 | DI54 | Digital input 54
66097 | 561 | DI55 | Digital input 55
66098 | 562 | DI56 | Digital input 56
66099 | 563 | DI57 | Digital input 57
66100 | 564 | DI58 | Digital input 58
66101 | 565 | DI59 | Digital input 59
66102 | 566 | DI60 | Digital input 60
66103 | 567 | DI61 | Digital input 61
66104 | 568 | DI62 | Digital input 62
66105 | 569 | DI63 | Digital input 63
66106 | 570 | DI64 | Digital input 64
66107 | 571 | DI65 | Digital input 65
66108 | 572 | DI66 | Digital input 66
66109 | 573 | DI67 | Digital input 67
66110 | 574 | DI68 | Digital input 68
66111 | 575 | DI69 | Digital input 69
66112 | 576 | DI70 | Digital input 70
66113 | 577 | DI71 | Digital input 71
66114 | 578 | DI72 | Digital input 72
66115 | 579 | DI73 | Digital input 73
66116 | 580 | DI74 | Digital input 74
66117 | 581 | DI75 | Digital input 75
66118 | 582 | DI76 | Digital input 76
66119 | 583 | DI77 | Digital input 77
66120 | 584 | DI78 | Digital input 78
66121 | 585 | DI79 | Digital input 79
66122 | 586 | DI80 | Digital input 80
66123 | 587 | DI81 | Digital input 81
66124 | 588 | DI82 | Digital input 82
66125 | 589 | DI83 | Digital input 83
66126 | 590 | DI84 | Digital input 84
66127 | 591 | DI85 | Digital input 85
66128 | 592 | DI86 | Digital input 86
66129 | 593 | DI87 | Digital input 87
66130 | 594 | DI88 | Digital input 88
66131 | 595 | DI89 | Digital input 89
66132 | 596 | DI90 | Digital input 90
66133 | 597 | DI91 | Digital input 91
66134 | 598 | DI92 | Digital input 92
66135 | 599 | DI93 | Digital input 93
66136 | 600 | DI94 | Digital input 94
66137 | 601 | DI95 | Digital input 95
66138 | 602 | DI96 | Digital input 96
66139 | 603 | DI97 | Digital input 97
66140 | 604 | DI98 | Digital input 98
66141 | 605 | DI99 | Digital input 99
66142 | 606 | DI100 | Digital input 100
66143 | 607 | DI101 | Digital input 101
66144 | 608 | DI102 | Digital input 102
66145 | 609 | DI103 | Digital input 103
66146 | 610 | DI104 | Digital input 104
66147 | 611 | DI105 | Digital input 105
66148 | 612 | DI106 | Digital input 106
66149 | 613 | DI107 | Digital input 107
66150 | 614 | DI108 | Digital input 108
66151 | 615 | DI109 | Digital input 109
66152 | 616 | DI110 | Digital input 110
66153 | 617 | DI111 | Digital input 111
66154 | 618 | DI112 | Digital input 112
66155 | 619 | DI113 | Digital input 113
66156 | 620 | DI114 | Digital input 114
66157 | 621 | DI115 | Digital input 115
66158 | 622 | Logical Output 33 | Logical Output 33
66159 | 623 | Logical Output 34 | Logical Output 34
66160 | 624 | Logical Output 35 | Logical Output 35
66161 | 625 | Logical Output 36 | Logical Output 36
66162 | 626 | Logical Output 37 | Logical Output 37
66163 | 627 | Logical Output 38 | Logical Output 38
66164 | 628 | Logical Output 39 | Logical Output 39
66165 | 629 | Logical Output 40 | Logical Output 40
66166 | 630 | Logical Output 41 | Logical Output 41
66167 | 631 | Logical Output 42 | Logical Output 42
66168 | 632 | Logical Output 43 | Logical Output 43
66169 | 633 | Logical Output 44 | Logical Output 44
66170 | 634 | Logical Output 45 | Logical Output 45
66171 | 635 | Logical Output 46 | Logical Output 46
66172 | 636 | Logical Output 47 | Logical Output 47
66173 | 637 | Logical Output 48 | Logical Output 48
66174 | 638 | Logical Output 49 | Logical Output 49
66175 | 639 | Logical Output 50 | Logical Output 50
66176 | 640 | Logical Output 51 | Logical Output 51
66177 | 641 | Logical Output 52 | Logical Output 52
66178 | 642 | Logical Output 53 | Logical Output 53
66179 | 643 | Logical Output 54 | Logical Output 54
66180 | 644 | Logical Output 55 | Logical Output 55
66181 | 645 | Logical Output 56 | Logical Output 56
66182 | 646 | Logical Output 57 | Logical Output 57
66183 | 647 | Logical Output 58 | Logical Output 58
66184 | 648 | Logical Output 59 | Logical Output 59
66185 | 649 | Logical Output 60 | Logical Output 60
66186 | 650 | Logical Output 61 | Logical Output 61
66187 | 651 | Logical Output 62 | Logical Output 62
66188 | 652 | Logical Output 63 | Logical Output 63
66189 | 653 | Logical Output 64 | Logical Output 64
Double points
IOA | IOA 2byte | Description | Name
196609 | 8193 | Object1 Breaker Status | Object1 Breaker Status
196610 | 8194 | Object2 Breaker Status | Object2 Breaker Status
196611 | 8195 | Object3 Breaker Status | Object3 Breaker Status
196612 | 8196 | Object4 Breaker Status | Object4 Breaker Status
196613 | 8197 | Object5 Breaker Status | Object5 Breaker Status
196614 | 8198 | Object6 Breaker Status | Object6 Breaker Status
196615 | 8199 | Object7 Breaker Status | Object7 Breaker Status
196616 | 8200 | Object8 Breaker Status | Object8 Breaker Status
196617 | 8201 | Object9 Breaker Status | Object9 Breaker Status
196618 | 8202 | Object10 Breaker Status | Object10 Breaker Status
196619 | 8203 | Ind.1 Object Status | Indicator 1 Object Status
196620 | 8204 | Ind.2 Object Status | Indicator 2 Object Status
196621 | 8205 | Ind.3 Object Status | Indicator 3 Object Status
196622 | 8206 | Ind.4 Object Status | Indicator 4 Object Status
196623 | 8207 | Ind.5 Object Status | Indicator 5 Object Status
196624 | 8208 | Object1 Withdraw Status | Object1 Withdraw Status
196625 | 8209 | Object2 Withdraw Status | Object2 Withdraw Status
196626 | 8210 | Object3 Withdraw Status | Object3 Withdraw Status
196627 | 8211 | Object4 Withdraw Status | Object4 Withdraw Status
196628 | 8212 | Object5 Withdraw Status | Object5 Withdraw Status
196629 | 8213 | Object6 Withdraw Status | Object6 Withdraw Status
196630 | 8214 | Object7 Withdraw Status | Object7 Withdraw Status
196631 | 8215 | Object8 Withdraw Status | Object8 Withdraw Status
196632 | 8216 | Object9 Withdraw Status | Object9 Withdraw Status
196633 | 8217 | Object10 Withdraw Status | Object10 Withdraw Status
196634 | 8218 | Ind.6 Object Status | Indicator 6 Object Status
196635 | 8219 | Ind.7 Object Status | Indicator 7 Object Status
196636 | 8220 | Ind.8 Object Status | Indicator 8 Object Status
196637 | 8221 | Ind.9 Object Status | Indicator 9 Object Status
196638 | 8222 | Ind.10 Object Status | Indicator 10 Object Status
196639 | 8223 | Ind.11 Object Status | Indicator 11 Object Status
196640 | 8224 | Ind.12 Object Status | Indicator 12 Object Status
196641 | 8225 | Ind.13 Object Status | Indicator 13 Object Status
196642 | 8226 | Ind.14 Object Status | Indicator 14 Object Status
196643 | 8227 | Ind.15 Object Status | Indicator 15 Object Status
196644 | 8228 | Ind.16 Object Status | Indicator 16 Object Status
196645 | 8229 | Ind.17 Object Status | Indicator 17 Object Status
196646 | 8230 | Ind.18 Object Status | Indicator 18 Object Status
196647 | 8231 | Ind.19 Object Status | Indicator 19 Object Status
196648 | 8232 | Ind.20 Object Status | Indicator 20 Object Status
196649 | 8233 | Phase-wise object Breaker Status A(L1) | Phase-wise object Breaker Status A(L1)
196650 | 8234 | Phase-wise object Breaker Status B(L2) | Phase-wise object Breaker Status B(L2)
196651 | 8235 | Phase-wise object Breaker Status C(L3) | Phase-wise object Breaker Status C(L3)
196652 | 8236 | Phase-wise object Withdraw Status | Phase-wise object Cart Status
Measured values
IOA | IOA 2byte | Description | Name
851969 | 16385 | Pri.Pha.curr.IL1 | Primary phase current IL1
851970 | 16386 | Pha.angle IL1 | Phase angle IL1
851971 | 16387 | Pri.Pha.curr.IL2 | Primary phase current IL2
851972 | 16388 | Pha.angle IL2 | Phase angle IL2
851973 | 16389 | Pri.Pha.curr.IL3 | Primary phase current IL3
851974 | 16390 | Pha.angle IL3 | Phase angle IL3
851975 | 16391 | Alg f avg | frequency average
851976 | 16392 | Pri.Res.curr.I01 | Primary residual current I01
851977 | 16393 | Pri.Res.curr.I02 | Primary residual current I02
851978 | 16394 | System volt UL1 mag | System voltage UL1 magnitude
851979 | 16395 | System volt UL1 ang | System voltage UL1 angle
851980 | 16396 | System volt UL2 mag | System voltage UL2 magnitude
851981 | 16397 | System volt UL2 ang | System voltage UL2 angle
851982 | 16398 | System volt UL3 mag | System voltage UL3 magnitude
851983 | 16399 | System volt UL3 ang | System voltage UL3 angle
851984 | 16400 | System volt UL12 mag | System voltage UL12 magnitude
851985 | 16401 | System volt UL12 ang | System voltage UL12 angle
851986 | 16402 | System volt UL23 mag | System voltage UL23 magnitude
851987 | 16403 | System volt UL23 ang | System voltage UL23 angle
851988 | 16404 | System volt UL31 mag | System voltage UL31 magnitude
851989 | 16405 | System volt UL31 ang | System voltage UL31 angle
851990 | 16406 | System volt U0 mag | System voltage U0 magnitude
851991 | 16407 | System volt U0 ang | System voltage U0 angle
851992 | 16408 | POW1 3PH Active power (P) | Three phase active power (P)
851993 | 16409 | POW1 3PH Reactive power (Q) | Three phase reactive power (Q)
851994 | 16410 | POW1 3PH Apparent power (S) | Three phase reactive power (S)
851995 | 16411 | POW1 3PH Cos(phi) | Three phase power cos(phi)
851996 | 16412 | Recorded fault value | Setup in menu Communication > General IO
851997 | 16413 | Recorded fault value | Setup in menu Communication > General IO
851998 | 16414 | Recorded fault value | Setup in menu Communication > General IO
851999 | 16415 | Recorded fault value | Setup in menu Communication > General IO
852000 | 16416 | Recorded fault value | Setup in menu Communication > General IO
852001 | 16417 | Recorded fault value | Setup in menu Communication > General IO
852002 | 16418 | Recorded fault value | Setup in menu Communication > General IO
852003 | 16419 | Recorded fault value | Setup in menu Communication > General IO
852004 | 16420 | Recorded fault value | Setup in menu Communication > General IO
852005 | 16421 | Recorded fault value | Setup in menu Communication > General IO
852006 | 16422 | Recorded fault value | Setup in menu Communication > General IO
852007 | 16423 | Recorded fault value | Setup in menu Communication > General IO
852008 | 16424 | Last fault reactance
852009 | 16425 | Last fault distance
852010 | 16426 | System volt U3 mag | System voltage U3 magnitude
852011 | 16427 | System volt U4 mag | System voltage U4 magnitude
852012 | 16428 | Pri.Pha.curr.I''L1 | Primary phase current I"L1
852013 | 16429 | Pha.angle I''L1 | Phase angle I"L1
852014 | 16430 | Pri.Pha.curr.I''L2 | Primary phase current I"L2
852015 | 16431 | Pha.angle I''L2 | Phase angle I"L2
852016 | 16432 | Pri.Pha.curr.I''L3 | Primary phase current I"L3
852017 | 16433 | Pha.angle I''L3 | Phase angle I"L3
852018 | 16434 | S1 Measurement | RTD&mA card sensor measurement 1
852019 | 16435 | S2 Measurement | RTD&mA card sensor measurement 2
852020 | 16436 | S3 Measurement | RTD&mA card sensor measurement 3
852021 | 16437 | S4 Measurement | RTD&mA card sensor measurement 4
852022 | 16438 | S5 Measurement | RTD&mA card sensor measurement 5
852023 | 16439 | S6 Measurement | RTD&mA card sensor measurement 6
852024 | 16440 | S7 Measurement | RTD&mA card sensor measurement 7
852025 | 16441 | S8 Measurement | RTD&mA card sensor measurement 8
852026 | 16442 | S9 Measurement | RTD&mA card sensor measurement 9
852027 | 16443 | S10 Measurement | RTD&mA card sensor measurement 10
852028 | 16444 | S11 Measurement | RTD&mA card sensor measurement 11
852029 | 16445 | S12 Measurement | RTD&mA card sensor measurement 12
852030 | 16446 | S13 Measurement | RTD&mA card sensor measurement 13
852031 | 16447 | S14 Measurement | RTD&mA card sensor measurement 14
852032 | 16448 | S15 Measurement | RTD&mA card sensor measurement 15
852033 | 16449 | S16 Measurement | RTD&mA card sensor measurement 16
852034 | 16450 | S7 Measurement mA | Sensor 7 Measurement mA
852035 | 16451 | S8 Measurement mA | Sensor 8 Measurement mA
852036 | 16452 | S15 Measurement mA | Sensor 15 Measurement mA
852037 | 16453 | S16 Measurement mA | Sensor 16 Measurement mA
852038 | 16454 | Voltage now | Voltage regulator supervised voltage now
852039 | 16455 | Voltage difference to set target | Voltage regulator voltage difference to target
852040 | 16456 | POW1 3PH Tan(phi) | 3PH Tan(phi)
852041 | 16457 | POW1 L1 Active power (P) | L1 Active power (P)
852042 | 16458 | POW1 L1 Reactive power (Q) | L1 Reactive power (Q)
852043 | 16459 | POW1 L1 Apparent power (S) | L1 Apparent power (S)
852044 | 16460 | POW1 L1 Cos(phi) | L1 Cos(phi)
852045 | 16461 | POW1 L1 Tan(phi) | L1 Tan(phi)
852046 | 16462 | POW1 L2 Active power (P) | L2 Active power (P)
852047 | 16463 | POW1 L2 Reactive power (Q) | L2 Reactive power (Q)
852048 | 16464 | POW1 L2 Apparent power (S) | L2 Apparent power (S)
852049 | 16465 | POW1 L2 Cos(phi) | L2 Cos(phi)
852050 | 16466 | POW1 L2 Tan(phi) | L2 Tan(phi)
852051 | 16467 | POW1 L3 Active power (P) | L3 Active power (P)
852052 | 16468 | POW1 L3 Reactive power (Q) | L3 Reactive power (Q)
852053 | 16469 | POW1 L3 Apparent power (S) | L3 Apparent power (S)
852054 | 16470 | POW1 L3 Cos(phi) | L3 Cos(phi)
852055 | 16471 | POW1 L3 Tan(phi) | L3 Tan(phi)
Integrated totals
IOA | IOA 2byte | Description | Name
983041 | 24577 | Internal Relay Fault status | Internal Relay Fault status
983042 | 24578 | Exp.Active Energy kWh | Exported Active Energy kWh
983043 | 24579 | Imp.Active Energy kWh | Imported Active Energy kWh
983044 | 24580 | Exp.React.Cap.E.kVarh | Exported React.Cap.E.kVarh
983045 | 24581 | Imp.React.Cap.E.kVarh | Imported React.Cap.E.kVarh
983046 | 24582 | Recordings in memory | Disturbance recordings in memory
983047 | 24583 | Max amount of recordings | Max amount of disturbance recordings
983048 | 24584 | Active setting group | Active setting group
983049 | 24585 | Tap location now (- 0 +) | Voltage regulator tap location now (- 0 +)
983050 | 24586 | Absolute tap location | Voltage regulator absolute tap location
983051 | 24587 | DI1 Counter | Digital input 1 Counter
983052 | 24588 | DI2 Counter | Digital input 2 Counter
983053 | 24589 | DI3 Counter | Digital input 3 Counter
983054 | 24590 | DI4 Counter | Digital input 4 Counter
983055 | 24591 | DI5 Counter | Digital input 5 Counter
983056 | 24592 | DI6 Counter | Digital input 6 Counter
983057 | 24593 | DI7 Counter | Digital input 7 Counter
983058 | 24594 | DI8 Counter | Digital input 8 Counter
983059 | 24595 | DI9 Counter | Digital input 9 Counter
983060 | 24596 | DI10 Counter | Digital input 10 Counter
983061 | 24597 | DI11 Counter | Digital input 11 Counter
983062 | 24598 | DI12 Counter | Digital input 12 Counter
983063 | 24599 | DI13 Counter | Digital input 13 Counter
983064 | 24600 | DI14 Counter | Digital input 14 Counter
983065 | 24601 | DI15 Counter | Digital input 15 Counter
983066 | 24602 | DI16 Counter | Digital input 16 Counter
983067 | 24603 | DI17 Counter | Digital input 17 Counter
983068 | 24604 | DI18 Counter | Digital input 18 Counter
983069 | 24605 | DI19 Counter | Digital input 19 Counter
983070 | 24606 | DI20 Counter | Digital input 20 Counter
983071 | 24607 | DI21 Counter | Digital input 21 Counter
983072 | 24608 | DI22 Counter | Digital input 22 Counter
983073 | 24609 | DI23 Counter | Digital input 23 Counter
983074 | 24610 | DI24 Counter | Digital input 24 Counter
983075 | 24611 | DI25 Counter | Digital input 25 Counter
983076 | 24612 | DI26 Counter | Digital input 26 Counter
983077 | 24613 | DI27 Counter | Digital input 27 Counter
983078 | 24614 | DI28 Counter | Digital input 28 Counter
983079 | 24615 | DI29 Counter | Digital input 29 Counter
983080 | 24616 | DI30 Counter | Digital input 30 Counter
983081 | 24617 | DI31 Counter | Digital input 31 Counter
983082 | 24618 | DI32 Counter | Digital input 32 Counter
983083 | 24619 | DI33 Counter | Digital input 33 Counter
983084 | 24620 | DI34 Counter | Digital input 34 Counter
983085 | 24621 | DI35 Counter | Digital input 35 Counter
983086 | 24622 | DI36 Counter | Digital input 36 Counter
983087 | 24623 | DI37 Counter | Digital input 37 Counter
983088 | 24624 | DI38 Counter | Digital input 38 Counter
983089 | 24625 | DI39 Counter | Digital input 39 Counter
983090 | 24626 | DI40 Counter | Digital input 40 Counter
983091 | 24627 | DI41 Counter | Digital input 41 Counter
983092 | 24628 | DI42 Counter | Digital input 42 Counter
983093 | 24629 | DI43 Counter | Digital input 43 Counter
983094 | 24630 | DI44 Counter | Digital input 44 Counter
983095 | 24631 | DI45 Counter | Digital input 45 Counter
983096 | 24632 | DI46 Counter | Digital input 46 Counter
983097 | 24633 | DI47 Counter | Digital input 47 Counter
983098 | 24634 | DI48 Counter | Digital input 48 Counter
983099 | 24635 | DI49 Counter | Digital input 49 Counter
983100 | 24636 | DI50 Counter | Digital input 50 Counter
983101 | 24637 | DI51 Counter | Digital input 51 Counter
Single commands
IOA | IOA 2byte | Description | Name
2949121 | 32769 | Reset Latches | Reset Latches
2949122 | 32770 | Logical Input 1 | Logical Input 1
2949123 | 32771 | Logical Input 2 | Logical Input 2
2949124 | 32772 | Logical Input 3 | Logical Input 3
2949125 | 32773 | Logical Input 4 | Logical Input 4
2949126 | 32774 | Logical Input 5 | Logical Input 5
2949127 | 32775 | Logical Input 6 | Logical Input 6
2949128 | 32776 | Logical Input 7 | Logical Input 7
2949129 | 32777 | Logical Input 8 | Logical Input 8
2949130 | 32778 | Logical Input 9 | Logical Input 9
2949131 | 32779 | Logical Input 10 | Logical Input 10
2949132 | 32780 | Logical Input 11 | Logical Input 11
2949133 | 32781 | Logical Input 12 | Logical Input 12
2949134 | 32782 | Logical Input 13 | Logical Input 13
2949135 | 32783 | Logical Input 14 | Logical Input 14
2949136 | 32784 | Logical Input 15 | Logical Input 15
2949137 | 32785 | Logical Input 16 | Logical Input 16
2949138 | 32786 | Logical Input 17 | Logical Input 17
2949139 | 32787 | Logical Input 18 | Logical Input 18
2949140 | 32788 | Logical Input 19 | Logical Input 19
2949141 | 32789 | Logical Input 20 | Logical Input 20
2949142 | 32790 | Logical Input 21 | Logical Input 21
2949143 | 32791 | Logical Input 22 | Logical Input 22
2949144 | 32792 | Logical Input 23 | Logical Input 23
2949145 | 32793 | Logical Input 24 | Logical Input 24
2949146 | 32794 | Logical Input 25 | Logical Input 25
2949147 | 32795 | Logical Input 26 | Logical Input 26
2949148 | 32796 | Logical Input 27 | Logical Input 27
2949149 | 32797 | Logical Input 28 | Logical Input 28
2949150 | 32798 | Logical Input 29 | Logical Input 29
2949151 | 32799 | Logical Input 30 | Logical Input 30
2949152 | 32800 | Logical Input 31 | Logical Input 31
2949153 | 32801 | Logical Input 32 | Logical Input 32
2949154 | 32802 | PCS1 Switch Status | Programmable control switch 1 status
2949155 | 32803 | PCS2 Switch Status | Programmable control switch 2 status
2949156 | 32804 | PCS3 Switch Status | Programmable control switch 3 status
2949157 | 32805 | PCS4 Switch Status | Programmable control switch 4 status
2949158 | 32806 | PCS5 Switch Status | Programmable control switch 5 status
2949159 | 32807 | AVR to Manual control | Automatic voltage regulator to manual control
Double commands
IOA | IOA 2byte | Description | Name
3014657 | 40961 | OBJECT1 CTRL | OBJECT1 Control
3014658 | 40962 | OBJECT2 CTRL | OBJECT2 Control
3014659 | 40963 | OBJECT3 CTRL | OBJECT3 Control
3014660 | 40964 | OBJECT4 CTRL | OBJECT4 Control
3014661 | 40965 | OBJECT5 CTRL | OBJECT5 Control
3014662 | 40966 | OBJECT6 CTRL | OBJECT6 Control
3014663 | 40967 | OBJECT7 CTRL | OBJECT7 Control
3014664 | 40968 | OBJECT8 CTRL | OBJECT8 Control
3014665 | 40969 | OBJECT9 CTRL | OBJECT9 Control
3014666 | 40970 | OBJECT10 CTRL | OBJECT10 Control
3014667 | 40971 | OBJECT S1 CTRL | Phase wise OBJECT Control