## AQ-250 v2.5.7.1-245
AQ-200 IED EVENT CODES AND SPA EVENTS
v2.5.7.1-245-g19016ef-AP1
NOTE: THIS MAP CAN BE DIFFERENT FROM THE ONE USED BY YOUR DEVICE! TO MAKE SURE YOU HAVE A MAP THAT MATCHES WITH YOUR DEVICE, GET IT FROM THE AQS CONFIGURATION FILE (TOOLS -> EVENTS AND LOGS -> EVENT LIST
Event Code | Block Description | Function | Event Description | SPA Event
1 | SYSTEM |  | Power on | 0E1
2 | SYSTEM |  | RTC change | 0E2
3 | SYSTEM |  | RTC time incorrect | 0E3
4 | SYSTEM |  | NTP time sync aquired | 0E4
5 | SYSTEM |  | NTP time change | 0E5
6 | SYSTEM |  | NTP time sync lost | 0E6
7 | SYSTEM |  | Measuring system suspended | 0E7
8 | SYSTEM |  | Measuring system activated | 0E8
9 | SYSTEM |  | Unknown event | 0E9
26 | SYSTEM |  | Sync input On | 0E26
27 | SYSTEM |  | Protection subsystem reset | 0E50
28 | SYSTEM |  | Storage reinitialized - no contents | 0E28
29 | SYSTEM |  | Storage reinitialized - new firmware detected | 0E29
30 | SYSTEM |  | Event buffer clear marker | 0E30
31 | SYSTEM |  | Event buffer initialized | 0E31
32 | SYSTEM |  | DblEth LinkA down | 0E32
33 | SYSTEM |  | DblEth LinkA OK | 0E33
34 | SYSTEM |  | DblEth LinkB down | 0E34
35 | SYSTEM |  | DblEth LinkB OK | 0E35
36 | SYSTEM |  | User access control HMI open | 0E36
37 | SYSTEM |  | User access control HMI close | 0E37
38 | SYSTEM |  | User access control settingtool open | 0E38
39 | SYSTEM |  | User access control settingtool close | 0E39
40 | SYSTEM |  | Event overload ON | 0E40
41 | SYSTEM |  | Event overload OFF | 0E41
42 | SYSTEM |  | Multi Level Control (61850) On | 0E42
43 | SYSTEM |  | Multi Level Control (61850) Off | 0E43
44 | SYSTEM |  | Latches reset | 0E44
64 | DIAGNOSTICS |  | Diagnostic Alarm ON | 1E0
65 | DIAGNOSTICS |  | Diagnostic Alarm OFF | 1E1
66 | DIAGNOSTICS |  | Configuration changed | 1E2
67 | DIAGNOSTICS |  | Configuration changed clear | 1E3
68 | DIAGNOSTICS |  | Network overload detected On | 1E4
69 | DIAGNOSTICS |  | Network overload detected Off | 1E5
70 | DIAGNOSTICS |  | Network loop detected On | 1E6
71 | DIAGNOSTICS |  | Network loop detected Off | 1E7
128 | IRF | Self supervision | Internal Relay Fault Activated | 2E0
129 | IRF | Self supervision | Internal Relay Fault Deactivated | 2E1
192 | GNSIG |  | Common Start On | 3E0
193 | GNSIG |  | Common Start Off | 3E1
194 | GNSIG |  | Common Trip On | 3E2
195 | GNSIG |  | Common Trip Off | 3E3
384 | PCS | Programmable control switch | Switch1 On | 6E0
385 | PCS | Programmable control switch | Switch1 Off | 6E1
386 | PCS | Programmable control switch | Switch2 On | 6E2
387 | PCS | Programmable control switch | Switch2 Off | 6E3
388 | PCS | Programmable control switch | Switch3 On | 6E4
389 | PCS | Programmable control switch | Switch3 Off | 6E5
390 | PCS | Programmable control switch | Switch4 On | 6E6
391 | PCS | Programmable control switch | Switch4 Off | 6E7
392 | PCS | Programmable control switch | Switch5 On | 6E8
393 | PCS | Programmable control switch | Switch5 Off | 6E9
448 | CTRL | Device in REMOTE mode | Ctrl state REMOTE | 7E0
449 | CTRL | Device in LOCAL mode | Ctrl state LOCAL | 7E1
450 | CTRL |  | Ctrl Authority REMOTE | 7E2
451 | CTRL |  | Ctrl Authority STATION | 7E3
512 | LOGIC1 | Logical outputs | Logical Out1 On (Logical Output 1) | 8E0
513 | LOGIC1 | Logical outputs | Logical Out1 Off (Logical Output 1) | 8E1
514 | LOGIC1 | Logical outputs | Logical Out2 On (Logical Output 2) | 8E2
515 | LOGIC1 | Logical outputs | Logical Out2 Off (Logical Output 2) | 8E3
516 | LOGIC1 | Logical outputs | Logical Out3 On (Logical Output 3) | 8E4
517 | LOGIC1 | Logical outputs | Logical Out3 Off (Logical Output 3) | 8E5
518 | LOGIC1 | Logical outputs | Logical Out4 On (Logical Output 4) | 8E6
519 | LOGIC1 | Logical outputs | Logical Out4 Off (Logical Output 4) | 8E7
520 | LOGIC1 | Logical outputs | Logical Out5 On (Logical Output 5) | 8E8
521 | LOGIC1 | Logical outputs | Logical Out5 Off (Logical Output 5) | 8E9
522 | LOGIC1 | Logical outputs | Logical Out6 On (Logical Output 6) | 8E10
523 | LOGIC1 | Logical outputs | Logical Out6 Off (Logical Output 6) | 8E11
524 | LOGIC1 | Logical outputs | Logical Out7 On (Logical Output 7) | 8E12
525 | LOGIC1 | Logical outputs | Logical Out7 Off (Logical Output 7) | 8E13
526 | LOGIC1 | Logical outputs | Logical Out8 On (Logical Output 8) | 8E14
527 | LOGIC1 | Logical outputs | Logical Out8 Off (Logical Output 8) | 8E15
528 | LOGIC1 | Logical outputs | Logical Out9 On (Logical Output 9) | 8E16
529 | LOGIC1 | Logical outputs | Logical Out9 Off (Logical Output 9) | 8E17
530 | LOGIC1 | Logical outputs | Logical Out10 On (Logical Output 10) | 8E18
531 | LOGIC1 | Logical outputs | Logical Out10 Off (Logical Output 10) | 8E19
532 | LOGIC1 | Logical outputs | Logical Out11 On (Logical Output 11) | 8E20
533 | LOGIC1 | Logical outputs | Logical Out11 Off (Logical Output 11) | 8E21
534 | LOGIC1 | Logical outputs | Logical Out12 On (Logical Output 12) | 8E22
535 | LOGIC1 | Logical outputs | Logical Out12 Off (Logical Output 12) | 8E23
536 | LOGIC1 | Logical outputs | Logical Out13 On (Logical Output 13) | 8E24
537 | LOGIC1 | Logical outputs | Logical Out13 Off (Logical Output 13) | 8E25
538 | LOGIC1 | Logical outputs | Logical Out14 On (Logical Output 14) | 8E26
539 | LOGIC1 | Logical outputs | Logical Out14 Off (Logical Output 14) | 8E27
540 | LOGIC1 | Logical outputs | Logical Out15 On (Logical Output 15) | 8E28
541 | LOGIC1 | Logical outputs | Logical Out15 Off (Logical Output 15) | 8E29
542 | LOGIC1 | Logical outputs | Logical Out16 On (Logical Output 16) | 8E30
543 | LOGIC1 | Logical outputs | Logical Out16 Off (Logical Output 16) | 8E31
544 | LOGIC1 | Logical outputs | Logical Out17 On (Logical Output 17) | 8E32
545 | LOGIC1 | Logical outputs | Logical Out17 Off (Logical Output 17) | 8E33
546 | LOGIC1 | Logical outputs | Logical Out18 On (Logical Output 18) | 8E34
547 | LOGIC1 | Logical outputs | Logical Out18 Off (Logical Output 18) | 8E35
548 | LOGIC1 | Logical outputs | Logical Out19 On (Logical Output 19) | 8E36
549 | LOGIC1 | Logical outputs | Logical Out19 Off (Logical Output 19) | 8E37
550 | LOGIC1 | Logical outputs | Logical Out20 On (Logical Output 20) | 8E38
551 | LOGIC1 | Logical outputs | Logical Out20 Off (Logical Output 20) | 8E39
552 | LOGIC1 | Logical outputs | Logical Out21 On (Logical Output 21) | 8E40
553 | LOGIC1 | Logical outputs | Logical Out21 Off (Logical Output 21) | 8E41
554 | LOGIC1 | Logical outputs | Logical Out22 On (Logical Output 22) | 8E42
555 | LOGIC1 | Logical outputs | Logical Out22 Off (Logical Output 22) | 8E43
556 | LOGIC1 | Logical outputs | Logical Out23 On (Logical Output 23) | 8E44
557 | LOGIC1 | Logical outputs | Logical Out23 Off (Logical Output 23) | 8E45
558 | LOGIC1 | Logical outputs | Logical Out24 On (Logical Output 24) | 8E46
559 | LOGIC1 | Logical outputs | Logical Out24 Off (Logical Output 24) | 8E47
560 | LOGIC1 | Logical outputs | Logical Out25 On (Logical Output 25) | 8E48
561 | LOGIC1 | Logical outputs | Logical Out25 Off (Logical Output 25) | 8E49
562 | LOGIC1 | Logical outputs | Logical Out26 On (Logical Output 26) | 8E50
563 | LOGIC1 | Logical outputs | Logical Out26 Off (Logical Output 26) | 8E51
564 | LOGIC1 | Logical outputs | Logical Out27 On (Logical Output 27) | 8E52
565 | LOGIC1 | Logical outputs | Logical Out27 Off (Logical Output 27) | 8E53
566 | LOGIC1 | Logical outputs | Logical Out28 On (Logical Output 28) | 8E54
567 | LOGIC1 | Logical outputs | Logical Out28 Off (Logical Output 28) | 8E55
568 | LOGIC1 | Logical outputs | Logical Out29 On (Logical Output 29) | 8E56
569 | LOGIC1 | Logical outputs | Logical Out29 Off (Logical Output 29) | 8E57
570 | LOGIC1 | Logical outputs | Logical Out30 On (Logical Output 30) | 8E58
571 | LOGIC1 | Logical outputs | Logical Out30 Off (Logical Output 30) | 8E59
572 | LOGIC1 | Logical outputs | Logical Out31 On (Logical Output 31) | 8E60
573 | LOGIC1 | Logical outputs | Logical Out31 Off (Logical Output 31) | 8E61
574 | LOGIC1 | Logical outputs | Logical Out32 On (Logical Output 32) | 8E62
575 | LOGIC1 | Logical outputs | Logical Out32 Off (Logical Output 32) | 8E63
576 | LOGIC2 | Logical inputs | Logical In1 On (Logical Input 1) | 9E0
577 | LOGIC2 | Logical inputs | Logical In1 Off (Logical Input 1) | 9E1
578 | LOGIC2 | Logical inputs | Logical In2 On (Logical Input 2) | 9E2
579 | LOGIC2 | Logical inputs | Logical In2 Off (Logical Input 2) | 9E3
580 | LOGIC2 | Logical inputs | Logical In3 On (Logical Input 3) | 9E4
581 | LOGIC2 | Logical inputs | Logical In3 Off (Logical Input 3) | 9E5
582 | LOGIC2 | Logical inputs | Logical In4 On (Logical Input 4) | 9E6
583 | LOGIC2 | Logical inputs | Logical In4 Off (Logical Input 4) | 9E7
584 | LOGIC2 | Logical inputs | Logical In5 On (Logical Input 5) | 9E8
585 | LOGIC2 | Logical inputs | Logical In5 Off (Logical Input 5) | 9E9
586 | LOGIC2 | Logical inputs | Logical In6 On (Logical Input 6) | 9E10
587 | LOGIC2 | Logical inputs | Logical In6 Off (Logical Input 6) | 9E11
588 | LOGIC2 | Logical inputs | Logical In7 On (Logical Input 7) | 9E12
589 | LOGIC2 | Logical inputs | Logical In7 Off (Logical Input 7) | 9E13
590 | LOGIC2 | Logical inputs | Logical In8 On (Logical Input 8) | 9E14
591 | LOGIC2 | Logical inputs | Logical In8 Off (Logical Input 8) | 9E15
592 | LOGIC2 | Logical inputs | Logical In9 On (Logical Input 9) | 9E16
593 | LOGIC2 | Logical inputs | Logical In9 Off (Logical Input 9) | 9E17
594 | LOGIC2 | Logical inputs | Logical In10 On (Logical Input 10) | 9E18
595 | LOGIC2 | Logical inputs | Logical In10 Off (Logical Input 10) | 9E19
596 | LOGIC2 | Logical inputs | Logical In11 On (Logical Input 11) | 9E20
597 | LOGIC2 | Logical inputs | Logical In11 Off (Logical Input 11) | 9E21
598 | LOGIC2 | Logical inputs | Logical In12 On (Logical Input 12) | 9E22
599 | LOGIC2 | Logical inputs | Logical In12 Off (Logical Input 12) | 9E23
600 | LOGIC2 | Logical inputs | Logical In13 On (Logical Input 13) | 9E24
601 | LOGIC2 | Logical inputs | Logical In13 Off (Logical Input 13) | 9E25
602 | LOGIC2 | Logical inputs | Logical In14 On (Logical Input 14) | 9E26
603 | LOGIC2 | Logical inputs | Logical In14 Off (Logical Input 14) | 9E27
604 | LOGIC2 | Logical inputs | Logical In15 On (Logical Input 15) | 9E28
605 | LOGIC2 | Logical inputs | Logical In15 Off (Logical Input 15) | 9E29
606 | LOGIC2 | Logical inputs | Logical In16 On (Logical Input 16) | 9E30
607 | LOGIC2 | Logical inputs | Logical In16 Off (Logical Input 16) | 9E31
608 | LOGIC2 | Logical inputs | Logical In17 On (Logical Input 17) | 9E32
609 | LOGIC2 | Logical inputs | Logical In17 Off (Logical Input 17) | 9E33
610 | LOGIC2 | Logical inputs | Logical In18 On (Logical Input 18) | 9E34
611 | LOGIC2 | Logical inputs | Logical In18 Off (Logical Input 18) | 9E35
612 | LOGIC2 | Logical inputs | Logical In19 On (Logical Input 19) | 9E36
613 | LOGIC2 | Logical inputs | Logical In19 Off (Logical Input 19) | 9E37
614 | LOGIC2 | Logical inputs | Logical In20 On (Logical Input 20) | 9E38
615 | LOGIC2 | Logical inputs | Logical In20 Off (Logical Input 20) | 9E39
616 | LOGIC2 | Logical inputs | Logical In21 On (Logical Input 21) | 9E40
617 | LOGIC2 | Logical inputs | Logical In21 Off (Logical Input 21) | 9E41
618 | LOGIC2 | Logical inputs | Logical In22 On (Logical Input 22) | 9E42
619 | LOGIC2 | Logical inputs | Logical In22 Off (Logical Input 22) | 9E43
620 | LOGIC2 | Logical inputs | Logical In23 On (Logical Input 23) | 9E44
621 | LOGIC2 | Logical inputs | Logical In23 Off (Logical Input 23) | 9E45
622 | LOGIC2 | Logical inputs | Logical In24 On (Logical Input 24) | 9E46
623 | LOGIC2 | Logical inputs | Logical In24 Off (Logical Input 24) | 9E47
624 | LOGIC2 | Logical inputs | Logical In25 On (Logical Input 25) | 9E48
625 | LOGIC2 | Logical inputs | Logical In25 Off (Logical Input 25) | 9E49
626 | LOGIC2 | Logical inputs | Logical In26 On (Logical Input 26) | 9E50
627 | LOGIC2 | Logical inputs | Logical In26 Off (Logical Input 26) | 9E51
628 | LOGIC2 | Logical inputs | Logical In27 On (Logical Input 27) | 9E52
629 | LOGIC2 | Logical inputs | Logical In27 Off (Logical Input 27) | 9E53
630 | LOGIC2 | Logical inputs | Logical In28 On (Logical Input 28) | 9E54
631 | LOGIC2 | Logical inputs | Logical In28 Off (Logical Input 28) | 9E55
632 | LOGIC2 | Logical inputs | Logical In29 On (Logical Input 29) | 9E56
633 | LOGIC2 | Logical inputs | Logical In29 Off (Logical Input 29) | 9E57
634 | LOGIC2 | Logical inputs | Logical In30 On (Logical Input 30) | 9E58
635 | LOGIC2 | Logical inputs | Logical In30 Off (Logical Input 30) | 9E59
636 | LOGIC2 | Logical inputs | Logical In31 On (Logical Input 31) | 9E60
637 | LOGIC2 | Logical inputs | Logical In31 Off (Logical Input 31) | 9E61
638 | LOGIC2 | Logical inputs | Logical In32 On (Logical Input 32) | 9E62
639 | LOGIC2 | Logical inputs | Logical In32 Off (Logical Input 32) | 9E63
640 | DIGI | Digital inputs | DI 1 On (DI1) | 10E0
641 | DIGI | Digital inputs | DI 1 Off (DI1) | 10E1
642 | DIGI | Digital inputs | DI 2 On (DI2) | 10E2
643 | DIGI | Digital inputs | DI 2 Off (DI2) | 10E3
644 | DIGI | Digital inputs | DI 3 On (DI3) | 10E4
645 | DIGI | Digital inputs | DI 3 Off (DI3) | 10E5
646 | DIGI | Digital inputs | DI 4 On (DI4) | 10E6
647 | DIGI | Digital inputs | DI 4 Off (DI4) | 10E7
648 | DIGI | Digital inputs | DI 5 On (DI5) | 10E8
649 | DIGI | Digital inputs | DI 5 Off (DI5) | 10E9
650 | DIGI | Digital inputs | DI 6 On (DI6) | 10E10
651 | DIGI | Digital inputs | DI 6 Off (DI6) | 10E11
652 | DIGI | Digital inputs | DI 7 On (DI7) | 10E12
653 | DIGI | Digital inputs | DI 7 Off (DI7) | 10E13
654 | DIGI | Digital inputs | DI 8 On (DI8) | 10E14
655 | DIGI | Digital inputs | DI 8 Off (DI8) | 10E15
656 | DIGI | Digital inputs | DI 9 On (DI9) | 10E16
657 | DIGI | Digital inputs | DI 9 Off (DI9) | 10E17
658 | DIGI | Digital inputs | DI 10 On (DI10) | 10E18
659 | DIGI | Digital inputs | DI 10 Off (DI10) | 10E19
660 | DIGI | Digital inputs | DI 11 On (DI11) | 10E20
661 | DIGI | Digital inputs | DI 11 Off (DI11) | 10E21
662 | DIGI | Digital inputs | DI 12 On (DI12) | 10E22
663 | DIGI | Digital inputs | DI 12 Off (DI12) | 10E23
664 | DIGI | Digital inputs | DI 13 On (DI13) | 10E24
665 | DIGI | Digital inputs | DI 13 Off (DI13) | 10E25
666 | DIGI | Digital inputs | DI 14 On (DI14) | 10E26
667 | DIGI | Digital inputs | DI 14 Off (DI14) | 10E27
668 | DIGI | Digital inputs | DI 15 On (DI15) | 10E28
669 | DIGI | Digital inputs | DI 15 Off (DI15) | 10E29
670 | DIGI | Digital inputs | DI 16 On (DI16) | 10E30
671 | DIGI | Digital inputs | DI 16 Off (DI16) | 10E31
672 | DIGI | Digital inputs | DI 17 On (DI17) | 10E32
673 | DIGI | Digital inputs | DI 17 Off (DI17) | 10E33
674 | DIGI | Digital inputs | DI 18 On (DI18) | 10E34
675 | DIGI | Digital inputs | DI 18 Off (DI18) | 10E35
676 | DIGI | Digital inputs | DI 19 On (DI19) | 10E36
677 | DIGI | Digital inputs | DI 19 Off (DI19) | 10E37
678 | DIGI | Digital inputs | DI 20 On (DI20) | 10E38
679 | DIGI | Digital inputs | DI 20 Off (DI20) | 10E39
680 | DIGI | Digital inputs | DI 21 On (DI21) | 10E40
681 | DIGI | Digital inputs | DI 21 Off (DI21) | 10E41
682 | DIGI | Digital inputs | DI 22 On (DI22) | 10E42
683 | DIGI | Digital inputs | DI 22 Off (DI22) | 10E43
684 | DIGI | Digital inputs | DI 23 On (DI23) | 10E44
685 | DIGI | Digital inputs | DI 23 Off (DI23) | 10E45
686 | DIGI | Digital inputs | DI 24 On (DI24) | 10E46
687 | DIGI | Digital inputs | DI 24 Off (DI24) | 10E47
688 | DIGI | Digital inputs | DI 25 On (DI25) | 10E48
689 | DIGI | Digital inputs | DI 25 Off (DI25) | 10E49
690 | DIGI | Digital inputs | DI 26 On (DI26) | 10E50
691 | DIGI | Digital inputs | DI 26 Off (DI26) | 10E51
692 | DIGI | Digital inputs | DI 27 On (DI27) | 10E52
693 | DIGI | Digital inputs | DI 27 Off (DI27) | 10E53
694 | DIGI | Digital inputs | DI 28 On (DI28) | 10E54
695 | DIGI | Digital inputs | DI 28 Off (DI28) | 10E55
696 | DIGI | Digital inputs | DI 29 On (DI29) | 10E56
697 | DIGI | Digital inputs | DI 29 Off (DI29) | 10E57
698 | DIGI | Digital inputs | DI 30 On (DI30) | 10E58
699 | DIGI | Digital inputs | DI 30 Off (DI30) | 10E59
700 | DIGI | Digital inputs | DI 31 On (DI31) | 10E60
701 | DIGI | Digital inputs | DI 31 Off (DI31) | 10E61
702 | DIGI | Digital inputs | DI 32 On (DI32) | 10E62
703 | DIGI | Digital inputs | DI 32 Off (DI32) | 10E63
704 | DIGI2 | Digital inputs | DI33 On (DI33) | 11E0
705 | DIGI2 | Digital inputs | DI33 Off (DI33) | 11E1
706 | DIGI2 | Digital inputs | DI34 On (DI34) | 11E2
707 | DIGI2 | Digital inputs | DI34 Off (DI34) | 11E3
708 | DIGI2 | Digital inputs | DI35 On (DI35) | 11E4
709 | DIGI2 | Digital inputs | DI35 Off (DI35) | 11E5
710 | DIGI2 | Digital inputs | DI36 On (DI36) | 11E6
711 | DIGI2 | Digital inputs | DI36 Off (DI36) | 11E7
712 | DIGI2 | Digital inputs | DI37 On (DI37) | 11E8
713 | DIGI2 | Digital inputs | DI37 Off (DI37) | 11E9
714 | DIGI2 | Digital inputs | DI38 On (DI38) | 11E10
715 | DIGI2 | Digital inputs | DI38 Off (DI38) | 11E11
716 | DIGI2 | Digital inputs | DI39 On (DI39) | 11E12
717 | DIGI2 | Digital inputs | DI39 Off (DI39) | 11E13
718 | DIGI2 | Digital inputs | DI40 On (DI40) | 11E14
719 | DIGI2 | Digital inputs | DI40 Off (DI40) | 11E15
720 | DIGI2 | Digital inputs | DI41 On (DI41) | 11E16
721 | DIGI2 | Digital inputs | DI41 Off (DI41) | 11E17
722 | DIGI2 | Digital inputs | DI42 On (DI42) | 11E18
723 | DIGI2 | Digital inputs | DI42 Off (DI42) | 11E19
724 | DIGI2 | Digital inputs | DI43 On (DI43) | 11E20
725 | DIGI2 | Digital inputs | DI43 Off (DI43) | 11E21
726 | DIGI2 | Digital inputs | DI44 On (DI44) | 11E22
727 | DIGI2 | Digital inputs | DI44 Off (DI44) | 11E23
728 | DIGI2 | Digital inputs | DI45 On (DI45) | 11E24
729 | DIGI2 | Digital inputs | DI45 Off (DI45) | 11E25
730 | DIGI2 | Digital inputs | DI46 On (DI46) | 11E26
731 | DIGI2 | Digital inputs | DI46 Off (DI46) | 11E27
732 | DIGI2 | Digital inputs | DI47 On (DI47) | 11E28
733 | DIGI2 | Digital inputs | DI47 Off (DI47) | 11E29
734 | DIGI2 | Digital inputs | DI48 On (DI48) | 11E30
735 | DIGI2 | Digital inputs | DI48 Off (DI48) | 11E31
736 | DIGI2 | Digital inputs | DI49 On (DI49) | 11E32
737 | DIGI2 | Digital inputs | DI49 Off (DI49) | 11E33
738 | DIGI2 | Digital inputs | DI50 On (DI50) | 11E34
739 | DIGI2 | Digital inputs | DI50 Off (DI50) | 11E35
740 | DIGI2 | Digital inputs | DI51 On (DI51) | 11E36
741 | DIGI2 | Digital inputs | DI51 Off (DI51) | 11E37
768 | DIGI3 | Digital inputs | DI 52 On (DI52) | 12E0
769 | DIGI3 | Digital inputs | DI 52 Off (DI52) | 12E1
770 | DIGI3 | Digital inputs | DI 53 On (DI53) | 12E2
771 | DIGI3 | Digital inputs | DI 53 Off (DI53) | 12E3
772 | DIGI3 | Digital inputs | DI 54 On (DI54) | 12E4
773 | DIGI3 | Digital inputs | DI 54 Off (DI54) | 12E5
774 | DIGI3 | Digital inputs | DI 55 On (DI55) | 12E6
775 | DIGI3 | Digital inputs | DI 55 Off (DI55) | 12E7
776 | DIGI3 | Digital inputs | DI 56 On (DI56) | 12E8
777 | DIGI3 | Digital inputs | DI 56 Off (DI56) | 12E9
778 | DIGI3 | Digital inputs | DI 57 On (DI57) | 12E10
779 | DIGI3 | Digital inputs | DI 57 Off (DI57) | 12E11
780 | DIGI3 | Digital inputs | DI 58 On (DI58) | 12E12
781 | DIGI3 | Digital inputs | DI 58 Off (DI58) | 12E13
782 | DIGI3 | Digital inputs | DI 59 On (DI59) | 12E14
783 | DIGI3 | Digital inputs | DI 59 Off (DI59) | 12E15
784 | DIGI3 | Digital inputs | DI 60 On (DI60) | 12E16
785 | DIGI3 | Digital inputs | DI 60 Off (DI60) | 12E17
786 | DIGI3 | Digital inputs | DI 61 On (DI61) | 12E18
787 | DIGI3 | Digital inputs | DI 61 Off (DI61) | 12E19
788 | DIGI3 | Digital inputs | DI 62 On (DI62) | 12E20
789 | DIGI3 | Digital inputs | DI 62 Off (DI62) | 12E21
790 | DIGI3 | Digital inputs | DI 63 On (DI63) | 12E22
791 | DIGI3 | Digital inputs | DI 63 Off (DI63) | 12E23
792 | DIGI3 | Digital inputs | DI 64 On (DI64) | 12E24
793 | DIGI3 | Digital inputs | DI 64 Off (DI64) | 12E25
794 | DIGI3 | Digital inputs | DI 65 On (DI65) | 12E26
795 | DIGI3 | Digital inputs | DI 65 Off (DI65) | 12E27
796 | DIGI3 | Digital inputs | DI 66 On (DI66) | 12E28
797 | DIGI3 | Digital inputs | DI 66 Off (DI66) | 12E29
798 | DIGI3 | Digital inputs | DI 67 On (DI67) | 12E30
799 | DIGI3 | Digital inputs | DI 67 Off (DI67) | 12E31
800 | DIGI3 | Digital inputs | DI 68 On (DI68) | 12E32
801 | DIGI3 | Digital inputs | DI 68 Off (DI68) | 12E33
802 | DIGI3 | Digital inputs | DI 69 On (DI69) | 12E34
803 | DIGI3 | Digital inputs | DI 69 Off (DI69) | 12E35
804 | DIGI3 | Digital inputs | DI 70 On (DI70) | 12E36
805 | DIGI3 | Digital inputs | DI 70 Off (DI70) | 12E37
806 | DIGI3 | Digital inputs | DI 71 On (DI71) | 12E38
807 | DIGI3 | Digital inputs | DI 71 Off (DI71) | 12E39
808 | DIGI3 | Digital inputs | DI 72 On (DI72) | 12E40
809 | DIGI3 | Digital inputs | DI 72 Off (DI72) | 12E41
810 | DIGI3 | Digital inputs | DI 73 On (DI73) | 12E42
811 | DIGI3 | Digital inputs | DI 73 Off (DI73) | 12E43
812 | DIGI3 | Digital inputs | DI 74 On (DI74) | 12E44
813 | DIGI3 | Digital inputs | DI 74 Off (DI74) | 12E45
814 | DIGI3 | Digital inputs | DI 75 On (DI75) | 12E46
815 | DIGI3 | Digital inputs | DI 75 Off (DI75) | 12E47
816 | DIGI3 | Digital inputs | DI 76 On (DI76) | 12E48
817 | DIGI3 | Digital inputs | DI 76 Off (DI76) | 12E49
818 | DIGI3 | Digital inputs | DI 77 On (DI77) | 12E50
819 | DIGI3 | Digital inputs | DI 77 Off (DI77) | 12E51
820 | DIGI3 | Digital inputs | DI 78 On (DI78) | 12E52
821 | DIGI3 | Digital inputs | DI 78 Off (DI78) | 12E53
822 | DIGI3 | Digital inputs | DI 79 On (DI79) | 12E54
823 | DIGI3 | Digital inputs | DI 79 Off (DI79) | 12E55
824 | DIGI3 | Digital inputs | DI 80 On (DI80) | 12E56
825 | DIGI3 | Digital inputs | DI 80 Off (DI80) | 12E57
826 | DIGI3 | Digital inputs | DI 81 On (DI81) | 12E58
827 | DIGI3 | Digital inputs | DI 81 Off (DI81) | 12E59
828 | DIGI3 | Digital inputs | DI 82 On (DI82) | 12E60
829 | DIGI3 | Digital inputs | DI 82 Off (DI82) | 12E61
830 | DIGI3 | Digital inputs | DI 83 On (DI83) | 12E62
831 | DIGI3 | Digital inputs | DI 83 Off (DI83) | 12E63
832 | DIGI4 | Digital inputs | DI 84 On (DI84) | 13E0
833 | DIGI4 | Digital inputs | DI 84 Off (DI84) | 13E1
834 | DIGI4 | Digital inputs | DI 85 On (DI85) | 13E2
835 | DIGI4 | Digital inputs | DI 85 Off (DI85) | 13E3
836 | DIGI4 | Digital inputs | DI 86 On (DI86) | 13E4
837 | DIGI4 | Digital inputs | DI 86 Off (DI86) | 13E5
838 | DIGI4 | Digital inputs | DI 87 On (DI87) | 13E6
839 | DIGI4 | Digital inputs | DI 87 Off (DI87) | 13E7
840 | DIGI4 | Digital inputs | DI 88 On (DI88) | 13E8
841 | DIGI4 | Digital inputs | DI 88 Off (DI88) | 13E9
842 | DIGI4 | Digital inputs | DI 89 On (DI89) | 13E10
843 | DIGI4 | Digital inputs | DI 89 Off (DI89) | 13E11
844 | DIGI4 | Digital inputs | DI 90 On (DI90) | 13E12
845 | DIGI4 | Digital inputs | DI 90 Off (DI90) | 13E13
846 | DIGI4 | Digital inputs | DI 91 On (DI91) | 13E14
847 | DIGI4 | Digital inputs | DI 91 Off (DI91) | 13E15
848 | DIGI4 | Digital inputs | DI 92 On (DI92) | 13E16
849 | DIGI4 | Digital inputs | DI 92 Off (DI92) | 13E17
850 | DIGI4 | Digital inputs | DI 93 On (DI93) | 13E18
851 | DIGI4 | Digital inputs | DI 93 Off (DI93) | 13E19
852 | DIGI4 | Digital inputs | DI 94 On (DI94) | 13E20
853 | DIGI4 | Digital inputs | DI 94 Off (DI94) | 13E21
854 | DIGI4 | Digital inputs | DI 95 On (DI95) | 13E22
855 | DIGI4 | Digital inputs | DI 95 Off (DI95) | 13E23
856 | DIGI4 | Digital inputs | DI 96 On (DI96) | 13E24
857 | DIGI4 | Digital inputs | DI 96 Off (DI96) | 13E25
858 | DIGI4 | Digital inputs | DI 97 On (DI97) | 13E26
859 | DIGI4 | Digital inputs | DI 97 Off (DI97) | 13E27
860 | DIGI4 | Digital inputs | DI 98 On (DI98) | 13E28
861 | DIGI4 | Digital inputs | DI 98 Off (DI98) | 13E29
862 | DIGI4 | Digital inputs | DI 99 On (DI99) | 13E30
863 | DIGI4 | Digital inputs | DI 99 Off (DI99) | 13E31
864 | DIGI4 | Digital inputs | DI100 On (DI100) | 13E32
865 | DIGI4 | Digital inputs | DI100 Off (DI100) | 13E33
866 | DIGI4 | Digital inputs | DI101 On (DI101) | 13E34
867 | DIGI4 | Digital inputs | DI101 Off (DI101) | 13E35
868 | DIGI4 | Digital inputs | DI102 On (DI102) | 13E36
869 | DIGI4 | Digital inputs | DI102 Off (DI102) | 13E37
870 | DIGI4 | Digital inputs | DI103 On (DI103) | 13E38
871 | DIGI4 | Digital inputs | DI103 Off (DI103) | 13E39
872 | DIGI4 | Digital inputs | DI104 On (DI104) | 13E40
873 | DIGI4 | Digital inputs | DI104 Off (DI104) | 13E41
874 | DIGI4 | Digital inputs | DI105 On (DI105) | 13E42
875 | DIGI4 | Digital inputs | DI105 Off (DI105) | 13E43
876 | DIGI4 | Digital inputs | DI106 On (DI106) | 13E44
877 | DIGI4 | Digital inputs | DI106 Off (DI106) | 13E45
878 | DIGI4 | Digital inputs | DI107 On (DI107) | 13E46
879 | DIGI4 | Digital inputs | DI107 Off (DI107) | 13E47
880 | DIGI4 | Digital inputs | DI108 On (DI108) | 13E48
881 | DIGI4 | Digital inputs | DI108 Off (DI108) | 13E49
882 | DIGI4 | Digital inputs | DI109 On (DI109) | 13E50
883 | DIGI4 | Digital inputs | DI109 Off (DI109) | 13E51
884 | DIGI4 | Digital inputs | DI110 On (DI110) | 13E52
885 | DIGI4 | Digital inputs | DI110 Off (DI110) | 13E53
886 | DIGI4 | Digital inputs | DI111 On (DI111) | 13E54
887 | DIGI4 | Digital inputs | DI111 Off (DI111) | 13E55
888 | DIGI4 | Digital inputs | DI112 On (DI112) | 13E56
889 | DIGI4 | Digital inputs | DI112 Off (DI112) | 13E57
890 | DIGI4 | Digital inputs | DI113 On (DI113) | 13E58
891 | DIGI4 | Digital inputs | DI113 Off (DI113) | 13E59
892 | DIGI4 | Digital inputs | DI114 On (DI114) | 13E60
893 | DIGI4 | Digital inputs | DI114 Off (DI114) | 13E61
894 | DIGI4 | Digital inputs | DI115 On (DI115) | 13E62
895 | DIGI4 | Digital inputs | DI115 Off (DI115) | 13E63
896 | LOGIC3 | Logical outputs | Logical Out33 On (Logical Output 33) | 14E0
897 | LOGIC3 | Logical outputs | Logical Out33 Off (Logical Output 33) | 14E1
898 | LOGIC3 | Logical outputs | Logical Out34 On (Logical Output 34) | 14E2
899 | LOGIC3 | Logical outputs | Logical Out34 Off (Logical Output 34) | 14E3
900 | LOGIC3 | Logical outputs | Logical Out35 On (Logical Output 35) | 14E4
901 | LOGIC3 | Logical outputs | Logical Out35 Off (Logical Output 35) | 14E5
902 | LOGIC3 | Logical outputs | Logical Out36 On (Logical Output 36) | 14E6
903 | LOGIC3 | Logical outputs | Logical Out36 Off (Logical Output 36) | 14E7
904 | LOGIC3 | Logical outputs | Logical Out37 On (Logical Output 37) | 14E8
905 | LOGIC3 | Logical outputs | Logical Out37 Off (Logical Output 37) | 14E9
906 | LOGIC3 | Logical outputs | Logical Out38 On (Logical Output 38) | 14E10
907 | LOGIC3 | Logical outputs | Logical Out38 Off (Logical Output 38) | 14E11
908 | LOGIC3 | Logical outputs | Logical Out39 On (Logical Output 39) | 14E12
909 | LOGIC3 | Logical outputs | Logical Out39 Off (Logical Output 39) | 14E13
910 | LOGIC3 | Logical outputs | Logical Out40 On (Logical Output 40) | 14E14
911 | LOGIC3 | Logical outputs | Logical Out40 Off (Logical Output 40) | 14E15
912 | LOGIC3 | Logical outputs | Logical Out41 On (Logical Output 41) | 14E16
913 | LOGIC3 | Logical outputs | Logical Out41 Off (Logical Output 41) | 14E17
914 | LOGIC3 | Logical outputs | Logical Out42 On (Logical Output 42) | 14E18
915 | LOGIC3 | Logical outputs | Logical Out42 Off (Logical Output 42) | 14E19
916 | LOGIC3 | Logical outputs | Logical Out43 On (Logical Output 43) | 14E20
917 | LOGIC3 | Logical outputs | Logical Out43 Off (Logical Output 43) | 14E21
918 | LOGIC3 | Logical outputs | Logical Out44 On (Logical Output 44) | 14E22
919 | LOGIC3 | Logical outputs | Logical Out44 Off (Logical Output 44) | 14E23
920 | LOGIC3 | Logical outputs | Logical Out45 On (Logical Output 45) | 14E24
921 | LOGIC3 | Logical outputs | Logical Out45 Off (Logical Output 45) | 14E25
922 | LOGIC3 | Logical outputs | Logical Out46 On (Logical Output 46) | 14E26
923 | LOGIC3 | Logical outputs | Logical Out46 Off (Logical Output 46) | 14E27
924 | LOGIC3 | Logical outputs | Logical Out47 On (Logical Output 47) | 14E28
925 | LOGIC3 | Logical outputs | Logical Out47 Off (Logical Output 47) | 14E29
926 | LOGIC3 | Logical outputs | Logical Out48 On (Logical Output 48) | 14E30
927 | LOGIC3 | Logical outputs | Logical Out48 Off (Logical Output 48) | 14E31
928 | LOGIC3 | Logical outputs | Logical Out49 On (Logical Output 49) | 14E32
929 | LOGIC3 | Logical outputs | Logical Out49 Off (Logical Output 49) | 14E33
930 | LOGIC3 | Logical outputs | Logical Out50 On (Logical Output 50) | 14E34
931 | LOGIC3 | Logical outputs | Logical Out50 Off (Logical Output 50) | 14E35
932 | LOGIC3 | Logical outputs | Logical Out51 On (Logical Output 51) | 14E36
933 | LOGIC3 | Logical outputs | Logical Out51 Off (Logical Output 51) | 14E37
934 | LOGIC3 | Logical outputs | Logical Out52 On (Logical Output 52) | 14E38
935 | LOGIC3 | Logical outputs | Logical Out52 Off (Logical Output 52) | 14E39
936 | LOGIC3 | Logical outputs | Logical Out53 On (Logical Output 53) | 14E40
937 | LOGIC3 | Logical outputs | Logical Out53 Off (Logical Output 53) | 14E41
938 | LOGIC3 | Logical outputs | Logical Out54 On (Logical Output 54) | 14E42
939 | LOGIC3 | Logical outputs | Logical Out54 Off (Logical Output 54) | 14E43
940 | LOGIC3 | Logical outputs | Logical Out55 On (Logical Output 55) | 14E44
941 | LOGIC3 | Logical outputs | Logical Out55 Off (Logical Output 55) | 14E45
942 | LOGIC3 | Logical outputs | Logical Out56 On (Logical Output 56) | 14E46
943 | LOGIC3 | Logical outputs | Logical Out56 Off (Logical Output 56) | 14E47
944 | LOGIC3 | Logical outputs | Logical Out57 On (Logical Output 57) | 14E48
945 | LOGIC3 | Logical outputs | Logical Out57 Off (Logical Output 57) | 14E49
946 | LOGIC3 | Logical outputs | Logical Out58 On (Logical Output 58) | 14E50
947 | LOGIC3 | Logical outputs | Logical Out58 Off (Logical Output 58) | 14E51
948 | LOGIC3 | Logical outputs | Logical Out59 On (Logical Output 59) | 14E52
949 | LOGIC3 | Logical outputs | Logical Out59 Off (Logical Output 59) | 14E53
950 | LOGIC3 | Logical outputs | Logical Out60 On (Logical Output 60) | 14E54
951 | LOGIC3 | Logical outputs | Logical Out60 Off (Logical Output 60) | 14E55
952 | LOGIC3 | Logical outputs | Logical Out61 On (Logical Output 61) | 14E56
953 | LOGIC3 | Logical outputs | Logical Out61 Off (Logical Output 61) | 14E57
954 | LOGIC3 | Logical outputs | Logical Out62 On (Logical Output 62) | 14E58
955 | LOGIC3 | Logical outputs | Logical Out62 Off (Logical Output 62) | 14E59
956 | LOGIC3 | Logical outputs | Logical Out63 On (Logical Output 63) | 14E60
957 | LOGIC3 | Logical outputs | Logical Out63 Off (Logical Output 63) | 14E61
958 | LOGIC3 | Logical outputs | Logical Out64 On (Logical Output 64) | 14E62
959 | LOGIC3 | Logical outputs | Logical Out64 Off (Logical Output 64) | 14E63
1024 | GOOSE1 | GOOSE input | GOOSE IN1 On (GOOSE IN1) | 16E0
1025 | GOOSE1 | GOOSE input | GOOSE IN1 Off (GOOSE IN1) | 16E1
1026 | GOOSE1 | GOOSE input | GOOSE IN2 On (GOOSE IN2) | 16E2
1027 | GOOSE1 | GOOSE input | GOOSE IN2 Off (GOOSE IN2) | 16E3
1028 | GOOSE1 | GOOSE input | GOOSE IN3 On (GOOSE IN3) | 16E4
1029 | GOOSE1 | GOOSE input | GOOSE IN3 Off (GOOSE IN3) | 16E5
1030 | GOOSE1 | GOOSE input | GOOSE IN4 On (GOOSE IN4) | 16E6
1031 | GOOSE1 | GOOSE input | GOOSE IN4 Off (GOOSE IN4) | 16E7
1032 | GOOSE1 | GOOSE input | GOOSE IN5 On (GOOSE IN5) | 16E8
1033 | GOOSE1 | GOOSE input | GOOSE IN5 Off (GOOSE IN5) | 16E9
1034 | GOOSE1 | GOOSE input | GOOSE IN6 On (GOOSE IN6) | 16E10
1035 | GOOSE1 | GOOSE input | GOOSE IN6 Off (GOOSE IN6) | 16E11
1036 | GOOSE1 | GOOSE input | GOOSE IN7 On (GOOSE IN7) | 16E12
1037 | GOOSE1 | GOOSE input | GOOSE IN7 Off (GOOSE IN7) | 16E13
1038 | GOOSE1 | GOOSE input | GOOSE IN8 On (GOOSE IN8) | 16E14
1039 | GOOSE1 | GOOSE input | GOOSE IN8 Off (GOOSE IN8) | 16E15
1040 | GOOSE1 | GOOSE input | GOOSE IN9 On (GOOSE IN9) | 16E16
1041 | GOOSE1 | GOOSE input | GOOSE IN9 Off (GOOSE IN9) | 16E17
1042 | GOOSE1 | GOOSE input | GOOSE IN10 On (GOOSE IN10) | 16E18
1043 | GOOSE1 | GOOSE input | GOOSE IN10 Off (GOOSE IN10) | 16E19
1044 | GOOSE1 | GOOSE input | GOOSE IN11 On (GOOSE IN11) | 16E20
1045 | GOOSE1 | GOOSE input | GOOSE IN11 Off (GOOSE IN11) | 16E21
1046 | GOOSE1 | GOOSE input | GOOSE IN12 On (GOOSE IN12) | 16E22
1047 | GOOSE1 | GOOSE input | GOOSE IN12 Off (GOOSE IN12) | 16E23
1048 | GOOSE1 | GOOSE input | GOOSE IN13 On (GOOSE IN13) | 16E24
1049 | GOOSE1 | GOOSE input | GOOSE IN13 Off (GOOSE IN13) | 16E25
1050 | GOOSE1 | GOOSE input | GOOSE IN14 On (GOOSE IN14) | 16E26
1051 | GOOSE1 | GOOSE input | GOOSE IN14 Off (GOOSE IN14) | 16E27
1052 | GOOSE1 | GOOSE input | GOOSE IN15 On (GOOSE IN15) | 16E28
1053 | GOOSE1 | GOOSE input | GOOSE IN15 Off (GOOSE IN15) | 16E29
1054 | GOOSE1 | GOOSE input | GOOSE IN16 On (GOOSE IN16) | 16E30
1055 | GOOSE1 | GOOSE input | GOOSE IN16 Off (GOOSE IN16) | 16E31
1056 | GOOSE1 | GOOSE input | GOOSE IN17 On (GOOSE IN17) | 16E32
1057 | GOOSE1 | GOOSE input | GOOSE IN17 Off (GOOSE IN17) | 16E33
1058 | GOOSE1 | GOOSE input | GOOSE IN18 On (GOOSE IN18) | 16E34
1059 | GOOSE1 | GOOSE input | GOOSE IN18 Off (GOOSE IN18) | 16E35
1060 | GOOSE1 | GOOSE input | GOOSE IN19 On (GOOSE IN19) | 16E36
1061 | GOOSE1 | GOOSE input | GOOSE IN19 Off (GOOSE IN19) | 16E37
1062 | GOOSE1 | GOOSE input | GOOSE IN20 On (GOOSE IN20) | 16E38
1063 | GOOSE1 | GOOSE input | GOOSE IN20 Off (GOOSE IN20) | 16E39
1064 | GOOSE1 | GOOSE input | GOOSE IN21 On (GOOSE IN21) | 16E40
1065 | GOOSE1 | GOOSE input | GOOSE IN21 Off (GOOSE IN21) | 16E41
1066 | GOOSE1 | GOOSE input | GOOSE IN22 On (GOOSE IN22) | 16E42
1067 | GOOSE1 | GOOSE input | GOOSE IN22 Off (GOOSE IN22) | 16E43
1068 | GOOSE1 | GOOSE input | GOOSE IN23 On (GOOSE IN23) | 16E44
1069 | GOOSE1 | GOOSE input | GOOSE IN23 Off (GOOSE IN23) | 16E45
1070 | GOOSE1 | GOOSE input | GOOSE IN24 On (GOOSE IN24) | 16E46
1071 | GOOSE1 | GOOSE input | GOOSE IN24 Off (GOOSE IN24) | 16E47
1072 | GOOSE1 | GOOSE input | GOOSE IN25 On (GOOSE IN25) | 16E48
1073 | GOOSE1 | GOOSE input | GOOSE IN25 Off (GOOSE IN25) | 16E49
1074 | GOOSE1 | GOOSE input | GOOSE IN26 On (GOOSE IN26) | 16E50
1075 | GOOSE1 | GOOSE input | GOOSE IN26 Off (GOOSE IN26) | 16E51
1076 | GOOSE1 | GOOSE input | GOOSE IN27 On (GOOSE IN27) | 16E52
1077 | GOOSE1 | GOOSE input | GOOSE IN27 Off (GOOSE IN27) | 16E53
1078 | GOOSE1 | GOOSE input | GOOSE IN28 On (GOOSE IN28) | 16E54
1079 | GOOSE1 | GOOSE input | GOOSE IN28 Off (GOOSE IN28) | 16E55
1080 | GOOSE1 | GOOSE input | GOOSE IN29 On (GOOSE IN29) | 16E56
1081 | GOOSE1 | GOOSE input | GOOSE IN29 Off (GOOSE IN29) | 16E57
1082 | GOOSE1 | GOOSE input | GOOSE IN30 On (GOOSE IN30) | 16E58
1083 | GOOSE1 | GOOSE input | GOOSE IN30 Off (GOOSE IN30) | 16E59
1084 | GOOSE1 | GOOSE input | GOOSE IN31 On (GOOSE IN31) | 16E60
1085 | GOOSE1 | GOOSE input | GOOSE IN31 Off (GOOSE IN31) | 16E61
1086 | GOOSE1 | GOOSE input | GOOSE IN32 On (GOOSE IN32) | 16E62
1087 | GOOSE1 | GOOSE input | GOOSE IN32 Off (GOOSE IN32) | 16E63
1088 | GOOSE2 | GOOSE input | GOOSE IN33 On (GOOSE IN33) | 17E0
1089 | GOOSE2 | GOOSE input | GOOSE IN33 Off (GOOSE IN33) | 17E1
1090 | GOOSE2 | GOOSE input | GOOSE IN34 On (GOOSE IN34) | 17E2
1091 | GOOSE2 | GOOSE input | GOOSE IN34 Off (GOOSE IN34) | 17E3
1092 | GOOSE2 | GOOSE input | GOOSE IN35 On (GOOSE IN35) | 17E4
1093 | GOOSE2 | GOOSE input | GOOSE IN35 Off (GOOSE IN35) | 17E5
1094 | GOOSE2 | GOOSE input | GOOSE IN36 On (GOOSE IN36) | 17E6
1095 | GOOSE2 | GOOSE input | GOOSE IN36 Off (GOOSE IN36) | 17E7
1096 | GOOSE2 | GOOSE input | GOOSE IN37 On (GOOSE IN37) | 17E8
1097 | GOOSE2 | GOOSE input | GOOSE IN37 Off (GOOSE IN37) | 17E9
1098 | GOOSE2 | GOOSE input | GOOSE IN38 On (GOOSE IN38) | 17E10
1099 | GOOSE2 | GOOSE input | GOOSE IN38 Off (GOOSE IN38) | 17E11
1100 | GOOSE2 | GOOSE input | GOOSE IN39 On (GOOSE IN39) | 17E12
1101 | GOOSE2 | GOOSE input | GOOSE IN39 Off (GOOSE IN39) | 17E13
1102 | GOOSE2 | GOOSE input | GOOSE IN40 On (GOOSE IN40) | 17E14
1103 | GOOSE2 | GOOSE input | GOOSE IN40 Off (GOOSE IN40) | 17E15
1104 | GOOSE2 | GOOSE input | GOOSE IN41 On (GOOSE IN41) | 17E16
1105 | GOOSE2 | GOOSE input | GOOSE IN41 Off (GOOSE IN41) | 17E17
1106 | GOOSE2 | GOOSE input | GOOSE IN42 On (GOOSE IN42) | 17E18
1107 | GOOSE2 | GOOSE input | GOOSE IN42 Off (GOOSE IN42) | 17E19
1108 | GOOSE2 | GOOSE input | GOOSE IN43 On (GOOSE IN43) | 17E20
1109 | GOOSE2 | GOOSE input | GOOSE IN43 Off (GOOSE IN43) | 17E21
1110 | GOOSE2 | GOOSE input | GOOSE IN44 On (GOOSE IN44) | 17E22
1111 | GOOSE2 | GOOSE input | GOOSE IN44 Off (GOOSE IN44) | 17E23
1112 | GOOSE2 | GOOSE input | GOOSE IN45 On (GOOSE IN45) | 17E24
1113 | GOOSE2 | GOOSE input | GOOSE IN45 Off (GOOSE IN45) | 17E25
1114 | GOOSE2 | GOOSE input | GOOSE IN46 On (GOOSE IN46) | 17E26
1115 | GOOSE2 | GOOSE input | GOOSE IN46 Off (GOOSE IN46) | 17E27
1116 | GOOSE2 | GOOSE input | GOOSE IN47 On (GOOSE IN47) | 17E28
1117 | GOOSE2 | GOOSE input | GOOSE IN47 Off (GOOSE IN47) | 17E29
1118 | GOOSE2 | GOOSE input | GOOSE IN48 On (GOOSE IN48) | 17E30
1119 | GOOSE2 | GOOSE input | GOOSE IN48 Off (GOOSE IN48) | 17E31
1120 | GOOSE2 | GOOSE input | GOOSE IN49 On (GOOSE IN49) | 17E32
1121 | GOOSE2 | GOOSE input | GOOSE IN49 Off (GOOSE IN49) | 17E33
1122 | GOOSE2 | GOOSE input | GOOSE IN50 On (GOOSE IN50) | 17E34
1123 | GOOSE2 | GOOSE input | GOOSE IN50 Off (GOOSE IN50) | 17E35
1124 | GOOSE2 | GOOSE input | GOOSE IN51 On (GOOSE IN51) | 17E36
1125 | GOOSE2 | GOOSE input | GOOSE IN51 Off (GOOSE IN51) | 17E37
1126 | GOOSE2 | GOOSE input | GOOSE IN52 On (GOOSE IN52) | 17E38
1127 | GOOSE2 | GOOSE input | GOOSE IN52 Off (GOOSE IN52) | 17E39
1128 | GOOSE2 | GOOSE input | GOOSE IN53 On (GOOSE IN53) | 17E40
1129 | GOOSE2 | GOOSE input | GOOSE IN53 Off (GOOSE IN53) | 17E41
1130 | GOOSE2 | GOOSE input | GOOSE IN54 On (GOOSE IN54) | 17E42
1131 | GOOSE2 | GOOSE input | GOOSE IN54 Off (GOOSE IN54) | 17E43
1132 | GOOSE2 | GOOSE input | GOOSE IN55 On (GOOSE IN55) | 17E44
1133 | GOOSE2 | GOOSE input | GOOSE IN55 Off (GOOSE IN55) | 17E45
1134 | GOOSE2 | GOOSE input | GOOSE IN56 On (GOOSE IN56) | 17E46
1135 | GOOSE2 | GOOSE input | GOOSE IN56 Off (GOOSE IN56) | 17E47
1136 | GOOSE2 | GOOSE input | GOOSE IN57 On (GOOSE IN57) | 17E48
1137 | GOOSE2 | GOOSE input | GOOSE IN57 Off (GOOSE IN57) | 17E49
1138 | GOOSE2 | GOOSE input | GOOSE IN58 On (GOOSE IN58) | 17E50
1139 | GOOSE2 | GOOSE input | GOOSE IN58 Off (GOOSE IN58) | 17E51
1140 | GOOSE2 | GOOSE input | GOOSE IN59 On (GOOSE IN59) | 17E52
1141 | GOOSE2 | GOOSE input | GOOSE IN59 Off (GOOSE IN59) | 17E53
1142 | GOOSE2 | GOOSE input | GOOSE IN60 On (GOOSE IN60) | 17E54
1143 | GOOSE2 | GOOSE input | GOOSE IN60 Off (GOOSE IN60) | 17E55
1144 | GOOSE2 | GOOSE input | GOOSE IN61 On (GOOSE IN61) | 17E56
1145 | GOOSE2 | GOOSE input | GOOSE IN61 Off (GOOSE IN61) | 17E57
1146 | GOOSE2 | GOOSE input | GOOSE IN62 On (GOOSE IN62) | 17E58
1147 | GOOSE2 | GOOSE input | GOOSE IN62 Off (GOOSE IN62) | 17E59
1148 | GOOSE2 | GOOSE input | GOOSE IN63 On (GOOSE IN63) | 17E60
1149 | GOOSE2 | GOOSE input | GOOSE IN63 Off (GOOSE IN63) | 17E61
1150 | GOOSE2 | GOOSE input | GOOSE IN64 On (GOOSE IN64) | 17E62
1151 | GOOSE2 | GOOSE input | GOOSE IN64 Off (GOOSE IN64) | 17E63
1152 | GOOSE3 | GOOSE input quality | GOOSE IN1 Quality Good (GOOSE IN1) | 18E0
1153 | GOOSE3 | GOOSE input quality | GOOSE IN1 Quality Bad (GOOSE IN1) | 18E1
1154 | GOOSE3 | GOOSE input quality | GOOSE IN2 Quality Good (GOOSE IN2) | 18E2
1155 | GOOSE3 | GOOSE input quality | GOOSE IN2 Quality Bad (GOOSE IN2) | 18E3
1156 | GOOSE3 | GOOSE input quality | GOOSE IN3 Quality Good (GOOSE IN3) | 18E4
1157 | GOOSE3 | GOOSE input quality | GOOSE IN3 Quality Bad (GOOSE IN3) | 18E5
1158 | GOOSE3 | GOOSE input quality | GOOSE IN4 Quality Good (GOOSE IN4) | 18E6
1159 | GOOSE3 | GOOSE input quality | GOOSE IN4 Quality Bad (GOOSE IN4) | 18E7
1160 | GOOSE3 | GOOSE input quality | GOOSE IN5 Quality Good (GOOSE IN5) | 18E8
1161 | GOOSE3 | GOOSE input quality | GOOSE IN5 Quality Bad (GOOSE IN5) | 18E9
1162 | GOOSE3 | GOOSE input quality | GOOSE IN6 Quality Good (GOOSE IN6) | 18E10
1163 | GOOSE3 | GOOSE input quality | GOOSE IN6 Quality Bad (GOOSE IN6) | 18E11
1164 | GOOSE3 | GOOSE input quality | GOOSE IN7 Quality Good (GOOSE IN7) | 18E12
1165 | GOOSE3 | GOOSE input quality | GOOSE IN7 Quality Bad (GOOSE IN7) | 18E13
1166 | GOOSE3 | GOOSE input quality | GOOSE IN8 Quality Good (GOOSE IN8) | 18E14
1167 | GOOSE3 | GOOSE input quality | GOOSE IN8 Quality Bad (GOOSE IN8) | 18E15
1168 | GOOSE3 | GOOSE input quality | GOOSE IN9 Quality Good (GOOSE IN9) | 18E16
1169 | GOOSE3 | GOOSE input quality | GOOSE IN9 Quality Bad (GOOSE IN9) | 18E17
1170 | GOOSE3 | GOOSE input quality | GOOSE IN10 Quality Good (GOOSE IN10) | 18E18
1171 | GOOSE3 | GOOSE input quality | GOOSE IN10 Quality Bad (GOOSE IN10) | 18E19
1172 | GOOSE3 | GOOSE input quality | GOOSE IN11 Quality Good (GOOSE IN11) | 18E20
1173 | GOOSE3 | GOOSE input quality | GOOSE IN11 Quality Bad (GOOSE IN11) | 18E21
1174 | GOOSE3 | GOOSE input quality | GOOSE IN12 Quality Good (GOOSE IN12) | 18E22
1175 | GOOSE3 | GOOSE input quality | GOOSE IN12 Quality Bad (GOOSE IN12) | 18E23
1176 | GOOSE3 | GOOSE input quality | GOOSE IN13 Quality Good (GOOSE IN13) | 18E24
1177 | GOOSE3 | GOOSE input quality | GOOSE IN13 Quality Bad (GOOSE IN13) | 18E25
1178 | GOOSE3 | GOOSE input quality | GOOSE IN14 Quality Good (GOOSE IN14) | 18E26
1179 | GOOSE3 | GOOSE input quality | GOOSE IN14 Quality Bad (GOOSE IN14) | 18E27
1180 | GOOSE3 | GOOSE input quality | GOOSE IN15 Quality Good (GOOSE IN15) | 18E28
1181 | GOOSE3 | GOOSE input quality | GOOSE IN15 Quality Bad (GOOSE IN15) | 18E29
1182 | GOOSE3 | GOOSE input quality | GOOSE IN16 Quality Good (GOOSE IN16) | 18E30
1183 | GOOSE3 | GOOSE input quality | GOOSE IN16 Quality Bad (GOOSE IN16) | 18E31
1184 | GOOSE3 | GOOSE input quality | GOOSE IN17 Quality Good (GOOSE IN17) | 18E32
1185 | GOOSE3 | GOOSE input quality | GOOSE IN17 Quality Bad (GOOSE IN17) | 18E33
1186 | GOOSE3 | GOOSE input quality | GOOSE IN18 Quality Good (GOOSE IN18) | 18E34
1187 | GOOSE3 | GOOSE input quality | GOOSE IN18 Quality Bad (GOOSE IN18) | 18E35
1188 | GOOSE3 | GOOSE input quality | GOOSE IN19 Quality Good (GOOSE IN19) | 18E36
1189 | GOOSE3 | GOOSE input quality | GOOSE IN19 Quality Bad (GOOSE IN19) | 18E37
1190 | GOOSE3 | GOOSE input quality | GOOSE IN20 Quality Good (GOOSE IN20) | 18E38
1191 | GOOSE3 | GOOSE input quality | GOOSE IN20 Quality Bad (GOOSE IN20) | 18E39
1192 | GOOSE3 | GOOSE input quality | GOOSE IN21 Quality Good (GOOSE IN21) | 18E40
1193 | GOOSE3 | GOOSE input quality | GOOSE IN21 Quality Bad (GOOSE IN21) | 18E41
1194 | GOOSE3 | GOOSE input quality | GOOSE IN22 Quality Good (GOOSE IN22) | 18E42
1195 | GOOSE3 | GOOSE input quality | GOOSE IN22 Quality Bad (GOOSE IN22) | 18E43
1196 | GOOSE3 | GOOSE input quality | GOOSE IN23 Quality Good (GOOSE IN23) | 18E44
1197 | GOOSE3 | GOOSE input quality | GOOSE IN23 Quality Bad (GOOSE IN23) | 18E45
1198 | GOOSE3 | GOOSE input quality | GOOSE IN24 Quality Good (GOOSE IN24) | 18E46
1199 | GOOSE3 | GOOSE input quality | GOOSE IN24 Quality Bad (GOOSE IN24) | 18E47
1200 | GOOSE3 | GOOSE input quality | GOOSE IN25 Quality Good (GOOSE IN25) | 18E48
1201 | GOOSE3 | GOOSE input quality | GOOSE IN25 Quality Bad (GOOSE IN25) | 18E49
1202 | GOOSE3 | GOOSE input quality | GOOSE IN26 Quality Good (GOOSE IN26) | 18E50
1203 | GOOSE3 | GOOSE input quality | GOOSE IN26 Quality Bad (GOOSE IN26) | 18E51
1204 | GOOSE3 | GOOSE input quality | GOOSE IN27 Quality Good (GOOSE IN27) | 18E52
1205 | GOOSE3 | GOOSE input quality | GOOSE IN27 Quality Bad (GOOSE IN27) | 18E53
1206 | GOOSE3 | GOOSE input quality | GOOSE IN28 Quality Good (GOOSE IN28) | 18E54
1207 | GOOSE3 | GOOSE input quality | GOOSE IN28 Quality Bad (GOOSE IN28) | 18E55
1208 | GOOSE3 | GOOSE input quality | GOOSE IN29 Quality Good (GOOSE IN29) | 18E56
1209 | GOOSE3 | GOOSE input quality | GOOSE IN29 Quality Bad (GOOSE IN29) | 18E57
1210 | GOOSE3 | GOOSE input quality | GOOSE IN30 Quality Good (GOOSE IN30) | 18E58
1211 | GOOSE3 | GOOSE input quality | GOOSE IN30 Quality Bad (GOOSE IN30) | 18E59
1212 | GOOSE3 | GOOSE input quality | GOOSE IN31 Quality Good (GOOSE IN31) | 18E60
1213 | GOOSE3 | GOOSE input quality | GOOSE IN31 Quality Bad (GOOSE IN31) | 18E61
1214 | GOOSE3 | GOOSE input quality | GOOSE IN32 Quality Good (GOOSE IN32) | 18E62
1215 | GOOSE3 | GOOSE input quality | GOOSE IN32 Quality Bad (GOOSE IN32) | 18E63
1216 | GOOSE4 | GOOSE input quality | GOOSE IN33 Quality Good (GOOSE IN33) | 19E0
1217 | GOOSE4 | GOOSE input quality | GOOSE IN33 Quality Bad (GOOSE IN33) | 19E1
1218 | GOOSE4 | GOOSE input quality | GOOSE IN34 Quality Good (GOOSE IN34) | 19E2
1219 | GOOSE4 | GOOSE input quality | GOOSE IN34 Quality Bad (GOOSE IN34) | 19E3
1220 | GOOSE4 | GOOSE input quality | GOOSE IN35 Quality Good (GOOSE IN35) | 19E4
1221 | GOOSE4 | GOOSE input quality | GOOSE IN35 Quality Bad (GOOSE IN35) | 19E5
1222 | GOOSE4 | GOOSE input quality | GOOSE IN36 Quality Good (GOOSE IN36) | 19E6
1223 | GOOSE4 | GOOSE input quality | GOOSE IN36 Quality Bad (GOOSE IN36) | 19E7
1224 | GOOSE4 | GOOSE input quality | GOOSE IN37 Quality Good (GOOSE IN37) | 19E8
1225 | GOOSE4 | GOOSE input quality | GOOSE IN37 Quality Bad (GOOSE IN37) | 19E9
1226 | GOOSE4 | GOOSE input quality | GOOSE IN38 Quality Good (GOOSE IN38) | 19E10
1227 | GOOSE4 | GOOSE input quality | GOOSE IN38 Quality Bad (GOOSE IN38) | 19E11
1228 | GOOSE4 | GOOSE input quality | GOOSE IN39 Quality Good (GOOSE IN39) | 19E12
1229 | GOOSE4 | GOOSE input quality | GOOSE IN39 Quality Bad (GOOSE IN39) | 19E13
1230 | GOOSE4 | GOOSE input quality | GOOSE IN40 Quality Good (GOOSE IN40) | 19E14
1231 | GOOSE4 | GOOSE input quality | GOOSE IN40 Quality Bad (GOOSE IN40) | 19E15
1232 | GOOSE4 | GOOSE input quality | GOOSE IN41 Quality Good (GOOSE IN41) | 19E16
1233 | GOOSE4 | GOOSE input quality | GOOSE IN41 Quality Bad (GOOSE IN41) | 19E17
1234 | GOOSE4 | GOOSE input quality | GOOSE IN42 Quality Good (GOOSE IN42) | 19E18
1235 | GOOSE4 | GOOSE input quality | GOOSE IN42 Quality Bad (GOOSE IN42) | 19E19
1236 | GOOSE4 | GOOSE input quality | GOOSE IN43 Quality Good (GOOSE IN43) | 19E20
1237 | GOOSE4 | GOOSE input quality | GOOSE IN43 Quality Bad (GOOSE IN43) | 19E21
1238 | GOOSE4 | GOOSE input quality | GOOSE IN44 Quality Good (GOOSE IN44) | 19E22
1239 | GOOSE4 | GOOSE input quality | GOOSE IN44 Quality Bad (GOOSE IN44) | 19E23
1240 | GOOSE4 | GOOSE input quality | GOOSE IN45 Quality Good (GOOSE IN45) | 19E24
1241 | GOOSE4 | GOOSE input quality | GOOSE IN45 Quality Bad (GOOSE IN45) | 19E25
1242 | GOOSE4 | GOOSE input quality | GOOSE IN46 Quality Good (GOOSE IN46) | 19E26
1243 | GOOSE4 | GOOSE input quality | GOOSE IN46 Quality Bad (GOOSE IN46) | 19E27
1244 | GOOSE4 | GOOSE input quality | GOOSE IN47 Quality Good (GOOSE IN47) | 19E28
1245 | GOOSE4 | GOOSE input quality | GOOSE IN47 Quality Bad (GOOSE IN47) | 19E29
1246 | GOOSE4 | GOOSE input quality | GOOSE IN48 Quality Good (GOOSE IN48) | 19E30
1247 | GOOSE4 | GOOSE input quality | GOOSE IN48 Quality Bad (GOOSE IN48) | 19E31
1248 | GOOSE4 | GOOSE input quality | GOOSE IN49 Quality Good (GOOSE IN49) | 19E32
1249 | GOOSE4 | GOOSE input quality | GOOSE IN49 Quality Bad (GOOSE IN49) | 19E33
1250 | GOOSE4 | GOOSE input quality | GOOSE IN50 Quality Good (GOOSE IN50) | 19E34
1251 | GOOSE4 | GOOSE input quality | GOOSE IN50 Quality Bad (GOOSE IN50) | 19E35
1252 | GOOSE4 | GOOSE input quality | GOOSE IN51 Quality Good (GOOSE IN51) | 19E36
1253 | GOOSE4 | GOOSE input quality | GOOSE IN51 Quality Bad (GOOSE IN51) | 19E37
1254 | GOOSE4 | GOOSE input quality | GOOSE IN52 Quality Good (GOOSE IN52) | 19E38
1255 | GOOSE4 | GOOSE input quality | GOOSE IN52 Quality Bad (GOOSE IN52) | 19E39
1256 | GOOSE4 | GOOSE input quality | GOOSE IN53 Quality Good (GOOSE IN53) | 19E40
1257 | GOOSE4 | GOOSE input quality | GOOSE IN53 Quality Bad (GOOSE IN53) | 19E41
1258 | GOOSE4 | GOOSE input quality | GOOSE IN54 Quality Good (GOOSE IN54) | 19E42
1259 | GOOSE4 | GOOSE input quality | GOOSE IN54 Quality Bad (GOOSE IN54) | 19E43
1260 | GOOSE4 | GOOSE input quality | GOOSE IN55 Quality Good (GOOSE IN55) | 19E44
1261 | GOOSE4 | GOOSE input quality | GOOSE IN55 Quality Bad (GOOSE IN55) | 19E45
1262 | GOOSE4 | GOOSE input quality | GOOSE IN56 Quality Good (GOOSE IN56) | 19E46
1263 | GOOSE4 | GOOSE input quality | GOOSE IN56 Quality Bad (GOOSE IN56) | 19E47
1264 | GOOSE4 | GOOSE input quality | GOOSE IN57 Quality Good (GOOSE IN57) | 19E48
1265 | GOOSE4 | GOOSE input quality | GOOSE IN57 Quality Bad (GOOSE IN57) | 19E49
1266 | GOOSE4 | GOOSE input quality | GOOSE IN58 Quality Good (GOOSE IN58) | 19E50
1267 | GOOSE4 | GOOSE input quality | GOOSE IN58 Quality Bad (GOOSE IN58) | 19E51
1268 | GOOSE4 | GOOSE input quality | GOOSE IN59 Quality Good (GOOSE IN59) | 19E52
1269 | GOOSE4 | GOOSE input quality | GOOSE IN59 Quality Bad (GOOSE IN59) | 19E53
1270 | GOOSE4 | GOOSE input quality | GOOSE IN60 Quality Good (GOOSE IN60) | 19E54
1271 | GOOSE4 | GOOSE input quality | GOOSE IN60 Quality Bad (GOOSE IN60) | 19E55
1272 | GOOSE4 | GOOSE input quality | GOOSE IN61 Quality Good (GOOSE IN61) | 19E56
1273 | GOOSE4 | GOOSE input quality | GOOSE IN61 Quality Bad (GOOSE IN61) | 19E57
1274 | GOOSE4 | GOOSE input quality | GOOSE IN62 Quality Good (GOOSE IN62) | 19E58
1275 | GOOSE4 | GOOSE input quality | GOOSE IN62 Quality Bad (GOOSE IN62) | 19E59
1276 | GOOSE4 | GOOSE input quality | GOOSE IN63 Quality Good (GOOSE IN63) | 19E60
1277 | GOOSE4 | GOOSE input quality | GOOSE IN63 Quality Bad (GOOSE IN63) | 19E61
1278 | GOOSE4 | GOOSE input quality | GOOSE IN64 Quality Good (GOOSE IN64) | 19E62
1279 | GOOSE4 | GOOSE input quality | GOOSE IN64 Quality Bad (GOOSE IN64) | 19E63
1280 | NOC1 | I> [50/51] Non-directional overcurrent | Start ON | 20E0
1281 | NOC1 | I> [50/51] Non-directional overcurrent | Start OFF | 20E1
1282 | NOC1 | I> [50/51] Non-directional overcurrent | Trip ON | 20E2
1283 | NOC1 | I> [50/51] Non-directional overcurrent | Trip OFF | 20E3
1284 | NOC1 | I> [50/51] Non-directional overcurrent | Block ON | 20E4
1285 | NOC1 | I> [50/51] Non-directional overcurrent | Block OFF | 20E5
1286 | NOC1 | I> [50/51] Non-directional overcurrent | Phase A Start On | 20E6
1287 | NOC1 | I> [50/51] Non-directional overcurrent | Phase A Start Off | 20E7
1288 | NOC1 | I> [50/51] Non-directional overcurrent | Phase B Start On | 20E8
1289 | NOC1 | I> [50/51] Non-directional overcurrent | Phase B Start Off | 20E9
1290 | NOC1 | I> [50/51] Non-directional overcurrent | Phase C Start On | 20E10
1291 | NOC1 | I> [50/51] Non-directional overcurrent | Phase C Start Off | 20E11
1292 | NOC1 | I> [50/51] Non-directional overcurrent | Phase A Trip On | 20E12
1293 | NOC1 | I> [50/51] Non-directional overcurrent | Phase A Trip Off | 20E13
1294 | NOC1 | I> [50/51] Non-directional overcurrent | Phase B Trip On | 20E14
1295 | NOC1 | I> [50/51] Non-directional overcurrent | Phase B Trip Off | 20E15
1296 | NOC1 | I> [50/51] Non-directional overcurrent | Phase C Trip On | 20E16
1297 | NOC1 | I> [50/51] Non-directional overcurrent | Phase C Trip Off | 20E17
1344 | NOC2 | I>> [50/51] Non-directional overcurrent | Start ON | 21E0
1345 | NOC2 | I>> [50/51] Non-directional overcurrent | Start OFF | 21E1
1346 | NOC2 | I>> [50/51] Non-directional overcurrent | Trip ON | 21E2
1347 | NOC2 | I>> [50/51] Non-directional overcurrent | Trip OFF | 21E3
1348 | NOC2 | I>> [50/51] Non-directional overcurrent | Block ON | 21E4
1349 | NOC2 | I>> [50/51] Non-directional overcurrent | Block OFF | 21E5
1350 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase A Start On | 21E6
1351 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase A Start Off | 21E7
1352 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase B Start On | 21E8
1353 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase B Start Off | 21E9
1354 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase C Start On | 21E10
1355 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase C Start Off | 21E11
1356 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase A Trip On | 21E12
1357 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase A Trip Off | 21E13
1358 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase B Trip On | 21E14
1359 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase B Trip Off | 21E15
1360 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase C Trip On | 21E16
1361 | NOC2 | I>> [50/51] Non-directional overcurrent | Phase C Trip Off | 21E17
1408 | NOC3 | I>>> [50/51] Non-directional overcurrent | Start ON | 22E0
1409 | NOC3 | I>>> [50/51] Non-directional overcurrent | Start OFF | 22E1
1410 | NOC3 | I>>> [50/51] Non-directional overcurrent | Trip ON | 22E2
1411 | NOC3 | I>>> [50/51] Non-directional overcurrent | Trip OFF | 22E3
1412 | NOC3 | I>>> [50/51] Non-directional overcurrent | Block ON | 22E4
1413 | NOC3 | I>>> [50/51] Non-directional overcurrent | Block OFF | 22E5
1414 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase A Start On | 22E6
1415 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase A Start Off | 22E7
1416 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase B Start On | 22E8
1417 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase B Start Off | 22E9
1418 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase C Start On | 22E10
1419 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase C Start Off | 22E11
1420 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase A Trip On | 22E12
1421 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase A Trip Off | 22E13
1422 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase B Trip On | 22E14
1423 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase B Trip Off | 22E15
1424 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase C Trip On | 22E16
1425 | NOC3 | I>>> [50/51] Non-directional overcurrent | Phase C Trip Off | 22E17
1472 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Start ON | 23E0
1473 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Start OFF | 23E1
1474 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Trip ON | 23E2
1475 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Trip OFF | 23E3
1476 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Block ON | 23E4
1477 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Block OFF | 23E5
1478 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase A Start On | 23E6
1479 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase A Start Off | 23E7
1480 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase B Start On | 23E8
1481 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase B Start Off | 23E9
1482 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase C Start On | 23E10
1483 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase C Start Off | 23E11
1484 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase A Trip On | 23E12
1485 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase A Trip Off | 23E13
1486 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase B Trip On | 23E14
1487 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase B Trip Off | 23E15
1488 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase C Trip On | 23E16
1489 | NOC4 | I>>>> [50/51] Non-directional overcurrent | Phase C Trip Off | 23E17
1536 | LOGIC4 | Logical double bit output | Logical Out1 00 On | 24E0
1537 | LOGIC4 | Logical double bit output | Logical Out1 01 On | 24E1
1538 | LOGIC4 | Logical double bit output | Logical Out1 10 On | 24E2
1539 | LOGIC4 | Logical double bit output | Logical Out1 11 On | 24E3
1540 | LOGIC4 | Logical double bit output | Logical Out2 00 On | 24E4
1541 | LOGIC4 | Logical double bit output | Logical Out2 01 On | 24E5
1542 | LOGIC4 | Logical double bit output | Logical Out2 10 On | 24E6
1543 | LOGIC4 | Logical double bit output | Logical Out2 11 On | 24E7
1544 | LOGIC4 | Logical double bit output | Logical Out3 00 On | 24E8
1545 | LOGIC4 | Logical double bit output | Logical Out3 01 On | 24E9
1546 | LOGIC4 | Logical double bit output | Logical Out3 10 On | 24E10
1547 | LOGIC4 | Logical double bit output | Logical Out3 11 On | 24E11
1548 | LOGIC4 | Logical double bit output | Logical Out4 00 On | 24E12
1549 | LOGIC4 | Logical double bit output | Logical Out4 01 On | 24E13
1550 | LOGIC4 | Logical double bit output | Logical Out4 10 On | 24E14
1551 | LOGIC4 | Logical double bit output | Logical Out4 11 On | 24E15
1552 | LOGIC4 | Logical double bit output | Logical Out5 00 On | 24E16
1553 | LOGIC4 | Logical double bit output | Logical Out5 01 On | 24E17
1554 | LOGIC4 | Logical double bit output | Logical Out5 10 On | 24E18
1555 | LOGIC4 | Logical double bit output | Logical Out5 11 On | 24E19
1556 | LOGIC4 | Logical double bit output | Logical Out6 00 On | 24E20
1557 | LOGIC4 | Logical double bit output | Logical Out6 01 On | 24E21
1558 | LOGIC4 | Logical double bit output | Logical Out6 10 On | 24E22
1559 | LOGIC4 | Logical double bit output | Logical Out6 11 On | 24E23
1560 | LOGIC4 | Logical double bit output | Logical Out7 00 On | 24E24
1561 | LOGIC4 | Logical double bit output | Logical Out7 01 On | 24E25
1562 | LOGIC4 | Logical double bit output | Logical Out7 10 On | 24E26
1563 | LOGIC4 | Logical double bit output | Logical Out7 11 On | 24E27
1564 | LOGIC4 | Logical double bit output | Logical Out8 00 On | 24E28
1565 | LOGIC4 | Logical double bit output | Logical Out8 01 On | 24E29
1566 | LOGIC4 | Logical double bit output | Logical Out8 10 On | 24E30
1567 | LOGIC4 | Logical double bit output | Logical Out8 11 On | 24E31
1568 | LOGIC4 | Logical double bit output | Logical Out9 00 On | 24E32
1569 | LOGIC4 | Logical double bit output | Logical Out9 01 On | 24E33
1570 | LOGIC4 | Logical double bit output | Logical Out9 10 On | 24E34
1571 | LOGIC4 | Logical double bit output | Logical Out9 11 On | 24E35
1572 | LOGIC4 | Logical double bit output | Logical Out10 00 On | 24E36
1573 | LOGIC4 | Logical double bit output | Logical Out10 01 On | 24E37
1574 | LOGIC4 | Logical double bit output | Logical Out10 10 On | 24E38
1575 | LOGIC4 | Logical double bit output | Logical Out10 11 On | 24E39
1576 | LOGIC4 |  | Logical TC1 Lower On | 24E40
1577 | LOGIC4 |  | Logical TC1 Lower Off | 24E41
1578 | LOGIC4 |  | Logical TC1 Higher On | 24E42
1579 | LOGIC4 |  | Logical TC1 Higher Off | 24E43
1580 | LOGIC4 |  | Logical TC2 Lower On | 24E44
1581 | LOGIC4 |  | Logical TC2 Lower Off | 24E45
1582 | LOGIC4 |  | Logical TC2 Higher On | 24E46
1583 | LOGIC4 |  | Logical TC2 Higher Off | 24E47
1584 | LOGIC4 |  | Logical TC3 Lower On | 24E48
1585 | LOGIC4 |  | Logical TC3 Lower Off | 24E49
1586 | LOGIC4 |  | Logical TC3 Higher On | 24E50
1587 | LOGIC4 |  | Logical TC3 Higher Off | 24E51
1664 | NEF1 | I0> [50N/51N] Non-directional earth fault | Start ON | 26E0
1665 | NEF1 | I0> [50N/51N] Non-directional earth fault | Start OFF | 26E1
1666 | NEF1 | I0> [50N/51N] Non-directional earth fault | Trip ON | 26E2
1667 | NEF1 | I0> [50N/51N] Non-directional earth fault | Trip OFF | 26E3
1668 | NEF1 | I0> [50N/51N] Non-directional earth fault | Block ON | 26E4
1669 | NEF1 | I0> [50N/51N] Non-directional earth fault | Block OFF | 26E5
1728 | NEF2 | I0>> [50N/51N] Non-directional earth fault | Start ON | 27E0
1729 | NEF2 | I0>> [50N/51N] Non-directional earth fault | Start OFF | 27E1
1730 | NEF2 | I0>> [50N/51N] Non-directional earth fault | Trip ON | 27E2
1731 | NEF2 | I0>> [50N/51N] Non-directional earth fault | Trip OFF | 27E3
1732 | NEF2 | I0>> [50N/51N] Non-directional earth fault | Block ON | 27E4
1733 | NEF2 | I0>> [50N/51N] Non-directional earth fault | Block OFF | 27E5
1792 | NEF3 | I0>>> [50N/51N] Non-directional earth fault | Start ON | 28E0
1793 | NEF3 | I0>>> [50N/51N] Non-directional earth fault | Start OFF | 28E1
1794 | NEF3 | I0>>> [50N/51N] Non-directional earth fault | Trip ON | 28E2
1795 | NEF3 | I0>>> [50N/51N] Non-directional earth fault | Trip OFF | 28E3
1796 | NEF3 | I0>>> [50N/51N] Non-directional earth fault | Block ON | 28E4
1797 | NEF3 | I0>>> [50N/51N] Non-directional earth fault | Block OFF | 28E5
1856 | NEF4 | I0>>>> [50N/51N] Non-directional earth fault | Start ON | 29E0
1857 | NEF4 | I0>>>> [50N/51N] Non-directional earth fault | Start OFF | 29E1
1858 | NEF4 | I0>>>> [50N/51N] Non-directional earth fault | Trip ON | 29E2
1859 | NEF4 | I0>>>> [50N/51N] Non-directional earth fault | Trip OFF | 29E3
1860 | NEF4 | I0>>>> [50N/51N] Non-directional earth fault | Block ON | 29E4
1861 | NEF4 | I0>>>> [50N/51N] Non-directional earth fault | Block OFF | 29E5
2048 | CUB1 | I2> [46/46R/46L] Current unbalance | Start ON | 32E0
2049 | CUB1 | I2> [46/46R/46L] Current unbalance | Start OFF | 32E1
2050 | CUB1 | I2> [46/46R/46L] Current unbalance | Trip ON | 32E2
2051 | CUB1 | I2> [46/46R/46L] Current unbalance | Trip OFF | 32E3
2052 | CUB1 | I2> [46/46R/46L] Current unbalance | Block ON | 32E4
2053 | CUB1 | I2> [46/46R/46L] Current unbalance | Block OFF | 32E5
2112 | CUB2 | I2>> [46/46R/46L] Current unbalance | Start ON | 33E0
2113 | CUB2 | I2>> [46/46R/46L] Current unbalance | Start OFF | 33E1
2114 | CUB2 | I2>> [46/46R/46L] Current unbalance | Trip ON | 33E2
2115 | CUB2 | I2>> [46/46R/46L] Current unbalance | Trip OFF | 33E3
2116 | CUB2 | I2>> [46/46R/46L] Current unbalance | Block ON | 33E4
2117 | CUB2 | I2>> [46/46R/46L] Current unbalance | Block OFF | 33E5
2176 | CUB3 | I2>>> [46/46R/46L] Current unbalance | Start ON | 34E0
2177 | CUB3 | I2>>> [46/46R/46L] Current unbalance | Start OFF | 34E1
2178 | CUB3 | I2>>> [46/46R/46L] Current unbalance | Trip ON | 34E2
2179 | CUB3 | I2>>> [46/46R/46L] Current unbalance | Trip OFF | 34E3
2180 | CUB3 | I2>>> [46/46R/46L] Current unbalance | Block ON | 34E4
2181 | CUB3 | I2>>> [46/46R/46L] Current unbalance | Block OFF | 34E5
2240 | CUB4 | I2>>>> [46/46R/46L] Current unbalance | Start ON | 35E0
2241 | CUB4 | I2>>>> [46/46R/46L] Current unbalance | Start OFF | 35E1
2242 | CUB4 | I2>>>> [46/46R/46L] Current unbalance | Trip ON | 35E2
2243 | CUB4 | I2>>>> [46/46R/46L] Current unbalance | Trip OFF | 35E3
2244 | CUB4 | I2>>>> [46/46R/46L] Current unbalance | Block ON | 35E4
2245 | CUB4 | I2>>>> [46/46R/46L] Current unbalance | Block OFF | 35E5
2368 | HOC1 | Ih> [50H/51H/68H] Harmonic overcurrent | Start ON | 37E0
2369 | HOC1 | Ih> [50H/51H/68H] Harmonic overcurrent | Start OFF | 37E1
2370 | HOC1 | Ih> [50H/51H/68H] Harmonic overcurrent | Trip ON | 37E2
2371 | HOC1 | Ih> [50H/51H/68H] Harmonic overcurrent | Trip OFF | 37E3
2372 | HOC1 | Ih> [50H/51H/68H] Harmonic overcurrent | Block ON | 37E4
2373 | HOC1 | Ih> [50H/51H/68H] Harmonic overcurrent | Block OFF | 37E5
2432 | HOC2 | Ih>> [50H/51H/68H] Harmonic overcurrent | Start ON | 38E0
2433 | HOC2 | Ih>> [50H/51H/68H] Harmonic overcurrent | Start OFF | 38E1
2434 | HOC2 | Ih>> [50H/51H/68H] Harmonic overcurrent | Trip ON | 38E2
2435 | HOC2 | Ih>> [50H/51H/68H] Harmonic overcurrent | Trip OFF | 38E3
2436 | HOC2 | Ih>> [50H/51H/68H] Harmonic overcurrent | Block ON | 38E4
2437 | HOC2 | Ih>> [50H/51H/68H] Harmonic overcurrent | Block OFF | 38E5
2496 | HOC3 | Ih>>> [50H/51H/68H] Harmonic overcurrent | Start ON | 39E0
2497 | HOC3 | Ih>>> [50H/51H/68H] Harmonic overcurrent | Start OFF | 39E1
2498 | HOC3 | Ih>>> [50H/51H/68H] Harmonic overcurrent | Trip ON | 39E2
2499 | HOC3 | Ih>>> [50H/51H/68H] Harmonic overcurrent | Trip OFF | 39E3
2500 | HOC3 | Ih>>> [50H/51H/68H] Harmonic overcurrent | Block ON | 39E4
2501 | HOC3 | Ih>>> [50H/51H/68H] Harmonic overcurrent | Block OFF | 39E5
2560 | HOC4 | Ih>>>> [50H/51H/68H] Harmonic overcurrent | Start ON | 40E0
2561 | HOC4 | Ih>>>> [50H/51H/68H] Harmonic overcurrent | Start OFF | 40E1
2562 | HOC4 | Ih>>>> [50H/51H/68H] Harmonic overcurrent | Trip ON | 40E2
2563 | HOC4 | Ih>>>> [50H/51H/68H] Harmonic overcurrent | Trip OFF | 40E3
2564 | HOC4 | Ih>>>> [50H/51H/68H] Harmonic overcurrent | Block ON | 40E4
2565 | HOC4 | Ih>>>> [50H/51H/68H] Harmonic overcurrent | Block OFF | 40E5
2688 | CLP1 | Cold load pick-up [CLPU] | LowStart ON | 42E0
2689 | CLP1 | Cold load pick-up [CLPU] | LowStart OFF | 42E1
2690 | CLP1 | Cold load pick-up [CLPU] | HighStart ON | 42E2
2691 | CLP1 | Cold load pick-up [CLPU] | HighStart OFF | 42E3
2692 | CLP1 | Cold load pick-up [CLPU] | LoadNormal ON | 42E4
2693 | CLP1 | Cold load pick-up [CLPU] | LoadNormal OFF | 42E5
2694 | CLP1 | Cold load pick-up [CLPU] | Overcurrent ON | 42E6
2695 | CLP1 | Cold load pick-up [CLPU] | Overcurrent OFF | 42E7
2696 | CLP1 | Cold load pick-up [CLPU] | CLPUActivated ON | 42E8
2697 | CLP1 | Cold load pick-up [CLPU] | CLPUActivated OFF | 42E9
2698 | CLP1 | Cold load pick-up [CLPU] | Block ON | 42E10
2699 | CLP1 | Cold load pick-up [CLPU] | Block OFF | 42E11
2752 | FLX1 | Fault locator [21FL] | Flocator triggered On | 43E0
2753 | FLX1 | Fault locator [21FL] | Flocator triggered Off | 43E1
2754 | FLX1 | Fault locator [21FL] | Flocator Calculation On | 43E2
2755 | FLX1 | Fault locator [21FL] | Flocator Calculation Off | 43E3
2816 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Start ON | 44E0
2817 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Start OFF | 44E1
2818 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Retrip ON | 44E2
2819 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Retrip OFF | 44E3
2820 | CBF1 | Circuit breaker failure protection [50BF/52BF] | CBFP ON | 44E4
2821 | CBF1 | Circuit breaker failure protection [50BF/52BF] | CBFP OFF | 44E5
2822 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Block ON | 44E6
2823 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Block OFF | 44E7
2824 | CBF1 | Circuit breaker failure protection [50BF/52BF] | DO monitor On | 44E8
2825 | CBF1 | Circuit breaker failure protection [50BF/52BF] | DO monitor Off | 44E9
2826 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Signal On | 44E10
2827 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Signal Off | 44E11
2828 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Phase current On | 44E12
2829 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Phase current Off | 44E13
2830 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Res current On | 44E14
2831 | CBF1 | Circuit breaker failure protection [50BF/52BF] | Res current Off | 44E15
2880 | SYN1 | Synchrocheck [25] | SYN1 Blocked On | 45E0
2881 | SYN1 | Synchrocheck [25] | SYN1 Blocked Off | 45E1
2882 | SYN1 | Synchrocheck [25] | SYN1 Ok On | 45E2
2883 | SYN1 | Synchrocheck [25] | SYN1 Ok Off | 45E3
2884 | SYN1 | Synchrocheck [25] | SYN1 Bypass On | 45E4
2885 | SYN1 | Synchrocheck [25] | SYN1 Bypass Off | 45E5
2886 | SYN1 | Synchrocheck [25] | SYN1 Volt condition OK | 45E6
2887 | SYN1 | Synchrocheck [25] | SYN1 Volt cond not match | 45E7
2888 | SYN1 | Synchrocheck [25] | SYN1 Volt diff Ok | 45E8
2889 | SYN1 | Synchrocheck [25] | SYN1 Volt diff out of setting | 45E9
2890 | SYN1 | Synchrocheck [25] | SYN1 Angle diff Ok | 45E10
2891 | SYN1 | Synchrocheck [25] | SYN1 Angle diff out of setting | 45E11
2892 | SYN1 | Synchrocheck [25] | SYN1 Frequency diff Ok | 45E12
2893 | SYN1 | Synchrocheck [25] | SYN1 Frequency diff out of setting | 45E13
2894 | SYN1 | Synchrocheck [25] | SYN2 Blocked On | 45E14
2895 | SYN1 | Synchrocheck [25] | SYN2 Blocked Off | 45E15
2896 | SYN1 | Synchrocheck [25] | SYN2 Ok On | 45E16
2897 | SYN1 | Synchrocheck [25] | SYN2 Ok Off | 45E17
2898 | SYN1 | Synchrocheck [25] | SYN2 Bypass On | 45E18
2899 | SYN1 | Synchrocheck [25] | SYN2 Bypass Off | 45E19
2900 | SYN1 | Synchrocheck [25] | SYN2 Volt condition OK | 45E20
2901 | SYN1 | Synchrocheck [25] | SYN2 Volt cond not match | 45E21
2902 | SYN1 | Synchrocheck [25] | SYN2 Volt diff Ok | 45E22
2903 | SYN1 | Synchrocheck [25] | SYN2 Volt diff out of setting | 45E23
2904 | SYN1 | Synchrocheck [25] | SYN2 Angle diff Ok | 45E24
2905 | SYN1 | Synchrocheck [25] | SYN2 Angle diff out of setting | 45E25
2906 | SYN1 | Synchrocheck [25] | SYN2 Frequency diff Ok | 45E26
2907 | SYN1 | Synchrocheck [25] | SYN2 Frequency diff out of setting | 45E27
2908 | SYN1 | Synchrocheck [25] | SYN3 Blocked On | 45E28
2909 | SYN1 | Synchrocheck [25] | SYN3 Blocked Off | 45E29
2910 | SYN1 | Synchrocheck [25] | SYN3 Ok On | 45E30
2911 | SYN1 | Synchrocheck [25] | SYN3 Ok Off | 45E31
2912 | SYN1 | Synchrocheck [25] | SYN3 Bypass On | 45E32
2913 | SYN1 | Synchrocheck [25] | SYN3 Bypass Off | 45E33
2914 | SYN1 | Synchrocheck [25] | SYN3 Volt condition OK | 45E34
2915 | SYN1 | Synchrocheck [25] | SYN3 Volt cond not match | 45E35
2916 | SYN1 | Synchrocheck [25] | SYN3 Volt diff Ok | 45E36
2917 | SYN1 | Synchrocheck [25] | SYN3 Volt diff out of setting | 45E37
2918 | SYN1 | Synchrocheck [25] | SYN3 Angle diff Ok | 45E38
2919 | SYN1 | Synchrocheck [25] | SYN3 Angle diff out of setting | 45E39
2920 | SYN1 | Synchrocheck [25] | SYN3 Frequency diff Ok | 45E40
2921 | SYN1 | Synchrocheck [25] | SYN3 Frequency diff out of setting | 45E41
2922 | SYN1 | Synchrocheck [25] | SYN1 Switch On | 45E42
2923 | SYN1 | Synchrocheck [25] | SYN1 Switch Off | 45E43
2924 | SYN1 | Synchrocheck [25] | SYN2 Switch On | 45E44
2925 | SYN1 | Synchrocheck [25] | SYN2 Switch Off | 45E45
2926 | SYN1 | Synchrocheck [25] | SYN3 Switch On | 45E46
2927 | SYN1 | Synchrocheck [25] | SYN3 Switch Off | 45E47
2944 | OBJ1 | Object 1 | Object Intermediate | 46E0
2945 | OBJ1 | Object 1 | Object Open | 46E1
2946 | OBJ1 | Object 1 | Object Close | 46E2
2947 | OBJ1 | Object 1 | Object Bad | 46E3
2948 | OBJ1 | Object 1 | WD Intermediate | 46E4
2949 | OBJ1 | Object 1 | WD Out | 46E5
2950 | OBJ1 | Object 1 | WD in | 46E6
2951 | OBJ1 | Object 1 | WD Bad | 46E7
2952 | OBJ1 | Object 1 | Open Request On | 46E8
2953 | OBJ1 | Object 1 | Open Request Off | 46E9
2954 | OBJ1 | Object 1 | Open Command On | 46E10
2955 | OBJ1 | Object 1 | Open Command Off | 46E11
2956 | OBJ1 | Object 1 | Close Request On | 46E12
2957 | OBJ1 | Object 1 | Close Request Off | 46E13
2958 | OBJ1 | Object 1 | Close Command On | 46E14
2959 | OBJ1 | Object 1 | Close Command Off | 46E15
2960 | OBJ1 | Object 1 | Open Blocked On | 46E16
2961 | OBJ1 | Object 1 | Open Blocked Off | 46E17
2962 | OBJ1 | Object 1 | Close Blocked On | 46E18
2963 | OBJ1 | Object 1 | Close Blocked Off | 46E19
2964 | OBJ1 | Object 1 | Object Ready | 46E20
2965 | OBJ1 | Object 1 | Object Not Ready | 46E21
2966 | OBJ1 | Object 1 | Sync Ok | 46E22
2967 | OBJ1 | Object 1 | Sync Not Ok | 46E23
2968 | OBJ1 | Object 1 | Open Command Fail | 46E24
2969 | OBJ1 | Object 1 | Close Command Fail | 46E25
2970 | OBJ1 | Object 1 | Final trip On | 46E26
2971 | OBJ1 | Object 1 | Final trip Off | 46E27
2972 | OBJ1 | Object 1 | Contact Abrasion Alarm On | 46E28
2973 | OBJ1 | Object 1 | Contact Abrasion Alarm Off | 46E29
2974 | OBJ1 | Object 1 | Switch Operating Time Exceeded On | 46E30
2975 | OBJ1 | Object 1 | Switch Operating Time Exceeded Off | 46E31
2976 | OBJ1 | Object 1 | XCBR Loc On | 46E32
2977 | OBJ1 | Object 1 | XCBR Loc Off | 46E33
2978 | OBJ1 | Object 1 | XSWI Loc On | 46E34
2979 | OBJ1 | Object 2 | XSWI LOC Off | 46E35
3008 | OBJ2 | Object 2 | Object Intermediate | 47E0
3009 | OBJ2 | Object 2 | Object Open | 47E1
3010 | OBJ2 | Object 2 | Object Close | 47E2
3011 | OBJ2 | Object 2 | Object Bad | 47E3
3012 | OBJ2 | Object 2 | WD Intermediate | 47E4
3013 | OBJ2 | Object 2 | WD Out | 47E5
3014 | OBJ2 | Object 2 | WD in | 47E6
3015 | OBJ2 | Object 2 | WD Bad | 47E7
3016 | OBJ2 | Object 2 | Open Request On | 47E8
3017 | OBJ2 | Object 2 | Open Request Off | 47E9
3018 | OBJ2 | Object 2 | Open Command On | 47E10
3019 | OBJ2 | Object 2 | Open Command Off | 47E11
3020 | OBJ2 | Object 2 | Close Request On | 47E12
3021 | OBJ2 | Object 2 | Close Request Off | 47E13
3022 | OBJ2 | Object 2 | Close Command On | 47E14
3023 | OBJ2 | Object 2 | Close Command Off | 47E15
3024 | OBJ2 | Object 2 | Open Blocked On | 47E16
3025 | OBJ2 | Object 2 | Open Blocked Off | 47E17
3026 | OBJ2 | Object 2 | Close Blocked On | 47E18
3027 | OBJ2 | Object 2 | Close Blocked Off | 47E19
3028 | OBJ2 | Object 2 | Object Ready | 47E20
3029 | OBJ2 | Object 2 | Object Not Ready | 47E21
3030 | OBJ2 | Object 2 | Sync Ok | 47E22
3031 | OBJ2 | Object 2 | Sync Not Ok | 47E23
3032 | OBJ2 | Object 2 | Open Command Fail | 47E24
3033 | OBJ2 | Object 2 | Close Command Fail | 47E25
3034 | OBJ2 | Object 2 | Final trip On | 47E26
3035 | OBJ2 | Object 2 | Final trip Off | 47E27
3036 | OBJ2 | Object 2 | Contact Abrasion Alarm On | 47E28
3037 | OBJ2 | Object 2 | Contact Abrasion Alarm Off | 47E29
3038 | OBJ2 | Object 2 | Switch Operating Time Exceeded On | 47E30
3039 | OBJ2 | Object 2 | Switch Operating Time Exceeded Off | 47E31
3040 | OBJ2 | Object 2 | XCBR Loc On | 47E32
3041 | OBJ2 | Object 2 | XCBR Loc Off | 47E33
3042 | OBJ2 | Object 2 | XSWI Loc On | 47E34
3043 | OBJ2 | Object 2 | XSWI LOC Off | 47E35
3072 | OBJ3 | Object 3 | Object Intermediate | 48E0
3073 | OBJ3 | Object 3 | Object Open | 48E1
3074 | OBJ3 | Object 3 | Object Close | 48E2
3075 | OBJ3 | Object 3 | Object Bad | 48E3
3076 | OBJ3 | Object 3 | WD Intermediate | 48E4
3077 | OBJ3 | Object 3 | WD Out | 48E5
3078 | OBJ3 | Object 3 | WD in | 48E6
3079 | OBJ3 | Object 3 | WD Bad | 48E7
3080 | OBJ3 | Object 3 | Open Request On | 48E8
3081 | OBJ3 | Object 3 | Open Request Off | 48E9
3082 | OBJ3 | Object 3 | Open Command On | 48E10
3083 | OBJ3 | Object 3 | Open Command Off | 48E11
3084 | OBJ3 | Object 3 | Close Request On | 48E12
3085 | OBJ3 | Object 3 | Close Request Off | 48E13
3086 | OBJ3 | Object 3 | Close Command On | 48E14
3087 | OBJ3 | Object 3 | Close Command Off | 48E15
3088 | OBJ3 | Object 3 | Open Blocked On | 48E16
3089 | OBJ3 | Object 3 | Open Blocked Off | 48E17
3090 | OBJ3 | Object 3 | Close Blocked On | 48E18
3091 | OBJ3 | Object 3 | Close Blocked Off | 48E19
3092 | OBJ3 | Object 3 | Object Ready | 48E20
3093 | OBJ3 | Object 3 | Object Not Ready | 48E21
3094 | OBJ3 | Object 3 | Sync Ok | 48E22
3095 | OBJ3 | Object 3 | Sync Not Ok | 48E23
3096 | OBJ3 | Object 3 | Open Command Fail | 48E24
3097 | OBJ3 | Object 3 | Close Command Fail | 48E25
3098 | OBJ3 | Object 3 | Final trip On | 48E26
3099 | OBJ3 | Object 3 | Final trip Off | 48E27
3100 | OBJ3 | Object 3 | Contact Abrasion Alarm On | 48E28
3101 | OBJ3 | Object 3 | Contact Abrasion Alarm Off | 48E29
3102 | OBJ3 | Object 3 | Switch Operating Time Exceeded On | 48E30
3103 | OBJ3 | Object 3 | Switch Operating Time Exceeded Off | 48E31
3104 | OBJ3 | Object 3 | XCBR Loc On | 48E32
3105 | OBJ3 | Object 3 | XCBR Loc Off | 48E33
3106 | OBJ3 | Object 3 | XSWI Loc On | 48E34
3107 | OBJ3 | Object 3 | XSWI LOC Off | 48E35
3136 | OBJ4 | Object 4 | Object Intermediate | 49E0
3137 | OBJ4 | Object 4 | Object Open | 49E1
3138 | OBJ4 | Object 4 | Object Close | 49E2
3139 | OBJ4 | Object 4 | Object Bad | 49E3
3140 | OBJ4 | Object 4 | WD Intermediate | 49E4
3141 | OBJ4 | Object 4 | WD Out | 49E5
3142 | OBJ4 | Object 4 | WD in | 49E6
3143 | OBJ4 | Object 4 | WD Bad | 49E7
3144 | OBJ4 | Object 4 | Open Request On | 49E8
3145 | OBJ4 | Object 4 | Open Request Off | 49E9
3146 | OBJ4 | Object 4 | Open Command On | 49E10
3147 | OBJ4 | Object 4 | Open Command Off | 49E11
3148 | OBJ4 | Object 4 | Close Request On | 49E12
3149 | OBJ4 | Object 4 | Close Request Off | 49E13
3150 | OBJ4 | Object 4 | Close Command On | 49E14
3151 | OBJ4 | Object 4 | Close Command Off | 49E15
3152 | OBJ4 | Object 4 | Open Blocked On | 49E16
3153 | OBJ4 | Object 4 | Open Blocked Off | 49E17
3154 | OBJ4 | Object 4 | Close Blocked On | 49E18
3155 | OBJ4 | Object 4 | Close Blocked Off | 49E19
3156 | OBJ4 | Object 4 | Object Ready | 49E20
3157 | OBJ4 | Object 4 | Object Not Ready | 49E21
3158 | OBJ4 | Object 4 | Sync Ok | 49E22
3159 | OBJ4 | Object 4 | Sync Not Ok | 49E23
3160 | OBJ4 | Object 4 | Open Command Fail | 49E24
3161 | OBJ4 | Object 4 | Close Command Fail | 49E25
3162 | OBJ4 | Object 4 | Final trip On | 49E26
3163 | OBJ4 | Object 4 | Final trip Off | 49E27
3164 | OBJ4 | Object 4 | Contact Abrasion Alarm On | 49E28
3165 | OBJ4 | Object 4 | Contact Abrasion Alarm Off | 49E29
3166 | OBJ4 | Object 4 | Switch Operating Time Exceeded On | 49E30
3167 | OBJ4 | Object 4 | Switch Operating Time Exceeded Off | 49E31
3168 | OBJ4 | Object 4 | XCBR Loc On | 49E32
3169 | OBJ4 | Object 4 | XCBR Loc Off | 49E33
3170 | OBJ4 | Object 4 | XSWI Loc On | 49E34
3171 | OBJ4 | Object 4 | XSWI LOC Off | 49E35
3200 | OBJ5 | Object 5 | Object Intermediate | 50E0
3201 | OBJ5 | Object 5 | Object Open | 50E1
3202 | OBJ5 | Object 5 | Object Close | 50E2
3203 | OBJ5 | Object 5 | Object Bad | 50E3
3204 | OBJ5 | Object 5 | WD Intermediate | 50E4
3205 | OBJ5 | Object 5 | WD Out | 50E5
3206 | OBJ5 | Object 5 | WD in | 50E6
3207 | OBJ5 | Object 5 | WD Bad | 50E7
3208 | OBJ5 | Object 5 | Open Request On | 50E8
3209 | OBJ5 | Object 5 | Open Request Off | 50E9
3210 | OBJ5 | Object 5 | Open Command On | 50E10
3211 | OBJ5 | Object 5 | Open Command Off | 50E11
3212 | OBJ5 | Object 5 | Close Request On | 50E12
3213 | OBJ5 | Object 5 | Close Request Off | 50E13
3214 | OBJ5 | Object 5 | Close Command On | 50E14
3215 | OBJ5 | Object 5 | Close Command Off | 50E15
3216 | OBJ5 | Object 5 | Open Blocked On | 50E16
3217 | OBJ5 | Object 5 | Open Blocked Off | 50E17
3218 | OBJ5 | Object 5 | Close Blocked On | 50E18
3219 | OBJ5 | Object 5 | Close Blocked Off | 50E19
3220 | OBJ5 | Object 5 | Object Ready | 50E20
3221 | OBJ5 | Object 5 | Object Not Ready | 50E21
3222 | OBJ5 | Object 5 | Sync Ok | 50E22
3223 | OBJ5 | Object 5 | Sync Not Ok | 50E23
3224 | OBJ5 | Object 5 | Open Command Fail | 50E24
3225 | OBJ5 | Object 5 | Close Command Fail | 50E25
3226 | OBJ5 | Object 5 | Final trip On | 50E26
3227 | OBJ5 | Object 5 | Final trip Off | 50E27
3228 | OBJ5 | Object 5 | Contact Abrasion Alarm On | 50E28
3229 | OBJ5 | Object 5 | Contact Abrasion Alarm Off | 50E29
3230 | OBJ5 | Object 5 | Switch Operating Time Exceeded On | 50E30
3231 | OBJ5 | Object 5 | Switch Operating Time Exceeded Off | 50E31
3232 | OBJ5 | Object 5 | XCBR Loc On | 50E32
3233 | OBJ5 | Object 5 | XCBR Loc Off | 50E33
3234 | OBJ5 | Object 5 | XSWI Loc On | 50E34
3235 | OBJ5 | Object 5 | XSWI LOC Off | 50E35
3264 | HSHC | High speed input | HSI1 On | 51E0
3265 | HSHC | High speed input | HSI1 Off | 51E1
3266 | HSHC | High speed input | HSI2 On | 51E2
3267 | HSHC | High speed input | HSI2 Off | 51E3
3268 | HSHC | High speed input | HSI3 On | 51E4
3269 | HSHC | High speed input | HSI3 Off | 51E5
3270 | HSHC | High speed input | HSI4 On | 51E6
3271 | HSHC | High speed input | HSI4 Off | 51E7
3272 | HSHC | High speed input | HSI5 On | 51E8
3273 | HSHC | High speed input | HSI5 Off | 51E9
3274 | HSHC | High speed input | HSI6 On | 51E10
3275 | HSHC | High speed input | HSI6 Off | 51E11
3276 | HSHC | High speed input | HSI7 On | 51E12
3277 | HSHC | High speed input | HSI7 Off | 51E13
3278 | HSHC | High speed input | HSI8 On | 51E14
3279 | HSHC | High speed input | HSI8 Off | 51E15
3280 | HSHC | High speed input | HSI9 On | 51E16
3281 | HSHC | High speed input | HSI9 Off | 51E17
3282 | HSHC | High speed input | HSI10 On | 51E18
3283 | HSHC | High speed input | HSI10 Off | 51E19
3284 | HSHC | High speed input | HSI11 On | 51E20
3285 | HSHC | High speed input | HSI11 Off | 51E21
3286 | HSHC | High speed input | HSI12 On | 51E22
3287 | HSHC | High speed input | HSI12 Off | 51E23
3328 | CTS1 | Current transformer supervision | Alarm On | 52E0
3329 | CTS1 | Current transformer supervision | Alarm Off | 52E1
3330 | CTS1 | Current transformer supervision | Block On | 52E2
3331 | CTS1 | Current transformer supervision | Block Off | 52E3
3392 | VTS1 | Voltage transformer supervision [60] | Bus VT fail Start On | 53E0
3393 | VTS1 | Voltage transformer supervision [60] | Bus VT fail Start Off | 53E1
3394 | VTS1 | Voltage transformer supervision [60] | Bus VT fail Trip On | 53E2
3395 | VTS1 | Voltage transformer supervision [60] | Bus VT fail Trip Off | 53E3
3396 | VTS1 | Voltage transformer supervision [60] | Bus VT fail Block On | 53E4
3397 | VTS1 | Voltage transformer supervision [60] | Bus VT fail Block Off | 53E5
3398 | VTS1 | Voltage transformer supervision [60] | Line VT fail On | 53E6
3399 | VTS1 | Voltage transformer supervision [60] | Line VT fail Off | 53E7
3400 | VTS1 | Voltage transformer supervision [60] | Bus Fuse fail On | 53E8
3401 | VTS1 | Voltage transformer supervision [60] | Bus Fuse fail Off | 53E9
3402 | VTS1 | Voltage transformer supervision [60] | Line Fuse fail On | 53E10
3403 | VTS1 | Voltage transformer supervision [60] | Line Fuse fail Off | 53E11
3456 | CTS2 | Current transformer supervision 2 | Alarm On | 54E0
3457 | CTS2 | Current transformer supervision 3 | Alarm Off | 54E1
3458 | CTS2 | Current transformer supervision 4 | Block On | 54E2
3459 | CTS2 | Current transformer supervision 5 | Block Off | 54E3
3520 | THD1 | Total Harmonic Distortion function | THD Start Phase On | 55E0
3521 | THD1 | Total Harmonic Distortion function | THD Start Phase Off | 55E1
3522 | THD1 | Total Harmonic Distortion function | THD Start I01 On | 55E2
3523 | THD1 | Total Harmonic Distortion function | THD Start I01 Off | 55E3
3524 | THD1 | Total Harmonic Distortion function | THD Start I02 On | 55E4
3525 | THD1 | Total Harmonic Distortion function | THD Start I02 Off | 55E5
3526 | THD1 | Total Harmonic Distortion function | THD Alarm Phase On | 55E6
3527 | THD1 | Total Harmonic Distortion function | THD Alarm Phase Off | 55E7
3528 | THD1 | Total Harmonic Distortion function | THD Alarm I01 On | 55E8
3529 | THD1 | Total Harmonic Distortion function | THD Alarm I01 Off | 55E9
3530 | THD1 | Total Harmonic Distortion function | THD Alarm I02 On | 55E10
3531 | THD1 | Total Harmonic Distortion function | THD Alarm I02 Off | 55E11
3532 | THD1 | Total Harmonic Distortion function | Blocked On | 55E12
3533 | THD1 | Total Harmonic Distortion function | Blocked Off | 55E13
3584 | FSP1 | Frequent start protection | Alarm On | 56E0
3585 | FSP1 | Frequent start protection | Alarm Off | 56E1
3586 | FSP1 | Frequent start protection | Inhibit On | 56E2
3587 | FSP1 | Frequent start protection | Inhibit Off | 56E3
3588 | FSP1 | Frequent start protection | Blocked On | 56E4
3589 | FSP1 | Frequent start protection | Blocked Off | 56E5
3648 | LCR1 | Motor start/locked rotor monitor [48/14] | Max.Start time exceed On | 57E0
3649 | LCR1 | Motor start/locked rotor monitor [48/14] | Max.Start time exceed Off | 57E1
3650 | LCR1 | Motor start/locked rotor monitor [48/14] | Set start time exceed On | 57E2
3651 | LCR1 | Motor start/locked rotor monitor [48/14] | Set start time exceed Off | 57E3
3652 | LCR1 | Motor start/locked rotor monitor [48/14] | Speed Switch not received On | 57E4
3653 | LCR1 | Motor start/locked rotor monitor [48/14] | Speed Switch not received Off | 57E5
3654 | LCR1 | Motor start/locked rotor monitor [48/14] | Start On | 57E6
3655 | LCR1 | Motor start/locked rotor monitor [48/14] | Start Off | 57E7
3656 | LCR1 | Motor start/locked rotor monitor [48/14] | Set time Trip On | 57E8
3657 | LCR1 | Motor start/locked rotor monitor [48/14] | Set time Trip Off | 57E9
3658 | LCR1 | Motor start/locked rotor monitor [48/14] | Max cap Trip On | 57E10
3659 | LCR1 | Motor start/locked rotor monitor [48/14] | Max cap Trip Off | 57E11
3660 | LCR1 | Motor start/locked rotor monitor [48/14] | Blocked On | 57E12
3661 | LCR1 | Motor start/locked rotor monitor [48/14] | Blocked Off | 57E13
3712 | CBW1 | Circuit breaker wear monitor | CBWEAR1 Triggered | 58E0
3713 | CBW1 | Circuit breaker wear monitor | CBWEAR1 Alarm1 On | 58E1
3714 | CBW1 | Circuit breaker wear monitor | CBWEAR1 Alarm1 Off | 58E2
3715 | CBW1 | Circuit breaker wear monitor | CBWEAR1 Alarm2 On | 58E3
3716 | CBW1 | Circuit breaker wear monitor | CBWEAR1 Alarm2 Off | 58E4
3776 | MJP1 | Mechanical jam protection | Start ON | 59E0
3777 | MJP1 | Mechanical jam protection | Start OFF | 59E1
3778 | MJP1 | Mechanical jam protection | Trip ON | 59E2
3779 | MJP1 | Mechanical jam protection | Trip OFF | 59E3
3780 | MJP1 | Mechanical jam protection | Block ON | 59E4
3781 | MJP1 | Mechanical jam protection | Block OFF | 59E5
3840 | NUC1 | I< [37] Non-directional undercurrent | Start ON | 60E0
3841 | NUC1 | I< [37] Non-directional undercurrent | Start OFF | 60E1
3842 | NUC1 | I< [37] Non-directional undercurrent | Trip ON | 60E2
3843 | NUC1 | I< [37] Non-directional undercurrent | Trip OFF | 60E3
3844 | NUC1 | I< [37] Non-directional undercurrent | Block ON | 60E4
3845 | NUC1 | I< [37] Non-directional undercurrent | Block OFF | 60E5
3904 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Init On | 61E0
3905 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Init Off | 61E1
3906 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Block On | 61E2
3907 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Block Off | 61E3
3908 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Active On | 61E4
3909 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Active Off | 61E5
3910 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Trip On | 61E6
3911 | SOF1 | Switch-on-to-fault [SOTF] | SOTF Trip Off | 61E7
3968 | MST1 | Motor status monitoring | Motor Stopped On | 62E0
3969 | MST1 | Motor status monitoring | Motor Stopped Off | 62E1
3970 | MST1 | Motor status monitoring | Motor Starting On | 62E2
3971 | MST1 | Motor status monitoring | Motor Starting Off | 62E3
3972 | MST1 | Motor status monitoring | Motor Running On | 62E4
3973 | MST1 | Motor status monitoring | Motor Running Off | 62E5
3974 | MST1 | Motor status monitoring | Motor Stalled On | 62E6
3975 | MST1 | Motor status monitoring | Motor Stalled Off | 62E7
3976 | MST1 | Motor status monitoring | Load not symm On | 62E8
3977 | MST1 | Motor status monitoring | Load not symm Off | 62E9
3978 | MST1 | Motor status monitoring | Load normal On | 62E10
3979 | MST1 | Motor status monitoring | Load normal Off | 62E11
3980 | MST1 | Motor status monitoring | Overload On | 62E12
3981 | MST1 | Motor status monitoring | Overload Off | 62E13
3982 | MST1 | Motor status monitoring | High Overcurrent On | 62E14
3983 | MST1 | Motor status monitoring | High Overcurrent Off | 62E15
4032 | AR1 | Auto-recloser [79] | AR Ready On | 63E0
4033 | AR1 | Auto-recloser [79] | AR Ready Off | 63E1
4034 | AR1 | Auto-recloser [79] | AR Locked Reset | 63E2
4035 | AR1 | Auto-recloser [79] | AR Reclosing request rejected On | 63E3
4036 | AR1 | Auto-recloser [79] | AR Reclosing request rejected Off | 63E4
4037 | AR1 | Auto-recloser [79] | AR Reclosing request On | 63E5
4038 | AR1 | Auto-recloser [79] | AR Reclosing request Off | 63E6
4039 | AR1 | Auto-recloser [79] | User Operated Obj AR halted and reset | 63E7
4040 | AR1 | Auto-recloser [79] | Object failure, AR locked | 63E8
4041 | AR1 | Auto-recloser [79] | Shot Failed | 63E9
4042 | AR1 | Auto-recloser [79] | AR cycle end due to Discr request | 63E10
4043 | AR1 | Auto-recloser [79] | AR Shot Clear | 63E11
4044 | AR1 | Auto-recloser [79] | Object Close Request On | 63E12
4045 | AR1 | Auto-recloser [79] | Object Open Request | 63E13
4046 | AR1 | Auto-recloser [79] | Inhibit condition On | 63E14
4047 | AR1 | Auto-recloser [79] | Inhibit condition Off | 63E15
4048 | AR1 | Auto-recloser [79] | Locking condition On | 63E16
4049 | AR1 | Auto-recloser [79] | Locking condition Off | 63E17
4050 | AR1 | Auto-recloser [79] | Reserved | 63E18
4051 | AR1 | Auto-recloser [79] | AR1 Request On | 63E19
4052 | AR1 | Auto-recloser [79] | AR1 Request Off | 63E20
4053 | AR1 | Auto-recloser [79] | AR2 Request On | 63E21
4054 | AR1 | Auto-recloser [79] | AR2 Request Off | 63E22
4055 | AR1 | Auto-recloser [79] | AR3 Request On | 63E23
4056 | AR1 | Auto-recloser [79] | AR3 Request Off | 63E24
4057 | AR1 | Auto-recloser [79] | AR4 Request On | 63E25
4058 | AR1 | Auto-recloser [79] | AR4 Request Off | 63E26
4059 | AR1 | Auto-recloser [79] | AR5 Request On | 63E27
4060 | AR1 | Auto-recloser [79] | AR5 Request Off | 63E28
4061 | AR1 | Auto-recloser [79] | Critical Request On | 63E29
4062 | AR1 | Auto-recloser [79] | Critical Request Off | 63E30
4063 | AR1 | Auto-recloser [79] | AR Running On | 63E31
4064 | AR1 | Auto-recloser [79] | AR Running Off | 63E32
4065 | AR1 | Auto-recloser [79] | Shot 1 Execute On | 63E33
4066 | AR1 | Auto-recloser [79] | Shot 1 Execute Off | 63E34
4067 | AR1 | Auto-recloser [79] | Shot 2 Execute On | 63E35
4068 | AR1 | Auto-recloser [79] | Shot 2 Execute Off | 63E36
4069 | AR1 | Auto-recloser [79] | Shot 3 Execute On | 63E37
4070 | AR1 | Auto-recloser [79] | Shot 3 Execute Off | 63E38
4071 | AR1 | Auto-recloser [79] | Shot 4 Execute On | 63E39
4072 | AR1 | Auto-recloser [79] | Shot 4 Execute Off | 63E40
4073 | AR1 | Auto-recloser [79] | Shot 5 Execute On | 63E41
4074 | AR1 | Auto-recloser [79] | Shot 5 Execute Off | 63E42
4075 | AR1 | Auto-recloser [79] | Seq Finished Final Trip Armed On | 63E43
4076 | AR1 | Auto-recloser [79] | Final Trip Executed | 63E44
4077 | AR1 | Auto-recloser [79] | Lock Out Time On | 63E45
4078 | AR1 | Auto-recloser [79] | Lock Out Time Off | 63E46
4079 | AR1 | Auto-recloser [79] | General Reclaim time On | 63E47
4080 | AR1 | Auto-recloser [79] | General Reclaim time Off | 63E48
4081 | AR1 | Auto-recloser [79] | Shot Start Time On | 63E49
4082 | AR1 | Auto-recloser [79] | Shot Start Time Off | 63E50
4083 | AR1 | Auto-recloser [79] | Dead Time On | 63E51
4084 | AR1 | Auto-recloser [79] | Dead Time Off | 63E52
4085 | AR1 | Auto-recloser [79] | Arc Discr Time On | 63E53
4086 | AR1 | Auto-recloser [79] | Arc Discr Time Off | 63E54
4087 | AR1 | Auto-recloser [79] | Shot Reclaim Time On | 63E55
4088 | AR1 | Auto-recloser [79] | Shot Reclaim Time Off | 63E56
4089 | AR1 | Auto-recloser [79] | Seq. finished Off | 63E57
4090 | AR1 | Auto-recloser [79] | Final Trip Executed Off | 63E58
4091 | AR1 | Auto-recloser [79] | Object Close Request Off | 63E59
4092 | AR1 | Auto-recloser [79] | AR On | 63E60
4093 | AR1 | Auto-recloser [79] | AR Off | 63E61
4094 | AR1 | Auto-recloser [79] | AR Running (DT) On | 63E62
4095 | AR1 | Auto-recloser [79] | AR Running (DT) Off | 63E63
4096 | DR1 | Disturbance recorder | Recorder triggered On | 64E0
4097 | DR1 | Disturbance recorder | Recorder triggered Off | 64E1
4098 | DR1 | Disturbance recorder | Recorder memory cleared | 64E2
4099 | DR1 | Disturbance recorder | Oldest record cleared | 64E3
4100 | DR1 | Disturbance recorder | Recorder memory full On | 64E4
4101 | DR1 | Disturbance recorder | Recorder memory full Off | 64E5
4102 | DR1 | Disturbance recorder | Recording On | 64E6
4103 | DR1 | Disturbance recorder | Recording Off | 64E7
4104 | DR1 | Disturbance recorder | Storing recording On | 64E8
4105 | DR1 | Disturbance recorder | Storing recording Off | 64E9
4106 | DR1 | Disturbance recorder | Newest record cleared | 64E10
4160 | SGS | Setting groups | SG2 Enabled | 65E0
4161 | SGS | Setting groups | SG2 Disabled | 65E1
4162 | SGS | Setting groups | SG3 Enabled | 65E2
4163 | SGS | Setting groups | SG3 Disabled | 65E3
4164 | SGS | Setting groups | SG4 Enabled | 65E4
4165 | SGS | Setting groups | SG4 Disabled | 65E5
4166 | SGS | Setting groups | SG5 Enabled | 65E6
4167 | SGS | Setting groups | SG5 Disabled | 65E7
4168 | SGS | Setting groups | SG6 Enabled | 65E8
4169 | SGS | Setting groups | SG6 Disabled | 65E9
4170 | SGS | Setting groups | SG7 Enabled | 65E10
4171 | SGS | Setting groups | SG7 Disabled | 65E11
4172 | SGS | Setting groups | SG8 Enabled | 65E12
4173 | SGS | Setting groups | SG8 Disabled | 65E13
4174 | SGS | Setting groups | SG1 Request On | 65E14
4175 | SGS | Setting groups | SG1 Request Off | 65E15
4176 | SGS | Setting groups | SG2 Request On | 65E16
4177 | SGS | Setting groups | SG2 Request Off | 65E17
4178 | SGS | Setting groups | SG3 Request On | 65E18
4179 | SGS | Setting groups | SG3 Request Off | 65E19
4180 | SGS | Setting groups | SG4 Request On | 65E20
4181 | SGS | Setting groups | SG4 Request Off | 65E21
4182 | SGS | Setting groups | SG5 Request On | 65E22
4183 | SGS | Setting groups | SG5 Request Off | 65E23
4184 | SGS | Setting groups | SG6 Request On | 65E24
4185 | SGS | Setting groups | SG6 Request Off | 65E25
4186 | SGS | Setting groups | SG7 Request On | 65E26
4187 | SGS | Setting groups | SG7 Request Off | 65E27
4188 | SGS | Setting groups | SG8 Request On | 65E28
4189 | SGS | Setting groups | SG8 Request Off | 65E29
4190 | SGS | Setting groups | Remote Change SG Req On | 65E30
4191 | SGS | Setting groups | Remote Change SG Req Off | 65E31
4192 | SGS | Setting groups | Local Change SG Req On | 65E32
4193 | SGS | Setting groups | Local Change SG Req On | 65E33
4194 | SGS | Setting groups | Force Change SG On | 65E34
4195 | SGS | Setting groups | Force Change SG Off | 65E35
4196 | SGS | Setting groups | SG Req. Fail Not configured SG On | 65E36
4197 | SGS | Setting groups | SG Req. Fail Not configured SG On | 65E37
4198 | SGS | Setting groups | Force Req. Fail Force not On | 65E38
4199 | SGS | Setting groups | Force Req. Fail Off | 65E39
4200 | SGS | Setting groups | SG Req. Fail Lower priority Req. On | 65E40
4201 | SGS | Setting groups | SG Req. Fail Lower priority Req. Off | 65E41
4202 | SGS | Setting groups | SG1 Active On | 65E42
4203 | SGS | Setting groups | SG1 Active Off | 65E43
4204 | SGS | Setting groups | SG2 Active On | 65E44
4205 | SGS | Setting groups | SG2 Active Off | 65E45
4206 | SGS | Setting groups | SG3 Active On | 65E46
4207 | SGS | Setting groups | SG3 Active Off | 65E47
4208 | SGS | Setting groups | SG4 Active On | 65E48
4209 | SGS | Setting groups | SG4 Active Off | 65E49
4210 | SGS | Setting groups | SG5 Active On | 65E50
4211 | SGS | Setting groups | SG5 Active Off | 65E51
4212 | SGS | Setting groups | SG6 Active On | 65E52
4213 | SGS | Setting groups | SG6 Active Off | 65E53
4214 | SGS | Setting groups | SG7 Active On | 65E54
4215 | SGS | Setting groups | SG7 Active Off | 65E55
4216 | SGS | Setting groups | SG8 Active On | 65E56
4217 | SGS | Setting groups | SG8 Active Off | 65E57
4224 | REF1 | I0d> [87N] Restricted earth fault / Cable end differential | REF Trip On | 66E0
4225 | REF1 | I0d> [87N] Restricted earth fault / Cable end differential | REF Trip Off | 66E1
4226 | REF1 | I0d> [87N] Restricted earth fault / Cable end differential | REF Block On | 66E2
4227 | REF1 | I0d> [87N] Restricted earth fault / Cable end differential | REF Block Off | 66E3
4288 | TOLF1 | TF> [49F] Line thermal overload protection | Alarm1 On | 67E0
4289 | TOLF1 | TF> [49F] Line thermal overload protection | Alarm1 Off | 67E1
4290 | TOLF1 | TF> [49F] Line thermal overload protection | Alarm2 On | 67E2
4291 | TOLF1 | TF> [49F] Line thermal overload protection | Alarm2 Off | 67E3
4292 | TOLF1 | TF> [49F] Line thermal overload protection | Inhibit On | 67E4
4293 | TOLF1 | TF> [49F] Line thermal overload protection | Inhibit Off | 67E5
4294 | TOLF1 | TF> [49F] Line thermal overload protection | Trip On | 67E6
4295 | TOLF1 | TF> [49F] Line thermal overload protection | Trip Off | 67E7
4296 | TOLF1 | TF> [49F] Line thermal overload protection | Block On | 67E8
4297 | TOLF1 | TF> [49F] Line thermal overload protection | Block Off | 67E9
4352 | TOLM1 | TM> [49M] Machine thermal overload protection | Alarm1 On | 68E0
4353 | TOLM1 | TM> [49M] Machine thermal overload protection | Alarm1 Off | 68E1
4354 | TOLM1 | TM> [49M] Machine thermal overload protection | Alarm2 On | 68E2
4355 | TOLM1 | TM> [49M] Machine thermal overload protection | Alarm2 Off | 68E3
4356 | TOLM1 | TM> [49M] Machine thermal overload protection | Inhibit On | 68E4
4357 | TOLM1 | TM> [49M] Machine thermal overload protection | Inhibit Off | 68E5
4358 | TOLM1 | TM> [49M] Machine thermal overload protection | Trip On | 68E6
4359 | TOLM1 | TM> [49M] Machine thermal overload protection | Trip Off | 68E7
4360 | TOLM1 | TM> [49M] Machine thermal overload protection | Block On | 68E8
4361 | TOLM1 | TM> [49M] Machine thermal overload protection | Block Off | 68E9
4416 | RTD1 | Resistance temperature detectors | S1 Alarm1 On | 69E0
4417 | RTD1 | Resistance temperature detectors | S1 Alarm1 Off | 69E1
4418 | RTD1 | Resistance temperature detectors | S1 Alarm2 On | 69E2
4419 | RTD1 | Resistance temperature detectors | S1 Alarm2 Off | 69E3
4420 | RTD1 | Resistance temperature detectors | S2 Alarm1 On | 69E4
4421 | RTD1 | Resistance temperature detectors | S2 Alarm1 Off | 69E5
4422 | RTD1 | Resistance temperature detectors | S2 Alarm2 On | 69E6
4423 | RTD1 | Resistance temperature detectors | S2 Alarm2 Off | 69E7
4424 | RTD1 | Resistance temperature detectors | S3 Alarm1 On | 69E8
4425 | RTD1 | Resistance temperature detectors | S3 Alarm1 Off | 69E9
4426 | RTD1 | Resistance temperature detectors | S3 Alarm2 On | 69E10
4427 | RTD1 | Resistance temperature detectors | S3 Alarm2 Off | 69E11
4428 | RTD1 | Resistance temperature detectors | S4 Alarm1 On | 69E12
4429 | RTD1 | Resistance temperature detectors | S4 Alarm1 Off | 69E13
4430 | RTD1 | Resistance temperature detectors | S4 Alarm2 On | 69E14
4431 | RTD1 | Resistance temperature detectors | S4 Alarm2 Off | 69E15
4432 | RTD1 | Resistance temperature detectors | S5 Alarm1 On | 69E16
4433 | RTD1 | Resistance temperature detectors | S5 Alarm1 Off | 69E17
4434 | RTD1 | Resistance temperature detectors | S5 Alarm2 On | 69E18
4435 | RTD1 | Resistance temperature detectors | S5 Alarm2 Off | 69E19
4436 | RTD1 | Resistance temperature detectors | S6 Alarm1 On | 69E20
4437 | RTD1 | Resistance temperature detectors | S6 Alarm1 Off | 69E21
4438 | RTD1 | Resistance temperature detectors | S6 Alarm2 On | 69E22
4439 | RTD1 | Resistance temperature detectors | S6 Alarm2 Off | 69E23
4440 | RTD1 | Resistance temperature detectors | S7 Alarm1 On | 69E24
4441 | RTD1 | Resistance temperature detectors | S7 Alarm1 Off | 69E25
4442 | RTD1 | Resistance temperature detectors | S7 Alarm2 On | 69E26
4443 | RTD1 | Resistance temperature detectors | S7 Alarm2 Off | 69E27
4444 | RTD1 | Resistance temperature detectors | S8 Alarm1 On | 69E28
4445 | RTD1 | Resistance temperature detectors | S8 Alarm1 Off | 69E29
4446 | RTD1 | Resistance temperature detectors | S8 Alarm2 On | 69E30
4447 | RTD1 | Resistance temperature detectors | S8 Alarm2 Off | 69E31
4448 | RTD1 | Resistance temperature detectors | S9 Alarm1 On | 69E32
4449 | RTD1 | Resistance temperature detectors | S9 Alarm1 Off | 69E33
4450 | RTD1 | Resistance temperature detectors | S9 Alarm2 On | 69E34
4451 | RTD1 | Resistance temperature detectors | S9 Alarm2 Off | 69E35
4452 | RTD1 | Resistance temperature detectors | S10 Alarm1 On | 69E36
4453 | RTD1 | Resistance temperature detectors | S10 Alarm1 Off | 69E37
4454 | RTD1 | Resistance temperature detectors | S10 Alarm2 On | 69E38
4455 | RTD1 | Resistance temperature detectors | S10 Alarm2 Off | 69E39
4456 | RTD1 | Resistance temperature detectors | S11 Alarm1 On | 69E40
4457 | RTD1 | Resistance temperature detectors | S11 Alarm1 Off | 69E41
4458 | RTD1 | Resistance temperature detectors | S11 Alarm2 On | 69E42
4459 | RTD1 | Resistance temperature detectors | S11 Alarm2 Off | 69E43
4460 | RTD1 | Resistance temperature detectors | S12 Alarm1 On | 69E44
4461 | RTD1 | Resistance temperature detectors | S12 Alarm1 Off | 69E45
4462 | RTD1 | Resistance temperature detectors | S12 Alarm2 On | 69E46
4463 | RTD1 | Resistance temperature detectors | S12 Alarm2 Off | 69E47
4464 | RTD1 | Resistance temperature detectors | S13 Alarm1 On | 69E48
4465 | RTD1 | Resistance temperature detectors | S13 Alarm1 Off | 69E49
4466 | RTD1 | Resistance temperature detectors | S13 Alarm2 On | 69E50
4467 | RTD1 | Resistance temperature detectors | S13 Alarm2 Off | 69E51
4468 | RTD1 | Resistance temperature detectors | S14 Alarm1 On | 69E52
4469 | RTD1 | Resistance temperature detectors | S14 Alarm1 Off | 69E53
4470 | RTD1 | Resistance temperature detectors | S14 Alarm2 On | 69E54
4471 | RTD1 | Resistance temperature detectors | S14 Alarm2 Off | 69E55
4472 | RTD1 | Resistance temperature detectors | S15 Alarm1 On | 69E56
4473 | RTD1 | Resistance temperature detectors | S15 Alarm1 Off | 69E57
4474 | RTD1 | Resistance temperature detectors | S15 Alarm2 On | 69E58
4475 | RTD1 | Resistance temperature detectors | S15 Alarm2 Off | 69E59
4476 | RTD1 | Resistance temperature detectors | S16 Alarm1 On | 69E60
4477 | RTD1 | Resistance temperature detectors | S16 Alarm1 Off | 69E61
4478 | RTD1 | Resistance temperature detectors | S16 Alarm2 On | 69E62
4479 | RTD1 | Resistance temperature detectors | S16 Alarm2 Off | 69E63
4480 | RTD2 | Resistance temperature detectors | S1 Meas Ok | 70E0
4481 | RTD2 | Resistance temperature detectors | S1 Meas Invalid | 70E1
4482 | RTD2 | Resistance temperature detectors | S2 Meas Ok | 70E2
4483 | RTD2 | Resistance temperature detectors | S2 Meas Invalid | 70E3
4484 | RTD2 | Resistance temperature detectors | S3 Meas Ok | 70E4
4485 | RTD2 | Resistance temperature detectors | S3 Meas Invalid | 70E5
4486 | RTD2 | Resistance temperature detectors | S4 Meas Ok | 70E6
4487 | RTD2 | Resistance temperature detectors | S4 Meas Invalid | 70E7
4488 | RTD2 | Resistance temperature detectors | S5 Meas Ok | 70E8
4489 | RTD2 | Resistance temperature detectors | S5 Meas Invalid | 70E9
4490 | RTD2 | Resistance temperature detectors | S6 Meas Ok | 70E10
4491 | RTD2 | Resistance temperature detectors | S6 Meas Invalid | 70E11
4492 | RTD2 | Resistance temperature detectors | S7 Meas Ok | 70E12
4493 | RTD2 | Resistance temperature detectors | S7 Meas Invalid | 70E13
4494 | RTD2 | Resistance temperature detectors | S8 Meas Ok | 70E14
4495 | RTD2 | Resistance temperature detectors | S8 Meas Invalid | 70E15
4496 | RTD2 | Resistance temperature detectors | S9 Meas Ok | 70E16
4497 | RTD2 | Resistance temperature detectors | S9 Meas Invalid | 70E17
4498 | RTD2 | Resistance temperature detectors | S10 Meas Ok | 70E18
4499 | RTD2 | Resistance temperature detectors | S10 Meas Invalid | 70E19
4500 | RTD2 | Resistance temperature detectors | S11 Meas Ok | 70E20
4501 | RTD2 | Resistance temperature detectors | S11 Meas Invalid | 70E21
4502 | RTD2 | Resistance temperature detectors | S12 Meas Ok | 70E22
4503 | RTD2 | Resistance temperature detectors | S12 Meas Invalid | 70E23
4504 | RTD2 | Resistance temperature detectors | S13 Meas Ok | 70E24
4505 | RTD2 | Resistance temperature detectors | S13 Meas Invalid | 70E25
4506 | RTD2 | Resistance temperature detectors | S14 Meas Ok | 70E26
4507 | RTD2 | Resistance temperature detectors | S14 Meas Invalid | 70E27
4508 | RTD2 | Resistance temperature detectors | S15 Meas Ok | 70E28
4509 | RTD2 | Resistance temperature detectors | S15 Meas Invalid | 70E29
4510 | RTD2 | Resistance temperature detectors | S16 Meas Ok | 70E30
4511 | RTD2 | Resistance temperature detectors | S16 Meas Invalid | 70E31
4544 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idb> Trip On | 71E0
4545 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idb> Trip Off | 71E1
4546 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idb> Blocked (ext) On | 71E2
4547 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idb> Blocked (ext) Off | 71E3
4548 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idi> Trip On | 71E4
4549 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idi> Trip Off | 71E5
4550 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idi> Blocked (ext) On | 71E6
4551 | DIF1 | Idb> [87T/87N/87G] Transformer differential | Idi> Blocked (ext) Off | 71E7
4552 | DIF1 | Idb> [87T/87N/87G] Transformer differential | 2.nd Harmonic Block On | 71E8
4553 | DIF1 | Idb> [87T/87N/87G] Transformer differential | 2.nd Harmonic Block Off | 71E9
4554 | DIF1 | Idb> [87T/87N/87G] Transformer differential | 5.th Harmonic Block On | 71E10
4555 | DIF1 | Idb> [87T/87N/87G] Transformer differential | 5.th Harmonic Block Off | 71E11
4556 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L1 2.nd harm On | 71E12
4557 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L1 2.nd harm Off | 71E13
4558 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L2 2.nd harm On | 71E14
4559 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L2 2.nd harm Off | 71E15
4560 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L3 2.nd harm On | 71E16
4561 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L3 2.nd harm Off | 71E17
4562 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L1 5.th harm On | 71E18
4563 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L1 5.th harm Off | 71E19
4564 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L2 5.th harm On | 71E20
4565 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L2 5.th harm Off | 71E21
4566 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L3 5.th harm On | 71E22
4567 | DIF1 | Idb> [87T/87N/87G] Transformer differential | L3 5.th harm Off | 71E23
4568 | DIF1 | Idb> [87T/87N/87G] Transformer differential | HV I0d> Block On | 71E24
4569 | DIF1 | Idb> [87T/87N/87G] Transformer differential | HV I0d> Block Off | 71E25
4570 | DIF1 | Idb> [87T/87N/87G] Transformer differential | HV I0d> Trip On | 71E26
4571 | DIF1 | Idb> [87T/87N/87G] Transformer differential | HV I0d> Trip Off | 71E27
4572 | DIF1 | Idb> [87T/87N/87G] Transformer differential | LV I0d> Block On | 71E28
4573 | DIF1 | Idb> [87T/87N/87G] Transformer differential | LV I0d> Block Off | 71E29
4574 | DIF1 | Idb> [87T/87N/87G] Transformer differential | LV I0d> Trip On | 71E30
4575 | DIF1 | Idb> [87T/87N/87G] Transformer differential | LV I0d> Trip Off | 71E31
4608 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Light/No load On | 72E0
4609 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Light/No load Off | 72E1
4610 | TRF1 | Idb> [87T/87N/87G] Transformer differential | HV side inrush On | 72E2
4611 | TRF1 | Idb> [87T/87N/87G] Transformer differential | HV side inrush Off | 72E3
4612 | TRF1 | Idb> [87T/87N/87G] Transformer differential | LV side inrush On | 72E4
4613 | TRF1 | Idb> [87T/87N/87G] Transformer differential | LV side inrush Off | 72E5
4614 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Load normal On | 72E6
4615 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Load normal Off | 72E7
4616 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Overloading On | 72E8
4617 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Overloading Off | 72E9
4618 | TRF1 | Idb> [87T/87N/87G] Transformer differential | High overload On | 72E10
4619 | TRF1 | Idb> [87T/87N/87G] Transformer differential | High overload Off | 72E11
4620 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Setting changes, calculating new trafo data | 72E12
4621 | TRF1 | Idb> [87T/87N/87G] Transformer differential | Calculation finished, possible restart | 72E13
4672 | TOLT1 | TT> [49T] Transformer thermal overload | Alarm1 On | 73E0
4673 | TOLT1 | TT> [49T] Transformer thermal overload | Alarm1 Off | 73E1
4674 | TOLT1 | TT> [49T] Transformer thermal overload | Alarm2 On | 73E2
4675 | TOLT1 | TT> [49T] Transformer thermal overload | Alarm2 Off | 73E3
4676 | TOLT1 | TT> [49T] Transformer thermal overload | Inhibit On | 73E4
4677 | TOLT1 | TT> [49T] Transformer thermal overload | Inhibit Off | 73E5
4678 | TOLT1 | TT> [49T] Transformer thermal overload | Trip On | 73E6
4679 | TOLT1 | TT> [49T] Transformer thermal overload | Trip Off | 73E7
4680 | TOLT1 | TT> [49T] Transformer thermal overload | Block On | 73E8
4681 | TOLT1 | TT> [49T] Transformer thermal overload | Block Off | 73E9
4736 | ARC1 | IArc> [50Arc] Arc fault protection | Zone1 Trip On | 74E0
4737 | ARC1 | IArc> [50Arc] Arc fault protection | Zone1 Trip Off | 74E1
4738 | ARC1 | IArc> [50Arc] Arc fault protection | Zone1 Block On | 74E2
4739 | ARC1 | IArc> [50Arc] Arc fault protection | Zone1 BlockOff | 74E3
4740 | ARC1 | IArc> [50Arc] Arc fault protection | Zone2 Trip On | 74E4
4741 | ARC1 | IArc> [50Arc] Arc fault protection | Zone2 Trip Off | 74E5
4742 | ARC1 | IArc> [50Arc] Arc fault protection | Zone2 Block On | 74E6
4743 | ARC1 | IArc> [50Arc] Arc fault protection | Zone2 BlockOff | 74E7
4744 | ARC1 | IArc> [50Arc] Arc fault protection | Zone3 Trip On | 74E8
4745 | ARC1 | IArc> [50Arc] Arc fault protection | Zone3 Trip Off | 74E9
4746 | ARC1 | IArc> [50Arc] Arc fault protection | Zone3 Block On | 74E10
4747 | ARC1 | IArc> [50Arc] Arc fault protection | Zone3 BlockOff | 74E11
4748 | ARC1 | IArc> [50Arc] Arc fault protection | Zone4 Trip On | 74E12
4749 | ARC1 | IArc> [50Arc] Arc fault protection | Zone4 Trip Off | 74E13
4750 | ARC1 | IArc> [50Arc] Arc fault protection | Zone4 Block On | 74E14
4751 | ARC1 | IArc> [50Arc] Arc fault protection | Zone4 BlockOff | 74E15
4752 | ARC1 | IArc> [50Arc] Arc fault protection | Ph Current Blocked On | 74E16
4753 | ARC1 | IArc> [50Arc] Arc fault protection | Ph Current Blocked Off | 74E17
4754 | ARC1 | IArc> [50Arc] Arc fault protection | Ph Current Start On | 74E18
4755 | ARC1 | IArc> [50Arc] Arc fault protection | Ph Current Start Off | 74E19
4756 | ARC1 | IArc> [50Arc] Arc fault protection | Res Current Blocked On | 74E20
4757 | ARC1 | IArc> [50Arc] Arc fault protection | Res Current Blocked Off | 74E21
4758 | ARC1 | IArc> [50Arc] Arc fault protection | Res Current Start On | 74E22
4759 | ARC1 | IArc> [50Arc] Arc fault protection | Res Current Start Off | 74E23
4760 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 1 Light On | 74E24
4761 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 1 Light Off | 74E25
4762 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 1 Pressure On | 74E26
4763 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 1 Pressure Off | 74E27
4764 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 2 Light On | 74E28
4765 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 2 Light Off | 74E29
4766 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 2 Pressure On | 74E30
4767 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 2 Pressure Off | 74E31
4768 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 3 Light On | 74E32
4769 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 3 Light Off | 74E33
4770 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 3 Pressure On | 74E34
4771 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 3 Pressure Off | 74E35
4772 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 4 Light On | 74E36
4773 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 4 Light Off | 74E37
4774 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 4 Pressure On | 74E38
4775 | ARC1 | IArc> [50Arc] Arc fault protection | Channel 4 Pressure Off | 74E39
4776 | ARC1 | IArc> [50Arc] Arc fault protection | DI Signal On | 74E40
4777 | ARC1 | IArc> [50Arc] Arc fault protection | DI Signal Off | 74E41
4778 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 1 Fault On | 74E42
4779 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 1 Fault Off | 74E43
4780 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 2 Fault On | 74E44
4781 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 2 Fault Off | 74E45
4782 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 3 Fault On | 74E46
4783 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 3 Fault Off | 74E47
4784 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 4 Fault On | 74E48
4785 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 Sensor 4 Fault Off | 74E49
4786 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 I/O-unit Fault On | 74E50
4787 | ARC1 | IArc> [50Arc] Arc fault protection | I/I0 Arc> Card 1 I/O-unit Fault On | 74E51
4800 | DOC1 | Idir> [67] Directional overcurrent | Start ON | 75E0
4801 | DOC1 | Idir> [67] Directional overcurrent | Start OFF | 75E1
4802 | DOC1 | Idir> [67] Directional overcurrent | Trip ON | 75E2
4803 | DOC1 | Idir> [67] Directional overcurrent | Trip OFF | 75E3
4804 | DOC1 | Idir> [67] Directional overcurrent | Block ON | 75E4
4805 | DOC1 | Idir> [67] Directional overcurrent | Block OFF | 75E5
4806 | DOC1 | Idir> [67] Directional overcurrent | No voltage, Protection locked On | 75E6
4807 | DOC1 | Idir> [67] Directional overcurrent | Voltage measurable, Protection locked Off | 75E7
4808 | DOC1 | Idir> [67] Directional overcurrent | Measuring live angle On | 75E8
4809 | DOC1 | Idir> [67] Directional overcurrent | Measuring live angle Off | 75E9
4810 | DOC1 | Idir> [67] Directional overcurrent | Using voltmem On | 75E10
4811 | DOC1 | Idir> [67] Directional overcurrent | Using voltmem Off | 75E11
4813 | DOC1 | Idir> [67] Directional overcurrent | Voltage mem Off Emergency non dir On | 75E13
4814 | DOC1 | Idir> [67] Directional overcurrent | Voltage mem Off Emergency non dir Off | 75E14
4864 | DOC2 | Idir>> [67] Directional overcurrent | Start ON | 76E0
4865 | DOC2 | Idir>> [67] Directional overcurrent | Start OFF | 76E1
4866 | DOC2 | Idir>> [67] Directional overcurrent | Trip ON | 76E2
4867 | DOC2 | Idir>> [67] Directional overcurrent | Trip OFF | 76E3
4868 | DOC2 | Idir>> [67] Directional overcurrent | Block ON | 76E4
4869 | DOC2 | Idir>> [67] Directional overcurrent | Block OFF | 76E5
4870 | DOC2 | Idir>> [67] Directional overcurrent | No voltage, Protection locked On | 76E6
4871 | DOC2 | Idir>> [67] Directional overcurrent | Voltage measurable, Protection locked Off | 76E7
4872 | DOC2 | Idir>> [67] Directional overcurrent | Measuring live angle On | 76E8
4873 | DOC2 | Idir>> [67] Directional overcurrent | Measuring live angle Off | 76E9
4874 | DOC2 | Idir>> [67] Directional overcurrent | Using voltmem On | 76E10
4875 | DOC2 | Idir>> [67] Directional overcurrent | Using voltmem Off | 76E11
4877 | DOC2 | Idir>> [67] Directional overcurrent | Voltage mem Off Emergency non dir On | 76E13
4878 | DOC2 | Idir>> [67] Directional overcurrent | Voltage mem Off Emergency non dir Off | 76E14
4928 | DOC3 | Idir>>> [67] Directional overcurrent | Start ON | 77E0
4929 | DOC3 | Idir>>> [67] Directional overcurrent | Start OFF | 77E1
4930 | DOC3 | Idir>>> [67] Directional overcurrent | Trip ON | 77E2
4931 | DOC3 | Idir>>> [67] Directional overcurrent | Trip OFF | 77E3
4932 | DOC3 | Idir>>> [67] Directional overcurrent | Block ON | 77E4
4933 | DOC3 | Idir>>> [67] Directional overcurrent | Block OFF | 77E5
4934 | DOC3 | Idir>>> [67] Directional overcurrent | No voltage, Protection locked On | 77E6
4935 | DOC3 | Idir>>> [67] Directional overcurrent | Voltage measurable, Protection locked Off | 77E7
4936 | DOC3 | Idir>>> [67] Directional overcurrent | Measuring live angle On | 77E8
4937 | DOC3 | Idir>>> [67] Directional overcurrent | Measuring live angle Off | 77E9
4938 | DOC3 | Idir>>> [67] Directional overcurrent | Using voltmem On | 77E10
4939 | DOC3 | Idir>>> [67] Directional overcurrent | Using voltmem Off | 77E11
4941 | DOC3 | Idir>>> [67] Directional overcurrent | Voltage mem Off Emergency non dir On | 77E13
4942 | DOC3 | Idir>>> [67] Directional overcurrent | Voltage mem Off Emergency non dir Off | 77E14
4992 | DOC4 | Idir>>>> [67] Directional overcurrent | Start ON | 78E0
4993 | DOC4 | Idir>>>> [67] Directional overcurrent | Start OFF | 78E1
4994 | DOC4 | Idir>>>> [67] Directional overcurrent | Trip ON | 78E2
4995 | DOC4 | Idir>>>> [67] Directional overcurrent | Trip OFF | 78E3
4996 | DOC4 | Idir>>>> [67] Directional overcurrent | Block ON | 78E4
4997 | DOC4 | Idir>>>> [67] Directional overcurrent | Block OFF | 78E5
4998 | DOC4 | Idir>>>> [67] Directional overcurrent | No voltage, Protection locked On | 78E6
4999 | DOC4 | Idir>>>> [67] Directional overcurrent | Voltage measurable, Protection locked Off | 78E7
5000 | DOC4 | Idir>>>> [67] Directional overcurrent | Measuring live angle On | 78E8
5001 | DOC4 | Idir>>>> [67] Directional overcurrent | Measuring live angle Off | 78E9
5002 | DOC4 | Idir>>>> [67] Directional overcurrent | Using voltmem On | 78E10
5003 | DOC4 | Idir>>>> [67] Directional overcurrent | Using voltmem Off | 78E11
5005 | DOC4 | Idir>>>> [67] Directional overcurrent | Voltage mem Off Emergency non dir On | 78E13
5006 | DOC4 | Idir>>>> [67] Directional overcurrent | Voltage mem Off Emergency non dir Off | 78E14
5184 | DEF1 | I0dir> [67N] Directional earth fault | Start ON | 81E0
5185 | DEF1 | I0dir> [67N] Directional earth fault | Start OFF | 81E1
5186 | DEF1 | I0dir> [67N] Directional earth fault | Trip ON | 81E2
5187 | DEF1 | I0dir> [67N] Directional earth fault | Trip OFF | 81E3
5188 | DEF1 | I0dir> [67N] Directional earth fault | Block ON | 81E4
5189 | DEF1 | I0dir> [67N] Directional earth fault | Block OFF | 81E5
5190 | DEF1 | I0dir>> [67N] Directional earth fault | I0Cosfi Start On | 81E6
5191 | DEF1 | I0dir>> [67N] Directional earth fault | I0Cosfi Start Off | 81E7
5192 | DEF1 | I0dir>> [67N] Directional earth fault | I0Sinfi Start On | 81E8
5193 | DEF1 | I0dir>> [67N] Directional earth fault | I0Sinfi Start Off | 81E9
5194 | DEF1 | I0dir>> [67N] Directional earth fault | I0Cosfi Trip On | 81E10
5195 | DEF1 | I0dir> [67N] Directional earth fault | I0Cosfi Trip Off | 81E11
5196 | DEF1 | I0dir> [67N] Directional earth fault | I0Sinfi Trip On | 81E12
5197 | DEF1 | I0dir> [67N] Directional earth fault | I0Sinfi Trip Off | 81E13
5248 | DEF2 | I0dir>> [67N] Directional earth fault | Start ON | 82E0
5249 | DEF2 | I0dir>> [67N] Directional earth fault | Start OFF | 82E1
5250 | DEF2 | I0dir>> [67N] Directional earth fault | Trip ON | 82E2
5251 | DEF2 | I0dir>> [67N] Directional earth fault | Trip OFF | 82E3
5252 | DEF2 | I0dir>> [67N] Directional earth fault | Block ON | 82E4
5253 | DEF2 | I0dir>> [67N] Directional earth fault | Block OFF | 82E5
5254 | DEF2 | I0dir>> [67N] Directional earth fault | I0Cosfi Start On | 82E6
5255 | DEF2 | I0dir>> [67N] Directional earth fault | I0Cosfi Start Off | 82E7
5256 | DEF2 | I0dir>> [67N] Directional earth fault | I0Sinfi Start On | 82E8
5257 | DEF2 | I0dir>> [67N] Directional earth fault | I0Sinfi Start Off | 82E9
5258 | DEF2 | I0dir>> [67N] Directional earth fault | I0Cosfi Trip On | 82E10
5259 | DEF2 | I0dir>> [67N] Directional earth fault | I0Cosfi Trip Off | 82E11
5260 | DEF2 | I0dir>> [67N] Directional earth fault | I0Sinfi Trip On | 82E12
5261 | DEF2 | I0dir>> [67N] Directional earth fault | I0Sinfi Trip Off | 82E13
5312 | DEF3 | I0dir>>> [67N] Directional earth fault | Start ON | 83E0
5313 | DEF3 | I0dir>>> [67N] Directional earth fault | Start OFF | 83E1
5314 | DEF3 | I0dir>>> [67N] Directional earth fault | Trip ON | 83E2
5315 | DEF3 | I0dir>>> [67N] Directional earth fault | Trip OFF | 83E3
5316 | DEF3 | I0dir>>> [67N] Directional earth fault | Block ON | 83E4
5317 | DEF3 | I0dir>>> [67N] Directional earth fault | Block OFF | 83E5
5318 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Cosfi Start On | 83E6
5319 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Cosfi Start Off | 83E7
5320 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Sinfi Start On | 83E8
5321 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Sinfi Start Off | 83E9
5322 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Cosfi Trip On | 83E10
5323 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Cosfi Trip Off | 83E11
5324 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Sinfi Trip On | 83E12
5325 | DEF3 | I0dir>>> [67N] Directional earth fault | I0Sinfi Trip Off | 83E13
5376 | DEF4 | I0dir>>>> [67N] Directional earth fault | Start ON | 84E0
5377 | DEF4 | I0dir>>>> [67N] Directional earth fault | Start OFF | 84E1
5378 | DEF4 | I0dir>>>> [67N] Directional earth fault | Trip ON | 84E2
5379 | DEF4 | I0dir>>>> [67N] Directional earth fault | Trip OFF | 84E3
5380 | DEF4 | I0dir>>>> [67N] Directional earth fault | Block ON | 84E4
5381 | DEF4 | I0dir>>>> [67N] Directional earth fault | Block OFF | 84E5
5382 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Cosfi Start On | 84E6
5383 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Cosfi Start Off | 84E7
5384 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Sinfi Start On | 84E8
5385 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Sinfi Start Off | 84E9
5386 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Cosfi Trip On | 84E10
5387 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Cosfi Trip Off | 84E11
5388 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Sinfi Trip On | 84E12
5389 | DEF4 | I0dir>>>> [67N] Directional earth fault | I0Sinfi Trip Off | 84E13
5440 | OV1 | U> [59] Overvoltage | Start ON | 85E0
5441 | OV1 | U> [59] Overvoltage | Start OFF | 85E1
5442 | OV1 | U> [59] Overvoltage | Trip ON | 85E2
5443 | OV1 | U> [59] Overvoltage | Trip OFF | 85E3
5444 | OV1 | U> [59] Overvoltage | Block ON | 85E4
5445 | OV1 | U> [59] Overvoltage | Block OFF | 85E5
5504 | OV2 | U>> [59] Overvoltage | Start ON | 86E0
5505 | OV2 | U>> [59] Overvoltage | Start OFF | 86E1
5506 | OV2 | U>> [59] Overvoltage | Trip ON | 86E2
5507 | OV2 | U>> [59] Overvoltage | Trip OFF | 86E3
5508 | OV2 | U>> [59] Overvoltage | Block ON | 86E4
5509 | OV2 | U>> [59] Overvoltage | Block OFF | 86E5
5568 | OV3 | U>>> [59] Overvoltage | Start ON | 87E0
5569 | OV3 | U>>> [59] Overvoltage | Start OFF | 87E1
5570 | OV3 | U>>> [59] Overvoltage | Trip ON | 87E2
5571 | OV3 | U>>> [59] Overvoltage | Trip OFF | 87E3
5572 | OV3 | U>>> [59] Overvoltage | Block ON | 87E4
5573 | OV3 | U>>> [59] Overvoltage | Block OFF | 87E5
5632 | OV4 | U>>>> [59] Overvoltage | Start ON | 88E0
5633 | OV4 | U>>>> [59] Overvoltage | Start OFF | 88E1
5634 | OV4 | U>>>> [59] Overvoltage | Trip ON | 88E2
5635 | OV4 | U>>>> [59] Overvoltage | Trip OFF | 88E3
5636 | OV4 | U>>>> [59] Overvoltage | Block ON | 88E4
5637 | OV4 | U>>>> [59] Overvoltage | Block OFF | 88E5
5696 | UV1 | U< [27] Undervoltage | Start ON | 89E0
5697 | UV1 | U< [27] Undervoltage | Start OFF | 89E1
5698 | UV1 | U< [27] Undervoltage | Trip ON | 89E2
5699 | UV1 | U< [27] Undervoltage | Trip OFF | 89E3
5700 | UV1 | U< [27] Undervoltage | Block ON | 89E4
5701 | UV1 | U< [27] Undervoltage | Block OFF | 89E5
5702 | UV1 | U< [27] Undervoltage | Undervoltage Block On | 89E6
5703 | UV1 | U< [27] Undervoltage | Undervoltage Block Off | 89E7
5760 | UV2 | U<< [27] Undervoltage | Start ON | 90E0
5761 | UV2 | U<< [27] Undervoltage | Start OFF | 90E1
5762 | UV2 | U<< [27] Undervoltage | Trip ON | 90E2
5763 | UV2 | U<< [27] Undervoltage | Trip OFF | 90E3
5764 | UV2 | U<< [27] Undervoltage | Block ON | 90E4
5765 | UV2 | U<< [27] Undervoltage | Block OFF | 90E5
5766 | UV2 | U<< [27] Undervoltage | Undervoltage Block On | 90E6
5767 | UV2 | U<< [27] Undervoltage | Undervoltage Block Off | 90E7
5824 | UV3 | U<<< [27] Undervoltage | Start ON | 91E0
5825 | UV3 | U<<< [27] Undervoltage | Start OFF | 91E1
5826 | UV3 | U<<< [27] Undervoltage | Trip ON | 91E2
5827 | UV3 | U<<< [27] Undervoltage | Trip OFF | 91E3
5828 | UV3 | U<<< [27] Undervoltage | Block ON | 91E4
5829 | UV3 | U<<< [27] Undervoltage | Block OFF | 91E5
5830 | UV3 | U<<< [27] Undervoltage | Undervoltage Block On | 91E6
5831 | UV3 | U<<< [27] Undervoltage | Undervoltage Block Off | 91E7
5888 | UV4 | U<<<< [27] Undervoltage | Start ON | 92E0
5889 | UV4 | U<<<< [27] Undervoltage | Start OFF | 92E1
5890 | UV4 | U<<<< [27] Undervoltage | Trip ON | 92E2
5891 | UV4 | U<<<< [27] Undervoltage | Trip OFF | 92E3
5892 | UV4 | U<<<< [27] Undervoltage | Block ON | 92E4
5893 | UV4 | U<<<< [27] Undervoltage | Block OFF | 92E5
5894 | UV4 | U<<<< [27] Undervoltage | Undervoltage Block On | 92E6
5895 | UV4 | U<<<< [27] Undervoltage | Undervoltage Block Off | 92E7
5952 | NOV1 | U0> [59N] Neutral overvoltage | Start ON | 93E0
5953 | NOV1 | U0> [59N] Neutral overvoltage | Start OFF | 93E1
5954 | NOV1 | U0> [59N] Neutral overvoltage | Trip ON | 93E2
5955 | NOV1 | U0> [59N] Neutral overvoltage | Trip OFF | 93E3
5956 | NOV1 | U0> [59N] Neutral overvoltage | Block ON | 93E4
5957 | NOV1 | U0> [59N] Neutral overvoltage | Block OFF | 93E5
6016 | NOV2 | U0>> [59N] Neutral overvoltage | Start ON | 94E0
6017 | NOV2 | U0>> [59N] Neutral overvoltage | Start OFF | 94E1
6018 | NOV2 | U0>> [59N] Neutral overvoltage | Trip ON | 94E2
6019 | NOV2 | U0>> [59N] Neutral overvoltage | Trip OFF | 94E3
6020 | NOV2 | U0>> [59N] Neutral overvoltage | Block ON | 94E4
6021 | NOV2 | U0>> [59N] Neutral overvoltage | Block OFF | 94E5
6080 | NOV3 | U0>>> [59N] Neutral overvoltage | Start ON | 95E0
6081 | NOV3 | U0>>> [59N] Neutral overvoltage | Start OFF | 95E1
6082 | NOV3 | U0>>> [59N] Neutral overvoltage | Trip ON | 95E2
6083 | NOV3 | U0>>> [59N] Neutral overvoltage | Trip OFF | 95E3
6084 | NOV3 | U0>>> [59N] Neutral overvoltage | Block ON | 95E4
6085 | NOV3 | U0>>> [59N] Neutral overvoltage | Block OFF | 95E5
6144 | NOV4 | U0>>>> [59N] Neutral overvoltage | Start ON | 96E0
6145 | NOV4 | U0>>>> [59N] Neutral overvoltage | Start OFF | 96E1
6146 | NOV4 | U0>>>> [59N] Neutral overvoltage | Trip ON | 96E2
6147 | NOV4 | U0>>>> [59N] Neutral overvoltage | Trip OFF | 96E3
6148 | NOV4 | U0>>>> [59N] Neutral overvoltage | Block ON | 96E4
6149 | NOV4 | U0>>>> [59N] Neutral overvoltage | Block OFF | 96E5
6208 | NJK1 | U0RECL Zero sequence recloser | U0RECL Request On | 97E0
6209 | NJK1 | U0RECL Zero sequence recloser | U0RECL Request Off | 97E1
6210 | NJK1 | U0RECL Zero sequence recloser | U0RECL Blocked On | 97E2
6211 | NJK1 | U0RECL Zero sequence recloser | U0RECL Blocked Off | 97E3
6212 | NJK1 | U0RECL Zero sequence recloser | U0RECL Active On | 97E4
6213 | NJK1 | U0RECL Zero sequence recloser | U0RECL Active Off | 97E5
6214 | NJK1 | U0RECL Zero sequence recloser | U0RECL Breaker close request On | 97E6
6215 | NJK1 | U0RECL Zero sequence recloser | U0RECL Breaker close request Off | 97E7
6216 | NJK1 | U0RECL Zero sequence recloser | U0RECL U0 Blocking On | 97E8
6217 | NJK1 | U0RECL Zero sequence recloser | U0RECL U0 Blocking Off | 97E9
6272 | FRQC1 | f> [81O] Overfrequency [Current] | f> [Curr] Start ON | 98E0
6273 | FRQC1 | f> [81O] Overfrequency [Current] | f> [Curr] Start OFF | 98E1
6274 | FRQC1 | f> [81O] Overfrequency [Current] | f> [Curr] Trip ON | 98E2
6275 | FRQC1 | f> [81O] Overfrequency [Current] | f> [Curr] Trip OFF | 98E3
6276 | FRQC1 | f>> [81O] Overfrequency [Current] | f>>[Curr] Start ON | 98E4
6277 | FRQC1 | f>> [81O] Overfrequency [Current] | f>> [Curr] Start OFF | 98E5
6278 | FRQC1 | f>> [81O] Overfrequency [Current] | f>> [Curr] Trip ON | 98E6
6279 | FRQC1 | f>> [81O] Overfrequency [Current] | f>> [Curr] Trip OFF | 98E7
6280 | FRQC1 | f>>> [81O] Overfrequency [Current] | f>>> [Curr] Start ON | 98E8
6281 | FRQC1 | f>>> [81O] Overfrequency [Current] | f>>> [Curr] Start OFF | 98E9
6282 | FRQC1 | f>>> [81O] Overfrequency [Current] | f>>> [Curr] Trip ON | 98E10
6283 | FRQC1 | f>>> [81O] Overfrequency [Current] | f>>> [Curr] Trip OFF | 98E11
6284 | FRQC1 | f>>>> [81O] Overfrequency [Current] | f>>>> [Curr] Start ON | 98E12
6285 | FRQC1 | f>>>> [81O] Overfrequency [Current] | f>>>> [Curr] Start OFF | 98E13
6286 | FRQC1 | f>>>> [81O] Overfrequency [Current] | f>>>> [Curr] Trip ON | 98E14
6287 | FRQC1 | f>>>> [81O] Overfrequency [Current] | f>>>> [Curr] Trip OFF | 98E15
6288 | FRQC1 | f< [81U] Underfrequency [Current] | f< [Curr] Start ON | 98E16
6289 | FRQC1 | f< [81U] Underfrequency [Current] | f< [Curr] Start OFF | 98E17
6290 | FRQC1 | f< [81U] Underfrequency [Current] | f< [Curr] Trip ON | 98E18
6291 | FRQC1 | f< [81U] Underfrequency [Current] | f< [Curr] Trip OFF | 98E19
6292 | FRQC1 | f<< [81U] Underfrequency [Current] | f<< [Curr] Start ON | 98E20
6293 | FRQC1 | f<< [81U] Underfrequency [Current] | f<< [Curr] Start OFF | 98E21
6294 | FRQC1 | f<< [81U] Underfrequency [Current] | f<< [Curr] Trip ON | 98E22
6295 | FRQC1 | f<< [81U] Underfrequency [Current] | f<< [Curr] Trip OFF | 98E23
6296 | FRQC1 | f<<< [81U] Underfrequency [Current] | f<<< [Curr] Start ON | 98E24
6297 | FRQC1 | f<<< [81U] Underfrequency [Current] | f<<< [Curr] Start OFF | 98E25
6298 | FRQC1 | f<<< [81U] Underfrequency [Current] | f<<< [Curr] Trip ON | 98E26
6299 | FRQC1 | f<<< [81U] Underfrequency [Current] | f<<< [Curr] Trip OFF | 98E27
6300 | FRQC1 | f<<<< [81U] Underfrequency [Current] | f<<<< [Curr] Start ON | 98E28
6301 | FRQC1 | f<<<< [81U] Underfrequency [Current] | f<<<< [Curr] Start OFF | 98E29
6302 | FRQC1 | f<<<< [81U] Underfrequency [Current] | f<<<< [Curr] Trip ON | 98E30
6303 | FRQC1 | f<<<< [81U] Underfrequency [Current] | f<<<< [Curr] Trip OFF | 98E31
6304 | FRQC1 | f> [81O] Overfrequency [Current] | f> [Curr] Block ON | 98E32
6305 | FRQC1 | f> [81O] Overfrequency [Current] | f> [Curr] Block OFF | 98E33
6306 | FRQC1 | f>> [81O] Overfrequency [Current] | f>> [Curr] Block ON | 98E34
6307 | FRQC1 | f>> [81O] Overfrequency [Current] | f>> [Curr] Block OFF | 98E35
6308 | FRQC1 | f>>> [81O] Overfrequency [Current] | f>>> [Curr] Block ON | 98E36
6309 | FRQC1 | f>>> [81O] Overfrequency [Current] | f>>> [Curr] Block OFF | 98E37
6310 | FRQC1 | f>>>> [81O] Overfrequency [Current] | f>>>> [Curr] Block ON | 98E38
6311 | FRQC1 | f>>>> [81O] Overfrequency [Current] | f>>>> [Curr] Block OFF | 98E39
6312 | FRQC1 | f< [81U] Underfrequency [Current] | f< [Curr] Block ON | 98E40
6313 | FRQC1 | f< [81U] Underfrequency [Current] | f< [Curr] Block OFF | 98E41
6314 | FRQC1 | f<< [81U] Underfrequency [Current] | f<< [Curr] Block ON | 98E42
6315 | FRQC1 | f<< [81U] Underfrequency [Current] | f<< [Curr] Block OFF | 98E43
6316 | FRQC1 | f<<< [81U] Underfrequency [Current] | f<<< [Curr] Block ON | 98E44
6317 | FRQC1 | f<<< [81U] Underfrequency [Current] | f<<< [Curr] Block OFF | 98E45
6318 | FRQC1 | f<<<< [81U] Underfrequency [Current] | f<<<< [Curr] Block ON | 98E46
6319 | FRQC1 | f<<<< [81U] Underfrequency [Current] | f<<<< [Curr] Block OFF | 98E47
6320 | FRQC1 | Frequency protection | Meas Curr Ok for f [curr] | 98E48
6321 | FRQC1 | Frequency protection | Meas Curr too low, f [curr] blocked | 98E49
6336 | FRQV1 | f> [81O] Overfrequency | f> Start ON | 99E0
6337 | FRQV1 | f> [81O] Overfrequency | f> Start OFF | 99E1
6338 | FRQV1 | f> [81O] Overfrequency | f> Trip ON | 99E2
6339 | FRQV1 | f> [81O] Overfrequency | f> Trip OFF | 99E3
6340 | FRQV1 | f>> [81O] Overfrequency | f>> Start ON | 99E4
6341 | FRQV1 | f>> [81O] Overfrequency | f>> Start OFF | 99E5
6342 | FRQV1 | f>> [81O] Overfrequency | f>> Trip ON | 99E6
6343 | FRQV1 | f>> [81O] Overfrequency | f>> Trip OFF | 99E7
6344 | FRQV1 | f>>> [81O] Overfrequency | f>>> Start ON | 99E8
6345 | FRQV1 | f>>> [81O] Overfrequency | f>>> Start OFF | 99E9
6346 | FRQV1 | f>>> [81O] Overfrequency | f>>> Trip ON | 99E10
6347 | FRQV1 | f>>> [81O] Overfrequency | f>>> Trip OFF | 99E11
6348 | FRQV1 | f>>>> [81O] Overfrequency | f>>>> Start ON | 99E12
6349 | FRQV1 | f>>>> [81O] Overfrequency | f>>>> Start OFF | 99E13
6350 | FRQV1 | f>>>> [81O] Overfrequency | f>>>> Trip ON | 99E14
6351 | FRQV1 | f>>>> [81O] Overfrequency | f>>>> Trip OFF | 99E15
6352 | FRQV1 | f< [81U] Underfrequency | f< Start ON | 99E16
6353 | FRQV1 | f< [81U] Underfrequency | f< Start OFF | 99E17
6354 | FRQV1 | f< [81U] Underfrequency | f< Trip ON | 99E18
6355 | FRQV1 | f< [81U] Underfrequency | f< Trip OFF | 99E19
6356 | FRQV1 | f<< [81U] Underfrequency | f<< Start ON | 99E20
6357 | FRQV1 | f<< [81U] Underfrequency | f<< Start OFF | 99E21
6358 | FRQV1 | f<< [81U] Underfrequency | f<< Trip ON | 99E22
6359 | FRQV1 | f<< [81U] Underfrequency | f<< Trip OFF | 99E23
6360 | FRQV1 | f<<< [81U] Underfrequency | f<<< Start ON | 99E24
6361 | FRQV1 | f<<< [81U] Underfrequency | f<<< Start OFF | 99E25
6362 | FRQV1 | f<<< [81U] Underfrequency | f<<< Trip ON | 99E26
6363 | FRQV1 | f<<< [81U] Underfrequency | f<<< Trip OFF | 99E27
6364 | FRQV1 | f<<<< [81U] Underfrequency | f<<<< Start ON | 99E28
6365 | FRQV1 | f<<<< [81U] Underfrequency | f<<<< Start OFF | 99E29
6366 | FRQV1 | f<<<< [81U] Underfrequency | f<<<< Trip ON | 99E30
6367 | FRQV1 | f<<<< [81U] Underfrequency | f<<<< Trip OFF | 99E31
6368 | FRQV1 | f> [81O] Overfrequency | f> Block ON | 99E32
6369 | FRQV1 | f> [81O] Overfrequency | f> Block OFF | 99E33
6370 | FRQV1 | f>> [81O] Overfrequency | f>> Block ON | 99E34
6371 | FRQV1 | f>> [81O] Overfrequency | f>> Block OFF | 99E35
6372 | FRQV1 | f>>> [81O] Overfrequency | f>>> Block ON | 99E36
6373 | FRQV1 | f>>> [81O] Overfrequency | f>>> Block OFF | 99E37
6374 | FRQV1 | f>>>> [81O] Overfrequency | f>>>> Block ON | 99E38
6375 | FRQV1 | f>>>> [81O] Overfrequency | f>>>> Block OFF | 99E39
6376 | FRQV1 | f< [81U] Underfrequency | f< Block ON | 99E40
6377 | FRQV1 | f< [81U] Underfrequency | f< Block OFF | 99E41
6378 | FRQV1 | f<< [81U] Underfrequency | f<< Block ON | 99E42
6379 | FRQV1 | f<< [81U] Underfrequency | f<< Block OFF | 99E43
6380 | FRQV1 | f<<< [81U] Underfrequency | f<<< Block ON | 99E44
6381 | FRQV1 | f<<< [81U] Underfrequency | f<<< Block OFF | 99E45
6382 | FRQV1 | f<<<< [81U] Underfrequency | f<<<< Block ON | 99E46
6383 | FRQV1 | f<<<< [81U] Underfrequency | f<<<< Block OFF | 99E47
6384 | FRQV1 | Frequency protection | f< Undervoltage Block ON | 99E48
6385 | FRQV1 | Frequency protection | f< Undervoltage Block OFF | 99E49
6386 | FRQV1 | Frequency protection | f<< Undervoltage Block ON | 99E50
6387 | FRQV1 | Frequency protection | f<< Undervoltage Block OFF | 99E51
6388 | FRQV1 | Frequency protection | f<<< Undervoltage Block ON | 99E52
6389 | FRQV1 | Frequency protection | f<<< Undervoltage Block OFF | 99E53
6390 | FRQV1 | Frequency protection | f<<<< Undervoltage Block ON | 99E54
6391 | FRQV1 | Frequency protection | f<<<< Undervoltage Block OFF | 99E55
6400 | OPW1 | P> [32O] Overpower | Start ON | 100E0
6401 | OPW1 | P> [32O] Overpower | Start OFF | 100E1
6402 | OPW1 | P> [32O] Overpower | Trip ON | 100E2
6403 | OPW1 | P> [32O] Overpower | Trip OFF | 100E3
6404 | OPW1 | P> [32O] Overpower | Block ON | 100E4
6405 | OPW1 | P> [32O] Overpower | Block OFF | 100E5
6464 | UPW1 | P< [32U] Underpower | Start ON | 101E0
6465 | UPW1 | P< [32U] Underpower | Start OFF | 101E1
6466 | UPW1 | P< [32U] Underpower | Trip ON | 101E2
6467 | UPW1 | P< [32U] Underpower | Trip OFF | 101E3
6468 | UPW1 | P< [32U] Underpower | Block ON | 101E4
6469 | UPW1 | P< [32U] Underpower | Block OFF | 101E5
6528 | RPW1 | Prev> [32R] Reverse power | Start ON | 102E0
6529 | RPW1 | Prev> [32R] Reverse power | Start OFF | 102E1
6530 | RPW1 | Prev> [32R] Reverse power | Trip ON | 102E2
6531 | RPW1 | Prev> [32R] Reverse power | Trip OFF | 102E3
6532 | RPW1 | Prev> [32R] Reverse power | Block ON | 102E4
6533 | RPW1 | Prev> [32R] Reverse power | Block OFF | 102E5
6592 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (1) Start ON | 103E0
6593 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (1) Start OFF | 103E1
6594 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (1) Trip ON | 103E2
6595 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (1) Trip OFF | 103E3
6596 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (2) Start ON | 103E4
6597 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (2) Start OFF | 103E5
6598 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (2) Trip ON | 103E6
6599 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (2) Trip OFF | 103E7
6600 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (3) Start ON | 103E8
6601 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (3) Start OFF | 103E9
6602 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (3) Trip ON | 103E10
6603 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (3) Trip OFF | 103E11
6604 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (4) Start ON | 103E12
6605 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (4) Start OFF | 103E13
6606 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (4) Trip ON | 103E14
6607 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (4) Trip OFF | 103E15
6608 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (5) Start ON | 103E16
6609 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (5) Start OFF | 103E17
6610 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (5) Trip ON | 103E18
6611 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (5) Trip OFF | 103E19
6612 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (6) Start ON | 103E20
6613 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (6) Start OFF | 103E21
6614 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (6) Trip ON | 103E22
6615 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (6) Trip OFF | 103E23
6616 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (7) Start ON | 103E24
6617 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (7) Start OFF | 103E25
6618 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (7) Trip ON | 103E26
6619 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (7) Trip OFF | 103E27
6620 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (8) Start ON | 103E28
6621 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (8) Start OFF | 103E29
6622 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (8) Trip ON | 103E30
6623 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (8) Trip OFF | 103E31
6624 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (1) Block ON | 103E32
6625 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (1) Block OFF | 103E33
6626 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (2) Block ON | 103E34
6627 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (2) Block OFF | 103E35
6628 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (3) Block ON | 103E36
6629 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (3) Block OFF | 103E37
6630 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (4) Block ON | 103E38
6631 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (4) Block OFF | 103E39
6632 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (5) Block ON | 103E40
6633 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (5) Block OFF | 103E41
6634 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (6) Block ON | 103E42
6635 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (6) Block OFF | 103E43
6636 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (7) Block ON | 103E44
6637 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (7) Block OFF | 103E45
6638 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (8) Block ON | 103E46
6639 | DFT1 | df/dt [81R] Rate-of-change-of-frequency | df/dt </> (8) Block OFF | 103E47
6656 | CIN1 | Indicator object 1 | Intermediate | 104E0
6657 | CIN1 | Indicator object 1 | Open | 104E1
6658 | CIN1 | Indicator object 1 | Close | 104E2
6659 | CIN1 | Indicator object 1 | Bad | 104E3
6720 | CIN2 | Indicator object 2 | Intermediate | 105E0
6721 | CIN2 | Indicator object 2 | Open | 105E1
6722 | CIN2 | Indicator object 2 | Close | 105E2
6723 | CIN2 | Indicator object 2 | Bad | 105E3
6784 | CIN3 | Indicator object 3 | Intermediate | 106E0
6785 | CIN3 | Indicator object 3 | Open | 106E1
6786 | CIN3 | Indicator object 3 | Close | 106E2
6787 | CIN3 | Indicator object 3 | Bad | 106E3
6848 | CIN4 | Indicator object 4 | Intermediate | 107E0
6849 | CIN4 | Indicator object 4 | Open | 107E1
6850 | CIN4 | Indicator object 4 | Close | 107E2
6851 | CIN4 | Indicator object 4 | Bad | 107E3
6912 | CIN5 | Indicator object 5 | Intermediate | 108E0
6913 | CIN5 | Indicator object 5 | Open | 108E1
6914 | CIN5 | Indicator object 5 | Close | 108E2
6915 | CIN5 | Indicator object 5 | Bad | 108E3
6976 | UEX1 | Q< [40] Underexcitation | Start ON | 109E0
6977 | UEX1 | Q< [40] Underexcitation | Start OFF | 109E1
6978 | UEX1 | Q< [40] Underexcitation | Trip ON | 109E2
6979 | UEX1 | Q< [40] Underexcitation | Trip OFF | 109E3
6980 | UEX1 | Q< [40] Underexcitation | Block ON | 109E4
6981 | UEX1 | Q< [40] Underexcitation | Block OFF | 109E5
7040 | SEF1 | U03rd> [64S] 100 % Stator earth fault | Start ON | 110E0
7041 | SEF1 | U03rd> [64S] 100 % Stator earth fault | Start OFF | 110E1
7042 | SEF1 | U03rd> [64S] 100 % Stator earth fault | Trip ON | 110E2
7043 | SEF1 | U03rd> [64S] 100 % Stator earth fault | Trip OFF | 110E3
7044 | SEF1 | U03rd> [64S] 100 % Stator earth fault | Block ON | 110E4
7045 | SEF1 | U03rd> [64S] 100 % Stator earth fault | Block OFF | 110E5
7104 | UIM1 | Z< [21U] Underimpedance | Start ON | 111E0
7105 | UIM1 | Z< [21U] Underimpedance | Start OFF | 111E1
7106 | UIM1 | Z< [21U] Underimpedance | Trip ON | 111E2
7107 | UIM1 | Z< [21U] Underimpedance | Trip OFF | 111E3
7108 | UIM1 | Z< [21U] Underimpedance | Block ON | 111E4
7109 | UIM1 | Z< [21U] Underimpedance | Block OFF | 111E5
7168 | VOC1 | Iv> [51V] Voltage-restrained overcurrent protection | Start ON | 112E0
7169 | VOC1 | Iv> [51V] Voltage-restrained overcurrent protection | Start OFF | 112E1
7170 | VOC1 | Iv> [51V] Voltage-restrained overcurrent protection | Trip ON | 112E2
7171 | VOC1 | Iv> [51V] Voltage-restrained overcurrent protection | Trip OFF | 112E3
7172 | VOC1 | Iv> [51V] Voltage-restrained overcurrent protection | Block ON | 112E4
7173 | VOC1 | Iv> [51V] Voltage-restrained overcurrent protection | Block OFF | 112E5
7232 | GST1 | Generator status monitoring | Light/No load On | 113E0
7233 | GST1 | Generator status monitoring | Light/No load Off | 113E1
7234 | GST1 | Generator status monitoring | HV side inrush On | 113E2
7235 | GST1 | Generator status monitoring | HV side inrush Off | 113E3
7236 | GST1 | Generator status monitoring | LV side inrush On | 113E4
7237 | GST1 | Generator status monitoring | LV side inrush Off | 113E5
7238 | GST1 | Generator status monitoring | Load normal On | 113E6
7239 | GST1 | Generator status monitoring | Load normal Off | 113E7
7240 | GST1 | Generator status monitoring | Overloading On | 113E8
7241 | GST1 | Generator status monitoring | Overloading Off | 113E9
7242 | GST1 | Generator status monitoring | High overload On | 113E10
7243 | GST1 | Generator status monitoring | High overload Off | 113E11
7244 | GST1 | Generator status monitoring | Setting changes, calculating new trafo data | 113E12
7245 | GST1 | Generator status monitoring | Calculation finished, possible restart | 113E13
7296 | IEF1 | I0Int> [67NT] Intermittent earth fault | Start FWD ON | 114E0
7297 | IEF1 | I0Int> [67NT] Intermittent earth fault | Start FWD OFF | 114E1
7298 | IEF1 | I0Int> [67NT] Intermittent earth fault | Start REV ON | 114E2
7299 | IEF1 | I0Int> [67NT] Intermittent earth fault | Start REV OFF | 114E3
7300 | IEF1 | I0Int> [67NT] Intermittent earth fault | Trip ON | 114E4
7301 | IEF1 | I0Int> [67NT] Intermittent earth fault | Trip OFF | 114E5
7302 | IEF1 | I0Int> [67NT] Intermittent earth fault | Block ON | 114E6
7303 | IEF1 | I0Int> [67NT] Intermittent earth fault | Block OFF | 114E7
7304 | IEF1 | I0Int> [67NT] Intermittent earth fault | Intermittent EF detected ON | 114E8
7305 | IEF1 | I0Int> [67NT] Intermittent earth fault | Intermittent EF detected OFF | 114E9
7306 | IEF1 | I0Int> [67NT] Intermittent earth fault | Normal earthfault detected | 114E10
7307 | IEF1 | I0Int> [67NT] Intermittent earth fault | Intermittent EF Locked | 114E11
7360 | VRG1 | AVR [90] Automatic voltage regulator | Tap Raise command On | 115E0
7361 | VRG1 | AVR [90] Automatic voltage regulator | Tap Raise command Off | 115E1
7362 | VRG1 | AVR [90] Automatic voltage regulator | Tap Lower command On | 115E2
7363 | VRG1 | AVR [90] Automatic voltage regulator | Tap Lower command Off | 115E3
7364 | VRG1 | AVR [90] Automatic voltage regulator | Block operation On | 115E4
7365 | VRG1 | AVR [90] Automatic voltage regulator | Block Operation Off | 115E5
7366 | VRG1 | AVR [90] Automatic voltage regulator | Block Output commands On | 115E6
7367 | VRG1 | AVR [90] Automatic voltage regulator | Block Output commands Off | 115E7
7368 | VRG1 | AVR [90] Automatic voltage regulator | Low voltage blocking On | 115E8
7369 | VRG1 | AVR [90] Automatic voltage regulator | Low voltage blocking Off | 115E9
7370 | VRG1 | AVR [90] Automatic voltage regulator | Overcurrent blocking On | 115E10
7371 | VRG1 | AVR [90] Automatic voltage regulator | Overcurrent blocking Off | 115E11
7372 | VRG1 | AVR [90] Automatic voltage regulator | Tap on highlimit On | 115E12
7373 | VRG1 | AVR [90] Automatic voltage regulator | Tap on highlimit Off | 115E13
7374 | VRG1 | AVR [90] Automatic voltage regulator | Tap on lowlimit On | 115E14
7375 | VRG1 | AVR [90] Automatic voltage regulator | Tap on lowlimit Off | 115E15
7376 | VRG1 | AVR [90] Automatic voltage regulator | Operation blocked On | 115E16
7377 | VRG1 | AVR [90] Automatic voltage regulator | Operation blocked Off | 115E17
7378 | VRG1 | AVR [90] Automatic voltage regulator | U>/< Start On | 115E18
7379 | VRG1 | AVR [90] Automatic voltage regulator | U>/< Start Off | 115E19
7380 | VRG1 | AVR [90] Automatic voltage regulator | U>>/<< Start On | 115E20
7381 | VRG1 | AVR [90] Automatic voltage regulator | U>>/<< Start Off | 115E21
7382 | VRG1 | AVR [90] Automatic voltage regulator | Control wait time On | 115E22
7383 | VRG1 | AVR [90] Automatic voltage regulator | Control wait time Off | 115E23
7384 | VRG1 | AVR [90] Automatic voltage regulator | Manual control On | 115E24
7385 | VRG1 | AVR [90] Automatic voltage regulator | Automatic control On | 115E25
7386 | VRG1 | AVR [90] Automatic voltage regulator | Tap raise requested On | 115E26
7387 | VRG1 | AVR [90] Automatic voltage regulator | Tap raise requested Off | 115E27
7388 | VRG1 | AVR [90] Automatic voltage regulator | Tap lower requested On | 115E28
7389 | VRG1 | AVR [90] Automatic voltage regulator | Tap lower requested Off | 115E29
7390 | VRG1 | AVR [90] Automatic voltage regulator | Transformer independent control On | 115E30
7391 | VRG1 | AVR [90] Automatic voltage regulator | Transformer parallel control On | 115E31
7392 | VRG1 | AVR [90] Automatic voltage regulator | Tranformer operates as Master On | 115E32
7393 | VRG1 | AVR [90] Automatic voltage regulator | Tranformer operates as follower On | 115E33
7394 | VRG1 | AVR [90] Automatic voltage regulator | Circulating reactive current mode On | 115E34
7395 | VRG1 | AVR [90] Automatic voltage regulator | Master and follower mode On | 115E35
7396 | VRG1 | AVR [90] Automatic voltage regulator | Parallel communication failure On | 115E36
7397 | VRG1 | AVR [90] Automatic voltage regulator | Parallel communication failure Off | 115E37
7398 | VRG1 | AVR [90] Automatic voltage regulator | Tap control circuit failure On | 115E38
7399 | VRG1 | AVR [90] Automatic voltage regulator | Tap control circuit failure Off | 115E39
7400 | VRG1 | AVR [90] Automatic voltage regulator | Tap difference failure On | 115E40
7401 | VRG1 | AVR [90] Automatic voltage regulator | Tap difference failure Off | 115E41
8192 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Start ON | 128E0
8193 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Start OFF | 128E1
8194 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Alarm ON | 128E2
8195 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Alarm OFF | 128E3
8196 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Trip ON | 128E4
8197 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Trip OFF | 128E5
8198 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Block ON | 128E6
8199 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (1)Block OFF | 128E7
8200 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)Start ON | 128E8
8201 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)Start OFF | 128E9
8202 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)Alarm ON | 128E10
8203 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)AlarmOFF | 128E11
8204 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)Trip ON | 128E12
8205 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)Trip OFF | 128E13
8206 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)Block ON | 128E14
8207 | VHZ1 | V/Hz [24] Volts-per-hertz overexcitation | (2)Block OFF | 128E15
8256 | UPF1 | PF< [55] Power factor protection | Block On | 129E0
8257 | UPF1 | PF< [55] Power factor protection | Block Off | 129E1
8258 | UPF1 | PF< [55] Power factor protection | Start On | 129E2
8259 | UPF1 | PF< [55] Power factor protection | Start Off | 129E3
8260 | UPF1 | PF< [55] Power factor protection | Trip On | 129E4
8261 | UPF1 | PF< [55] Power factor protection | Trip Off | 129E5
8262 | UPF1 | PF< [55] Power factor protection | Alarm Start On | 129E6
8263 | UPF1 | PF< [55] Power factor protection | Alarm Start Off | 129E7
8264 | UPF1 | PF< [55] Power factor protection | Alarm On | 129E8
8265 | UPF1 | PF< [55] Power factor protection | Alarm Off | 129E9
8320 | VUB1 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start ON | 130E0
8321 | VUB1 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start OFF | 130E1
8322 | VUB1 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip ON | 130E2
8323 | VUB1 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip OFF | 130E3
8324 | VUB1 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block ON | 130E4
8325 | VUB1 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block OFF | 130E5
8384 | VUB2 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start ON | 131E0
8385 | VUB2 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start OFF | 131E1
8386 | VUB2 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip ON | 131E2
8387 | VUB2 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip OFF | 131E3
8388 | VUB2 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block ON | 131E4
8389 | VUB2 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block OFF | 131E5
8448 | VUB3 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start ON | 132E0
8449 | VUB3 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start OFF | 132E1
8450 | VUB3 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip ON | 132E2
8451 | VUB3 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip OFF | 132E3
8452 | VUB3 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block ON | 132E4
8453 | VUB3 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block OFF | 132E5
8512 | VUB4 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start ON | 133E0
8513 | VUB4 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Start OFF | 133E1
8514 | VUB4 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip ON | 133E2
8515 | VUB4 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Trip OFF | 133E3
8516 | VUB4 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block ON | 133E4
8517 | VUB4 | U1/U2 >/< [47/27P/59PN] Sequence voltage | Block OFF | 133E5
8576 | PGS1 | Programmable stage | PS1 >/< Start ON | 134E0
8577 | PGS1 | Programmable stage | PS1 >/< Start OFF | 134E1
8578 | PGS1 | Programmable stage | PS1 >/< Trip ON | 134E2
8579 | PGS1 | Programmable stage | PS1 >/< Trip OFF | 134E3
8580 | PGS1 | Programmable stage | PS1 >/< Block ON | 134E4
8581 | PGS1 | Programmable stage | PS1 >/< Block OFF | 134E5
8582 | PGS1 | Programmable stage | PS2 >/< Start ON | 134E6
8583 | PGS1 | Programmable stage | PS2 >/< Start OFF | 134E7
8584 | PGS1 | Programmable stage | PS2 >/< Trip ON | 134E8
8585 | PGS1 | Programmable stage | PS2 >/< Trip OFF | 134E9
8586 | PGS1 | Programmable stage | PS2 >/< Block ON | 134E10
8587 | PGS1 | Programmable stage | PS2 >/< Block OFF | 134E11
8588 | PGS1 | Programmable stage | PS3 >/< Start ON | 134E12
8589 | PGS1 | Programmable stage | PS3 >/< Start OFF | 134E13
8590 | PGS1 | Programmable stage | PS3 >/< Trip ON | 134E14
8591 | PGS1 | Programmable stage | PS3 >/< Trip OFF | 134E15
8592 | PGS1 | Programmable stage | PS3 >/< Block ON | 134E16
8593 | PGS1 | Programmable stage | PS3 >/< Block OFF | 134E17
8594 | PGS1 | Programmable stage | PS4 >/< Start ON | 134E18
8595 | PGS1 | Programmable stage | PS4 >/< Start OFF | 134E19
8596 | PGS1 | Programmable stage | PS4 >/< Trip ON | 134E20
8597 | PGS1 | Programmable stage | PS4 >/< Trip OFF | 134E21
8598 | PGS1 | Programmable stage | PS4 >/< Block ON | 134E22
8599 | PGS1 | Programmable stage | PS4 >/< Block OFF | 134E23
8600 | PGS1 | Programmable stage | PS5 >/< Start ON | 134E24
8601 | PGS1 | Programmable stage | PS5 >/< Start OFF | 134E25
8602 | PGS1 | Programmable stage | PS5 >/< Trip ON | 134E26
8603 | PGS1 | Programmable stage | PS5 >/< Trip OFF | 134E27
8604 | PGS1 | Programmable stage | PS5 >/< Block ON | 134E28
8605 | PGS1 | Programmable stage | PS5 >/< Block OFF | 134E29
8606 | PGS1 | Programmable stage | reserved | 134E30
8607 | PGS1 | Programmable stage | reserved | 134E31
8608 | PGS1 | Programmable stage | PS6 >/< Start ON | 134E32
8609 | PGS1 | Programmable stage | PS6 >/< Start OFF | 134E33
8610 | PGS1 | Programmable stage | PS6 >/< Trip ON | 134E34
8611 | PGS1 | Programmable stage | PS6 >/< Trip OFF | 134E35
8612 | PGS1 | Programmable stage | PS6 >/< Block ON | 134E36
8613 | PGS1 | Programmable stage | PS6 >/< Block OFF | 134E37
8614 | PGS1 | Programmable stage | PS7 >/< Start ON | 134E38
8615 | PGS1 | Programmable stage | PS7 >/< Start OFF | 134E39
8616 | PGS1 | Programmable stage | PS7 >/< Trip ON | 134E40
8617 | PGS1 | Programmable stage | PS7 >/< Trip OFF | 134E41
8618 | PGS1 | Programmable stage | PS7 >/< Block ON | 134E42
8619 | PGS1 | Programmable stage | PS7 >/< Block OFF | 134E43
8620 | PGS1 | Programmable stage | PS8 >/< Start ON | 134E44
8621 | PGS1 | Programmable stage | PS8 >/< Start OFF | 134E45
8622 | PGS1 | Programmable stage | PS8 >/< Trip ON | 134E46
8623 | PGS1 | Programmable stage | PS8 >/< Trip OFF | 134E47
8624 | PGS1 | Programmable stage | PS8 >/< Block ON | 134E48
8625 | PGS1 | Programmable stage | PS8 >/< Block OFF | 134E49
8626 | PGS1 | Programmable stage | PS9 >/< Start ON | 134E50
8627 | PGS1 | Programmable stage | PS9 >/< Start OFF | 134E51
8628 | PGS1 | Programmable stage | PS9 >/< Trip ON | 134E52
8629 | PGS1 | Programmable stage | PS9 >/< Trip OFF | 134E53
8630 | PGS1 | Programmable stage | PS9 >/< Block ON | 134E54
8631 | PGS1 | Programmable stage | PS9 >/< Block OFF | 134E55
8632 | PGS1 | Programmable stage | PS10 >/< Start ON | 134E56
8633 | PGS1 | Programmable stage | PS10 >/< Start OFF | 134E57
8634 | PGS1 | Programmable stage | PS10 >/< Trip ON | 134E58
8635 | PGS1 | Programmable stage | PS10 >/< Trip OFF | 134E59
8636 | PGS1 | Programmable stage | PS10 >/< Block ON | 134E60
8637 | PGS1 | Programmable stage | PS10 >/< Block OFF | 134E61
8640 | EMON1 | Monitoring functions (E215/E255) | I> (50) Detect On | 135E0
8641 | EMON1 | Monitoring functions (E215/E255) | I> (50) Detect Off | 135E1
8642 | EMON1 | Monitoring functions (E215/E255) | I0> (50N) Detect On | 135E2
8643 | EMON1 | Monitoring functions (E215/E255) | I0> (50N) Detect Off | 135E3
8644 | EMON1 | Monitoring functions (E215/E255) | Idir> (67) Detect On | 135E4
8645 | EMON1 | Monitoring functions (E215/E255) | Idir> (67) Detect Off | 135E5
8646 | EMON1 | Monitoring functions (E215/E255) | I0dir> (67N) Detect On | 135E6
8647 | EMON1 | Monitoring functions (E215/E255) | I0dir> (67N) Detect Off | 135E7
8648 | EMON1 | Monitoring functions (E215/E255) | I0Int> (67NT) Detect FWD On | 135E8
8649 | EMON1 | Monitoring functions (E215/E255) | I0Int> (67NT) Detect FWD Off | 135E9
8650 | EMON1 | Monitoring functions (E215/E255) | I0Int> (67NT) Detect REV On | 135E10
8651 | EMON1 | Monitoring functions (E215/E255) | I0Int> (67NT) Detect REV Off | 135E11
8652 | EMON1 | Monitoring functions (E215/E255) | U< (27) Undervoltage detected On | 135E12
8653 | EMON1 | Monitoring functions (E215/E255) | U< (27) Undervoltage detected Off | 135E13
8654 | EMON1 | Monitoring functions (E215/E255) | U< (27) No voltage detected On | 135E14
8655 | EMON1 | Monitoring functions (E215/E255) | U< (27) No voltage detected Off | 135E15
8656 | EMON1 | Monitoring functions (E215/E255) | U0> (59N) Overvoltage detected On | 135E16
8657 | EMON1 | Monitoring functions (E215/E255) | U0> (59N) Overvoltage detected Off | 135E17
8658 | EMON1 | Monitoring functions (E215/E255) | FL (21FL) Triggered On | 135E18
8659 | EMON1 | Monitoring functions (E215/E255) | FL (21FL) Triggered On | 135E19
8832 | MBIO | Modbus ADAM Module | ModuleA Ch1 Invalid ON | 138E0
8833 | MBIO | Modbus ADAM Module | ModuleA Ch1 Invalid OFF | 138E1
8834 | MBIO | Modbus ADAM Module | ModuleA Ch2 Invalid ON | 138E2
8835 | MBIO | Modbus ADAM Module | ModuleA Ch2 Invalid OFF | 138E3
8836 | MBIO | Modbus ADAM Module | ModuleA Ch3 Invalid ON | 138E4
8837 | MBIO | Modbus ADAM Module | ModuleA Ch3 Invalid OFF | 138E5
8838 | MBIO | Modbus ADAM Module | ModuleA Ch4 Invalid ON | 138E6
8839 | MBIO | Modbus ADAM Module | ModuleA Ch4 Invalid OFF | 138E7
8840 | MBIO | Modbus ADAM Module | ModuleA Ch5 Invalid ON | 138E8
8841 | MBIO | Modbus ADAM Module | ModuleA Ch5 Invalid OFF | 138E9
8842 | MBIO | Modbus ADAM Module | ModuleA Ch6 Invalid ON | 138E10
8843 | MBIO | Modbus ADAM Module | ModuleA Ch6 Invalid OFF | 138E11
8844 | MBIO | Modbus ADAM Module | ModuleA Ch7 Invalid ON | 138E12
8845 | MBIO | Modbus ADAM Module | ModuleA Ch7 Invalid OFF | 138E13
8846 | MBIO | Modbus ADAM Module | ModuleA Ch8 Invalid ON | 138E14
8847 | MBIO | Modbus ADAM Module | ModuleA Ch8 Invalid OFF | 138E15
8848 | MBIO | Modbus ADAM Module | ModuleB Ch1 Invalid ON | 138E16
8849 | MBIO | Modbus ADAM Module | ModuleB Ch1 Invalid OFF | 138E17
8850 | MBIO | Modbus ADAM Module | ModuleB Ch2 Invalid ON | 138E18
8851 | MBIO | Modbus ADAM Module | ModuleB Ch2 Invalid OFF | 138E19
8852 | MBIO | Modbus ADAM Module | ModuleB Ch3 Invalid ON | 138E20
8853 | MBIO | Modbus ADAM Module | ModuleB Ch3 Invalid OFF | 138E21
8854 | MBIO | Modbus ADAM Module | ModuleB Ch4 Invalid ON | 138E22
8855 | MBIO | Modbus ADAM Module | ModuleB Ch4 Invalid OFF | 138E23
8856 | MBIO | Modbus ADAM Module | ModuleB Ch5 Invalid ON | 138E24
8857 | MBIO | Modbus ADAM Module | ModuleB Ch5 Invalid OFF | 138E25
8858 | MBIO | Modbus ADAM Module | ModuleB Ch6 Invalid ON | 138E26
8859 | MBIO | Modbus ADAM Module | ModuleB Ch6 Invalid OFF | 138E27
8860 | MBIO | Modbus ADAM Module | ModuleB Ch7 Invalid ON | 138E28
8861 | MBIO | Modbus ADAM Module | ModuleB Ch7 Invalid OFF | 138E29
8862 | MBIO | Modbus ADAM Module | ModuleB Ch8 Invalid ON | 138E30
8863 | MBIO | Modbus ADAM Module | ModuleB Ch8 Invalid OFF | 138E31
8864 | MBIO | Modbus ADAM Module | ModuleC Ch1 Invalid ON | 138E32
8865 | MBIO | Modbus ADAM Module | ModuleC Ch1 Invalid OFF | 138E33
8866 | MBIO | Modbus ADAM Module | ModuleC Ch2 Invalid ON | 138E34
8867 | MBIO | Modbus ADAM Module | ModuleC Ch2 Invalid OFF | 138E35
8868 | MBIO | Modbus ADAM Module | ModuleC Ch3 Invalid ON | 138E36
8869 | MBIO | Modbus ADAM Module | ModuleC Ch3 Invalid OFF | 138E37
8870 | MBIO | Modbus ADAM Module | ModuleC Ch4 Invalid ON | 138E38
8871 | MBIO | Modbus ADAM Module | ModuleC Ch4 Invalid OFF | 138E39
8872 | MBIO | Modbus ADAM Module | ModuleC Ch5 Invalid ON | 138E40
8873 | MBIO | Modbus ADAM Module | ModuleC Ch5 Invalid OFF | 138E41
8874 | MBIO | Modbus ADAM Module | ModuleC Ch6 Invalid ON | 138E42
8875 | MBIO | Modbus ADAM Module | ModuleC Ch6 Invalid OFF | 138E43
8876 | MBIO | Modbus ADAM Module | ModuleC Ch7 Invalid ON | 138E44
8877 | MBIO | Modbus ADAM Module | ModuleC Ch7 Invalid OFF | 138E45
8878 | MBIO | Modbus ADAM Module | ModuleC Ch8 Invalid ON | 138E46
8879 | MBIO | Modbus ADAM Module | ModuleC Ch8 Invalid OFF | 138E47
9536 | UIM2 | Z<< [21U] Underimpedance | Start ON | 149E0
9537 | UIM2 | Z<< [21U] Underimpedance | Start OFF | 149E1
9538 | UIM2 | Z<< [21U] Underimpedance | Trip ON | 149E2
9539 | UIM2 | Z<< [21U] Underimpedance | Trip OFF | 149E3
9540 | UIM2 | Z<< [21U] Underimpedance | Block ON | 149E4
9541 | UIM2 | Z<< [21U] Underimpedance | Block OFF | 149E5
9600 | OBJ6 | Object 6 | Object Intermediate | 150E0
9601 | OBJ6 | Object 6 | Object Open | 150E1
9602 | OBJ6 | Object 6 | Object Close | 150E2
9603 | OBJ6 | Object 6 | Object Bad | 150E3
9604 | OBJ6 | Object 6 | WD Intermediate | 150E4
9605 | OBJ6 | Object 6 | WD Out | 150E5
9606 | OBJ6 | Object 6 | WD in | 150E6
9607 | OBJ6 | Object 6 | WD Bad | 150E7
9608 | OBJ6 | Object 6 | Open Request On | 150E8
9609 | OBJ6 | Object 6 | Open Request Off | 150E9
9610 | OBJ6 | Object 6 | Open Command On | 150E10
9611 | OBJ6 | Object 6 | Open Command Off | 150E11
9612 | OBJ6 | Object 6 | Close Request On | 150E12
9613 | OBJ6 | Object 6 | Close Request Off | 150E13
9614 | OBJ6 | Object 6 | Close Command On | 150E14
9615 | OBJ6 | Object 6 | Close Command Off | 150E15
9616 | OBJ6 | Object 6 | Open Blocked On | 150E16
9617 | OBJ6 | Object 6 | Open Blocked Off | 150E17
9618 | OBJ6 | Object 6 | Close Blocked On | 150E18
9619 | OBJ6 | Object 6 | Close Blocked Off | 150E19
9620 | OBJ6 | Object 6 | Object Ready | 150E20
9621 | OBJ6 | Object 6 | Object Not Ready | 150E21
9622 | OBJ6 | Object 6 | Sync Ok | 150E22
9623 | OBJ6 | Object 6 | Sync Not Ok | 150E23
9624 | OBJ6 | Object 6 | Open Command Fail | 150E24
9625 | OBJ6 | Object 6 | Close Command Fail | 150E25
9626 | OBJ6 | Object 6 | Final trip On | 150E26
9627 | OBJ6 | Object 6 | Final trip Off | 150E27
9628 | OBJ6 | Object 6 | Contact Abrasion Alarm On | 150E28
9629 | OBJ6 | Object 6 | Contact Abrasion Alarm Off | 150E29
9630 | OBJ6 | Object 6 | Switch Operating Time Exceeded On | 150E30
9631 | OBJ6 | Object 6 | Switch Operating Time Exceeded Off | 150E31
9632 | OBJ6 | Object 6 | XCBR Loc On | 150E32
9633 | OBJ6 | Object 6 | XCBR Loc Off | 150E33
9634 | OBJ6 | Object 6 | XSWI Loc On | 150E34
9635 | OBJ6 | Object 6 | XSWI LOC Off | 150E35
9664 | OBJ7 | Object 7 | Object Intermediate | 151E0
9665 | OBJ7 | Object 7 | Object Open | 151E1
9666 | OBJ7 | Object 7 | Object Close | 151E2
9667 | OBJ7 | Object 7 | Object Bad | 151E3
9668 | OBJ7 | Object 7 | WD Intermediate | 151E4
9669 | OBJ7 | Object 7 | WD Out | 151E5
9670 | OBJ7 | Object 7 | WD in | 151E6
9671 | OBJ7 | Object 7 | WD Bad | 151E7
9672 | OBJ7 | Object 7 | Open Request On | 151E8
9673 | OBJ7 | Object 7 | Open Request Off | 151E9
9674 | OBJ7 | Object 7 | Open Command On | 151E10
9675 | OBJ7 | Object 7 | Open Command Off | 151E11
9676 | OBJ7 | Object 7 | Close Request On | 151E12
9677 | OBJ7 | Object 7 | Close Request Off | 151E13
9678 | OBJ7 | Object 7 | Close Command On | 151E14
9679 | OBJ7 | Object 7 | Close Command Off | 151E15
9680 | OBJ7 | Object 7 | Open Blocked On | 151E16
9681 | OBJ7 | Object 7 | Open Blocked Off | 151E17
9682 | OBJ7 | Object 7 | Close Blocked On | 151E18
9683 | OBJ7 | Object 7 | Close Blocked Off | 151E19
9684 | OBJ7 | Object 7 | Object Ready | 151E20
9685 | OBJ7 | Object 7 | Object Not Ready | 151E21
9686 | OBJ7 | Object 7 | Sync Ok | 151E22
9687 | OBJ7 | Object 7 | Sync Not Ok | 151E23
9688 | OBJ7 | Object 7 | Open Command Fail | 151E24
9689 | OBJ7 | Object 7 | Close Command Fail | 151E25
9690 | OBJ7 | Object 7 | Final trip On | 151E26
9691 | OBJ7 | Object 7 | Final trip Off | 151E27
9692 | OBJ7 | Object 7 | Contact Abrasion Alarm On | 151E28
9693 | OBJ7 | Object 7 | Contact Abrasion Alarm Off | 151E29
9694 | OBJ7 | Object 7 | Switch Operating Time Exceeded On | 151E30
9695 | OBJ7 | Object 7 | Switch Operating Time Exceeded Off | 151E31
9696 | OBJ7 | Object 7 | XCBR Loc On | 151E32
9697 | OBJ7 | Object 7 | XCBR Loc Off | 151E33
9698 | OBJ7 | Object 7 | XSWI Loc On | 151E34
9699 | OBJ7 | Object 7 | XSWI LOC Off | 151E35
9728 | OBJ8 | Object 8 | Object Intermediate | 152E0
9729 | OBJ8 | Object 8 | Object Open | 152E1
9730 | OBJ8 | Object 8 | Object Close | 152E2
9731 | OBJ8 | Object 8 | Object Bad | 152E3
9732 | OBJ8 | Object 8 | WD Intermediate | 152E4
9733 | OBJ8 | Object 8 | WD Out | 152E5
9734 | OBJ8 | Object 8 | WD in | 152E6
9735 | OBJ8 | Object 8 | WD Bad | 152E7
9736 | OBJ8 | Object 8 | Open Request On | 152E8
9737 | OBJ8 | Object 8 | Open Request Off | 152E9
9738 | OBJ8 | Object 8 | Open Command On | 152E10
9739 | OBJ8 | Object 8 | Open Command Off | 152E11
9740 | OBJ8 | Object 8 | Close Request On | 152E12
9741 | OBJ8 | Object 8 | Close Request Off | 152E13
9742 | OBJ8 | Object 8 | Close Command On | 152E14
9743 | OBJ8 | Object 8 | Close Command Off | 152E15
9744 | OBJ8 | Object 8 | Open Blocked On | 152E16
9745 | OBJ8 | Object 8 | Open Blocked Off | 152E17
9746 | OBJ8 | Object 8 | Close Blocked On | 152E18
9747 | OBJ8 | Object 8 | Close Blocked Off | 152E19
9748 | OBJ8 | Object 8 | Object Ready | 152E20
9749 | OBJ8 | Object 8 | Object Not Ready | 152E21
9750 | OBJ8 | Object 8 | Sync Ok | 152E22
9751 | OBJ8 | Object 8 | Sync Not Ok | 152E23
9752 | OBJ8 | Object 8 | Open Command Fail | 152E24
9753 | OBJ8 | Object 8 | Close Command Fail | 152E25
9754 | OBJ8 | Object 8 | Final trip On | 152E26
9755 | OBJ8 | Object 8 | Final trip Off | 152E27
9756 | OBJ8 | Object 8 | Contact Abrasion Alarm On | 152E28
9757 | OBJ8 | Object 8 | Contact Abrasion Alarm Off | 152E29
9758 | OBJ8 | Object 8 | Switch Operating Time Exceeded On | 152E30
9759 | OBJ8 | Object 8 | Switch Operating Time Exceeded Off | 152E31
9760 | OBJ8 | Object 8 | XCBR Loc On | 152E32
9761 | OBJ8 | Object 8 | XCBR Loc Off | 152E33
9762 | OBJ8 | Object 8 | XSWI Loc On | 152E34
9763 | OBJ8 | Object 8 | XSWI LOC Off | 152E35
9792 | OBJ9 | Object 9 | Object Intermediate | 153E0
9793 | OBJ9 | Object 9 | Object Open | 153E1
9794 | OBJ9 | Object 9 | Object Close | 153E2
9795 | OBJ9 | Object 9 | Object Bad | 153E3
9796 | OBJ9 | Object 9 | WD Intermediate | 153E4
9797 | OBJ9 | Object 9 | WD Out | 153E5
9798 | OBJ9 | Object 9 | WD in | 153E6
9799 | OBJ9 | Object 9 | WD Bad | 153E7
9800 | OBJ9 | Object 9 | Open Request On | 153E8
9801 | OBJ9 | Object 9 | Open Request Off | 153E9
9802 | OBJ9 | Object 9 | Open Command On | 153E10
9803 | OBJ9 | Object 9 | Open Command Off | 153E11
9804 | OBJ9 | Object 9 | Close Request On | 153E12
9805 | OBJ9 | Object 9 | Close Request Off | 153E13
9806 | OBJ9 | Object 9 | Close Command On | 153E14
9807 | OBJ9 | Object 9 | Close Command Off | 153E15
9808 | OBJ9 | Object 9 | Open Blocked On | 153E16
9809 | OBJ9 | Object 9 | Open Blocked Off | 153E17
9810 | OBJ9 | Object 9 | Close Blocked On | 153E18
9811 | OBJ9 | Object 9 | Close Blocked Off | 153E19
9812 | OBJ9 | Object 9 | Object Ready | 153E20
9813 | OBJ9 | Object 9 | Object Not Ready | 153E21
9814 | OBJ9 | Object 9 | Sync Ok | 153E22
9815 | OBJ9 | Object 9 | Sync Not Ok | 153E23
9816 | OBJ9 | Object 9 | Open Command Fail | 153E24
9817 | OBJ9 | Object 9 | Close Command Fail | 153E25
9818 | OBJ9 | Object 9 | Final trip On | 153E26
9819 | OBJ9 | Object 9 | Final trip Off | 153E27
9820 | OBJ9 | Object 9 | Contact Abrasion Alarm On | 153E28
9821 | OBJ9 | Object 9 | Contact Abrasion Alarm Off | 153E29
9822 | OBJ9 | Object 9 | Switch Operating Time Exceeded On | 153E30
9823 | OBJ9 | Object 9 | Switch Operating Time Exceeded Off | 153E31
9824 | OBJ9 | Object 9 | XCBR Loc On | 153E32
9825 | OBJ9 | Object 9 | XCBR Loc Off | 153E33
9826 | OBJ9 | Object 9 | XSWI Loc On | 153E34
9827 | OBJ9 | Object 9 | XSWI LOC Off | 153E35
9856 | OBJ10 | Object 10 | Object Intermediate | 154E0
9857 | OBJ10 | Object 10 | Object Open | 154E1
9858 | OBJ10 | Object 10 | Object Close | 154E2
9859 | OBJ10 | Object 10 | Object Bad | 154E3
9860 | OBJ10 | Object 10 | WD Intermediate | 154E4
9861 | OBJ10 | Object 10 | WD Out | 154E5
9862 | OBJ10 | Object 10 | WD in | 154E6
9863 | OBJ10 | Object 10 | WD Bad | 154E7
9864 | OBJ10 | Object 10 | Open Request On | 154E8
9865 | OBJ10 | Object 10 | Open Request Off | 154E9
9866 | OBJ10 | Object 10 | Open Command On | 154E10
9867 | OBJ10 | Object 10 | Open Command Off | 154E11
9868 | OBJ10 | Object 10 | Close Request On | 154E12
9869 | OBJ10 | Object 10 | Close Request Off | 154E13
9870 | OBJ10 | Object 10 | Close Command On | 154E14
9871 | OBJ10 | Object 10 | Close Command Off | 154E15
9872 | OBJ10 | Object 10 | Open Blocked On | 154E16
9873 | OBJ10 | Object 10 | Open Blocked Off | 154E17
9874 | OBJ10 | Object 10 | Close Blocked On | 154E18
9875 | OBJ10 | Object 10 | Close Blocked Off | 154E19
9876 | OBJ10 | Object 10 | Object Ready | 154E20
9877 | OBJ10 | Object 10 | Object Not Ready | 154E21
9878 | OBJ10 | Object 10 | Sync Ok | 154E22
9879 | OBJ10 | Object 10 | Sync Not Ok | 154E23
9880 | OBJ10 | Object 10 | Open Command Fail | 154E24
9881 | OBJ10 | Object 10 | Close Command Fail | 154E25
9882 | OBJ10 | Object 10 | Final trip On | 154E26
9883 | OBJ10 | Object 10 | Final trip Off | 154E27
9884 | OBJ10 | Object 10 | Contact Abrasion Alarm On | 154E28
9885 | OBJ10 | Object 10 | Contact Abrasion Alarm Off | 154E29
9886 | OBJ10 | Object 10 | Switch Operating Time Exceeded On | 154E30
9887 | OBJ10 | Object 10 | Switch Operating Time Exceeded Off | 154E31
9888 | OBJ10 | Object 10 | XCBR Loc On | 154E32
9889 | OBJ10 | Object 10 | XCBR Loc Off | 154E33
9890 | OBJ10 | Object 10 | XSWI Loc On | 154E34
9891 | OBJ10 | Object 10 | XSWI LOC Off | 154E35
9920 | VJP1 | [78] Vector jump | Block On | 155E0
9921 | VJP1 | [78] Vector jump | Block Off | 155E1
9922 | VJP1 | [78] Vector jump | Trip On | 155E2
9923 | VJP1 | [78] Vector jump | Trip Off | 155E3
9924 | VJP1 | [78] Vector jump | Alarm On | 155E4
9925 | VJP1 | [78] Vector jump | Alarm Off | 155E5
9984 | GMAG | Measurement value recorder | FCL on limit On | 156E0
9985 | GMAG | Measurement value recorder | FCL on limit Off | 156E1
9986 | GMAG | Running hour counter | UEL in operation On | 156E2
9987 | GMAG | Running hour counter | UEL in operation Off | 156E3
9988 | GMAG | Running hour counter | SCL Overexcitation On | 156E4
9989 | GMAG | Running hour counter | SCL Overexcitation Off | 156E5
9990 | GMAG | Generator commander | SCL Underexcitation On | 156E6
9991 | GMAG | Generator commander | SCL Underexcitation Off | 156E7
9992 | GMAG | Generator commander | High IP On | 156E8
9993 | GMAG | Generator commander | High IP Off | 156E9
9994 | GMAG | Generator commander | Inst FCL On | 156E10
9995 | GMAG | Generator commander | Inst FCL Off | 156E11
9996 | GMAG | Generator commander | Low supply voltage On | 156E12
9997 | GMAG | Generator commander | Low supply voltage Off | 156E13
9998 | GMAG | Generator commander | FCR Mode On | 156E14
9999 | GMAG | Generator commander | FCR Mode Off | 156E15
10000 | GMAG | Generator commander | AVR Mode On | 156E16
10001 | GMAG | Generator commander | AVR Mode Off | 156E17
10002 | GMAG | Generator commander | Low meas volt On | 156E18
10003 | GMAG | Generator commander | Low meas volt Off | 156E19
10004 | GMAG | Generator commander | IGBT Shorted On | 156E20
10005 | GMAG | Generator commander | IGBT Shorted Off | 156E21
10006 | GMAG | Generator commander | PWM Enable On | 156E22
10007 | GMAG | Generator commander | PWM Enable Off | 156E23
10008 | GMAG | Generator commander | PWM DO1 On | 156E24
10009 | GMAG | Generator commander | PWM DO1 Off | 156E25
10010 | GMAG | Generator commander | PWM DO2 On | 156E26
10011 | GMAG | Generator commander | PWM DO2 Off | 156E27
10012 | GMAG | Generator commander | Rectifier trip On | 156E28
10013 | GMAG | Generator commander | Rectifier trip Off | 156E29
10014 | GMAG | Generator commander | Temp high breaker 1 On | 156E30
10015 | GMAG | Generator commander | Temp high breaker 1 Off | 156E31
10016 | GMAG | Generator commander | Temp high breaker 2 On | 156E32
10017 | GMAG | Generator commander | Temp high breaker 2 Off | 156E33
10018 | GMAG | Generator commander | Excitation On | 156E34
10019 | GMAG | Generator commander | Exc On Cmd Off | 156E35
10020 | GMAG | Generator commander | Excitation Off | 156E36
10021 | GMAG | Generator commander | Exc Off Cmd Off | 156E37
10022 | GMAG | Generator commander | Diode fault On | 156E38
10023 | GMAG | Generator commander | Diode fault Off | 156E39
10024 | GMAG | Generator commander | Overcurrent On | 156E40
10025 | GMAG | Generator commander | Overcurrent Off | 156E41
10026 | GMAG | Generator commander | PWM DI1 On | 156E42
10027 | GMAG | Generator commander | PWM DI1 Off | 156E43
10028 | GMAG | Generator commander | PWM DI2 On | 156E44
10029 | GMAG | Generator commander | PWM DI2 Off | 156E45
10030 | GMAG | Generator commander | PWM DI3 On | 156E46
10031 | GMAG | Generator commander | PWM DI3 Off | 156E47
10032 | GMAG | Generator commander | PWM DI4 On | 156E48
10033 | GMAG | Generator commander | PWM DI4 Off | 156E49
10034 | GMAG | Generator commander | PWM DI5 On | 156E50
10035 | GMAG | Generator commander | PWM DI5 Off | 156E51
10036 | GMAG | Generator commander | PWM DI6 On | 156E52
10037 | GMAG | Generator commander | PWM DI6 Off | 156E53
10038 | GMAG | Generator commander | PWM DI7 On | 156E54
10039 | GMAG | Generator commander | PWM DI7 Off | 156E55
10040 | GMAG | Generator commander | PWM DI8 On | 156E56
10041 | GMAG | Generator commander | PWM DI8 Off | 156E57
10048 | GMAG1 | Generator commander | Synchronised On | 157E0
10049 | GMAG1 | Generator commander | Synchronised Off | 157E1
10050 | GMAG1 | Generator commander | Islandmode On | 157E2
10051 | GMAG1 | Generator commander | Islandmode Off | 157E3
10052 | GMAG1 | Generator commander | FB is Open On | 157E4
10053 | GMAG1 | Generator commander | FB is Open Off | 157E5
10054 | GMAG1 | Generator commander | FB is Closed On | 157E6
10055 | GMAG1 | Generator commander | FB is Closed Off | 157E7
10056 | GMAG1 | Generator commander | Field flashing On | 157E8
10057 | GMAG1 | Generator commander | Field flashing Off | 157E9
10058 | GMAG1 | Generator commander | Long field flashing On | 157E10
10059 | GMAG1 | Generator commander | Long field flashing Off | 157E11
10060 | GMAG1 | Generator commander | Test mode On | 157E12
10061 | GMAG1 | Generator commander | Test mode Off | 157E13
10062 | GMAG1 | Generator commander | Phase retard On | 157E14
10063 | GMAG1 | Generator commander | Phase retard Off | 157E15
10064 | GMAG1 | Generator commander | Reset On | 157E16
10065 | GMAG1 | Generator commander | Reset Off | 157E17
10066 | GMAG1 | Generator commander | Command AVR On | 157E18
10067 | GMAG1 | Generator commander | Command AVR Off | 157E19
10068 | GMAG1 | Generator commander | Command FCR On | 157E20
10069 | GMAG1 | Generator commander | Command FCR Off | 157E21
10070 | GMAG1 | Generator commander | Command MVar On | 157E22
10071 | GMAG1 | Generator commander | Command MVar Off | 157E23
10072 | GMAG1 | Generator commander | Command PF On | 157E24
10073 | GMAG1 | Generator commander | Command PF Off | 157E25
10074 | GMAG1 | Generator commander | Excitation run order On | 157E26
10075 | GMAG1 | Generator commander | Excitation run order Off | 157E27
10076 | GMAG1 | Generator commander | Increase On | 157E28
10077 | GMAG1 | Generator commander | Increase Off | 157E29
10078 | GMAG1 | Generator commander | Decrease On | 157E30
10079 | GMAG1 | Generator commander | Decrease Off | 157E31
10080 | GMAG1 | Generator commander | AVR Bus On | 157E32
10081 | GMAG1 | Generator commander | AVR Bus Off | 157E33
10082 | GMAG1 | Generator commander | FCR Bus On | 157E34
10083 | GMAG1 | Generator commander | FCR Bus Off | 157E35
10084 | GMAG1 | Generator commander | MVar Bus On | 157E36
10085 | GMAG1 | Generator commander | MVar Bus Off | 157E37
10086 | GMAG1 | Generator commander | PF Bus On | 157E38
10087 | GMAG1 | Generator commander | PF Bus Off | 157E39
10088 | GMAG1 | Generator commander | Overriding control On | 157E40
10089 | GMAG1 | Generator commander | Overriding control Off | 157E41
10090 | GMAG1 | Generator commander | Increase MVAR/PF On | 157E42
10091 | GMAG1 | Generator commander | Increase MVAR/PF Off | 157E43
10092 | GMAG1 | Generator commander | Decrease MVAR/PF On | 157E44
10093 | GMAG1 | Generator commander | Decrease MVAR/PF Off | 157E45
10094 | GMAG1 | Generator commander | Low Q error On | 157E46
10095 | GMAG1 | Generator commander | Low Q error Off | 157E47
10096 | GMAG1 | Generator commander | AVR ref on lowlim On | 157E48
10097 | GMAG1 | Generator commander | AVR ref on lowlim Off | 157E49
10098 | GMAG1 | Generator commander | AVR ref on highlim On | 157E50
10099 | GMAG1 | Generator commander | AVR ref on highlim Off | 157E51
10100 | GMAG1 | Generator commander | FCR ref on lowlim On | 157E52
10101 | GMAG1 | Generator commander | FCR ref on lowlim Off | 157E53
10102 | GMAG1 | Generator commander | FCR ref on highlim On | 157E54
10103 | GMAG1 | Generator commander | FCR ref on highlim Off | 157E55
10104 | GMAG1 | Generator commander | VHZ limit active On | 157E56
10105 | GMAG1 | Generator commander | VHZ limit active Off | 157E57
10106 | GMAG1 | Generator commander | Process panel activated On | 157E58
10107 | GMAG1 | Generator commander | Process panel activated Off | 157E59
10108 | GMAG1 | Generator commander | Parameters active On | 157E60
10109 | GMAG1 | Generator commander | Parameters active Off | 157E61
10110 | GMAG1 | Generator commander | Bus activated On | 157E62
10111 | GMAG1 | Generator commander | Bus activated Off | 157E63
10112 | GMAG2 | Generator commander | Reset and excitation off On | 158E0
10113 | GMAG2 | Generator commander | Reset and excitation off Off | 158E1
10114 | GMAG2 | Generator commander | Field breaker does not open On | 158E2
10115 | GMAG2 | Generator commander | Field breaker does not open Off | 158E3
10116 | GMAG2 | Generator commander | New reference start On | 158E4
10117 | GMAG2 | Generator commander | New reference start Off | 158E5
10118 | GMAG2 | Generator commander | GB is closed On | 158E6
10119 | GMAG2 | Generator commander | GB is closed Off | 158E7
10120 | GMAG2 | Generator commander | FB off GB on On | 158E8
10121 | GMAG2 | Generator commander | FB off GB on Off | 158E9
10122 | GMAG2 | Generator commander | Disturbed mode On | 158E10
10123 | GMAG2 | Generator commander | Disturbed mode Off | 158E11
10124 | GMAG2 | Generator commander | Disturbed mode pulse On | 158E12
10125 | GMAG2 | Generator commander | Disturbed mode pulse Off | 158E13
10126 | GMAG2 | Generator commander | Following line voltage On | 158E14
10127 | GMAG2 | Generator commander | Following line voltage Off | 158E15
10128 | GMAG2 | Generator commander | Test Square enable On | 158E16
10129 | GMAG2 | Generator commander | Test Square enable Off | 158E17
10130 | GMAG2 | Generator commander | Order open FB On | 158E18
10131 | GMAG2 | Generator commander | Order open FB Off | 158E19
10132 | GMAG2 | Generator commander | Order close FB On | 158E20
10133 | GMAG2 | Generator commander | Order close FB Off | 158E21
10134 | GMAG2 | Generator commander | Q unloaded On | 158E22
10135 | GMAG2 | Generator commander | Q unloaded Off | 158E23
10136 | GMAG2 | Generator commander | MVAR ref on high On | 158E24
10137 | GMAG2 | Generator commander | MVAR ref on high Off | 158E25
10138 | GMAG2 | Generator commander | MVAR ref on low On | 158E26
10139 | GMAG2 | Generator commander | MVAR ref on low Off | 158E27
10140 | GMAG2 | Generator commander | PF ref on high On | 158E28
10141 | GMAG2 | Generator commander | PF ref on high Off | 158E29
10142 | GMAG2 | Generator commander | PF ref on low On | 158E30
10143 | GMAG2 | Generator commander | PF ref on low Off | 158E31
10144 | GMAG2 | Generator commander | AVR start Ref On | 158E32
10145 | GMAG2 | Generator commander | AVR start Ref Off | 158E33
10146 | GMAG2 | Generator commander | FCR start Ref On | 158E34
10147 | GMAG2 | Generator commander | FCR start Ref Off | 158E35
10148 | GMAG2 | Generator commander | Unload MVAR On | 158E36
10149 | GMAG2 | Generator commander | Unload MVAR Off | 158E37
10150 | GMAG2 | Generator commander | PWM DO3 On | 158E38
10151 | GMAG2 | Generator commander | PWM DO3 Off | 158E39
10152 | GMAG2 | Generator commander | PWM DO4 On | 158E40
10153 | GMAG2 | Generator commander | PWM DO4 Off | 158E41
10154 | GMAG2 | Generator commander | MVAR Mode On | 158E42
10155 | GMAG2 | Generator commander | MVAR Mode Off | 158E43
10156 | GMAG2 | Generator commander | PF Mode On | 158E44
10157 | GMAG2 | Generator commander | PF Mode Off | 158E45
10158 | GMAG2 | Generator commander | PSS Enabled On | 158E46
10159 | GMAG2 | Generator commander | PSS Enabled Off | 158E47
10160 | GMAG2 | Generator commander | PSS Blocked On | 158E48
10161 | GMAG2 | Generator commander | PSS Blocked Off | 158E49
10176 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 1 On (Alarm 1) | 159E0
10177 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 1 Off (Alarm 1) | 159E1
10178 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 2 On (Alarm 2) | 159E2
10179 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 2 Off (Alarm 2) | 159E3
10180 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 3 On (Alarm 3) | 159E4
10181 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 3 Off (Alarm 3) | 159E5
10182 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 4 On (Alarm 4) | 159E6
10183 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 4 Off (Alarm 4) | 159E7
10184 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 5 On (Alarm 5) | 159E8
10185 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 5 Off (Alarm 5) | 159E9
10186 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 6 On (Alarm 6) | 159E10
10187 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 6 Off (Alarm 6) | 159E11
10188 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 7 On (Alarm 7) | 159E12
10189 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 7 Off (Alarm 7) | 159E13
10190 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 8 On (Alarm 8) | 159E14
10191 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 8 Off (Alarm 8) | 159E15
10192 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 9 On (Alarm 9) | 159E16
10193 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 9 Off (Alarm 9) | 159E17
10194 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 10 On (Alarm 10) | 159E18
10195 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 10 Off (Alarm 10) | 159E19
10196 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 11 On (Alarm 11) | 159E20
10197 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 11 Off (Alarm 11) | 159E21
10198 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 12 On (Alarm 12) | 159E22
10199 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 12 Off (Alarm 12) | 159E23
10200 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 13 On (Alarm 13) | 159E24
10201 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 13 Off (Alarm 13) | 159E25
10202 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 14 On (Alarm 14) | 159E26
10203 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 14 Off (Alarm 14) | 159E27
10204 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 15 On (Alarm 15) | 159E28
10205 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 15 Off (Alarm 15) | 159E29
10206 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 16 On (Alarm 16) | 159E30
10207 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 16 Off (Alarm 16) | 159E31
10208 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 17 On (Alarm 17) | 159E32
10209 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 17 Off (Alarm 17) | 159E33
10210 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 18 On (Alarm 18) | 159E34
10211 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 18 Off (Alarm 18) | 159E35
10212 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 19 On (Alarm 19) | 159E36
10213 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 19 Off (Alarm 19) | 159E37
10214 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 20 On (Alarm 20) | 159E38
10215 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 20 Off (Alarm 20) | 159E39
10216 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 21 On (Alarm 21) | 159E40
10217 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 21 Off (Alarm 21) | 159E41
10218 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 22 On (Alarm 22) | 159E42
10219 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 22 Off (Alarm 22) | 159E43
10220 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 23 On (Alarm 23) | 159E44
10221 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 23 Off (Alarm 23) | 159E45
10222 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 24 On (Alarm 24) | 159E46
10223 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 24 Off (Alarm 24) | 159E47
10224 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 25 On (Alarm 25) | 159E48
10225 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 25 Off (Alarm 25) | 159E49
10226 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 26 On (Alarm 26) | 159E50
10227 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 26 Off (Alarm 26) | 159E51
10228 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 27 On (Alarm 27) | 159E52
10229 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 27 Off (Alarm 27) | 159E53
10230 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 28 On (Alarm 28) | 159E54
10231 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 28 Off (Alarm 28) | 159E55
10232 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 29 On (Alarm 29) | 159E56
10233 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 29 Off (Alarm 29) | 159E57
10234 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 30 On (Alarm 30) | 159E58
10235 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 30 Off (Alarm 30) | 159E59
10236 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 31 On (Alarm 31) | 159E60
10237 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 31 Off (Alarm 31) | 159E61
10238 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 32 On (Alarm 32) | 159E62
10239 | ALARM1 | AQ-S214 and AQ-S254 alarms | Alarm 32 Off (Alarm 32) | 159E63
10240 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 33 On (Alarm 33) | 160E0
10241 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 33 Off (Alarm 33) | 160E1
10242 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 34 On (Alarm 34) | 160E2
10243 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 34 Off (Alarm 34) | 160E3
10244 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 35 On (Alarm 35) | 160E4
10245 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 35 Off (Alarm 35) | 160E5
10246 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 36 On (Alarm 36) | 160E6
10247 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 36 Off (Alarm 36) | 160E7
10248 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 37 On (Alarm 37) | 160E8
10249 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 37 Off (Alarm 37) | 160E9
10250 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 38 On (Alarm 38) | 160E10
10251 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 38 Off (Alarm 38) | 160E11
10252 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 39 On (Alarm 39) | 160E12
10253 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 39 Off (Alarm 39) | 160E13
10254 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 40 On (Alarm 40) | 160E14
10255 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 40 Off (Alarm 40) | 160E15
10256 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 41 On (Alarm 41) | 160E16
10257 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 41 Off (Alarm 41) | 160E17
10258 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 42 On (Alarm 42) | 160E18
10259 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 42 Off (Alarm 42) | 160E19
10260 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 43 On (Alarm 43) | 160E20
10261 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 43 Off (Alarm 43) | 160E21
10262 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 44 On (Alarm 44) | 160E22
10263 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 44 Off (Alarm 44) | 160E23
10264 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 45 On (Alarm 45) | 160E24
10265 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 45 Off (Alarm 45) | 160E25
10266 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 46 On (Alarm 46) | 160E26
10267 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 46 Off (Alarm 46) | 160E27
10268 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 47 On (Alarm 47) | 160E28
10269 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 47 Off (Alarm 47) | 160E29
10270 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 48 On (Alarm 48) | 160E30
10271 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 48 Off (Alarm 48) | 160E31
10272 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 49 On (Alarm 49) | 160E32
10273 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 49 Off (Alarm 49) | 160E33
10274 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 50 On (Alarm 50) | 160E34
10275 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 50 Off (Alarm 50) | 160E35
10276 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 51 On (Alarm 51) | 160E36
10277 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 51 Off (Alarm 51) | 160E37
10278 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 52 On (Alarm 52) | 160E38
10279 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 52 Off (Alarm 52) | 160E39
10280 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 53 On (Alarm 53) | 160E40
10281 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 53 Off (Alarm 53) | 160E41
10282 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 54 On (Alarm 54) | 160E42
10283 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 54 Off (Alarm 54) | 160E43
10284 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 55 On (Alarm 55) | 160E44
10285 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 55 Off (Alarm 55) | 160E45
10286 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 56 On (Alarm 56) | 160E46
10287 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 56 Off (Alarm 56) | 160E47
10288 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 57 On (Alarm 57) | 160E48
10289 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 57 Off (Alarm 57) | 160E49
10290 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 58 On (Alarm 58) | 160E50
10291 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 58 Off (Alarm 58) | 160E51
10292 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 59 On (Alarm 59) | 160E52
10293 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 59 Off (Alarm 59) | 160E53
10294 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 60 On (Alarm 60) | 160E54
10295 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 60 Off (Alarm 60) | 160E55
10296 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 61 On (Alarm 61) | 160E56
10297 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 61 Off (Alarm 61) | 160E57
10298 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 62 On (Alarm 62) | 160E58
10299 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 62 Off (Alarm 62) | 160E59
10300 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 63 On (Alarm 63) | 160E60
10301 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 63 Off (Alarm 63) | 160E61
10302 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 64 On (Alarm 64) | 160E62
10303 | ALARM2 | AQ-S214 and AQ-S254 alarms | Alarm 64 Off (Alarm 64) | 160E63
10304 | IAE1 | Inadvertent energizing | Start ON | 161E0
10305 | IAE1 | Inadvertent energizing | Start OFF | 161E1
10306 | IAE1 | Inadvertent energizing | Trip ON | 161E2
10307 | IAE1 | Inadvertent energizing | Trip OFF | 161E3
10308 | IAE1 | Inadvertent energizing | Block ON | 161E4
10309 | IAE1 | Inadvertent energizing | Block OFF | 161E5
10310 | IAE1 | Inadvertent energizing | Low Current On | 161E6
10311 | IAE1 | Inadvertent energizing | Low Current Off | 161E7
10312 | IAE1 | Inadvertent energizing | Low Voltage On | 161E8
10313 | IAE1 | Inadvertent energizing | Low Voltage On | 161E9
10368 | GSYN | Synchronizer | Synchronizing Blocked On | 162E0
10369 | GSYN | Synchronizer | Synchronizing Blocked Off | 162E1
10370 | GSYN | Synchronizer | Synchronizing Running On | 162E2
10371 | GSYN | Synchronizer | Synchronizing Running Off | 162E3
10372 | GSYN | Synchronizer | Synchr. Increase Voltage On | 162E4
10373 | GSYN | Synchronizer | Synchr. Increase Voltage Off | 162E5
10374 | GSYN | Synchronizer | Synchr. Decrease Voltage On | 162E6
10375 | GSYN | Synchronizer | Synchr. Decrease Voltage Off | 162E7
10376 | GSYN | Synchronizer | Synchr. Increase Frequency On | 162E8
10377 | GSYN | Synchronizer | Synchr. Increase Frequency Off | 162E9
10378 | GSYN | Synchronizer | Synchr. Decrease Frequency On | 162E10
10379 | GSYN | Synchronizer | Synchr. Decrease Frequency Off | 162E11
10380 | GSYN | Synchronizer | Synchronizer BRK Close On | 162E12
10381 | GSYN | Synchronizer | Synchronizer BRK Close Off | 162E13
10382 | GSYN | Synchronizer | Synchronizer Long Sync. Time On | 162E14
10383 | GSYN | Synchronizer | Synchronizer Long Sync. Time Off | 162E15
10384 | GSYN | Synchronizer | Synchroswitch Close fail Re-init On | 162E16
10385 | GSYN | Synchronizer | Synchroswitch Close fail Re-init Off | 162E17
10386 | GSYN | Synchronizer | Synchroswitching requested On | 162E18
10387 | GSYN | Synchronizer | Synchroswitching requested Off | 162E19
10388 | GSYN | Synchronizer | GSYN Voltage Mag.Difference Ok | 162E20
10389 | GSYN | Synchronizer | GSYN Voltage Mag.Difference Not Ok | 162E21
10390 | GSYN | Synchronizer | GSYN Voltage Freq.Difference Ok | 162E22
10391 | GSYN | Synchronizer | GSYN Voltage Freq.Difference Not Ok | 162E23
10392 | GSYN | Synchronizer | GSYN Voltage Ang.Difference Ok | 162E24
10393 | GSYN | Synchronizer | GSYN Voltage Ang.Difference Not Ok | 162E25
10394 | GSYN | Synchronizer | GSYN Nets Standstill On | 162E26
10395 | GSYN | Synchronizer | GSYN Nets Standstill Off | 162E27
10396 | GSYN | Synchronizer | GSYN Nets Departing On | 162E28
10397 | GSYN | Synchronizer | GSYN Nets Departing Off | 162E29
10398 | GSYN | Synchronizer | GSYN Nets Enclosing On | 162E30
10399 | GSYN | Synchronizer | GSYN Nets Enclosing Off | 162E31
10432 | VREC | Measurement value recorder | Trigger On | 163E0
10433 | VREC | Measurement value recorder | Trigger Off | 163E1
10496 | PWR1 | P/Q/S Power protection | Start ON | 164E0
10497 | PWR1 | P/Q/S Power protection | Start OFF | 164E1
10498 | PWR1 | P/Q/S Power protection | Trip ON | 164E2
10499 | PWR1 | P/Q/S Power protection | Trip OFF | 164E3
10500 | PWR1 | P/Q/S Power protection | Block ON | 164E4
10501 | PWR1 | P/Q/S Power protection | Block OFF | 164E5
10560 | PWR2 | P/Q/S Power protection | Start ON | 165E0
10561 | PWR2 | P/Q/S Power protection | Start OFF | 165E1
10562 | PWR2 | P/Q/S Power protection | Trip ON | 165E2
10563 | PWR2 | P/Q/S Power protection | Trip OFF | 165E3
10564 | PWR2 | P/Q/S Power protection | Block ON | 165E4
10565 | PWR2 | P/Q/S Power protection | Block OFF | 165E5
10624 | PWR3 | P/Q/S Power protection | Start ON | 166E0
10625 | PWR3 | P/Q/S Power protection | Start OFF | 166E1
10626 | PWR3 | P/Q/S Power protection | Trip ON | 166E2
10627 | PWR3 | P/Q/S Power protection | Trip OFF | 166E3
10628 | PWR3 | P/Q/S Power protection | Block ON | 166E4
10629 | PWR3 | P/Q/S Power protection | Block OFF | 166E5
10688 | PWR4 | P/Q/S Power protection | Start ON | 167E0
10689 | PWR4 | P/Q/S Power protection | Start OFF | 167E1
10690 | PWR4 | P/Q/S Power protection | Trip ON | 167E2
10691 | PWR4 | P/Q/S Power protection | Trip OFF | 167E3
10692 | PWR4 | P/Q/S Power protection | Block ON | 167E4
10693 | PWR4 | P/Q/S Power protection | Block OFF | 167E5
10752 | CIN6 | Indicator object 1 | Intermediate | 168E0
10753 | CIN6 | Indicator object 1 | Open | 168E1
10754 | CIN6 | Indicator object 1 | Close | 168E2
10755 | CIN6 | Indicator object 1 | Bad | 168E3
10816 | CIN7 | Indicator object 2 | Intermediate | 169E0
10817 | CIN7 | Indicator object 2 | Open | 169E1
10818 | CIN7 | Indicator object 2 | Close | 169E2
10819 | CIN7 | Indicator object 2 | Bad | 169E3
10880 | CIN8 | Indicator object 3 | Intermediate | 170E0
10881 | CIN8 | Indicator object 3 | Open | 170E1
10882 | CIN8 | Indicator object 3 | Close | 170E2
10883 | CIN8 | Indicator object 3 | Bad | 170E3
10944 | CIN9 | Indicator object 4 | Intermediate | 171E0
10945 | CIN9 | Indicator object 4 | Open | 171E1
10946 | CIN9 | Indicator object 4 | Close | 171E2
10947 | CIN9 | Indicator object 4 | Bad | 171E3
11008 | CIN10 | Indicator object 5 | Intermediate | 172E0
11009 | CIN10 | Indicator object 5 | Open | 172E1
11010 | CIN10 | Indicator object 5 | Close | 172E2
11011 | CIN10 | Indicator object 5 | Bad | 172E3
11072 | CIN11 | Indicator object 11 | Intermediate | 173E0
11073 | CIN11 | Indicator object 11 | Open | 173E1
11074 | CIN11 | Indicator object 11 | Close | 173E2
11075 | CIN11 | Indicator object 11 | Bad | 173E3
11136 | CIN12 | Indicator object 12 | Intermediate | 174E0
11137 | CIN12 | Indicator object 12 | Open | 174E1
11138 | CIN12 | Indicator object 12 | Close | 174E2
11139 | CIN12 | Indicator object 12 | Bad | 174E3
11200 | CIN13 | Indicator object 13 | Intermediate | 175E0
11201 | CIN13 | Indicator object 13 | Open | 175E1
11202 | CIN13 | Indicator object 13 | Close | 175E2
11203 | CIN13 | Indicator object 13 | Bad | 175E3
11264 | CIN14 | Indicator object 14 | Intermediate | 176E0
11265 | CIN14 | Indicator object 14 | Open | 176E1
11266 | CIN14 | Indicator object 14 | Close | 176E2
11267 | CIN14 | Indicator object 14 | Bad | 176E3
11328 | CIN15 | Indicator object 15 | Intermediate | 177E0
11329 | CIN15 | Indicator object 15 | Open | 177E1
11330 | CIN15 | Indicator object 15 | Close | 177E2
11331 | CIN15 | Indicator object 15 | Bad | 177E3
11392 | CIN16 | Indicator object 16 | Intermediate | 178E0
11393 | CIN16 | Indicator object 16 | Open | 178E1
11394 | CIN16 | Indicator object 16 | Close | 178E2
11395 | CIN16 | Indicator object 16 | Bad | 178E3
11456 | CIN17 | Indicator object 17 | Intermediate | 179E0
11457 | CIN17 | Indicator object 17 | Open | 179E1
11458 | CIN17 | Indicator object 17 | Close | 179E2
11459 | CIN17 | Indicator object 17 | Bad | 179E3
11520 | CIN18 | Indicator object 18 | Intermediate | 180E0
11521 | CIN18 | Indicator object 18 | Open | 180E1
11522 | CIN18 | Indicator object 18 | Close | 180E2
11523 | CIN18 | Indicator object 18 | Bad | 180E3
11584 | CIN19 | Indicator object 19 | Intermediate | 181E0
11585 | CIN19 | Indicator object 19 | Open | 181E1
11586 | CIN19 | Indicator object 19 | Close | 181E2
11587 | CIN19 | Indicator object 19 | Bad | 181E3
11648 | CIN20 | Indicator object 20 | Intermediate | 182E0
11649 | CIN20 | Indicator object 20 | Open | 182E1
11650 | CIN20 | Indicator object 20 | Close | 182E2
11651 | CIN20 | Indicator object 20 | Bad | 182E3
11712 | RHC1 | Running hour counter | Running hour counter On | 183E0
11713 | RHC1 | Running hour counter | Running hour counter Off | 183E1
11714 | RHC1 | Running hour counter | Running hour counter cleared On | 183E2
11715 | RHC1 | Running hour counter | Running hour counter cleared Off | 183E3
11776 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 65 On (Alarm 65) | 184E0
11777 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 65 Off (Alarm 65) | 184E1
11778 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 66 On (Alarm 66) | 184E2
11779 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 66 Off (Alarm 66) | 184E3
11780 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 67 On (Alarm 67) | 184E4
11781 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 67 Off (Alarm 67) | 184E5
11782 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 68 On (Alarm 68) | 184E6
11783 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 68 Off (Alarm 68) | 184E7
11784 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 69 On (Alarm 69) | 184E8
11785 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 69 Off (Alarm 69) | 184E9
11786 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 70 On (Alarm 70) | 184E10
11787 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 70 Off (Alarm 70) | 184E11
11788 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 71 On (Alarm 71) | 184E12
11789 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 71 Off (Alarm 71) | 184E13
11790 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 72 On (Alarm 72) | 184E14
11791 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 72 Off (Alarm 72) | 184E15
11792 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 73 On (Alarm 73) | 184E16
11793 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 73 Off (Alarm 73) | 184E17
11794 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 74 On (Alarm 74) | 184E18
11795 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 74 Off (Alarm 74) | 184E19
11796 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 75 On (Alarm 75) | 184E20
11797 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 75 Off (Alarm 75) | 184E21
11798 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 76 On (Alarm 76) | 184E22
11799 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 76 Off (Alarm 76) | 184E23
11800 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 77 On (Alarm 77) | 184E24
11801 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 77 Off (Alarm 77) | 184E25
11802 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 78 On (Alarm 78) | 184E26
11803 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 78 Off (Alarm 78) | 184E27
11804 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 79 On (Alarm 79) | 184E28
11805 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 79 Off (Alarm 79) | 184E29
11806 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 80 On (Alarm 80) | 184E30
11807 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 80 Off (Alarm 80) | 184E31
11808 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 81 On (Alarm 81) | 184E32
11809 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 81 Off (Alarm 81) | 184E33
11810 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 82 On (Alarm 82) | 184E34
11811 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 82 Off (Alarm 82) | 184E35
11812 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 83 On (Alarm 83) | 184E36
11813 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 83 Off (Alarm 83) | 184E37
11814 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 84 On (Alarm 84) | 184E38
11815 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 84 Off (Alarm 84) | 184E39
11816 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 85 On (Alarm 85) | 184E40
11817 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 85 Off (Alarm 85) | 184E41
11818 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 86 On (Alarm 86) | 184E42
11819 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 86 Off (Alarm 86) | 184E43
11820 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 87 On (Alarm 87) | 184E44
11821 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 87 Off (Alarm 87) | 184E45
11822 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 88 On (Alarm 88) | 184E46
11823 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 88 Off (Alarm 88) | 184E47
11824 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 89 On (Alarm 89) | 184E48
11825 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 89 Off (Alarm 89) | 184E49
11826 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 90 On (Alarm 90) | 184E50
11827 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 90 Off (Alarm 90) | 184E51
11828 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 91 On (Alarm 91) | 184E52
11829 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 91 Off (Alarm 91) | 184E53
11830 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 92 On (Alarm 92) | 184E54
11831 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 92 Off (Alarm 92) | 184E55
11832 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 93 On (Alarm 93) | 184E56
11833 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 93 Off (Alarm 93) | 184E57
11834 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 94 On (Alarm 94) | 184E58
11835 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 94 Off (Alarm 94) | 184E59
11836 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 95 On (Alarm 95) | 184E60
11837 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 95 Off (Alarm 95) | 184E61
11838 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 96 On (Alarm 96) | 184E62
11839 | ALARM3 | AQ-S214 and AQ-S254 alarms | Alarm 96 Off (Alarm 96) | 184E63
11840 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 97 On (Alarm 97) | 185E0
11841 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 97 Off (Alarm 97) | 185E1
11842 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 98 On (Alarm 98) | 185E2
11843 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 98 Off (Alarm 98) | 185E3
11844 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 99 On (Alarm 99) | 185E4
11845 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 99 Off (Alarm 99) | 185E5
11846 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 100 On (Alarm 100) | 185E6
11847 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 100 Off (Alarm 100) | 185E7
11848 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 101 On (Alarm 101) | 185E8
11849 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 101 Off (Alarm 101) | 185E9
11850 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 102 On (Alarm 102) | 185E10
11851 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 102 Off (Alarm 102) | 185E11
11852 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 103 On (Alarm 103) | 185E12
11853 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 103 Off (Alarm 103) | 185E13
11854 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 104 On (Alarm 104) | 185E14
11855 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 104 Off (Alarm 104) | 185E15
11856 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 105 On (Alarm 105) | 185E16
11857 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 105 Off (Alarm 105) | 185E17
11858 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 106 On (Alarm 106) | 185E18
11859 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 106 Off (Alarm 106) | 185E19
11860 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 107 On (Alarm 107) | 185E20
11861 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 107 Off (Alarm 107) | 185E21
11862 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 108 On (Alarm 108) | 185E22
11863 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 108 Off (Alarm 108) | 185E23
11864 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 109 On (Alarm 109) | 185E24
11865 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 109 Off (Alarm 109) | 185E25
11866 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 110 On (Alarm 110) | 185E26
11867 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 110 Off (Alarm 110) | 185E27
11868 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 111 On (Alarm 111) | 185E28
11869 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 111 Off (Alarm 111) | 185E29
11870 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 112 On (Alarm 112) | 185E30
11871 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 112 Off (Alarm 112) | 185E31
11872 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 113 On (Alarm 113) | 185E32
11873 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 113 Off (Alarm 113) | 185E33
11874 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 114 On (Alarm 114) | 185E34
11875 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 114 Off (Alarm 114) | 185E35
11876 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 115 On (Alarm 115) | 185E36
11877 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 115 Off (Alarm 115) | 185E37
11878 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 116 On (Alarm 116) | 185E38
11879 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 116 Off (Alarm 116) | 185E39
11880 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 117 On (Alarm 117) | 185E40
11881 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 117 Off (Alarm 117) | 185E41
11882 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 118 On (Alarm 118) | 185E42
11883 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 118 Off (Alarm 118) | 185E43
11884 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 119 On (Alarm 119) | 185E44
11885 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 119 Off (Alarm 119) | 185E45
11886 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 120 On (Alarm 120) | 185E46
11887 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 120 Off (Alarm 120) | 185E47
11888 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 121 On (Alarm 121) | 185E48
11889 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 121 Off (Alarm 121) | 185E49
11890 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 122 On (Alarm 122) | 185E50
11891 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 122 Off (Alarm 122) | 185E51
11892 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 123 On (Alarm 123) | 185E52
11893 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 123 Off (Alarm 123) | 185E53
11894 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 124 On (Alarm 124) | 185E54
11895 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 124 Off (Alarm 124) | 185E55
11896 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 125 On (Alarm 125) | 185E56
11897 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 125 Off (Alarm 125) | 185E57
11898 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 126 On (Alarm 126) | 185E58
11899 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 126 Off (Alarm 126) | 185E59
11900 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 127 On (Alarm 127) | 185E60
11901 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 127 Off (Alarm 127) | 185E61
11902 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 128 On (Alarm 128) | 185E62
11903 | ALARM4 | AQ-S214 and AQ-S254 alarms | Alarm 128 Off (Alarm 128) | 185E63
12096 | LDIF1 | Line differential | Idb> Trip On | 189E0
12097 | LDIF1 | Line differential | Idb> Trip Off | 189E1
12098 | LDIF1 | Line differential | Idb> Blocked (ext) On | 189E2
12099 | LDIF1 | Line differential | Idb> Blocked (ext) Off | 189E3
12100 | LDIF1 | Line differential | Idi> Trip On | 189E4
12101 | LDIF1 | Line differential | Idi> Trip Off | 189E5
12102 | LDIF1 | Line differential | Idi> Blocked (ext) On | 189E6
12103 | LDIF1 | Line differential | Idi> Blocked (ext) Off | 189E7
12104 | LDIF1 | Line differential | 2.nd Harmonic Block On | 189E8
12105 | LDIF1 | Line differential | 2.nd Harmonic Block Off | 189E9
12106 | LDIF1 | Line differential | 5.th Harmonic Block On | 189E10
12107 | LDIF1 | Line differential | 5.th Harmonic Block Off | 189E11
12108 | LDIF1 | Line differential | L1 2.nd harm On | 189E12
12109 | LDIF1 | Line differential | L1 2.nd harm Off | 189E13
12110 | LDIF1 | Line differential | L2 2.nd harm On | 189E14
12111 | LDIF1 | Line differential | L2 2.nd harm Off | 189E15
12112 | LDIF1 | Line differential | L3 2.nd harm On | 189E16
12113 | LDIF1 | Line differential | L3 2.nd harm Off | 189E17
12114 | LDIF1 | Line differential | L1 5.th harm On | 189E18
12115 | LDIF1 | Line differential | L1 5.th harm Off | 189E19
12116 | LDIF1 | Line differential | L2 5.th harm On | 189E20
12117 | LDIF1 | Line differential | L2 5.th harm Off | 189E21
12118 | LDIF1 | Line differential | L3 5.th harm On | 189E22
12119 | LDIF1 | Line differential | L3 5.th harm Off | 189E23
12160 | M1VT1 | Voltage memory | Voltage memory enabled | 190E0
12161 | M1VT1 | Voltage memory | Voltage memory disabled | 190E1
12162 | M1VT1 | Voltage memory | Voltage low detected On | 190E2
12163 | M1VT1 | Voltage memory | Voltage low detected Off | 190E3
12164 | M1VT1 | Voltage memory | Current high detected On | 190E4
12165 | M1VT1 | Voltage memory | Current high detected Off | 190E5
12166 | M1VT1 | Voltage memory | Frequency tracked from CT On | 190E6
12167 | M1VT1 | Voltage memory | Frequency tracked from CT Off | 190E7
12168 | M1VT1 | Voltage memory | Using Voltage memory On | 190E8
12169 | M1VT1 | Voltage memory | Using Voltage memory Off | 190E9
12170 | M1VT1 | Voltage memory | Voltage memory blocked On | 190E10
12171 | M1VT1 | Voltage memory | Voltage memory blocked Off | 190E11
12288 | NOCS1 | Single pole non-directional overcurrent | Start ON | 192E0
12289 | NOCS1 | Single pole non-directional overcurrent | Start OFF | 192E1
12290 | NOCS1 | Single pole non-directional overcurrent | Trip ON | 192E2
12291 | NOCS1 | Single pole non-directional overcurrent | Trip OFF | 192E3
12292 | NOCS1 | Single pole non-directional overcurrent | Block ON | 192E4
12293 | NOCS1 | Single pole non-directional overcurrent | Block OFF | 192E5
12294 | NOCS1 | Single pole non-directional overcurrent | L1 Start ON | 192E6
12295 | NOCS1 | Single pole non-directional overcurrent | L1 Start OFF | 192E7
12296 | NOCS1 | Single pole non-directional overcurrent | L2 Start ON | 192E8
12297 | NOCS1 | Single pole non-directional overcurrent | L2 Start OFF | 192E9
12298 | NOCS1 | Single pole non-directional overcurrent | L3 Start ON | 192E10
12299 | NOCS1 | Single pole non-directional overcurrent | L3 Start OFF | 192E11
12300 | NOCS1 | Single pole non-directional overcurrent | L1 Trip ON | 192E12
12301 | NOCS1 | Single pole non-directional overcurrent | L1 Trip OFF | 192E13
12302 | NOCS1 | Single pole non-directional overcurrent | L2 Trip ON | 192E14
12303 | NOCS1 | Single pole non-directional overcurrent | L2 Trip OFF | 192E15
12304 | NOCS1 | Single pole non-directional overcurrent | L3 Trip ON | 192E16
12305 | NOCS1 | Single pole non-directional overcurrent | L3 Trip OFF | 192E17
12352 | OBJS1 | Single pole object | Object A(L1) Intermediate | 193E0
12353 | OBJS1 | Single pole object | Object A(L1) Open | 193E1
12354 | OBJS1 | Single pole object | Object A(L1) Close | 193E2
12355 | OBJS1 | Single pole object | Object A(L1) Bad | 193E3
12356 | OBJS1 | Single pole object | Object B(L2) Open | 193E4
12357 | OBJS1 | Single pole object | Object B(L2) Close | 193E5
12358 | OBJS1 | Single pole object | Object B(L2) Bad | 193E6
12359 | OBJS1 | Single pole object | Object B(L2) Intermediate | 193E7
12360 | OBJS1 | Single pole object | Object C(L3) Open | 193E8
12361 | OBJS1 | Single pole object | Object C(L3) Close | 193E9
12362 | OBJS1 | Single pole object | Object C(L3) Bad | 193E10
12363 | OBJS1 | Single pole object | Object C(L3) Intermediate | 193E11
12364 | OBJS1 | Single pole object | WD Cart Intermediate | 193E12
12365 | OBJS1 | Single pole object | WD Cart Open | 193E13
12366 | OBJS1 | Single pole object | WD Cart Close | 193E14
12367 | OBJS1 | Single pole object | WD Cart Bad | 193E15
12368 | OBJS1 | Single pole object | Object A(L1) Open Command On | 193E16
12369 | OBJS1 | Single pole object | Object A(L1) Open Command Off | 193E17
12370 | OBJS1 | Single pole object | Object B(L2) Open Command On | 193E18
12371 | OBJS1 | Single pole object | Object B(L2) Open Command Off | 193E19
12372 | OBJS1 | Single pole object | Object C(L3) Open Command On | 193E20
12373 | OBJS1 | Single pole object | Object C(L3) Open Command Off | 193E21
12374 | OBJS1 | Single pole object | Close Command On | 193E22
12375 | OBJS1 | Single pole object | Close Command Off | 193E23
12376 | OBJS1 | Single pole object | Open Commands Blocked | 193E24
12377 | OBJS1 | Single pole object | Open Commands Allowed | 193E25
12378 | OBJS1 | Single pole object | Close Commands Blocked | 193E26
12379 | OBJS1 | Single pole object | Close Commands Allowed | 193E27
12380 | OBJS1 | Single pole object | Object Is Ready | 193E28
12381 | OBJS1 | Single pole object | Object Not Ready, Wait for Ready | 193E29
12382 | OBJS1 | Single pole object | Sync Is Ok | 193E30
12383 | OBJS1 | Single pole object | Sync Not Ok Wait for sync | 193E31
12384 | OBJS1 | Single pole object | Final Trip On | 193E32
12385 | OBJS1 | Single pole object | Final Trip Off | 193E33
12386 | OBJS1 | Single pole object | Open Command Fail On | 193E34
12387 | OBJS1 | Single pole object | Open Command Fail Off | 193E35
12388 | OBJS1 | Single pole object | Close Command Fail On | 193E36
12389 | OBJS1 | Single pole object | Close Command Fail Off | 193E37
12390 | OBJS1 | Single pole object | L1 Open Command Timeout On | 193E38
12391 | OBJS1 | Single pole object | L1 Open Command Timeout On | 193E39
12392 | OBJS1 | Single pole object | L2 Open Command Timeout On | 193E40
12393 | OBJS1 | Single pole object | L2 Open Command Timeout On | 193E41
12394 | OBJS1 | Single pole object | L3 Open Command Timeout On | 193E42
12395 | OBJS1 | Single pole object | L3 Open Command Timeout On | 193E43
12396 | OBJS1 | Single pole object | Close Command Timeout On | 193E44
12397 | OBJS1 | Single pole object | Close Command Timeout On | 193E45
12416 | NOCS2 | Single pole non-directional overcurrent | Start ON | 194E0
12417 | NOCS2 | Single pole non-directional overcurrent | Start OFF | 194E1
12418 | NOCS2 | Single pole non-directional overcurrent | Trip ON | 194E2
12419 | NOCS2 | Single pole non-directional overcurrent | Trip OFF | 194E3
12420 | NOCS2 | Single pole non-directional overcurrent | Block ON | 194E4
12421 | NOCS2 | Single pole non-directional overcurrent | Block OFF | 194E5
12422 | NOCS2 | Single pole non-directional overcurrent | L1 Start ON | 194E6
12423 | NOCS2 | Single pole non-directional overcurrent | L1 Start OFF | 194E7
12424 | NOCS2 | Single pole non-directional overcurrent | L2 Start ON | 194E8
12425 | NOCS2 | Single pole non-directional overcurrent | L2 Start OFF | 194E9
12426 | NOCS2 | Single pole non-directional overcurrent | L3 Start ON | 194E10
12427 | NOCS2 | Single pole non-directional overcurrent | L3 Start OFF | 194E11
12428 | NOCS2 | Single pole non-directional overcurrent | L1 Trip ON | 194E12
12429 | NOCS2 | Single pole non-directional overcurrent | L1 Trip OFF | 194E13
12430 | NOCS2 | Single pole non-directional overcurrent | L2 Trip ON | 194E14
12431 | NOCS2 | Single pole non-directional overcurrent | L2 Trip OFF | 194E15
12432 | NOCS2 | Single pole non-directional overcurrent | L3 Trip ON | 194E16
12433 | NOCS2 | Single pole non-directional overcurrent | L3 Trip OFF | 194E17
12480 | SGS2 | Transformer setting groups | SG2 Enabled | 195E0
12481 | SGS2 | Transformer setting groups | SG2 Disabled | 195E1
12482 | SGS2 | Transformer setting groups | SG3 Enabled | 195E2
12483 | SGS2 | Transformer setting groups | SG3 Disabled | 195E3
12484 | SGS2 | Transformer setting groups | SG4 Enabled | 195E4
12485 | SGS2 | Transformer setting groups | SG4 Disabled | 195E5
12486 | SGS2 | Transformer setting groups | SG5 Enabled | 195E6
12487 | SGS2 | Transformer setting groups | SG5 Disabled | 195E7
12488 | SGS2 | Transformer setting groups | SG6 Enabled | 195E8
12489 | SGS2 | Transformer setting groups | SG6 Disabled | 195E9
12490 | SGS2 | Transformer setting groups | SG7 Enabled | 195E10
12491 | SGS2 | Transformer setting groups | SG7 Disabled | 195E11
12492 | SGS2 | Transformer setting groups | SG8 Enabled | 195E12
12493 | SGS2 | Transformer setting groups | SG8 Disabled | 195E13
12494 | SGS2 | Transformer setting groups | SG1 Request On | 195E14
12495 | SGS2 | Transformer setting groups | SG1 Request Off | 195E15
12496 | SGS2 | Transformer setting groups | SG2 Request On | 195E16
12497 | SGS2 | Transformer setting groups | SG2 Request Off | 195E17
12498 | SGS2 | Transformer setting groups | SG3 Request On | 195E18
12499 | SGS2 | Transformer setting groups | SG3 Request Off | 195E19
12500 | SGS2 | Transformer setting groups | SG4 Request On | 195E20
12501 | SGS2 | Transformer setting groups | SG4 Request Off | 195E21
12502 | SGS2 | Transformer setting groups | SG5 Request On | 195E22
12503 | SGS2 | Transformer setting groups | SG5 Request Off | 195E23
12504 | SGS2 | Transformer setting groups | SG6 Request On | 195E24
12505 | SGS2 | Transformer setting groups | SG6 Request Off | 195E25
12506 | SGS2 | Transformer setting groups | SG7 Request On | 195E26
12507 | SGS2 | Transformer setting groups | SG7 Request Off | 195E27
12508 | SGS2 | Transformer setting groups | SG8 Request On | 195E28
12509 | SGS2 | Transformer setting groups | SG8 Request Off | 195E29
12510 | SGS2 | Transformer setting groups | Remote Change SG Req On | 195E30
12511 | SGS2 | Transformer setting groups | Remote Change SG Req Off | 195E31
12512 | SGS2 | Transformer setting groups | Local Change SG Req On | 195E32
12513 | SGS2 | Transformer setting groups | Local Change SG Req On | 195E33
12514 | SGS2 | Transformer setting groups | Force Change SG On | 195E34
12515 | SGS2 | Transformer setting groups | Force Change SG Off | 195E35
12516 | SGS2 | Transformer setting groups | SG Req. Fail Not configured SG On | 195E36
12517 | SGS2 | Transformer setting groups | SG Req. Fail Not configured SG On | 195E37
12518 | SGS2 | Transformer setting groups | Force Req. Fail Force not On | 195E38
12519 | SGS2 | Transformer setting groups | Force Req. Fail Off | 195E39
12520 | SGS2 | Transformer setting groups | SG Req. Fail Lower priority Req. On | 195E40
12521 | SGS2 | Transformer setting groups | SG Req. Fail Lower priority Req. Off | 195E41
12522 | SGS2 | Transformer setting groups | SG1 Active On | 195E42
12523 | SGS2 | Transformer setting groups | SG1 Active Off | 195E43
12524 | SGS2 | Transformer setting groups | SG2 Active On | 195E44
12525 | SGS2 | Transformer setting groups | SG2 Active Off | 195E45
12526 | SGS2 | Transformer setting groups | SG3 Active On | 195E46
12527 | SGS2 | Transformer setting groups | SG3 Active Off | 195E47
12528 | SGS2 | Transformer setting groups | SG4 Active On | 195E48
12529 | SGS2 | Transformer setting groups | SG4 Active Off | 195E49
12530 | SGS2 | Transformer setting groups | SG5 Active On | 195E50
12531 | SGS2 | Transformer setting groups | SG5 Active Off | 195E51
12532 | SGS2 | Transformer setting groups | SG6 Active On | 195E52
12533 | SGS2 | Transformer setting groups | SG6 Active Off | 195E53
12534 | SGS2 | Transformer setting groups | SG7 Active On | 195E54
12535 | SGS2 | Transformer setting groups | SG7 Active Off | 195E55
12536 | SGS2 | Transformer setting groups | SG8 Active On | 195E56
12537 | SGS2 | Transformer setting groups | SG8 Active Off | 195E57
12544 | URX1 | Underreactance | Start ON | 196E0
12545 | URX1 | Underreactance | Start OFF | 196E1
12546 | URX1 | Underreactance | Trip ON | 196E2
12547 | URX1 | Underreactance | Trip OFF | 196E3
12548 | URX1 | Underreactance | Block ON | 196E4
12549 | URX1 | Underreactance | Block OFF | 196E5
12608 | URX2 | Underreactance | Start ON | 197E0
12609 | URX2 | Underreactance | Start OFF | 197E1
12610 | URX2 | Underreactance | Trip ON | 197E2
12611 | URX2 | Underreactance | Trip OFF | 197E3
12612 | URX2 | Underreactance | Block ON | 197E4
12613 | URX2 | Underreactance | Block OFF | 197E5
12736 | MGWB1 | Modbusgateway bit signals | On Bit 1 (Acq.Bit.1) | 199E0
12737 | MGWB1 | Modbusgateway bit signals | Off Bit 1 (Acq.Bit.1) | 199E1
12738 | MGWB1 | Modbusgateway bit signals | On Bit 2 (Acq.Bit.2) | 199E2
12739 | MGWB1 | Modbusgateway bit signals | Off Bit 2 (Acq.Bit.2) | 199E3
12740 | MGWB1 | Modbusgateway bit signals | On Bit 3 (Acq.Bit.3) | 199E4
12741 | MGWB1 | Modbusgateway bit signals | Off Bit 3 (Acq.Bit.3) | 199E5
12742 | MGWB1 | Modbusgateway bit signals | On Bit 4 (Acq.Bit.4) | 199E6
12743 | MGWB1 | Modbusgateway bit signals | Off Bit 4 (Acq.Bit.4) | 199E7
12744 | MGWB1 | Modbusgateway bit signals | On Bit 5 (Acq.Bit.5) | 199E8
12745 | MGWB1 | Modbusgateway bit signals | Off Bit 5 (Acq.Bit.5) | 199E9
12746 | MGWB1 | Modbusgateway bit signals | On Bit 6 (Acq.Bit.6) | 199E10
12747 | MGWB1 | Modbusgateway bit signals | Off Bit 6 (Acq.Bit.6) | 199E11
12748 | MGWB1 | Modbusgateway bit signals | On Bit 7 (Acq.Bit.7) | 199E12
12749 | MGWB1 | Modbusgateway bit signals | Off Bit 7 (Acq.Bit.7) | 199E13
12750 | MGWB1 | Modbusgateway bit signals | On Bit 8 (Acq.Bit.8) | 199E14
12751 | MGWB1 | Modbusgateway bit signals | Off Bit 8 (Acq.Bit.8) | 199E15
12752 | MGWB1 | Modbusgateway bit signals | On Bit 9 (Acq.Bit.9) | 199E16
12753 | MGWB1 | Modbusgateway bit signals | Off Bit 9 (Acq.Bit.9) | 199E17
12754 | MGWB1 | Modbusgateway bit signals | On Bit 10 (Acq.Bit.10) | 199E18
12755 | MGWB1 | Modbusgateway bit signals | Off Bit 10 (Acq.Bit.10) | 199E19
12756 | MGWB1 | Modbusgateway bit signals | On Bit 11 (Acq.Bit.11) | 199E20
12757 | MGWB1 | Modbusgateway bit signals | Off Bit 11 (Acq.Bit.11) | 199E21
12758 | MGWB1 | Modbusgateway bit signals | On Bit 12 (Acq.Bit.12) | 199E22
12759 | MGWB1 | Modbusgateway bit signals | Off Bit 12 (Acq.Bit.12) | 199E23
12760 | MGWB1 | Modbusgateway bit signals | On Bit 13 (Acq.Bit.13) | 199E24
12761 | MGWB1 | Modbusgateway bit signals | Off Bit 13 (Acq.Bit.13) | 199E25
12762 | MGWB1 | Modbusgateway bit signals | On Bit 14 (Acq.Bit.14) | 199E26
12763 | MGWB1 | Modbusgateway bit signals | Off Bit 14 (Acq.Bit.14) | 199E27
12764 | MGWB1 | Modbusgateway bit signals | On Bit 15 (Acq.Bit.15) | 199E28
12765 | MGWB1 | Modbusgateway bit signals | Off Bit 15 (Acq.Bit.15) | 199E29
12766 | MGWB1 | Modbusgateway bit signals | On Bit 16 (Acq.Bit.16) | 199E30
12767 | MGWB1 | Modbusgateway bit signals | Off Bit 16 (Acq.Bit.16) | 199E31
12768 | MGWB1 | Modbusgateway bit signals | On Bit 17 (Acq.Bit.17) | 199E32
12769 | MGWB1 | Modbusgateway bit signals | Off Bit 17 (Acq.Bit.17) | 199E33
12770 | MGWB1 | Modbusgateway bit signals | On Bit 18 (Acq.Bit.18) | 199E34
12771 | MGWB1 | Modbusgateway bit signals | Off Bit 18 (Acq.Bit.18) | 199E35
12772 | MGWB1 | Modbusgateway bit signals | On Bit 19 (Acq.Bit.19) | 199E36
12773 | MGWB1 | Modbusgateway bit signals | Off Bit 19 (Acq.Bit.19) | 199E37
12774 | MGWB1 | Modbusgateway bit signals | On Bit 20 (Acq.Bit.20) | 199E38
12775 | MGWB1 | Modbusgateway bit signals | Off Bit 20 (Acq.Bit.20) | 199E39
12776 | MGWB1 | Modbusgateway bit signals | On Bit 21 (Acq.Bit.21) | 199E40
12777 | MGWB1 | Modbusgateway bit signals | Off Bit 21 (Acq.Bit.21) | 199E41
12778 | MGWB1 | Modbusgateway bit signals | On Bit 22 (Acq.Bit.22) | 199E42
12779 | MGWB1 | Modbusgateway bit signals | Off Bit 22 (Acq.Bit.22) | 199E43
12780 | MGWB1 | Modbusgateway bit signals | On Bit 23 (Acq.Bit.23) | 199E44
12781 | MGWB1 | Modbusgateway bit signals | Off Bit 23 (Acq.Bit.23) | 199E45
12782 | MGWB1 | Modbusgateway bit signals | On Bit 24 (Acq.Bit.24) | 199E46
12783 | MGWB1 | Modbusgateway bit signals | Off Bit 24 (Acq.Bit.24) | 199E47
12784 | MGWB1 | Modbusgateway bit signals | On Bit 25 (Acq.Bit.25) | 199E48
12785 | MGWB1 | Modbusgateway bit signals | Off Bit 25 (Acq.Bit.25) | 199E49
12786 | MGWB1 | Modbusgateway bit signals | On Bit 26 (Acq.Bit.26) | 199E50
12787 | MGWB1 | Modbusgateway bit signals | Off Bit 26 (Acq.Bit.26) | 199E51
12788 | MGWB1 | Modbusgateway bit signals | On Bit 27 (Acq.Bit.27) | 199E52
12789 | MGWB1 | Modbusgateway bit signals | Off Bit 27 (Acq.Bit.27) | 199E53
12790 | MGWB1 | Modbusgateway bit signals | On Bit 28 (Acq.Bit.28) | 199E54
12791 | MGWB1 | Modbusgateway bit signals | Off Bit 28 (Acq.Bit.28) | 199E55
12792 | MGWB1 | Modbusgateway bit signals | On Bit 29 (Acq.Bit.29) | 199E56
12793 | MGWB1 | Modbusgateway bit signals | Off Bit 29 (Acq.Bit.29) | 199E57
12794 | MGWB1 | Modbusgateway bit signals | On Bit 30 (Acq.Bit.30) | 199E58
12795 | MGWB1 | Modbusgateway bit signals | Off Bit 30 (Acq.Bit.30) | 199E59
12796 | MGWB1 | Modbusgateway bit signals | On Bit 31 (Acq.Bit.31) | 199E60
12797 | MGWB1 | Modbusgateway bit signals | Off Bit 31 (Acq.Bit.31) | 199E61
12798 | MGWB1 | Modbusgateway bit signals | On Bit 32 (Acq.Bit.32) | 199E62
12799 | MGWB1 | Modbusgateway bit signals | Off Bit 32 (Acq.Bit.32) | 199E63
12800 | MGWB2 | Modbusgateway bit signals | On Bit 33 (Acq.Bit.33) | 200E0
12801 | MGWB2 | Modbusgateway bit signals | Off Bit 33 (Acq.Bit.33) | 200E1
12802 | MGWB2 | Modbusgateway bit signals | On Bit 34 (Acq.Bit.34) | 200E2
12803 | MGWB2 | Modbusgateway bit signals | Off Bit 34 (Acq.Bit.34) | 200E3
12804 | MGWB2 | Modbusgateway bit signals | On Bit 35 (Acq.Bit.35) | 200E4
12805 | MGWB2 | Modbusgateway bit signals | Off Bit 35 (Acq.Bit.35) | 200E5
12806 | MGWB2 | Modbusgateway bit signals | On Bit 36 (Acq.Bit.36) | 200E6
12807 | MGWB2 | Modbusgateway bit signals | Off Bit 36 (Acq.Bit.36) | 200E7
12808 | MGWB2 | Modbusgateway bit signals | On Bit 37 (Acq.Bit.37) | 200E8
12809 | MGWB2 | Modbusgateway bit signals | Off Bit 37 (Acq.Bit.37) | 200E9
12810 | MGWB2 | Modbusgateway bit signals | On Bit 38 (Acq.Bit.38) | 200E10
12811 | MGWB2 | Modbusgateway bit signals | Off Bit 38 (Acq.Bit.38) | 200E11
12812 | MGWB2 | Modbusgateway bit signals | On Bit 39 (Acq.Bit.39) | 200E12
12813 | MGWB2 | Modbusgateway bit signals | Off Bit 39 (Acq.Bit.39) | 200E13
12814 | MGWB2 | Modbusgateway bit signals | On Bit 40 (Acq.Bit.40) | 200E14
12815 | MGWB2 | Modbusgateway bit signals | Off Bit 40 (Acq.Bit.40) | 200E15
12816 | MGWB2 | Modbusgateway bit signals | On Bit 41 (Acq.Bit.41) | 200E16
12817 | MGWB2 | Modbusgateway bit signals | Off Bit 41 (Acq.Bit.41) | 200E17
12818 | MGWB2 | Modbusgateway bit signals | On Bit 42 (Acq.Bit.42) | 200E18
12819 | MGWB2 | Modbusgateway bit signals | Off Bit 42 (Acq.Bit.42) | 200E19
12820 | MGWB2 | Modbusgateway bit signals | On Bit 43 (Acq.Bit.43) | 200E20
12821 | MGWB2 | Modbusgateway bit signals | Off Bit 43 (Acq.Bit.43) | 200E21
12822 | MGWB2 | Modbusgateway bit signals | On Bit 44 (Acq.Bit.44) | 200E22
12823 | MGWB2 | Modbusgateway bit signals | Off Bit 44 (Acq.Bit.44) | 200E23
12824 | MGWB2 | Modbusgateway bit signals | On Bit 45 (Acq.Bit.45) | 200E24
12825 | MGWB2 | Modbusgateway bit signals | Off Bit 45 (Acq.Bit.45) | 200E25
12826 | MGWB2 | Modbusgateway bit signals | On Bit 46 (Acq.Bit.46) | 200E26
12827 | MGWB2 | Modbusgateway bit signals | Off Bit 46 (Acq.Bit.46) | 200E27
12828 | MGWB2 | Modbusgateway bit signals | On Bit 47 (Acq.Bit.47) | 200E28
12829 | MGWB2 | Modbusgateway bit signals | Off Bit 47 (Acq.Bit.47) | 200E29
12830 | MGWB2 | Modbusgateway bit signals | On Bit 48 (Acq.Bit.48) | 200E30
12831 | MGWB2 | Modbusgateway bit signals | Off Bit 48 (Acq.Bit.48) | 200E31
12832 | MGWB2 | Modbusgateway bit signals | On Bit 49 (Acq.Bit.49) | 200E32
12833 | MGWB2 | Modbusgateway bit signals | Off Bit 49 (Acq.Bit.49) | 200E33
12834 | MGWB2 | Modbusgateway bit signals | On Bit 50 (Acq.Bit.50) | 200E34
12835 | MGWB2 | Modbusgateway bit signals | Off Bit 50 (Acq.Bit.50) | 200E35
12836 | MGWB2 | Modbusgateway bit signals | On Bit 51 (Acq.Bit.51) | 200E36
12837 | MGWB2 | Modbusgateway bit signals | Off Bit 51 (Acq.Bit.51) | 200E37
12838 | MGWB2 | Modbusgateway bit signals | On Bit 52 (Acq.Bit.52) | 200E38
12839 | MGWB2 | Modbusgateway bit signals | Off Bit 52 (Acq.Bit.52) | 200E39
12840 | MGWB2 | Modbusgateway bit signals | On Bit 53 (Acq.Bit.53) | 200E40
12841 | MGWB2 | Modbusgateway bit signals | Off Bit 53 (Acq.Bit.53) | 200E41
12842 | MGWB2 | Modbusgateway bit signals | On Bit 54 (Acq.Bit.54) | 200E42
12843 | MGWB2 | Modbusgateway bit signals | Off Bit 54 (Acq.Bit.54) | 200E43
12844 | MGWB2 | Modbusgateway bit signals | On Bit 55 (Acq.Bit.55) | 200E44
12845 | MGWB2 | Modbusgateway bit signals | Off Bit 55 (Acq.Bit.55) | 200E45
12846 | MGWB2 | Modbusgateway bit signals | On Bit 56 (Acq.Bit.56) | 200E46
12847 | MGWB2 | Modbusgateway bit signals | Off Bit 56 (Acq.Bit.56) | 200E47
12848 | MGWB2 | Modbusgateway bit signals | On Bit 57 (Acq.Bit.57) | 200E48
12849 | MGWB2 | Modbusgateway bit signals | Off Bit 57 (Acq.Bit.57) | 200E49
12850 | MGWB2 | Modbusgateway bit signals | On Bit 58 (Acq.Bit.58) | 200E50
12851 | MGWB2 | Modbusgateway bit signals | Off Bit 58 (Acq.Bit.58) | 200E51
12852 | MGWB2 | Modbusgateway bit signals | On Bit 59 (Acq.Bit.59) | 200E52
12853 | MGWB2 | Modbusgateway bit signals | Off Bit 59 (Acq.Bit.59) | 200E53
12854 | MGWB2 | Modbusgateway bit signals | On Bit 60 (Acq.Bit.60) | 200E54
12855 | MGWB2 | Modbusgateway bit signals | Off Bit 60 (Acq.Bit.60) | 200E55
12856 | MGWB2 | Modbusgateway bit signals | On Bit 61 (Acq.Bit.61) | 200E56
12857 | MGWB2 | Modbusgateway bit signals | Off Bit 61 (Acq.Bit.61) | 200E57
12858 | MGWB2 | Modbusgateway bit signals | On Bit 62 (Acq.Bit.62) | 200E58
12859 | MGWB2 | Modbusgateway bit signals | Off Bit 62 (Acq.Bit.62) | 200E59
12860 | MGWB2 | Modbusgateway bit signals | On Bit 63 (Acq.Bit.63) | 200E60
12861 | MGWB2 | Modbusgateway bit signals | Off Bit 63 (Acq.Bit.63) | 200E61
12862 | MGWB2 | Modbusgateway bit signals | On Bit 64 (Acq.Bit.64) | 200E62
12863 | MGWB2 | Modbusgateway bit signals | Off Bit 64 (Acq.Bit.64) | 200E63
12864 | MGWB3 | Modbusgateway bit signals | On Bit 65 (Acq.Bit.65) | 201E0
12865 | MGWB3 | Modbusgateway bit signals | Off Bit 65 (Acq.Bit.65) | 201E1
12866 | MGWB3 | Modbusgateway bit signals | On Bit 66 (Acq.Bit.66) | 201E2
12867 | MGWB3 | Modbusgateway bit signals | Off Bit 66 (Acq.Bit.66) | 201E3
12868 | MGWB3 | Modbusgateway bit signals | On Bit 67 (Acq.Bit.67) | 201E4
12869 | MGWB3 | Modbusgateway bit signals | Off Bit 67 (Acq.Bit.67) | 201E5
12870 | MGWB3 | Modbusgateway bit signals | On Bit 68 (Acq.Bit.68) | 201E6
12871 | MGWB3 | Modbusgateway bit signals | Off Bit 68 (Acq.Bit.68) | 201E7
12872 | MGWB3 | Modbusgateway bit signals | On Bit 69 (Acq.Bit.69) | 201E8
12873 | MGWB3 | Modbusgateway bit signals | Off Bit 69 (Acq.Bit.69) | 201E9
12874 | MGWB3 | Modbusgateway bit signals | On Bit 70 (Acq.Bit.70) | 201E10
12875 | MGWB3 | Modbusgateway bit signals | Off Bit 70 (Acq.Bit.70) | 201E11
12876 | MGWB3 | Modbusgateway bit signals | On Bit 71 (Acq.Bit.71) | 201E12
12877 | MGWB3 | Modbusgateway bit signals | Off Bit 71 (Acq.Bit.71) | 201E13
12878 | MGWB3 | Modbusgateway bit signals | On Bit 72 (Acq.Bit.72) | 201E14
12879 | MGWB3 | Modbusgateway bit signals | Off Bit 72 (Acq.Bit.72) | 201E15
12880 | MGWB3 | Modbusgateway bit signals | On Bit 73 (Acq.Bit.73) | 201E16
12881 | MGWB3 | Modbusgateway bit signals | Off Bit 73 (Acq.Bit.73) | 201E17
12882 | MGWB3 | Modbusgateway bit signals | On Bit 74 (Acq.Bit.74) | 201E18
12883 | MGWB3 | Modbusgateway bit signals | Off Bit 74 (Acq.Bit.74) | 201E19
12884 | MGWB3 | Modbusgateway bit signals | On Bit 75 (Acq.Bit.75) | 201E20
12885 | MGWB3 | Modbusgateway bit signals | Off Bit 75 (Acq.Bit.75) | 201E21
12886 | MGWB3 | Modbusgateway bit signals | On Bit 76 (Acq.Bit.76) | 201E22
12887 | MGWB3 | Modbusgateway bit signals | Off Bit 76 (Acq.Bit.76) | 201E23
12888 | MGWB3 | Modbusgateway bit signals | On Bit 77 (Acq.Bit.77) | 201E24
12889 | MGWB3 | Modbusgateway bit signals | Off Bit 77 (Acq.Bit.77) | 201E25
12890 | MGWB3 | Modbusgateway bit signals | On Bit 78 (Acq.Bit.78) | 201E26
12891 | MGWB3 | Modbusgateway bit signals | Off Bit 78 (Acq.Bit.78) | 201E27
12892 | MGWB3 | Modbusgateway bit signals | On Bit 79 (Acq.Bit.79) | 201E28
12893 | MGWB3 | Modbusgateway bit signals | Off Bit 79 (Acq.Bit.79) | 201E29
12894 | MGWB3 | Modbusgateway bit signals | On Bit 80 (Acq.Bit.80) | 201E30
12895 | MGWB3 | Modbusgateway bit signals | Off Bit 80 (Acq.Bit.80) | 201E31
12896 | MGWB3 | Modbusgateway bit signals | On Bit 81 (Acq.Bit.81) | 201E32
12897 | MGWB3 | Modbusgateway bit signals | Off Bit 81 (Acq.Bit.81) | 201E33
12898 | MGWB3 | Modbusgateway bit signals | On Bit 82 (Acq.Bit.82) | 201E34
12899 | MGWB3 | Modbusgateway bit signals | Off Bit 82 (Acq.Bit.82) | 201E35
12900 | MGWB3 | Modbusgateway bit signals | On Bit 83 (Acq.Bit.83) | 201E36
12901 | MGWB3 | Modbusgateway bit signals | Off Bit 83 (Acq.Bit.83) | 201E37
12902 | MGWB3 | Modbusgateway bit signals | On Bit 84 (Acq.Bit.84) | 201E38
12903 | MGWB3 | Modbusgateway bit signals | Off Bit 84 (Acq.Bit.84) | 201E39
12904 | MGWB3 | Modbusgateway bit signals | On Bit 85 (Acq.Bit.85) | 201E40
12905 | MGWB3 | Modbusgateway bit signals | Off Bit 85 (Acq.Bit.85) | 201E41
12906 | MGWB3 | Modbusgateway bit signals | On Bit 86 (Acq.Bit.86) | 201E42
12907 | MGWB3 | Modbusgateway bit signals | Off Bit 86 (Acq.Bit.86) | 201E43
12908 | MGWB3 | Modbusgateway bit signals | On Bit 87 (Acq.Bit.87) | 201E44
12909 | MGWB3 | Modbusgateway bit signals | Off Bit 87 (Acq.Bit.87) | 201E45
12910 | MGWB3 | Modbusgateway bit signals | On Bit 88 (Acq.Bit.88) | 201E46
12911 | MGWB3 | Modbusgateway bit signals | Off Bit 88 (Acq.Bit.88) | 201E47
12912 | MGWB3 | Modbusgateway bit signals | On Bit 89 (Acq.Bit.89) | 201E48
12913 | MGWB3 | Modbusgateway bit signals | Off Bit 89 (Acq.Bit.89) | 201E49
12914 | MGWB3 | Modbusgateway bit signals | On Bit 90 (Acq.Bit.90) | 201E50
12915 | MGWB3 | Modbusgateway bit signals | Off Bit 90 (Acq.Bit.90) | 201E51
12916 | MGWB3 | Modbusgateway bit signals | On Bit 91 (Acq.Bit.91) | 201E52
12917 | MGWB3 | Modbusgateway bit signals | Off Bit 91 (Acq.Bit.91) | 201E53
12918 | MGWB3 | Modbusgateway bit signals | On Bit 92 (Acq.Bit.92) | 201E54
12919 | MGWB3 | Modbusgateway bit signals | Off Bit 92 (Acq.Bit.92) | 201E55
12920 | MGWB3 | Modbusgateway bit signals | On Bit 93 (Acq.Bit.93) | 201E56
12921 | MGWB3 | Modbusgateway bit signals | Off Bit 93 (Acq.Bit.93) | 201E57
12922 | MGWB3 | Modbusgateway bit signals | On Bit 94 (Acq.Bit.94) | 201E58
12923 | MGWB3 | Modbusgateway bit signals | Off Bit 94 (Acq.Bit.94) | 201E59
12924 | MGWB3 | Modbusgateway bit signals | On Bit 95 (Acq.Bit.95) | 201E60
12925 | MGWB3 | Modbusgateway bit signals | Off Bit 95 (Acq.Bit.95) | 201E61
12926 | MGWB3 | Modbusgateway bit signals | On Bit 96 (Acq.Bit.96) | 201E62
12927 | MGWB3 | Modbusgateway bit signals | Off Bit 96 (Acq.Bit.96) | 201E63
12928 | MGWB4 | Modbusgateway bit signals | On Bit 97 (Acq.Bit.97) | 202E0
12929 | MGWB4 | Modbusgateway bit signals | Off Bit 97 (Acq.Bit.97) | 202E1
12930 | MGWB4 | Modbusgateway bit signals | On Bit 98 (Acq.Bit.98) | 202E2
12931 | MGWB4 | Modbusgateway bit signals | Off Bit 98 (Acq.Bit.98) | 202E3
12932 | MGWB4 | Modbusgateway bit signals | On Bit 99 (Acq.Bit.99) | 202E4
12933 | MGWB4 | Modbusgateway bit signals | Off Bit 99 (Acq.Bit.99) | 202E5
12934 | MGWB4 | Modbusgateway bit signals | On Bit 100 (Acq.Bit.100) | 202E6
12935 | MGWB4 | Modbusgateway bit signals | Off Bit 100 (Acq.Bit.100) | 202E7
12936 | MGWB4 | Modbusgateway bit signals | On Bit 101 (Acq.Bit.101) | 202E8
12937 | MGWB4 | Modbusgateway bit signals | Off Bit 101 (Acq.Bit.101) | 202E9
12938 | MGWB4 | Modbusgateway bit signals | On Bit 102 (Acq.Bit.102) | 202E10
12939 | MGWB4 | Modbusgateway bit signals | Off Bit 102 (Acq.Bit.102) | 202E11
12940 | MGWB4 | Modbusgateway bit signals | On Bit 103 (Acq.Bit.103) | 202E12
12941 | MGWB4 | Modbusgateway bit signals | Off Bit 103 (Acq.Bit.103) | 202E13
12942 | MGWB4 | Modbusgateway bit signals | On Bit 104 (Acq.Bit.104) | 202E14
12943 | MGWB4 | Modbusgateway bit signals | Off Bit 104 (Acq.Bit.104) | 202E15
12944 | MGWB4 | Modbusgateway bit signals | On Bit 105 (Acq.Bit.105) | 202E16
12945 | MGWB4 | Modbusgateway bit signals | Off Bit 105 (Acq.Bit.105) | 202E17
12946 | MGWB4 | Modbusgateway bit signals | On Bit 106 (Acq.Bit.106) | 202E18
12947 | MGWB4 | Modbusgateway bit signals | Off Bit 106 (Acq.Bit.106) | 202E19
12948 | MGWB4 | Modbusgateway bit signals | On Bit 107 (Acq.Bit.107) | 202E20
12949 | MGWB4 | Modbusgateway bit signals | Off Bit 107 (Acq.Bit.107) | 202E21
12950 | MGWB4 | Modbusgateway bit signals | On Bit 108 (Acq.Bit.108) | 202E22
12951 | MGWB4 | Modbusgateway bit signals | Off Bit 108 (Acq.Bit.108) | 202E23
12952 | MGWB4 | Modbusgateway bit signals | On Bit 109 (Acq.Bit.109) | 202E24
12953 | MGWB4 | Modbusgateway bit signals | Off Bit 109 (Acq.Bit.109) | 202E25
12954 | MGWB4 | Modbusgateway bit signals | On Bit 110 (Acq.Bit.110) | 202E26
12955 | MGWB4 | Modbusgateway bit signals | Off Bit 110 (Acq.Bit.110) | 202E27
12956 | MGWB4 | Modbusgateway bit signals | On Bit 111 (Acq.Bit.111) | 202E28
12957 | MGWB4 | Modbusgateway bit signals | Off Bit 111 (Acq.Bit.111) | 202E29
12958 | MGWB4 | Modbusgateway bit signals | On Bit 112 (Acq.Bit.112) | 202E30
12959 | MGWB4 | Modbusgateway bit signals | Off Bit 112 (Acq.Bit.112) | 202E31
12960 | MGWB4 | Modbusgateway bit signals | On Bit 113 (Acq.Bit.113) | 202E32
12961 | MGWB4 | Modbusgateway bit signals | Off Bit 113 (Acq.Bit.113) | 202E33
12962 | MGWB4 | Modbusgateway bit signals | On Bit 114 (Acq.Bit.114) | 202E34
12963 | MGWB4 | Modbusgateway bit signals | Off Bit 114 (Acq.Bit.114) | 202E35
12964 | MGWB4 | Modbusgateway bit signals | On Bit 115 (Acq.Bit.115) | 202E36
12965 | MGWB4 | Modbusgateway bit signals | Off Bit 115 (Acq.Bit.115) | 202E37
12966 | MGWB4 | Modbusgateway bit signals | On Bit 116 (Acq.Bit.116) | 202E38
12967 | MGWB4 | Modbusgateway bit signals | Off Bit 116 (Acq.Bit.116) | 202E39
12968 | MGWB4 | Modbusgateway bit signals | On Bit 117 (Acq.Bit.117) | 202E40
12969 | MGWB4 | Modbusgateway bit signals | Off Bit 117 (Acq.Bit.117) | 202E41
12970 | MGWB4 | Modbusgateway bit signals | On Bit 118 (Acq.Bit.118) | 202E42
12971 | MGWB4 | Modbusgateway bit signals | Off Bit 118 (Acq.Bit.118) | 202E43
12972 | MGWB4 | Modbusgateway bit signals | On Bit 119 (Acq.Bit.119) | 202E44
12973 | MGWB4 | Modbusgateway bit signals | Off Bit 119 (Acq.Bit.119) | 202E45
12974 | MGWB4 | Modbusgateway bit signals | On Bit 120 (Acq.Bit.120) | 202E46
12975 | MGWB4 | Modbusgateway bit signals | Off Bit 120 (Acq.Bit.120) | 202E47
12976 | MGWB4 | Modbusgateway bit signals | On Bit 121 (Acq.Bit.121) | 202E48
12977 | MGWB4 | Modbusgateway bit signals | Off Bit 121 (Acq.Bit.121) | 202E49
12978 | MGWB4 | Modbusgateway bit signals | On Bit 122 (Acq.Bit.122) | 202E50
12979 | MGWB4 | Modbusgateway bit signals | Off Bit 122 (Acq.Bit.122) | 202E51
12980 | MGWB4 | Modbusgateway bit signals | On Bit 123 (Acq.Bit.123) | 202E52
12981 | MGWB4 | Modbusgateway bit signals | Off Bit 123 (Acq.Bit.123) | 202E53
12982 | MGWB4 | Modbusgateway bit signals | On Bit 124 (Acq.Bit.124) | 202E54
12983 | MGWB4 | Modbusgateway bit signals | Off Bit 124 (Acq.Bit.124) | 202E55
12984 | MGWB4 | Modbusgateway bit signals | On Bit 125 (Acq.Bit.125) | 202E56
12985 | MGWB4 | Modbusgateway bit signals | Off Bit 125 (Acq.Bit.125) | 202E57
12986 | MGWB4 | Modbusgateway bit signals | On Bit 126 (Acq.Bit.126) | 202E58
12987 | MGWB4 | Modbusgateway bit signals | Off Bit 126 (Acq.Bit.126) | 202E59
12988 | MGWB4 | Modbusgateway bit signals | On Bit 127 (Acq.Bit.127) | 202E60
12989 | MGWB4 | Modbusgateway bit signals | Off Bit 127 (Acq.Bit.127) | 202E61
12990 | MGWB4 | Modbusgateway bit signals | On Bit 128 (Acq.Bit.128) | 202E62
12991 | MGWB4 | Modbusgateway bit signals | Off Bit 128 (Acq.Bit.128) | 202E63
12992 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 1 (Acq.Binary.1) | 203E0
12993 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 1 (Acq.Binary.1) | 203E1
12994 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 1 (Acq.Binary.1) | 203E2
12995 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 1 (Acq.Binary.1) | 203E3
12996 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 2 (Acq.Binary.2) | 203E4
12997 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 2 (Acq.Binary.2) | 203E5
12998 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 2 (Acq.Binary.2) | 203E6
12999 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 2 (Acq.Binary.2) | 203E7
13000 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 3 (Acq.Binary.3) | 203E8
13001 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 3 (Acq.Binary.3) | 203E9
13002 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 3 (Acq.Binary.3) | 203E10
13003 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 3 (Acq.Binary.3) | 203E11
13004 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 4 (Acq.Binary.4) | 203E12
13005 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 4 (Acq.Binary.4) | 203E13
13006 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 4 (Acq.Binary.4) | 203E14
13007 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 4 (Acq.Binary.4) | 203E15
13008 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 5 (Acq.Binary.5) | 203E16
13009 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 5 (Acq.Binary.5) | 203E17
13010 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 5 (Acq.Binary.5) | 203E18
13011 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 5 (Acq.Binary.5) | 203E19
13012 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 6 (Acq.Binary.6) | 203E20
13013 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 6 (Acq.Binary.6) | 203E21
13014 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 6 (Acq.Binary.6) | 203E22
13015 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 6 (Acq.Binary.6) | 203E23
13016 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 7 (Acq.Binary.7) | 203E24
13017 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 7 (Acq.Binary.7) | 203E25
13018 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 7 (Acq.Binary.7) | 203E26
13019 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 7 (Acq.Binary.7) | 203E27
13020 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 8 (Acq.Binary.8) | 203E28
13021 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 8 (Acq.Binary.8) | 203E29
13022 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 8 (Acq.Binary.8) | 203E30
13023 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 8 (Acq.Binary.8) | 203E31
13024 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 9 (Acq.Binary.9) | 203E32
13025 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 9 (Acq.Binary.9) | 203E33
13026 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 9 (Acq.Binary.9) | 203E34
13027 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 9 (Acq.Binary.9) | 203E35
13028 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 10 (Acq.Binary.10) | 203E36
13029 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 10 (Acq.Binary.10) | 203E37
13030 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 10 (Acq.Binary.10) | 203E38
13031 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 10 (Acq.Binary.10) | 203E39
13032 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 11 (Acq.Binary.11) | 203E40
13033 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 11 (Acq.Binary.11) | 203E41
13034 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 11 (Acq.Binary.11) | 203E42
13035 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 11 (Acq.Binary.11) | 203E43
13036 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 12 (Acq.Binary.12) | 203E44
13037 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 12 (Acq.Binary.12) | 203E45
13038 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 12 (Acq.Binary.12) | 203E46
13039 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 12 (Acq.Binary.12) | 203E47
13040 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 13 (Acq.Binary.13) | 203E48
13041 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 13 (Acq.Binary.13) | 203E49
13042 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 13 (Acq.Binary.13) | 203E50
13043 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 13 (Acq.Binary.13) | 203E51
13044 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 14 (Acq.Binary.14) | 203E52
13045 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 14 (Acq.Binary.14) | 203E53
13046 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 14 (Acq.Binary.14) | 203E54
13047 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 14 (Acq.Binary.14) | 203E55
13048 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 15 (Acq.Binary.15) | 203E56
13049 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 15 (Acq.Binary.15) | 203E57
13050 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 15 (Acq.Binary.15) | 203E58
13051 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 15 (Acq.Binary.15) | 203E59
13052 | MGWD1 | Modbusgateway doublebit signals | Off Off Double Bit 16 (Acq.Binary.16) | 203E60
13053 | MGWD1 | Modbusgateway doublebit signals | On Off Double Bit 16 (Acq.Binary.16) | 203E61
13054 | MGWD1 | Modbusgateway doublebit signals | Off On Double Bit 16 (Acq.Binary.16) | 203E62
13055 | MGWD1 | Modbusgateway doublebit signals | On On Double Bit 16 (Acq.Binary.16) | 203E63
13056 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 17 (Acq.Binary.17) | 204E0
13057 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 17 (Acq.Binary.17) | 204E1
13058 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 17 (Acq.Binary.17) | 204E2
13059 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 17 (Acq.Binary.17) | 204E3
13060 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 18 (Acq.Binary.18) | 204E4
13061 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 18 (Acq.Binary.18) | 204E5
13062 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 18 (Acq.Binary.18) | 204E6
13063 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 18 (Acq.Binary.18) | 204E7
13064 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 19 (Acq.Binary.19) | 204E8
13065 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 19 (Acq.Binary.19) | 204E9
13066 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 19 (Acq.Binary.19) | 204E10
13067 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 19 (Acq.Binary.19) | 204E11
13068 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 20 (Acq.Binary.20) | 204E12
13069 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 20 (Acq.Binary.20) | 204E13
13070 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 20 (Acq.Binary.20) | 204E14
13071 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 20 (Acq.Binary.20) | 204E15
13072 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 21 (Acq.Binary.21) | 204E16
13073 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 21 (Acq.Binary.21) | 204E17
13074 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 21 (Acq.Binary.21) | 204E18
13075 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 21 (Acq.Binary.21) | 204E19
13076 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 22 (Acq.Binary.22) | 204E20
13077 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 22 (Acq.Binary.22) | 204E21
13078 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 22 (Acq.Binary.22) | 204E22
13079 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 22 (Acq.Binary.22) | 204E23
13080 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 23 (Acq.Binary.23) | 204E24
13081 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 23 (Acq.Binary.23) | 204E25
13082 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 23 (Acq.Binary.23) | 204E26
13083 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 23 (Acq.Binary.23) | 204E27
13084 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 24 (Acq.Binary.24) | 204E28
13085 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 24 (Acq.Binary.24) | 204E29
13086 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 24 (Acq.Binary.24) | 204E30
13087 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 24 (Acq.Binary.24) | 204E31
13088 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 25 (Acq.Binary.25) | 204E32
13089 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 25 (Acq.Binary.25) | 204E33
13090 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 25 (Acq.Binary.25) | 204E34
13091 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 25 (Acq.Binary.25) | 204E35
13092 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 26 (Acq.Binary.26) | 204E36
13093 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 26 (Acq.Binary.26) | 204E37
13094 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 26 (Acq.Binary.26) | 204E38
13095 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 26 (Acq.Binary.26) | 204E39
13096 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 27 (Acq.Binary.27) | 204E40
13097 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 27 (Acq.Binary.27) | 204E41
13098 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 27 (Acq.Binary.27) | 204E42
13099 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 27 (Acq.Binary.27) | 204E43
13100 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 28 (Acq.Binary.28) | 204E44
13101 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 28 (Acq.Binary.28) | 204E45
13102 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 28 (Acq.Binary.28) | 204E46
13103 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 28 (Acq.Binary.28) | 204E47
13104 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 29 (Acq.Binary.29) | 204E48
13105 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 29 (Acq.Binary.29) | 204E49
13106 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 29 (Acq.Binary.29) | 204E50
13107 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 29 (Acq.Binary.29) | 204E51
13108 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 30 (Acq.Binary.30) | 204E52
13109 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 30 (Acq.Binary.30) | 204E53
13110 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 30 (Acq.Binary.30) | 204E54
13111 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 30 (Acq.Binary.30) | 204E55
13112 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 31 (Acq.Binary.31) | 204E56
13113 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 31 (Acq.Binary.31) | 204E57
13114 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 31 (Acq.Binary.31) | 204E58
13115 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 31 (Acq.Binary.31) | 204E59
13116 | MGWD2 | Modbusgateway doublebit signals | Off Off Double Bit 32 (Acq.Binary.32) | 204E60
13117 | MGWD2 | Modbusgateway doublebit signals | On Off Double Bit 32 (Acq.Binary.32) | 204E61
13118 | MGWD2 | Modbusgateway doublebit signals | Off On Double Bit 32 (Acq.Binary.32) | 204E62
13119 | MGWD2 | Modbusgateway doublebit signals | On On Double Bit 32 (Acq.Binary.32) | 204E63
13120 | CPB1 | Capacitor bank status | Capacitor disconnected On | 205E0
13121 | CPB1 | Capacitor bank status | Capacitor disconnected Off | 205E1
13122 | CPB1 | Capacitor bank status | Capacitor connected On | 205E2
13123 | CPB1 | Capacitor bank status | Capacitor connected Off | 205E3
13124 | CPB1 | Capacitor bank status | Capacitor discharging On | 205E4
13125 | CPB1 | Capacitor bank status | Capacitor discharging Off | 205E5
13126 | CPB1 | Capacitor bank status | Capacitor overvoltage On | 205E6
13127 | CPB1 | Capacitor bank status | Capacitor overvoltage Off | 205E7
13184 | COL1 | Capacitor bank overload | Start ON | 206E0
13185 | COL1 | Capacitor bank overload | Start OFF | 206E1
13186 | COL1 | Capacitor bank overload | Trip ON | 206E2
13187 | COL1 | Capacitor bank overload | Trip OFF | 206E3
13188 | COL1 | Capacitor bank overload | Block ON | 206E4
13189 | COL1 | Capacitor bank overload | Block OFF | 206E5
13248 | COL2 | Capacitor bank overload | Start ON | 207E0
13249 | COL2 | Capacitor bank overload | Start OFF | 207E1
13250 | COL2 | Capacitor bank overload | Trip ON | 207E2
13251 | COL2 | Capacitor bank overload | Trip OFF | 207E3
13252 | COL2 | Capacitor bank overload | Block ON | 207E4
13253 | COL2 | Capacitor bank overload | Block OFF | 207E5
13312 | CNU1 | Capacitor bank neutral unbalance | Alarm Start On | 208E0
13313 | CNU1 | Capacitor bank neutral unbalance | Alarm Start Off | 208E1
13314 | CNU1 | Capacitor bank neutral unbalance | Alarm On | 208E2
13315 | CNU1 | Capacitor bank neutral unbalance | Alarm Off | 208E3
13316 | CNU1 | Capacitor bank neutral unbalance | Trip Start On | 208E4
13317 | CNU1 | Capacitor bank neutral unbalance | Trip Start Off | 208E5
13318 | CNU1 | Capacitor bank neutral unbalance | Trip On | 208E6
13319 | CNU1 | Capacitor bank neutral unbalance | Trip Off | 208E7
13320 | CNU1 | Capacitor bank neutral unbalance | Blocked On | 208E8
13321 | CNU1 | Capacitor bank neutral unbalance | Blocked Off | 208E9
13322 | CNU1 | Capacitor bank neutral unbalance | Unbalance detected On | 208E10
13323 | CNU1 | Capacitor bank neutral unbalance | Unbalance detected Off | 208E11
13324 | CNU1 | Capacitor bank neutral unbalance | Compensating natural unbalance On | 208E12
13325 | CNU1 | Capacitor bank neutral unbalance | Compensating natural unbalance Off | 208E13
13376 | CRF1 |  | Dummy event for SPA | 209E0
13440 | OOS1 | Pole slip | Pole Slip detection Start ON | 210E0
13441 | OOS1 | Pole slip | Pole Slip detection Start OFF | 210E1
13442 | OOS1 | Pole slip | Pole Slip detected Trip ON | 210E2
13443 | OOS1 | Pole slip | Pole Slip detected Trip OFF | 210E3
13444 | OOS1 | Pole slip | Pole Slip detection Blocked ON | 210E4
13445 | OOS1 | Pole slip | Pole Slip detection Blocked OFF | 210E5
13446 | OOS1 | Pole slip | Pole Slip Z locus entered chacacteristics | 210E6
13447 | OOS1 | Pole slip | Pole Slip Z locus exit chacacteristics | 210E7
13448 | OOS1 | Pole slip | Pole Slip Z locus outside R+ Blinder ON | 210E8
13449 | OOS1 | Pole slip | Pole Slip Z locus outside R+ Blinder OFF | 210E9
13450 | OOS1 | Pole slip | Pole Slip Z locus Inside R+ Blinder ON | 210E10
13451 | OOS1 | Pole slip | Pole Slip Z locus Inside R+ Blinder OFF | 210E11
13452 | OOS1 | Pole slip | Pole Slip Z locus outside R- Blinder ON | 210E12
13453 | OOS1 | Pole slip | Pole Slip Z locus outside R- Blinder OFF | 210E13
13454 | OOS1 | Pole slip | Pole Slip Z locus Inside R- Blinder ON | 210E14
13455 | OOS1 | Pole slip | Pole Slip Z locus Inside R- Blinder OFF | 210E15
13456 | OOS1 | Pole slip | Pole Slip Z locus between R Blinders ON | 210E16
13457 | OOS1 | Pole slip | Pole Slip Z locus between R Blinders OFF | 210E17
13458 | OOS1 | Pole slip | Pole Slip Z locus travel time criteria ON | 210E18
13459 | OOS1 | Pole slip | Pole Slip Z locus travel time criteria OFF | 210E19
13460 | OOS1 | Pole slip | Pole Slip Detected ON | 210E20
13461 | OOS1 | Pole slip | Pole Slip Detected OFF | 210E21
13462 | OOS1 | Pole slip | Reset time finished ON | 210E22
13463 | OOS1 | Pole slip | Reset time finished, slip counters reset OFF | 210E23
13504 | THDV1 | Voltage THD | Voltage THD Start On | 211E0
13505 | THDV1 | Voltage THD | Voltage THD Start Off | 211E1
13506 | THDV1 | Voltage THD | Voltage THD Alarm On | 211E2
13507 | THDV1 | Voltage THD | Voltage THD Alarm Off | 211E3
13508 | THDV1 | Voltage THD | Voltage THD Alarm Blocked On | 211E4
13509 | THDV1 | Voltage THD | Voltage THD Alarm Blocked Off | 211E5
13568 | GOOSE5 | Goose sub status | GOOSE Subscription status 1 Active | 212E0
13569 | GOOSE5 | Goose sub status | GOOSE Subscription status 1 Not active | 212E1
13570 | GOOSE5 | Goose sub status | GOOSE Subscription status 2 Active | 212E2
13571 | GOOSE5 | Goose sub status | GOOSE Subscription status 2 Not active | 212E3
13572 | GOOSE5 | Goose sub status | GOOSE Subscription status 3 Active | 212E4
13573 | GOOSE5 | Goose sub status | GOOSE Subscription status 3 Not active | 212E5
13574 | GOOSE5 | Goose sub status | GOOSE Subscription status 4 Active | 212E6
13575 | GOOSE5 | Goose sub status | GOOSE Subscription status 4 Not active | 212E7
13576 | GOOSE5 | Goose sub status | GOOSE Subscription status 5 Active | 212E8
13577 | GOOSE5 | Goose sub status | GOOSE Subscription status 5 Not active | 212E9
13578 | GOOSE5 | Goose sub status | GOOSE Subscription status 6 Active | 212E10
13579 | GOOSE5 | Goose sub status | GOOSE Subscription status 6 Not active | 212E11
13580 | GOOSE5 | Goose sub status | GOOSE Subscription status 7 Active | 212E12
13581 | GOOSE5 | Goose sub status | GOOSE Subscription status 7 Not active | 212E13
13582 | GOOSE5 | Goose sub status | GOOSE Subscription status 8 Active | 212E14
13583 | GOOSE5 | Goose sub status | GOOSE Subscription status 8 Not active | 212E15
13584 | GOOSE5 | Goose sub status | GOOSE Subscription status 9 Active | 212E16
13585 | GOOSE5 | Goose sub status | GOOSE Subscription status 9 Not active | 212E17
13586 | GOOSE5 | Goose sub status | GOOSE Subscription status 10 Active | 212E18
13587 | GOOSE5 | Goose sub status | GOOSE Subscription status 10 Not active | 212E19
13588 | GOOSE5 | Goose sub status | GOOSE Subscription status 11 Active | 212E20
13589 | GOOSE5 | Goose sub status | GOOSE Subscription status 11 Not active | 212E21
13590 | GOOSE5 | Goose sub status | GOOSE Subscription status 12 Active | 212E22
13591 | GOOSE5 | Goose sub status | GOOSE Subscription status 12 Not active | 212E23
13592 | GOOSE5 | Goose sub status | GOOSE Subscription status 13 Active | 212E24
13593 | GOOSE5 | Goose sub status | GOOSE Subscription status 13 Not active | 212E25
13594 | GOOSE5 | Goose sub status | GOOSE Subscription status 14 Active | 212E26
13595 | GOOSE5 | Goose sub status | GOOSE Subscription status 14 Not active | 212E27
13596 | GOOSE5 | Goose sub status | GOOSE Subscription status 15 Active | 212E28
13597 | GOOSE5 | Goose sub status | GOOSE Subscription status 15 Not active | 212E29
13598 | GOOSE5 | Goose sub status | GOOSE Subscription status 16 Active | 212E30
13599 | GOOSE5 | Goose sub status | GOOSE Subscription status 16 Not active | 212E31
13600 | GOOSE5 | Goose sub status | GOOSE Subscription status 17 Active | 212E32
13601 | GOOSE5 | Goose sub status | GOOSE Subscription status 17 Not active | 212E33
13602 | GOOSE5 | Goose sub status | GOOSE Subscription status 18 Active | 212E34
13603 | GOOSE5 | Goose sub status | GOOSE Subscription status 18 Not active | 212E35
13604 | GOOSE5 | Goose sub status | GOOSE Subscription status 19 Active | 212E36
13605 | GOOSE5 | Goose sub status | GOOSE Subscription status 19 Not active | 212E37
13606 | GOOSE5 | Goose sub status | GOOSE Subscription status 20 Active | 212E38
13607 | GOOSE5 | Goose sub status | GOOSE Subscription status 20 Not active | 212E39
13608 | GOOSE5 | Goose sub status | GOOSE Subscription status 21 Active | 212E40
13609 | GOOSE5 | Goose sub status | GOOSE Subscription status 21 Not active | 212E41
13610 | GOOSE5 | Goose sub status | GOOSE Subscription status 22 Active | 212E42
13611 | GOOSE5 | Goose sub status | GOOSE Subscription status 22 Not active | 212E43
13612 | GOOSE5 | Goose sub status | GOOSE Subscription status 23 Active | 212E44
13613 | GOOSE5 | Goose sub status | GOOSE Subscription status 23 Not active | 212E45
13614 | GOOSE5 | Goose sub status | GOOSE Subscription status 24 Active | 212E46
13615 | GOOSE5 | Goose sub status | GOOSE Subscription status 24 Not active | 212E47
13616 | GOOSE5 | Goose sub status | GOOSE Subscription status 25 Active | 212E48
13617 | GOOSE5 | Goose sub status | GOOSE Subscription status 25 Not active | 212E49
13618 | GOOSE5 | Goose sub status | GOOSE Subscription status 26 Active | 212E50
13619 | GOOSE5 | Goose sub status | GOOSE Subscription status 26 Not active | 212E51
13620 | GOOSE5 | Goose sub status | GOOSE Subscription status 27 Active | 212E52
13621 | GOOSE5 | Goose sub status | GOOSE Subscription status 27 Not active | 212E53
13622 | GOOSE5 | Goose sub status | GOOSE Subscription status 28 Active | 212E54
13623 | GOOSE5 | Goose sub status | GOOSE Subscription status 28 Not active | 212E55
13624 | GOOSE5 | Goose sub status | GOOSE Subscription status 29 Active | 212E56
13625 | GOOSE5 | Goose sub status | GOOSE Subscription status 29 Not active | 212E57
13626 | GOOSE5 | Goose sub status | GOOSE Subscription status 30 Active | 212E58
13627 | GOOSE5 | Goose sub status | GOOSE Subscription status 30 Not active | 212E59
13628 | GOOSE5 | Goose sub status | GOOSE Subscription status 31 Active | 212E60
13629 | GOOSE5 | Goose sub status | GOOSE Subscription status 31 Not active | 212E61
13630 | GOOSE5 | Goose sub status | GOOSE Subscription status 32 Active | 212E62
13631 | GOOSE5 | Goose sub status | GOOSE Subscription status 32 Not active | 212E63
13632 | GOOSE6 | Goose sub status | GOOSE Subscription status 33 Active | 213E0
13633 | GOOSE6 | Goose sub status | GOOSE Subscription status 33 Not active | 213E1
13634 | GOOSE6 | Goose sub status | GOOSE Subscription status 34 Active | 213E2
13635 | GOOSE6 | Goose sub status | GOOSE Subscription status 34 Not active | 213E3
13636 | GOOSE6 | Goose sub status | GOOSE Subscription status 35 Active | 213E4
13637 | GOOSE6 | Goose sub status | GOOSE Subscription status 35 Not active | 213E5
13638 | GOOSE6 | Goose sub status | GOOSE Subscription status 36 Active | 213E6
13639 | GOOSE6 | Goose sub status | GOOSE Subscription status 36 Not active | 213E7
13640 | GOOSE6 | Goose sub status | GOOSE Subscription status 37 Active | 213E8
13641 | GOOSE6 | Goose sub status | GOOSE Subscription status 37 Not active | 213E9
13642 | GOOSE6 | Goose sub status | GOOSE Subscription status 38 Active | 213E10
13643 | GOOSE6 | Goose sub status | GOOSE Subscription status 38 Not active | 213E11
13644 | GOOSE6 | Goose sub status | GOOSE Subscription status 39 Active | 213E12
13645 | GOOSE6 | Goose sub status | GOOSE Subscription status 39 Not active | 213E13
13646 | GOOSE6 | Goose sub status | GOOSE Subscription status 40 Active | 213E14
13647 | GOOSE6 | Goose sub status | GOOSE Subscription status 40 Not active | 213E15
13648 | GOOSE6 | Goose sub status | GOOSE Subscription status 41 Active | 213E16
13649 | GOOSE6 | Goose sub status | GOOSE Subscription status 41 Not active | 213E17
13650 | GOOSE6 | Goose sub status | GOOSE Subscription status 42 Active | 213E18
13651 | GOOSE6 | Goose sub status | GOOSE Subscription status 42 Not active | 213E19
13652 | GOOSE6 | Goose sub status | GOOSE Subscription status 43 Active | 213E20
13653 | GOOSE6 | Goose sub status | GOOSE Subscription status 43 Not active | 213E21
13654 | GOOSE6 | Goose sub status | GOOSE Subscription status 44 Active | 213E22
13655 | GOOSE6 | Goose sub status | GOOSE Subscription status 44 Not active | 213E23
13656 | GOOSE6 | Goose sub status | GOOSE Subscription status 45 Active | 213E24
13657 | GOOSE6 | Goose sub status | GOOSE Subscription status 45 Not active | 213E25
13658 | GOOSE6 | Goose sub status | GOOSE Subscription status 46 Active | 213E26
13659 | GOOSE6 | Goose sub status | GOOSE Subscription status 46 Not active | 213E27
13660 | GOOSE6 | Goose sub status | GOOSE Subscription status 47 Active | 213E28
13661 | GOOSE6 | Goose sub status | GOOSE Subscription status 47 Not active | 213E29
13662 | GOOSE6 | Goose sub status | GOOSE Subscription status 48 Active | 213E30
13663 | GOOSE6 | Goose sub status | GOOSE Subscription status 48 Not active | 213E31
13664 | GOOSE6 | Goose sub status | GOOSE Subscription status 49 Active | 213E32
13665 | GOOSE6 | Goose sub status | GOOSE Subscription status 49 Not active | 213E33
13666 | GOOSE6 | Goose sub status | GOOSE Subscription status 50 Active | 213E34
13667 | GOOSE6 | Goose sub status | GOOSE Subscription status 50 Not active | 213E35
13668 | GOOSE6 | Goose sub status | GOOSE Subscription status 51 Active | 213E36
13669 | GOOSE6 | Goose sub status | GOOSE Subscription status 51 Not active | 213E37
13670 | GOOSE6 | Goose sub status | GOOSE Subscription status 52 Active | 213E38
13671 | GOOSE6 | Goose sub status | GOOSE Subscription status 52 Not active | 213E39
13672 | GOOSE6 | Goose sub status | GOOSE Subscription status 53 Active | 213E40
13673 | GOOSE6 | Goose sub status | GOOSE Subscription status 53 Not active | 213E41
13674 | GOOSE6 | Goose sub status | GOOSE Subscription status 54 Active | 213E42
13675 | GOOSE6 | Goose sub status | GOOSE Subscription status 54 Not active | 213E43
13676 | GOOSE6 | Goose sub status | GOOSE Subscription status 55 Active | 213E44
13677 | GOOSE6 | Goose sub status | GOOSE Subscription status 55 Not active | 213E45
13678 | GOOSE6 | Goose sub status | GOOSE Subscription status 56 Active | 213E46
13679 | GOOSE6 | Goose sub status | GOOSE Subscription status 56 Not active | 213E47
13680 | GOOSE6 | Goose sub status | GOOSE Subscription status 57 Active | 213E48
13681 | GOOSE6 | Goose sub status | GOOSE Subscription status 57 Not active | 213E49
13682 | GOOSE6 | Goose sub status | GOOSE Subscription status 58 Active | 213E50
13683 | GOOSE6 | Goose sub status | GOOSE Subscription status 58 Not active | 213E51
13684 | GOOSE6 | Goose sub status | GOOSE Subscription status 59 Active | 213E52
13685 | GOOSE6 | Goose sub status | GOOSE Subscription status 59 Not active | 213E53
13686 | GOOSE6 | Goose sub status | GOOSE Subscription status 60 Active | 213E54
13687 | GOOSE6 | Goose sub status | GOOSE Subscription status 60 Not active | 213E55
13688 | GOOSE6 | Goose sub status | GOOSE Subscription status 61 Active | 213E56
13689 | GOOSE6 | Goose sub status | GOOSE Subscription status 61 Not active | 213E57
13690 | GOOSE6 | Goose sub status | GOOSE Subscription status 62 Active | 213E58
13691 | GOOSE6 | Goose sub status | GOOSE Subscription status 62 Not active | 213E59
13692 | GOOSE6 | Goose sub status | GOOSE Subscription status 63 Active | 213E60
13693 | GOOSE6 | Goose sub status | GOOSE Subscription status 63 Not active | 213E61
13694 | GOOSE6 | Goose sub status | GOOSE Subscription status 64 Active | 213E62
13695 | GOOSE6 | Goose sub status | GOOSE Subscription status 64 Not active | 213E63
13696 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 1 True | 214E0
13697 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 1 False | 214E1
13698 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 2 True | 214E2
13699 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 2 False | 214E3
13700 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 3 True | 214E4
13701 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 3 False | 214E5
13702 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 4 True | 214E6
13703 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 4 False | 214E7
13704 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 5 True | 214E8
13705 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 5 False | 214E9
13706 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 6 True | 214E10
13707 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 6 False | 214E11
13708 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 7 True | 214E12
13709 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 7 False | 214E13
13710 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 8 True | 214E14
13711 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 8 False | 214E15
13712 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 9 True | 214E16
13713 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 9 False | 214E17
13714 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 10 True | 214E18
13715 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 10 False | 214E19
13716 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 11 True | 214E20
13717 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 11 False | 214E21
13718 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 12 True | 214E22
13719 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 12 False | 214E23
13720 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 13 True | 214E24
13721 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 13 False | 214E25
13722 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 14 True | 214E26
13723 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 14 False | 214E27
13724 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 15 True | 214E28
13725 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 15 False | 214E29
13726 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 16 True | 214E30
13727 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 16 False | 214E31
13728 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 17 True | 214E32
13729 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 17 False | 214E33
13730 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 18 True | 214E34
13731 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 18 False | 214E35
13732 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 19 True | 214E36
13733 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 19 False | 214E37
13734 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 20 True | 214E38
13735 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 20 False | 214E39
13736 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 21 True | 214E40
13737 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 21 False | 214E41
13738 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 22 True | 214E42
13739 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 22 False | 214E43
13740 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 23 True | 214E44
13741 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 23 False | 214E45
13742 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 24 True | 214E46
13743 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 24 False | 214E47
13744 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 25 True | 214E48
13745 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 25 False | 214E49
13746 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 26 True | 214E50
13747 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 26 False | 214E51
13748 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 27 True | 214E52
13749 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 27 False | 214E53
13750 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 28 True | 214E54
13751 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 28 False | 214E55
13752 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 29 True | 214E56
13753 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 29 False | 214E57
13754 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 30 True | 214E58
13755 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 30 False | 214E59
13756 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 31 True | 214E60
13757 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 31 False | 214E61
13758 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 32 True | 214E62
13759 | GOOSE7 | Goose sub status | GOOSE Processing simulated messages 32 False | 214E63
13760 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 33 True | 215E0
13761 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 33 False | 215E1
13762 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 34 True | 215E2
13763 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 34 False | 215E3
13764 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 35 True | 215E4
13765 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 35 False | 215E5
13766 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 36 True | 215E6
13767 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 36 False | 215E7
13768 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 37 True | 215E8
13769 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 37 False | 215E9
13770 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 38 True | 215E10
13771 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 38 False | 215E11
13772 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 39 True | 215E12
13773 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 39 False | 215E13
13774 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 40 True | 215E14
13775 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 40 False | 215E15
13776 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 41 True | 215E16
13777 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 41 False | 215E17
13778 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 42 True | 215E18
13779 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 42 False | 215E19
13780 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 43 True | 215E20
13781 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 43 False | 215E21
13782 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 44 True | 215E22
13783 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 44 False | 215E23
13784 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 45 True | 215E24
13785 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 45 False | 215E25
13786 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 46 True | 215E26
13787 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 46 False | 215E27
13788 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 47 True | 215E28
13789 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 47 False | 215E29
13790 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 48 True | 215E30
13791 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 48 False | 215E31
13792 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 49 True | 215E32
13793 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 49 False | 215E33
13794 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 50 True | 215E34
13795 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 50 False | 215E35
13796 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 51 True | 215E36
13797 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 51 False | 215E37
13798 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 52 True | 215E38
13799 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 52 False | 215E39
13800 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 53 True | 215E40
13801 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 53 False | 215E41
13802 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 54 True | 215E42
13803 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 54 False | 215E43
13804 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 55 True | 215E44
13805 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 55 False | 215E45
13806 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 56 True | 215E46
13807 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 56 False | 215E47
13808 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 57 True | 215E48
13809 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 57 False | 215E49
13810 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 58 True | 215E50
13811 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 58 False | 215E51
13812 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 59 True | 215E52
13813 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 59 False | 215E53
13814 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 60 True | 215E54
13815 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 60 False | 215E55
13816 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 61 True | 215E56
13817 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 61 False | 215E57
13818 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 62 True | 215E58
13819 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 62 False | 215E59
13820 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 63 True | 215E60
13821 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 63 False | 215E61
13822 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 64 True | 215E62
13823 | GOOSE8 | Goose sub status | GOOSE Processing simulated messages 64 False | 215E63
13888 | UCP1 | Capacitor bank current unbalance | Alarm Start ON | 217E0
13889 | UCP1 | Capacitor bank current unbalance | Alarm Start OFF | 217E1
13890 | UCP1 | Capacitor bank current unbalance | Alarm ON | 217E2
13891 | UCP1 | Capacitor bank current unbalance | Alarm OFF | 217E3
13892 | UCP1 | Capacitor bank current unbalance | Start ON | 217E4
13893 | UCP1 | Capacitor bank current unbalance | Start OFF | 217E5
13894 | UCP1 | Capacitor bank current unbalance | Trip ON | 217E6
13895 | UCP1 | Capacitor bank current unbalance | Trip OFF | 217E7
13896 | UCP1 | Capacitor bank current unbalance | Block ON | 217E8
13897 | UCP1 | Capacitor bank current unbalance | Block OFF | 217E9
13898 | UCP1 | Capacitor bank current unbalance | Harmonic block ON | 217E10
13899 | UCP1 | Capacitor bank current unbalance | Harmonic block OFF | 217E11
13952 | PGS1B | Programmable stage | PS6 >/< Start ON | 218E0
13953 | PGS1B | Programmable stage | PS6 >/< Start OFF | 218E1
13954 | PGS1B | Programmable stage | PS6 >/< Trip ON | 218E2
13955 | PGS1B | Programmable stage | PS6 >/< Trip OFF | 218E3
13956 | PGS1B | Programmable stage | PS6 >/< Block ON | 218E4
13957 | PGS1B | Programmable stage | PS6 >/< Block OFF | 218E5
13958 | PGS1B | Programmable stage | PS7 >/< Start ON | 218E6
13959 | PGS1B | Programmable stage | PS7 >/< Start OFF | 218E7
13960 | PGS1B | Programmable stage | PS7 >/< Trip ON | 218E8
13961 | PGS1B | Programmable stage | PS7 >/< Trip OFF | 218E9
13962 | PGS1B | Programmable stage | PS7 >/< Block ON | 218E10
13963 | PGS1B | Programmable stage | PS7 >/< Block OFF | 218E11
13964 | PGS1B | Programmable stage | PS8 >/< Start ON | 218E12
13965 | PGS1B | Programmable stage | PS8 >/< Start OFF | 218E13
13966 | PGS1B | Programmable stage | PS8 >/< Trip ON | 218E14
13967 | PGS1B | Programmable stage | PS8 >/< Trip OFF | 218E15
13968 | PGS1B | Programmable stage | PS8 >/< Block ON | 218E16
13969 | PGS1B | Programmable stage | PS8 >/< Block OFF | 218E17
13970 | PGS1B | Programmable stage | PS9 >/< Start ON | 218E18
13971 | PGS1B | Programmable stage | PS9 >/< Start OFF | 218E19
13972 | PGS1B | Programmable stage | PS9 >/< Trip ON | 218E20
13973 | PGS1B | Programmable stage | PS9 >/< Trip OFF | 218E21
13974 | PGS1B | Programmable stage | PS9 >/< Block ON | 218E22
13975 | PGS1B | Programmable stage | PS9 >/< Block OFF | 218E23
13976 | PGS1B | Programmable stage | PS10 >/< Start ON | 218E24
13977 | PGS1B | Programmable stage | PS10 >/< Start OFF | 218E25
13978 | PGS1B | Programmable stage | PS10 >/< Trip ON | 218E26
13979 | PGS1B | Programmable stage | PS10 >/< Trip OFF | 218E27
13980 | PGS1B | Programmable stage | PS10 >/< Block ON | 218E28
13981 | PGS1B | Programmable stage | PS10 >/< Block OFF | 218E29
14016 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 1 True | 219E0
14017 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 1 False | 219E1
14018 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 2 True | 219E2
14019 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 2 False | 219E3
14020 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 3 True | 219E4
14021 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 3 False | 219E5
14022 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 4 True | 219E6
14023 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 4 False | 219E7
14024 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 5 True | 219E8
14025 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 5 False | 219E9
14026 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 6 True | 219E10
14027 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 6 False | 219E11
14028 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 7 True | 219E12
14029 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 7 False | 219E13
14030 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 8 True | 219E14
14031 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 8 False | 219E15
14032 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 9 True | 219E16
14033 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 9 False | 219E17
14034 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 10 True | 219E18
14035 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 10 False | 219E19
14036 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 11 True | 219E20
14037 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 11 False | 219E21
14038 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 12 True | 219E22
14039 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 12 False | 219E23
14040 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 13 True | 219E24
14041 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 13 False | 219E25
14042 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 14 True | 219E26
14043 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 14 False | 219E27
14044 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 15 True | 219E28
14045 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 15 False | 219E29
14046 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 16 True | 219E30
14047 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 16 False | 219E31
14048 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 17 True | 219E32
14049 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 17 False | 219E33
14050 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 18 True | 219E34
14051 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 18 False | 219E35
14052 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 19 True | 219E36
14053 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 19 False | 219E37
14054 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 20 True | 219E38
14055 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 20 False | 219E39
14056 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 21 True | 219E40
14057 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 21 False | 219E41
14058 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 22 True | 219E42
14059 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 22 False | 219E43
14060 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 23 True | 219E44
14061 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 23 False | 219E45
14062 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 24 True | 219E46
14063 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 24 False | 219E47
14064 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 25 True | 219E48
14065 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 25 False | 219E49
14066 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 26 True | 219E50
14067 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 26 False | 219E51
14068 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 27 True | 219E52
14069 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 27 False | 219E53
14070 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 28 True | 219E54
14071 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 28 False | 219E55
14072 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 29 True | 219E56
14073 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 29 False | 219E57
14074 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 30 True | 219E58
14075 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 30 False | 219E59
14076 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 31 True | 219E60
14077 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 31 False | 219E61
14078 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 32 True | 219E62
14079 | GOOSE9 | Goose commissioning status | GOOSE Receive needs commissioning 32 False | 219E63
14080 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 33 True | 220E0
14081 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 33 False | 220E1
14082 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 34 True | 220E2
14083 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 34 False | 220E3
14084 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 35 True | 220E4
14085 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 35 False | 220E5
14086 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 36 True | 220E6
14087 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 36 False | 220E7
14088 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 37 True | 220E8
14089 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 37 False | 220E9
14090 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 38 True | 220E10
14091 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 38 False | 220E11
14092 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 39 True | 220E12
14093 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 39 False | 220E13
14094 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 40 True | 220E14
14095 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 40 False | 220E15
14096 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 41 True | 220E16
14097 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 41 False | 220E17
14098 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 42 True | 220E18
14099 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 42 False | 220E19
14100 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 43 True | 220E20
14101 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 43 False | 220E21
14102 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 44 True | 220E22
14103 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 44 False | 220E23
14104 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 45 True | 220E24
14105 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 45 False | 220E25
14106 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 46 True | 220E26
14107 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 46 False | 220E27
14108 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 47 True | 220E28
14109 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 47 False | 220E29
14110 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 48 True | 220E30
14111 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 48 False | 220E31
14112 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 49 True | 220E32
14113 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 49 False | 220E33
14114 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 50 True | 220E34
14115 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 50 False | 220E35
14116 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 51 True | 220E36
14117 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 51 False | 220E37
14118 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 52 True | 220E38
14119 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 52 False | 220E39
14120 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 53 True | 220E40
14121 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 53 False | 220E41
14122 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 54 True | 220E42
14123 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 54 False | 220E43
14124 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 55 True | 220E44
14125 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 55 False | 220E45
14126 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 56 True | 220E46
14127 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 56 False | 220E47
14128 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 57 True | 220E48
14129 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 57 False | 220E49
14130 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 58 True | 220E50
14131 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 58 False | 220E51
14132 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 59 True | 220E52
14133 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 59 False | 220E53
14134 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 60 True | 220E54
14135 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 60 False | 220E55
14136 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 61 True | 220E56
14137 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 61 False | 220E57
14138 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 62 True | 220E58
14139 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 62 False | 220E59
14140 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 63 True | 220E60
14141 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 63 False | 220E61
14142 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 64 True | 220E62
14143 | GOOSE10 | Goose commissioning status | GOOSE Receive needs commissioning 64 False | 220E63
14144 | EFX1 |  | Start forward on | 221E0
14145 | EFX1 |  | Start forward off | 221E1
14146 | EFX1 |  | Trip forward on | 221E2
14147 | EFX1 |  | Trip forward off | 221E3
14148 | EFX1 |  | Start reverse on | 221E4
14149 | EFX1 |  | Start reverse off | 221E5
14150 | EFX1 |  | Trip reverse on | 221E6
14151 | EFX1 |  | Trip reverse off | 221E7
14152 | EFX1 |  | Block on | 221E8
14153 | EFX1 |  | Block off | 221E9
14208 | EFX2 |  | Start forward on | 222E0
14209 | EFX2 |  | Start forward off | 222E1
14210 | EFX2 |  | Trip forward on | 222E2
14211 | EFX2 |  | Trip forward off | 222E3
14212 | EFX2 |  | Start reverse on | 222E4
14213 | EFX2 |  | Start reverse off | 222E5
14214 | EFX2 |  | Trip reverse on | 222E6
14215 | EFX2 |  | Trip reverse off | 222E7
14216 | EFX2 |  | Block on | 222E8
14217 | EFX2 |  | Block off | 222E9
14272 | EFX3 |  | Start forward on | 223E0
14273 | EFX3 |  | Start forward off | 223E1
14274 | EFX3 |  | Trip forward on | 223E2
14275 | EFX3 |  | Trip forward off | 223E3
14276 | EFX3 |  | Start reverse on | 223E4
14277 | EFX3 |  | Start reverse off | 223E5
14278 | EFX3 |  | Trip reverse on | 223E6
14279 | EFX3 |  | Trip reverse off | 223E7
14280 | EFX3 |  | Block on | 223E8
14281 | EFX3 |  | Block off | 223E9
14336 | EFX4 |  | Start forward on | 224E0
14337 | EFX4 |  | Start forward off | 224E1
14338 | EFX4 |  | Trip forward on | 224E2
14339 | EFX4 |  | Trip forward off | 224E3
14340 | EFX4 |  | Start reverse on | 224E4
14341 | EFX4 |  | Start reverse off | 224E5
14342 | EFX4 |  | Trip reverse on | 224E6
14343 | EFX4 |  | Trip reverse off | 224E7
14344 | EFX4 |  | Block on | 224E8
14345 | EFX4 |  | Block off | 224E9
14400 | ARCS1 |  | Arc Channel 1 On | 225E0
14401 | ARCS1 |  | Arc Channel 1 Off | 225E1
14402 | ARCS1 |  | Arc Channel 2 On | 225E2
14403 | ARCS1 |  | Arc Channel 2 Off | 225E3
14404 | ARCS1 |  | Arc Channel 3 On | 225E4
14405 | ARCS1 |  | Arc Channel 3 Off | 225E5
14406 | ARCS1 |  | Arc Channel 4 On | 225E6
14407 | ARCS1 |  | Arc Channel 4 Off | 225E7
14408 | ARCS1 |  | Arc Channel 5 On | 225E8
14409 | ARCS1 |  | Arc Channel 5 Off | 225E9
14410 | ARCS1 |  | Arc Channel 6 On | 225E10
14411 | ARCS1 |  | Arc Channel 6 Off | 225E11
14412 | ARCS1 |  | Arc Channel 7 On | 225E12
14413 | ARCS1 |  | Arc Channel 7 Off | 225E13
14414 | ARCS1 |  | Arc Channel 8 On | 225E14
14415 | ARCS1 |  | Arc Channel 8 Off | 225E15
14416 | ARCS1 |  | Arc Channel 9 On | 225E16
14417 | ARCS1 |  | Arc Channel 9 Off | 225E17
14418 | ARCS1 |  | Arc Channel 10 On | 225E18
14419 | ARCS1 |  | Arc Channel 10 Off | 225E19
14420 | ARCS1 |  | Arc Channel 11 On | 225E20
14421 | ARCS1 |  | Arc Channel 11 Off | 225E21
14422 | ARCS1 |  | Arc Channel 12 On | 225E22
14423 | ARCS1 |  | Arc Channel 12 Off | 225E23
14424 | ARCS1 |  | Arc Channel 13 On | 225E24
14425 | ARCS1 |  | Arc Channel 13 Off | 225E25
14426 | ARCS1 |  | Arc Channel 14 On | 225E26
14427 | ARCS1 |  | Arc Channel 14 Off | 225E27
14428 | ARCS1 |  | Arc Channel 15 On | 225E28
14429 | ARCS1 |  | Arc Channel 15 Off | 225E29
14430 | ARCS1 |  | Arc Channel 16 On | 225E30
14431 | ARCS1 |  | Arc Channel 16 Off | 225E31
14432 | ARCS1 |  | Arc Channel 17 On | 225E32
14433 | ARCS1 |  | Arc Channel 17 Off | 225E33
14434 | ARCS1 |  | Arc Channel 18 On | 225E34
14435 | ARCS1 |  | Arc Channel 18 Off | 225E35
14436 | ARCS1 |  | Arc Channel 19 On | 225E36
14437 | ARCS1 |  | Arc Channel 19 Off | 225E37
14438 | ARCS1 |  | Arc Channel 20 On | 225E38
14439 | ARCS1 |  | Arc Channel 20 Off | 225E39
14440 | ARCS1 |  | Arc Channel 21 On | 225E40
14441 | ARCS1 |  | Arc Channel 21 Off | 225E41
14442 | ARCS1 |  | Arc Channel 22 On | 225E42
14443 | ARCS1 |  | Arc Channel 22 Off | 225E43
14444 | ARCS1 |  | Arc Channel 23 On | 225E44
14445 | ARCS1 |  | Arc Channel 23 Off | 225E45
14446 | ARCS1 |  | Arc Channel 24 On | 225E46
14447 | ARCS1 |  | Arc Channel 24 Off | 225E47
14464 | ARCS2 |  | Arc Fiber 1 On | 226E0
14465 | ARCS2 |  | Arc fiber 1 Off | 226E1
14466 | ARCS2 |  | Arc Fiber 2 On | 226E2
14467 | ARCS2 |  | Arc fiber 2 Off | 226E3
14468 | ARCS2 |  | Arc Fiber 3 On | 226E4
14469 | ARCS2 |  | Arc fiber 3 Off | 226E5
14470 | ARCS2 |  | Arc Fiber 4 On | 226E6
14471 | ARCS2 |  | Arc fiber 4 Off | 226E7
14472 | ARCS2 |  | Arc Fiber 5 On | 226E8
14473 | ARCS2 |  | Arc fiber 5 Off | 226E9
14474 | ARCS2 |  | Arc Fiber 6 On | 226E10
14475 | ARCS2 |  | Arc fiber 6 Off | 226E11
14476 | ARCS2 |  | Arc Fiber 7 On | 226E12
14477 | ARCS2 |  | Arc fiber 7 Off | 226E13
14478 | ARCS2 |  | Arc Fiber 8 On | 226E14
14479 | ARCS2 |  | Arc fiber 8 Off | 226E15
14480 | ARCS2 |  | Arc Fiber 9 On | 226E16
14481 | ARCS2 |  | Arc fiber 9 Off | 226E17
14482 | ARCS2 |  | Arc Fiber 10 On | 226E18
14483 | ARCS2 |  | Arc fiber 10 Off | 226E19
14484 | ARCS2 |  | Arc Fiber 11 On | 226E20
14485 | ARCS2 |  | Arc fiber 11 Off | 226E21
14486 | ARCS2 |  | Arc Fiber 12 On | 226E22
14487 | ARCS2 |  | Arc fiber 12 Off | 226E23
14488 | ARCS2 |  | Arc Fiber 13 On | 226E24
14489 | ARCS2 |  | Arc fiber 13 Off | 226E25
14490 | ARCS2 |  | Arc Fiber 14 On | 226E26
14491 | ARCS2 |  | Arc fiber 14 Off | 226E27
14492 | ARCS2 |  | Arc Fiber 15 On | 226E28
14493 | ARCS2 |  | Arc fiber 15 Off | 226E29
14494 | ARCS2 |  | Arc Fiber 16 On | 226E30
14495 | ARCS2 |  | Arc fiber 16 Off | 226E31
14496 | ARCS2 |  | Arc Fiber 17 On | 226E32
14497 | ARCS2 |  | Arc fiber 17 Off | 226E33
14498 | ARCS2 |  | Arc Fiber 18 On | 226E34
14499 | ARCS2 |  | Arc fiber 18 Off | 226E35
14528 | ARCSE1 |  | Arc Channel 1 Error On | 227E0
14529 | ARCSE1 |  | Arc Channel 1 Error Off | 227E1
14530 | ARCSE1 |  | Arc Channel 2 Error On | 227E2
14531 | ARCSE1 |  | Arc Channel 2 Error Off | 227E3
14532 | ARCSE1 |  | Arc Channel 3 Error On | 227E4
14533 | ARCSE1 |  | Arc Channel 3 Error Off | 227E5
14534 | ARCSE1 |  | Arc Channel 4 Error On | 227E6
14535 | ARCSE1 |  | Arc Channel 4 Error Off | 227E7
14536 | ARCSE1 |  | Arc Channel 5 Error On | 227E8
14537 | ARCSE1 |  | Arc Channel 5 Error Off | 227E9
14538 | ARCSE1 |  | Arc Channel 6 Error On | 227E10
14539 | ARCSE1 |  | Arc Channel 6 Error Off | 227E11
14540 | ARCSE1 |  | Arc Channel 7 Error On | 227E12
14541 | ARCSE1 |  | Arc Channel 7 Error Off | 227E13
14542 | ARCSE1 |  | Arc Channel 8 Error On | 227E14
14543 | ARCSE1 |  | Arc Channel 8 Error Off | 227E15
14544 | ARCSE1 |  | Arc Channel 9 Error On | 227E16
14545 | ARCSE1 |  | Arc Channel 9 Error Off | 227E17
14546 | ARCSE1 |  | Arc Channel 10 Error On | 227E18
14547 | ARCSE1 |  | Arc Channel 10 Error Off | 227E19
14548 | ARCSE1 |  | Arc Channel 11 Error On | 227E20
14549 | ARCSE1 |  | Arc Channel 11 Error Off | 227E21
14550 | ARCSE1 |  | Arc Channel 12 Error On | 227E22
14551 | ARCSE1 |  | Arc Channel 12 Error Off | 227E23
14552 | ARCSE1 |  | Arc Channel 13 Error On | 227E24
14553 | ARCSE1 |  | Arc Channel 13 Error Off | 227E25
14554 | ARCSE1 |  | Arc Channel 14 Error On | 227E26
14555 | ARCSE1 |  | Arc Channel 14 Error Off | 227E27
14556 | ARCSE1 |  | Arc Channel 15 Error On | 227E28
14557 | ARCSE1 |  | Arc Channel 15 Error Off | 227E29
14558 | ARCSE1 |  | Arc Channel 16 Error On | 227E30
14559 | ARCSE1 |  | Arc Channel 16 Error Off | 227E31
14560 | ARCSE1 |  | Arc Channel 17 Error On | 227E32
14561 | ARCSE1 |  | Arc Channel 17 Error Off | 227E33
14562 | ARCSE1 |  | Arc Channel 18 Error On | 227E34
14563 | ARCSE1 |  | Arc Channel 18 Error Off | 227E35
14564 | ARCSE1 |  | Arc Channel 19 Error On | 227E36
14565 | ARCSE1 |  | Arc Channel 19 Error Off | 227E37
14566 | ARCSE1 |  | Arc Channel 20 Error On | 227E38
14567 | ARCSE1 |  | Arc Channel 20 Error Off | 227E39
14568 | ARCSE1 |  | Arc Channel 21 Error On | 227E40
14569 | ARCSE1 |  | Arc Channel 21 Error Off | 227E41
14570 | ARCSE1 |  | Arc Channel 22 Error On | 227E42
14571 | ARCSE1 |  | Arc Channel 22 Error Off | 227E43
14572 | ARCSE1 |  | Arc Channel 23 Error On | 227E44
14573 | ARCSE1 |  | Arc Channel 23 Error Off | 227E45
14574 | ARCSE1 |  | Arc Channel 24 Error On | 227E46
14575 | ARCSE1 |  | Arc Channel 24 Error Off | 227E47
14592 | ARCSE2 |  | Arc Fiber 1 Error On | 228E0
14593 | ARCSE2 |  | Arc Fiber 1 Error Off | 228E1
14594 | ARCSE2 |  | Arc Fiber 2 Error On | 228E2
14595 | ARCSE2 |  | Arc Fiber 2 Error Off | 228E3
14596 | ARCSE2 |  | Arc Fiber 3 Error On | 228E4
14597 | ARCSE2 |  | Arc Fiber 3 Error Off | 228E5
14598 | ARCSE2 |  | Arc Fiber 4 Error On | 228E6
14599 | ARCSE2 |  | Arc Fiber 4 Error Off | 228E7
14600 | ARCSE2 |  | Arc Fiber 5 Error On | 228E8
14601 | ARCSE2 |  | Arc Fiber 5 Error Off | 228E9
14602 | ARCSE2 |  | Arc Fiber 6 Error On | 228E10
14603 | ARCSE2 |  | Arc Fiber 6 Error Off | 228E11
14604 | ARCSE2 |  | Arc Fiber 7 Error On | 228E12
14605 | ARCSE2 |  | Arc Fiber 7 Error Off | 228E13
14606 | ARCSE2 |  | Arc Fiber 8 Error On | 228E14
14607 | ARCSE2 |  | Arc Fiber 8 Error Off | 228E15
14608 | ARCSE2 |  | Arc Fiber 9 Error On | 228E16
14609 | ARCSE2 |  | Arc Fiber 9 Error Off | 228E17
14610 | ARCSE2 |  | Arc Fiber 10 Error On | 228E18
14611 | ARCSE2 |  | Arc Fiber 10 Error Off | 228E19
14612 | ARCSE2 |  | Arc Fiber 11 Error On | 228E20
14613 | ARCSE2 |  | Arc Fiber 11 Error Off | 228E21
14614 | ARCSE2 |  | Arc Fiber 12 Error On | 228E22
14615 | ARCSE2 |  | Arc Fiber 12 Error Off | 228E23
14616 | ARCSE2 |  | Arc Fiber 13 Error On | 228E24
14617 | ARCSE2 |  | Arc Fiber 13 Error Off | 228E25
14618 | ARCSE2 |  | Arc Fiber 14 Error On | 228E26
14619 | ARCSE2 |  | Arc Fiber 14 Error Off | 228E27
14620 | ARCSE2 |  | Arc Fiber 15 Error On | 228E28
14621 | ARCSE2 |  | Arc Fiber 15 Error Off | 228E29
14622 | ARCSE2 |  | Arc Fiber 16 Error On | 228E30
14623 | ARCSE2 |  | Arc Fiber 16 Error Off | 228E31
14624 | ARCSE2 |  | Arc Fiber 17 Error On | 228E32
14625 | ARCSE2 |  | Arc Fiber 17 Error Off | 228E33
14626 | ARCSE2 |  | Arc Fiber 18 Error On | 228E34
14627 | ARCSE2 |  | Arc Fiber 18 Error Off | 228E35
14656 | ARCOE1 |  | Arc HSO 1 On | 229E0
14657 | ARCOE1 |  | Arc HSO 1 Off | 229E1
14658 | ARCOE1 |  | Arc HSO 2 On | 229E2
14659 | ARCOE1 |  | Arc HSO 2 Off | 229E3
14660 | ARCOE1 |  | Arc HSO 3 On | 229E4
14661 | ARCOE1 |  | Arc HSO 3 Off | 229E5
14662 | ARCOE1 |  | Arc HSO 4 On | 229E6
14663 | ARCOE1 |  | Arc HSO 4 Off | 229E7
14664 | ARCOE1 |  | Arc HSO 5 On | 229E8
14665 | ARCOE1 |  | Arc HSO 5 Off | 229E9
14666 | ARCOE1 |  | Arc HSO 6 On | 229E10
14667 | ARCOE1 |  | Arc HSO 6 Off | 229E11
14668 | ARCOE1 |  | Arc HSO 7 On | 229E12
14669 | ARCOE1 |  | Arc HSO 7 Off | 229E13
14670 | ARCOE1 |  | Arc HSO 8 On | 229E14
14671 | ARCOE1 |  | Arc HSO 8 Off | 229E15
14672 | ARCOE1 |  | Arc HSO 9 On | 229E16
14673 | ARCOE1 |  | Arc HSO 9 Off | 229E17
14674 | ARCOE1 |  | Arc HSO 10 On | 229E18
14675 | ARCOE1 |  | Arc HSO 10 Off | 229E19
14676 | ARCOE1 |  | Arc HSO 11 On | 229E20
14677 | ARCOE1 |  | Arc HSO 11 Off | 229E21
14678 | ARCOE1 |  | Arc HSO 12 On | 229E22
14679 | ARCOE1 |  | Arc HSO 12 Off | 229E23
14720 | ARCOE2 |  | Arc QD 1 On | 230E0
14721 | ARCOE2 |  | Arc QD 1 Off | 230E1
14722 | ARCOE2 |  | Arc QD 2 On | 230E2
14723 | ARCOE2 |  | Arc QD 2 Off | 230E3
14724 | ARCOE2 |  | Arc QD 3 On | 230E4
14725 | ARCOE2 |  | Arc QD 3 Off | 230E5
14726 | ARCOE2 |  | Arc QD 4 On | 230E6
14727 | ARCOE2 |  | Arc QD 4 Off | 230E7
14728 | ARCOE2 |  | Arc QD 5 On | 230E8
14729 | ARCOE2 |  | Arc QD 5 Off | 230E9
14730 | ARCOE2 |  | Arc QD 6 On | 230E10
14731 | ARCOE2 |  | Arc QD 6 Off | 230E11
14784 | PFC1 | Power factor controller | Increase capacitance request on | 231E0
14785 | PFC1 | Power factor controller | Increase capacitance request off | 231E1
14786 | PFC1 | Power factor controller | Decrease capacitance request on | 231E2
14787 | PFC1 | Power factor controller | Decrease capacitance request off | 231E3
14788 | PFC1 | Power factor controller | Switching time on | 231E4
14789 | PFC1 | Power factor controller | Switching time off | 231E5
14790 | PFC1 | Power factor controller | Manual control mode on | 231E6
14791 | PFC1 | Power factor controller | Manual control mode off | 231E7
14792 | PFC1 | Power factor controller | PFC block on | 231E8
14793 | PFC1 | Power factor controller | PFC block off | 231E9
14794 | PFC1 | Power factor controller | Bank 1 discharging on | 231E10
14795 | PFC1 | Power factor controller | Bank 1 discharging off | 231E11
14796 | PFC1 | Power factor controller | Bank 2 discharging on | 231E12
14797 | PFC1 | Power factor controller | Bank 2 discharging off | 231E13
14798 | PFC1 | Power factor controller | Bank 3 discharging on | 231E14
14799 | PFC1 | Power factor controller | Bank 3 discharging off | 231E15
14800 | PFC1 | Power factor controller | Bank 4 discharging on | 231E16
14801 | PFC1 | Power factor controller | Bank 4 discharging off | 231E17
14802 | PFC1 | Power factor controller | Bank 5 discharging on | 231E18
14803 | PFC1 | Power factor controller | Bank 5 discharging off | 231E19
14804 | PFC1 | Power factor controller | Switching failure on | 231E20
14805 | PFC1 | Power factor controller | Switching failure off | 231E21
14806 | PFC1 | Power factor controller | Starting increase capacitance On | 231E22
14807 | PFC1 | Power factor controller | Starting increase capacitance Off | 231E23
14808 | PFC1 | Power factor controller | Starting decrease capacitance On | 231E24
14809 | PFC1 | Power factor controller | Starting decrease capacitance Off | 231E25
14848 | SYNX1 | Synchrocheck X | SYN1 Voltage difference Ok On | 232E0
14849 | SYNX1 | Synchrocheck X | SYN1 Voltage difference Ok Off | 232E1
14850 | SYNX1 | Synchrocheck X | SYN1 Angle difference Ok On | 232E2
14851 | SYNX1 | Synchrocheck X | SYN1 Angle difference Ok Off | 232E3
14852 | SYNX1 | Synchrocheck X | SYN1 Frequency difference Ok On | 232E4
14853 | SYNX1 | Synchrocheck X | SYN1 Frequency difference Ok On | 232E5
14854 | SYNX1 | Synchrocheck X | SYN1 Live Live Condition On | 232E6
14855 | SYNX1 | Synchrocheck X | SYN1 Live Live Condition Off | 232E7
14856 | SYNX1 | Synchrocheck X | SYN1 Live Dead Condition On | 232E8
14857 | SYNX1 | Synchrocheck X | SYN1 Live Dead Condition Off | 232E9
14858 | SYNX1 | Synchrocheck X | SYN1 Dead Live Condition On | 232E10
14859 | SYNX1 | Synchrocheck X | SYN1 Dead Live Condition Off | 232E11
14860 | SYNX1 | Synchrocheck X | SYN1 Dead Dead Condition On | 232E12
14861 | SYNX1 | Synchrocheck X | SYN1 Dead Dead Condition On | 232E13
14862 | SYNX1 | Synchrocheck X | SYN1 Voltage Difference too high Vbus > Vline On | 232E14
14863 | SYNX1 | Synchrocheck X | SYN1 Voltage Difference too high Vbus > Vline Off | 232E15
14864 | SYNX1 | Synchrocheck X | SYN1 Voltage Difference too high Vline > Vbus On | 232E16
14865 | SYNX1 | Synchrocheck X | SYN1 Voltage Difference too high Vline > Vbus Off | 232E17
14866 | SYNX1 | Synchrocheck X | SYN1 Frequency Difference too high fbus > fline On | 232E18
14867 | SYNX1 | Synchrocheck X | SYN1 Frequency Difference too high fbus > fline Off | 232E19
14868 | SYNX1 | Synchrocheck X | SYN1 Frequency Difference too high fline > fbus On | 232E20
14869 | SYNX1 | Synchrocheck X | SYN1 Frequency Difference too high fline > fbus Off | 232E21
14870 | SYNX1 | Synchrocheck X | SYN1 Angle Difference too high a bus leads a line On | 232E22
14871 | SYNX1 | Synchrocheck X | SYN1 Angle Difference too high a bus leads a line Off | 232E23
14872 | SYNX1 | Synchrocheck X | SYN1 Angle Difference too high a line leads a bus On | 232E24
14873 | SYNX1 | Synchrocheck X | SYN1 Angle Difference too high a line leads a bus Off | 232E25
14874 | SYNX1 | Synchrocheck X | SYN1 Bus voltage Live On | 232E26
14875 | SYNX1 | Synchrocheck X | SYN1 Bus voltage Live Off | 232E27
14876 | SYNX1 | Synchrocheck X | SYN1 Bus voltage Dead On | 232E28
14877 | SYNX1 | Synchrocheck X | SYN1 Bus voltage Dead Off | 232E29
14878 | SYNX1 | Synchrocheck X | SYN1 Line voltage Live On | 232E30
14879 | SYNX1 | Synchrocheck X | SYN1 Line voltage Live Off | 232E31
14880 | SYNX1 | Synchrocheck X | SYN1 Line voltage Dead On | 232E32
14881 | SYNX1 | Synchrocheck X | SYN1 Line voltage Dead Off | 232E33
14912 | SYNX2 | Synchrocheck X | SYN2 Voltage difference Ok On | 233E0
14913 | SYNX2 | Synchrocheck X | SYN2 Voltage difference Ok Off | 233E1
14914 | SYNX2 | Synchrocheck X | SYN2 Angle difference Ok On | 233E2
14915 | SYNX2 | Synchrocheck X | SYN2 Angle difference Ok Off | 233E3
14916 | SYNX2 | Synchrocheck X | SYN2 Frequency difference Ok On | 233E4
14917 | SYNX2 | Synchrocheck X | SYN2 Frequency difference Ok On | 233E5
14918 | SYNX2 | Synchrocheck X | SYN2 Live Live Condition On | 233E6
14919 | SYNX2 | Synchrocheck X | SYN2 Live Live Condition Off | 233E7
14920 | SYNX2 | Synchrocheck X | SYN2 Live Dead Condition On | 233E8
14921 | SYNX2 | Synchrocheck X | SYN2 Live Dead Condition Off | 233E9
14922 | SYNX2 | Synchrocheck X | SYN2 Dead Live Condition On | 233E10
14923 | SYNX2 | Synchrocheck X | SYN2 Dead Live Condition Off | 233E11
14924 | SYNX2 | Synchrocheck X | SYN2 Dead Dead Condition On | 233E12
14925 | SYNX2 | Synchrocheck X | SYN2 Dead Dead Condition On | 233E13
14926 | SYNX2 | Synchrocheck X | SYN2 Voltage Difference too high Vbus > Vline On | 233E14
14927 | SYNX2 | Synchrocheck X | SYN2 Voltage Difference too high Vbus > Vline Off | 233E15
14928 | SYNX2 | Synchrocheck X | SYN2 Voltage Difference too high Vline > Vbus On | 233E16
14929 | SYNX2 | Synchrocheck X | SYN2 Voltage Difference too high Vline > Vbus Off | 233E17
14930 | SYNX2 | Synchrocheck X | SYN2 Frequency Difference too high fbus > fline On | 233E18
14931 | SYNX2 | Synchrocheck X | SYN2 Frequency Difference too high fbus > fline Off | 233E19
14932 | SYNX2 | Synchrocheck X | SYN2 Frequency Difference too high fline > fbus On | 233E20
14933 | SYNX2 | Synchrocheck X | SYN2 Frequency Difference too high fline > fbus Off | 233E21
14934 | SYNX2 | Synchrocheck X | SYN2 Angle Difference too high a bus leads a line On | 233E22
14935 | SYNX2 | Synchrocheck X | SYN2 Angle Difference too high a bus leads a line Off | 233E23
14936 | SYNX2 | Synchrocheck X | SYN2 Angle Difference too high a line leads a bus On | 233E24
14937 | SYNX2 | Synchrocheck X | SYN2 Angle Difference too high a line leads a bus Off | 233E25
14938 | SYNX2 | Synchrocheck X | SYN2 Bus voltage Live On | 233E26
14939 | SYNX2 | Synchrocheck X | SYN2 Bus voltage Live Off | 233E27
14940 | SYNX2 | Synchrocheck X | SYN2 Bus voltage Dead On | 233E28
14941 | SYNX2 | Synchrocheck X | SYN2 Bus voltage Dead Off | 233E29
14942 | SYNX2 | Synchrocheck X | SYN2 Line voltage Live On | 233E30
14943 | SYNX2 | Synchrocheck X | SYN2 Line voltage Live Off | 233E31
14944 | SYNX2 | Synchrocheck X | SYN2 Line voltage Dead On | 233E32
14945 | SYNX2 | Synchrocheck X | SYN2 Line voltage Dead Off | 233E33
14976 | SYNX3 | Synchrocheck X | SYN3 Voltage difference Ok On | 234E0
14977 | SYNX3 | Synchrocheck X | SYN3 Voltage difference Ok Off | 234E1
14978 | SYNX3 | Synchrocheck X | SYN3 Angle difference Ok On | 234E2
14979 | SYNX3 | Synchrocheck X | SYN3 Angle difference Ok Off | 234E3
14980 | SYNX3 | Synchrocheck X | SYN3 Frequency difference Ok On | 234E4
14981 | SYNX3 | Synchrocheck X | SYN3 Frequency difference Ok On | 234E5
14982 | SYNX3 | Synchrocheck X | SYN3 Live Live Condition On | 234E6
14983 | SYNX3 | Synchrocheck X | SYN3 Live Live Condition Off | 234E7
14984 | SYNX3 | Synchrocheck X | SYN3 Live Dead Condition On | 234E8
14985 | SYNX3 | Synchrocheck X | SYN3 Live Dead Condition Off | 234E9
14986 | SYNX3 | Synchrocheck X | SYN3 Dead Live Condition On | 234E10
14987 | SYNX3 | Synchrocheck X | SYN3 Dead Live Condition Off | 234E11
14988 | SYNX3 | Synchrocheck X | SYN3 Dead Dead Condition On | 234E12
14989 | SYNX3 | Synchrocheck X | SYN3 Dead Dead Condition On | 234E13
14990 | SYNX3 | Synchrocheck X | SYN3 Voltage Difference too high Vbus > Vline On | 234E14
14991 | SYNX3 | Synchrocheck X | SYN3 Voltage Difference too high Vbus > Vline Off | 234E15
14992 | SYNX3 | Synchrocheck X | SYN3 Voltage Difference too high Vline > Vbus On | 234E16
14993 | SYNX3 | Synchrocheck X | SYN3 Voltage Difference too high Vline > Vbus Off | 234E17
14994 | SYNX3 | Synchrocheck X | SYN3 Frequency Difference too high fbus > fline On | 234E18
14995 | SYNX3 | Synchrocheck X | SYN3 Frequency Difference too high fbus > fline Off | 234E19
14996 | SYNX3 | Synchrocheck X | SYN3 Frequency Difference too high fline > fbus On | 234E20
14997 | SYNX3 | Synchrocheck X | SYN3 Frequency Difference too high fline > fbus Off | 234E21
14998 | SYNX3 | Synchrocheck X | SYN3 Angle Difference too high a bus leads a line On | 234E22
14999 | SYNX3 | Synchrocheck X | SYN3 Angle Difference too high a bus leads a line Off | 234E23
15000 | SYNX3 | Synchrocheck X | SYN3 Angle Difference too high a line leads a bus On | 234E24
15001 | SYNX3 | Synchrocheck X | SYN3 Angle Difference too high a line leads a bus Off | 234E25
15002 | SYNX3 | Synchrocheck X | SYN3 Bus voltage Live On | 234E26
15003 | SYNX3 | Synchrocheck X | SYN3 Bus voltage Live Off | 234E27
15004 | SYNX3 | Synchrocheck X | SYN3 Bus voltage Dead On | 234E28
15005 | SYNX3 | Synchrocheck X | SYN3 Bus voltage Dead Off | 234E29
15006 | SYNX3 | Synchrocheck X | SYN3 Line voltage Live On | 234E30
15007 | SYNX3 | Synchrocheck X | SYN3 Line voltage Live Off | 234E31
15008 | SYNX3 | Synchrocheck X | SYN3 Line voltage Dead On | 234E32
15009 | SYNX3 | Synchrocheck X | SYN3 Line voltage Dead Off | 234E33

## AQ-250 v2.5.7.1-303-AP2
Event Code | Block Description | Event Description | SPA Event
1 | SYSTEM | Power on | 0E1
2 | SYSTEM | RTC change | 0E2
3 | SYSTEM | RTC time incorrect | 0E3
4 | SYSTEM | NTP time sync aquired | 0E4
5 | SYSTEM | NTP time change | 0E5
6 | SYSTEM | NTP time sync lost | 0E6
7 | SYSTEM | Measuring system suspended | 0E7
8 | SYSTEM | Measuring system activated | 0E8
9 | SYSTEM | Unknown event | 0E9
26 | SYSTEM | Sync input On | 0E26
27 | SYSTEM | Protection subsystem reset | 0E50
28 | SYSTEM | Storage reinitialized - no contents | 0E28
29 | SYSTEM | Storage reinitialized - new firmware detected | 0E29
30 | SYSTEM | Event buffer clear marker | 0E30
31 | SYSTEM | Event buffer initialized | 0E31
32 | SYSTEM | DblEth LinkA down | 0E32
33 | SYSTEM | DblEth LinkA OK | 0E33
34 | SYSTEM | DblEth LinkB down | 0E34
35 | SYSTEM | DblEth LinkB OK | 0E35
36 | SYSTEM | User access control HMI open | 0E36
37 | SYSTEM | User access control HMI close | 0E37
38 | SYSTEM | User access control settingtool open | 0E38
39 | SYSTEM | User access control settingtool close | 0E39
40 | SYSTEM | Event overload On | 0E40
41 | SYSTEM | Event overload Off | 0E41
42 | SYSTEM | Multi Level Control (61850) On | 0E42
43 | SYSTEM | Multi Level Control (61850) Off | 0E43
44 | SYSTEM | Latches reset | 0E44
45 | SYSTEM | Slot K Eth. port 1 link OK | 0E45
46 | SYSTEM | Slot K Eth. port 1 link down | 0E46
47 | SYSTEM | Slot K Eth. port 2 link OK | 0E47
48 | SYSTEM | Slot K Eth. port 2 link down | 0E48
49 | SYSTEM | Slot L Eth. port 1 link OK | 0E49
50 | SYSTEM | Slot L Eth. port 1 link down | 0E50
51 | SYSTEM | Slot L Eth. port 2 link OK | 0E51
52 | SYSTEM | Slot L Eth. port 2 link down | 0E52
53 | SYSTEM | Slot M Eth. port 1 link OK | 0E53
54 | SYSTEM | Slot M Eth. port 1 link down | 0E54
55 | SYSTEM | Slot M Eth. port 2 link OK | 0E55
56 | SYSTEM | Slot M Eth. port 2 link down | 0E56
57 | SYSTEM | Slot N Eth. port 1 link OK | 0E57
58 | SYSTEM | Slot N Eth. port 1 link down | 0E58
59 | SYSTEM | Slot N Eth. port 2 link OK | 0E59
60 | SYSTEM | Slot N Eth. port 2 link down | 0E60
64 | DIAGNOSTICS | Diagnostic Alarm On | 1E0
65 | DIAGNOSTICS | Diagnostic Alarm Off | 1E1
66 | DIAGNOSTICS | Configuration changed | 1E2
67 | DIAGNOSTICS | Configuration changed clear | 1E3
68 | DIAGNOSTICS | Network overload detected On | 1E4
69 | DIAGNOSTICS | Network overload detected Off | 1E5
70 | DIAGNOSTICS | Network loop detected On | 1E6
71 | DIAGNOSTICS | Network loop detected Off | 1E7
128 | IRF | Internal Relay Fault Activated | 2E0
129 | IRF | Internal Relay Fault Deactivated | 2E1
192 | GNSIG | Common Start On | 3E0
193 | GNSIG | Common Start Off | 3E1
194 | GNSIG | Common Trip On | 3E2
195 | GNSIG | Common Trip Off | 3E3
384 | PCS | Switch1 On | 6E0
385 | PCS | Switch1 Off | 6E1
386 | PCS | Switch2 On | 6E2
387 | PCS | Switch2 Off | 6E3
388 | PCS | Switch3 On | 6E4
389 | PCS | Switch3 Off | 6E5
390 | PCS | Switch4 On | 6E6
391 | PCS | Switch4 Off | 6E7
392 | PCS | Switch5 On | 6E8
393 | PCS | Switch5 Off | 6E9
448 | CTRL | Ctrl state REMOTE | 7E0
449 | CTRL | Ctrl state LOCAL | 7E1
450 | CTRL | Ctrl Authority REMOTE | 7E2
451 | CTRL | Ctrl Authority STATION | 7E3
512 | LOGIC1 | Logical Out1 On (Logical Output 1) | 8E0
513 | LOGIC1 | Logical Out1 Off (Logical Output 1) | 8E1
514 | LOGIC1 | Logical Out2 On (Logical Output 2) | 8E2
515 | LOGIC1 | Logical Out2 Off (Logical Output 2) | 8E3
516 | LOGIC1 | Logical Out3 On (Logical Output 3) | 8E4
517 | LOGIC1 | Logical Out3 Off (Logical Output 3) | 8E5
518 | LOGIC1 | Logical Out4 On (Logical Output 4) | 8E6
519 | LOGIC1 | Logical Out4 Off (Logical Output 4) | 8E7
520 | LOGIC1 | Logical Out5 On (Logical Output 5) | 8E8
521 | LOGIC1 | Logical Out5 Off (Logical Output 5) | 8E9
522 | LOGIC1 | Logical Out6 On (Logical Output 6) | 8E10
523 | LOGIC1 | Logical Out6 Off (Logical Output 6) | 8E11
524 | LOGIC1 | Logical Out7 On (Logical Output 7) | 8E12
525 | LOGIC1 | Logical Out7 Off (Logical Output 7) | 8E13
526 | LOGIC1 | Logical Out8 On (Logical Output 8) | 8E14
527 | LOGIC1 | Logical Out8 Off (Logical Output 8) | 8E15
528 | LOGIC1 | Logical Out9 On (Logical Output 9) | 8E16
529 | LOGIC1 | Logical Out9 Off (Logical Output 9) | 8E17
530 | LOGIC1 | Logical Out10 On (Logical Output 10) | 8E18
531 | LOGIC1 | Logical Out10 Off (Logical Output 10) | 8E19
532 | LOGIC1 | Logical Out11 On (Logical Output 11) | 8E20
533 | LOGIC1 | Logical Out11 Off (Logical Output 11) | 8E21
534 | LOGIC1 | Logical Out12 On (Logical Output 12) | 8E22
535 | LOGIC1 | Logical Out12 Off (Logical Output 12) | 8E23
536 | LOGIC1 | Logical Out13 On (Logical Output 13) | 8E24
537 | LOGIC1 | Logical Out13 Off (Logical Output 13) | 8E25
538 | LOGIC1 | Logical Out14 On (Logical Output 14) | 8E26
539 | LOGIC1 | Logical Out14 Off (Logical Output 14) | 8E27
540 | LOGIC1 | Logical Out15 On (Logical Output 15) | 8E28
541 | LOGIC1 | Logical Out15 Off (Logical Output 15) | 8E29
542 | LOGIC1 | Logical Out16 On (Logical Output 16) | 8E30
543 | LOGIC1 | Logical Out16 Off (Logical Output 16) | 8E31
544 | LOGIC1 | Logical Out17 On (Logical Output 17) | 8E32
545 | LOGIC1 | Logical Out17 Off (Logical Output 17) | 8E33
546 | LOGIC1 | Logical Out18 On (Logical Output 18) | 8E34
547 | LOGIC1 | Logical Out18 Off (Logical Output 18) | 8E35
548 | LOGIC1 | Logical Out19 On (Logical Output 19) | 8E36
549 | LOGIC1 | Logical Out19 Off (Logical Output 19) | 8E37
550 | LOGIC1 | Logical Out20 On (Logical Output 20) | 8E38
551 | LOGIC1 | Logical Out20 Off (Logical Output 20) | 8E39
552 | LOGIC1 | Logical Out21 On (Logical Output 21) | 8E40
553 | LOGIC1 | Logical Out21 Off (Logical Output 21) | 8E41
554 | LOGIC1 | Logical Out22 On (Logical Output 22) | 8E42
555 | LOGIC1 | Logical Out22 Off (Logical Output 22) | 8E43
556 | LOGIC1 | Logical Out23 On (Logical Output 23) | 8E44
557 | LOGIC1 | Logical Out23 Off (Logical Output 23) | 8E45
558 | LOGIC1 | Logical Out24 On (Logical Output 24) | 8E46
559 | LOGIC1 | Logical Out24 Off (Logical Output 24) | 8E47
560 | LOGIC1 | Logical Out25 On (Logical Output 25) | 8E48
561 | LOGIC1 | Logical Out25 Off (Logical Output 25) | 8E49
562 | LOGIC1 | Logical Out26 On (Logical Output 26) | 8E50
563 | LOGIC1 | Logical Out26 Off (Logical Output 26) | 8E51
564 | LOGIC1 | Logical Out27 On (Logical Output 27) | 8E52
565 | LOGIC1 | Logical Out27 Off (Logical Output 27) | 8E53
566 | LOGIC1 | Logical Out28 On (Logical Output 28) | 8E54
567 | LOGIC1 | Logical Out28 Off (Logical Output 28) | 8E55
568 | LOGIC1 | Logical Out29 On (Logical Output 29) | 8E56
569 | LOGIC1 | Logical Out29 Off (Logical Output 29) | 8E57
570 | LOGIC1 | Logical Out30 On (Logical Output 30) | 8E58
571 | LOGIC1 | Logical Out30 Off (Logical Output 30) | 8E59
572 | LOGIC1 | Logical Out31 On (Logical Output 31) | 8E60
573 | LOGIC1 | Logical Out31 Off (Logical Output 31) | 8E61
574 | LOGIC1 | Logical Out32 On (Logical Output 32) | 8E62
575 | LOGIC1 | Logical Out32 Off (Logical Output 32) | 8E63
576 | LOGIC2 | Logical In1 On (Logical Input 1) | 9E0
577 | LOGIC2 | Logical In1 Off (Logical Input 1) | 9E1
578 | LOGIC2 | Logical In2 On (Logical Input 2) | 9E2
579 | LOGIC2 | Logical In2 Off (Logical Input 2) | 9E3
580 | LOGIC2 | Logical In3 On (Logical Input 3) | 9E4
581 | LOGIC2 | Logical In3 Off (Logical Input 3) | 9E5
582 | LOGIC2 | Logical In4 On (Logical Input 4) | 9E6
583 | LOGIC2 | Logical In4 Off (Logical Input 4) | 9E7
584 | LOGIC2 | Logical In5 On (Logical Input 5) | 9E8
585 | LOGIC2 | Logical In5 Off (Logical Input 5) | 9E9
586 | LOGIC2 | Logical In6 On (Logical Input 6) | 9E10
587 | LOGIC2 | Logical In6 Off (Logical Input 6) | 9E11
588 | LOGIC2 | Logical In7 On (Logical Input 7) | 9E12
589 | LOGIC2 | Logical In7 Off (Logical Input 7) | 9E13
590 | LOGIC2 | Logical In8 On (Logical Input 8) | 9E14
591 | LOGIC2 | Logical In8 Off (Logical Input 8) | 9E15
592 | LOGIC2 | Logical In9 On (Logical Input 9) | 9E16
593 | LOGIC2 | Logical In9 Off (Logical Input 9) | 9E17
594 | LOGIC2 | Logical In10 On (Logical Input 10) | 9E18
595 | LOGIC2 | Logical In10 Off (Logical Input 10) | 9E19
596 | LOGIC2 | Logical In11 On (Logical Input 11) | 9E20
597 | LOGIC2 | Logical In11 Off (Logical Input 11) | 9E21
598 | LOGIC2 | Logical In12 On (Logical Input 12) | 9E22
599 | LOGIC2 | Logical In12 Off (Logical Input 12) | 9E23
600 | LOGIC2 | Logical In13 On (Logical Input 13) | 9E24
601 | LOGIC2 | Logical In13 Off (Logical Input 13) | 9E25
602 | LOGIC2 | Logical In14 On (Logical Input 14) | 9E26
603 | LOGIC2 | Logical In14 Off (Logical Input 14) | 9E27
604 | LOGIC2 | Logical In15 On (Logical Input 15) | 9E28
605 | LOGIC2 | Logical In15 Off (Logical Input 15) | 9E29
606 | LOGIC2 | Logical In16 On (Logical Input 16) | 9E30
607 | LOGIC2 | Logical In16 Off (Logical Input 16) | 9E31
608 | LOGIC2 | Logical In17 On (Logical Input 17) | 9E32
609 | LOGIC2 | Logical In17 Off (Logical Input 17) | 9E33
610 | LOGIC2 | Logical In18 On (Logical Input 18) | 9E34
611 | LOGIC2 | Logical In18 Off (Logical Input 18) | 9E35
612 | LOGIC2 | Logical In19 On (Logical Input 19) | 9E36
613 | LOGIC2 | Logical In19 Off (Logical Input 19) | 9E37
614 | LOGIC2 | Logical In20 On (Logical Input 20) | 9E38
615 | LOGIC2 | Logical In20 Off (Logical Input 20) | 9E39
616 | LOGIC2 | Logical In21 On (Logical Input 21) | 9E40
617 | LOGIC2 | Logical In21 Off (Logical Input 21) | 9E41
618 | LOGIC2 | Logical In22 On (Logical Input 22) | 9E42
619 | LOGIC2 | Logical In22 Off (Logical Input 22) | 9E43
620 | LOGIC2 | Logical In23 On (Logical Input 23) | 9E44
621 | LOGIC2 | Logical In23 Off (Logical Input 23) | 9E45
622 | LOGIC2 | Logical In24 On (Logical Input 24) | 9E46
623 | LOGIC2 | Logical In24 Off (Logical Input 24) | 9E47
624 | LOGIC2 | Logical In25 On (Logical Input 25) | 9E48
625 | LOGIC2 | Logical In25 Off (Logical Input 25) | 9E49
626 | LOGIC2 | Logical In26 On (Logical Input 26) | 9E50
627 | LOGIC2 | Logical In26 Off (Logical Input 26) | 9E51
628 | LOGIC2 | Logical In27 On (Logical Input 27) | 9E52
629 | LOGIC2 | Logical In27 Off (Logical Input 27) | 9E53
630 | LOGIC2 | Logical In28 On (Logical Input 28) | 9E54
631 | LOGIC2 | Logical In28 Off (Logical Input 28) | 9E55
632 | LOGIC2 | Logical In29 On (Logical Input 29) | 9E56
633 | LOGIC2 | Logical In29 Off (Logical Input 29) | 9E57
634 | LOGIC2 | Logical In30 On (Logical Input 30) | 9E58
635 | LOGIC2 | Logical In30 Off (Logical Input 30) | 9E59
636 | LOGIC2 | Logical In31 On (Logical Input 31) | 9E60
637 | LOGIC2 | Logical In31 Off (Logical Input 31) | 9E61
638 | LOGIC2 | Logical In32 On (Logical Input 32) | 9E62
639 | LOGIC2 | Logical In32 Off (Logical Input 32) | 9E63
640 | DIGI | DI 1 On (DI1) | 10E0
641 | DIGI | DI 1 Off (DI1) | 10E1
642 | DIGI | DI 2 On (DI2) | 10E2
643 | DIGI | DI 2 Off (DI2) | 10E3
644 | DIGI | DI 3 On (DI3) | 10E4
645 | DIGI | DI 3 Off (DI3) | 10E5
646 | DIGI | DI 4 On (DI4) | 10E6
647 | DIGI | DI 4 Off (DI4) | 10E7
648 | DIGI | DI 5 On (DI5) | 10E8
649 | DIGI | DI 5 Off (DI5) | 10E9
650 | DIGI | DI 6 On (DI6) | 10E10
651 | DIGI | DI 6 Off (DI6) | 10E11
652 | DIGI | DI 7 On (DI7) | 10E12
653 | DIGI | DI 7 Off (DI7) | 10E13
654 | DIGI | DI 8 On (DI8) | 10E14
655 | DIGI | DI 8 Off (DI8) | 10E15
656 | DIGI | DI 9 On (DI9) | 10E16
657 | DIGI | DI 9 Off (DI9) | 10E17
658 | DIGI | DI 10 On (DI10) | 10E18
659 | DIGI | DI 10 Off (DI10) | 10E19
660 | DIGI | DI 11 On (DI11) | 10E20
661 | DIGI | DI 11 Off (DI11) | 10E21
662 | DIGI | DI 12 On (DI12) | 10E22
663 | DIGI | DI 12 Off (DI12) | 10E23
664 | DIGI | DI 13 On (DI13) | 10E24
665 | DIGI | DI 13 Off (DI13) | 10E25
666 | DIGI | DI 14 On (DI14) | 10E26
667 | DIGI | DI 14 Off (DI14) | 10E27
668 | DIGI | DI 15 On (DI15) | 10E28
669 | DIGI | DI 15 Off (DI15) | 10E29
670 | DIGI | DI 16 On (DI16) | 10E30
671 | DIGI | DI 16 Off (DI16) | 10E31
672 | DIGI | DI 17 On (DI17) | 10E32
673 | DIGI | DI 17 Off (DI17) | 10E33
674 | DIGI | DI 18 On (DI18) | 10E34
675 | DIGI | DI 18 Off (DI18) | 10E35
676 | DIGI | DI 19 On (DI19) | 10E36
677 | DIGI | DI 19 Off (DI19) | 10E37
678 | DIGI | DI 20 On (DI20) | 10E38
679 | DIGI | DI 20 Off (DI20) | 10E39
680 | DIGI | DI 21 On (DI21) | 10E40
681 | DIGI | DI 21 Off (DI21) | 10E41
682 | DIGI | DI 22 On (DI22) | 10E42
683 | DIGI | DI 22 Off (DI22) | 10E43
684 | DIGI | DI 23 On (DI23) | 10E44
685 | DIGI | DI 23 Off (DI23) | 10E45
686 | DIGI | DI 24 On (DI24) | 10E46
687 | DIGI | DI 24 Off (DI24) | 10E47
688 | DIGI | DI 25 On (DI25) | 10E48
689 | DIGI | DI 25 Off (DI25) | 10E49
690 | DIGI | DI 26 On (DI26) | 10E50
691 | DIGI | DI 26 Off (DI26) | 10E51
692 | DIGI | DI 27 On (DI27) | 10E52
693 | DIGI | DI 27 Off (DI27) | 10E53
694 | DIGI | DI 28 On (DI28) | 10E54
695 | DIGI | DI 28 Off (DI28) | 10E55
696 | DIGI | DI 29 On (DI29) | 10E56
697 | DIGI | DI 29 Off (DI29) | 10E57
698 | DIGI | DI 30 On (DI30) | 10E58
699 | DIGI | DI 30 Off (DI30) | 10E59
700 | DIGI | DI 31 On (DI31) | 10E60
701 | DIGI | DI 31 Off (DI31) | 10E61
702 | DIGI | DI 32 On (DI32) | 10E62
703 | DIGI | DI 32 Off (DI32) | 10E63
704 | DIGI2 | DI33 On (DI33) | 11E0
705 | DIGI2 | DI33 Off (DI33) | 11E1
706 | DIGI2 | DI34 On (DI34) | 11E2
707 | DIGI2 | DI34 Off (DI34) | 11E3
708 | DIGI2 | DI35 On (DI35) | 11E4
709 | DIGI2 | DI35 Off (DI35) | 11E5
710 | DIGI2 | DI36 On (DI36) | 11E6
711 | DIGI2 | DI36 Off (DI36) | 11E7
712 | DIGI2 | DI37 On (DI37) | 11E8
713 | DIGI2 | DI37 Off (DI37) | 11E9
714 | DIGI2 | DI38 On (DI38) | 11E10
715 | DIGI2 | DI38 Off (DI38) | 11E11
716 | DIGI2 | DI39 On (DI39) | 11E12
717 | DIGI2 | DI39 Off (DI39) | 11E13
718 | DIGI2 | DI40 On (DI40) | 11E14
719 | DIGI2 | DI40 Off (DI40) | 11E15
720 | DIGI2 | DI41 On (DI41) | 11E16
721 | DIGI2 | DI41 Off (DI41) | 11E17
722 | DIGI2 | DI42 On (DI42) | 11E18
723 | DIGI2 | DI42 Off (DI42) | 11E19
724 | DIGI2 | DI43 On (DI43) | 11E20
725 | DIGI2 | DI43 Off (DI43) | 11E21
726 | DIGI2 | DI44 On (DI44) | 11E22
727 | DIGI2 | DI44 Off (DI44) | 11E23
728 | DIGI2 | DI45 On (DI45) | 11E24
729 | DIGI2 | DI45 Off (DI45) | 11E25
730 | DIGI2 | DI46 On (DI46) | 11E26
731 | DIGI2 | DI46 Off (DI46) | 11E27
732 | DIGI2 | DI47 On (DI47) | 11E28
733 | DIGI2 | DI47 Off (DI47) | 11E29
734 | DIGI2 | DI48 On (DI48) | 11E30
735 | DIGI2 | DI48 Off (DI48) | 11E31
736 | DIGI2 | DI49 On (DI49) | 11E32
737 | DIGI2 | DI49 Off (DI49) | 11E33
738 | DIGI2 | DI50 On (DI50) | 11E34
739 | DIGI2 | DI50 Off (DI50) | 11E35
740 | DIGI2 | DI51 On (DI51) | 11E36
741 | DIGI2 | DI51 Off (DI51) | 11E37
768 | DIGI3 | DI 52 On (DI52) | 12E0
769 | DIGI3 | DI 52 Off (DI52) | 12E1
770 | DIGI3 | DI 53 On (DI53) | 12E2
771 | DIGI3 | DI 53 Off (DI53) | 12E3
772 | DIGI3 | DI 54 On (DI54) | 12E4
773 | DIGI3 | DI 54 Off (DI54) | 12E5
774 | DIGI3 | DI 55 On (DI55) | 12E6
775 | DIGI3 | DI 55 Off (DI55) | 12E7
776 | DIGI3 | DI 56 On (DI56) | 12E8
777 | DIGI3 | DI 56 Off (DI56) | 12E9
778 | DIGI3 | DI 57 On (DI57) | 12E10
779 | DIGI3 | DI 57 Off (DI57) | 12E11
780 | DIGI3 | DI 58 On (DI58) | 12E12
781 | DIGI3 | DI 58 Off (DI58) | 12E13
782 | DIGI3 | DI 59 On (DI59) | 12E14
783 | DIGI3 | DI 59 Off (DI59) | 12E15
784 | DIGI3 | DI 60 On (DI60) | 12E16
785 | DIGI3 | DI 60 Off (DI60) | 12E17
786 | DIGI3 | DI 61 On (DI61) | 12E18
787 | DIGI3 | DI 61 Off (DI61) | 12E19
788 | DIGI3 | DI 62 On (DI62) | 12E20
789 | DIGI3 | DI 62 Off (DI62) | 12E21
790 | DIGI3 | DI 63 On (DI63) | 12E22
791 | DIGI3 | DI 63 Off (DI63) | 12E23
792 | DIGI3 | DI 64 On (DI64) | 12E24
793 | DIGI3 | DI 64 Off (DI64) | 12E25
794 | DIGI3 | DI 65 On (DI65) | 12E26
795 | DIGI3 | DI 65 Off (DI65) | 12E27
796 | DIGI3 | DI 66 On (DI66) | 12E28
797 | DIGI3 | DI 66 Off (DI66) | 12E29
798 | DIGI3 | DI 67 On (DI67) | 12E30
799 | DIGI3 | DI 67 Off (DI67) | 12E31
800 | DIGI3 | DI 68 On (DI68) | 12E32
801 | DIGI3 | DI 68 Off (DI68) | 12E33
802 | DIGI3 | DI 69 On (DI69) | 12E34
803 | DIGI3 | DI 69 Off (DI69) | 12E35
804 | DIGI3 | DI 70 On (DI70) | 12E36
805 | DIGI3 | DI 70 Off (DI70) | 12E37
806 | DIGI3 | DI 71 On (DI71) | 12E38
807 | DIGI3 | DI 71 Off (DI71) | 12E39
808 | DIGI3 | DI 72 On (DI72) | 12E40
809 | DIGI3 | DI 72 Off (DI72) | 12E41
810 | DIGI3 | DI 73 On (DI73) | 12E42
811 | DIGI3 | DI 73 Off (DI73) | 12E43
812 | DIGI3 | DI 74 On (DI74) | 12E44
813 | DIGI3 | DI 74 Off (DI74) | 12E45
814 | DIGI3 | DI 75 On (DI75) | 12E46
815 | DIGI3 | DI 75 Off (DI75) | 12E47
816 | DIGI3 | DI 76 On (DI76) | 12E48
817 | DIGI3 | DI 76 Off (DI76) | 12E49
818 | DIGI3 | DI 77 On (DI77) | 12E50
819 | DIGI3 | DI 77 Off (DI77) | 12E51
820 | DIGI3 | DI 78 On (DI78) | 12E52
821 | DIGI3 | DI 78 Off (DI78) | 12E53
822 | DIGI3 | DI 79 On (DI79) | 12E54
823 | DIGI3 | DI 79 Off (DI79) | 12E55
824 | DIGI3 | DI 80 On (DI80) | 12E56
825 | DIGI3 | DI 80 Off (DI80) | 12E57
826 | DIGI3 | DI 81 On (DI81) | 12E58
827 | DIGI3 | DI 81 Off (DI81) | 12E59
828 | DIGI3 | DI 82 On (DI82) | 12E60
829 | DIGI3 | DI 82 Off (DI82) | 12E61
830 | DIGI3 | DI 83 On (DI83) | 12E62
831 | DIGI3 | DI 83 Off (DI83) | 12E63
832 | DIGI4 | DI 84 On (DI84) | 13E0
833 | DIGI4 | DI 84 Off (DI84) | 13E1
834 | DIGI4 | DI 85 On (DI85) | 13E2
835 | DIGI4 | DI 85 Off (DI85) | 13E3
836 | DIGI4 | DI 86 On (DI86) | 13E4
837 | DIGI4 | DI 86 Off (DI86) | 13E5
838 | DIGI4 | DI 87 On (DI87) | 13E6
839 | DIGI4 | DI 87 Off (DI87) | 13E7
840 | DIGI4 | DI 88 On (DI88) | 13E8
841 | DIGI4 | DI 88 Off (DI88) | 13E9
842 | DIGI4 | DI 89 On (DI89) | 13E10
843 | DIGI4 | DI 89 Off (DI89) | 13E11
844 | DIGI4 | DI 90 On (DI90) | 13E12
845 | DIGI4 | DI 90 Off (DI90) | 13E13
846 | DIGI4 | DI 91 On (DI91) | 13E14
847 | DIGI4 | DI 91 Off (DI91) | 13E15
848 | DIGI4 | DI 92 On (DI92) | 13E16
849 | DIGI4 | DI 92 Off (DI92) | 13E17
850 | DIGI4 | DI 93 On (DI93) | 13E18
851 | DIGI4 | DI 93 Off (DI93) | 13E19
852 | DIGI4 | DI 94 On (DI94) | 13E20
853 | DIGI4 | DI 94 Off (DI94) | 13E21
854 | DIGI4 | DI 95 On (DI95) | 13E22
855 | DIGI4 | DI 95 Off (DI95) | 13E23
856 | DIGI4 | DI 96 On (DI96) | 13E24
857 | DIGI4 | DI 96 Off (DI96) | 13E25
858 | DIGI4 | DI 97 On (DI97) | 13E26
859 | DIGI4 | DI 97 Off (DI97) | 13E27
860 | DIGI4 | DI 98 On (DI98) | 13E28
861 | DIGI4 | DI 98 Off (DI98) | 13E29
862 | DIGI4 | DI 99 On (DI99) | 13E30
863 | DIGI4 | DI 99 Off (DI99) | 13E31
864 | DIGI4 | DI100 On (DI100) | 13E32
865 | DIGI4 | DI100 Off (DI100) | 13E33
866 | DIGI4 | DI101 On (DI101) | 13E34
867 | DIGI4 | DI101 Off (DI101) | 13E35
868 | DIGI4 | DI102 On (DI102) | 13E36
869 | DIGI4 | DI102 Off (DI102) | 13E37
870 | DIGI4 | DI103 On (DI103) | 13E38
871 | DIGI4 | DI103 Off (DI103) | 13E39
872 | DIGI4 | DI104 On (DI104) | 13E40
873 | DIGI4 | DI104 Off (DI104) | 13E41
874 | DIGI4 | DI105 On (DI105) | 13E42
875 | DIGI4 | DI105 Off (DI105) | 13E43
876 | DIGI4 | DI106 On (DI106) | 13E44
877 | DIGI4 | DI106 Off (DI106) | 13E45
878 | DIGI4 | DI107 On (DI107) | 13E46
879 | DIGI4 | DI107 Off (DI107) | 13E47
880 | DIGI4 | DI108 On (DI108) | 13E48
881 | DIGI4 | DI108 Off (DI108) | 13E49
882 | DIGI4 | DI109 On (DI109) | 13E50
883 | DIGI4 | DI109 Off (DI109) | 13E51
884 | DIGI4 | DI110 On (DI110) | 13E52
885 | DIGI4 | DI110 Off (DI110) | 13E53
886 | DIGI4 | DI111 On (DI111) | 13E54
887 | DIGI4 | DI111 Off (DI111) | 13E55
888 | DIGI4 | DI112 On (DI112) | 13E56
889 | DIGI4 | DI112 Off (DI112) | 13E57
890 | DIGI4 | DI113 On (DI113) | 13E58
891 | DIGI4 | DI113 Off (DI113) | 13E59
892 | DIGI4 | DI114 On (DI114) | 13E60
893 | DIGI4 | DI114 Off (DI114) | 13E61
894 | DIGI4 | DI115 On (DI115) | 13E62
895 | DIGI4 | DI115 Off (DI115) | 13E63
896 | LOGIC3 | Logical Out33 On (Logical Output 33) | 14E0
897 | LOGIC3 | Logical Out33 Off (Logical Output 33) | 14E1
898 | LOGIC3 | Logical Out34 On (Logical Output 34) | 14E2
899 | LOGIC3 | Logical Out34 Off (Logical Output 34) | 14E3
900 | LOGIC3 | Logical Out35 On (Logical Output 35) | 14E4
901 | LOGIC3 | Logical Out35 Off (Logical Output 35) | 14E5
902 | LOGIC3 | Logical Out36 On (Logical Output 36) | 14E6
903 | LOGIC3 | Logical Out36 Off (Logical Output 36) | 14E7
904 | LOGIC3 | Logical Out37 On (Logical Output 37) | 14E8
905 | LOGIC3 | Logical Out37 Off (Logical Output 37) | 14E9
906 | LOGIC3 | Logical Out38 On (Logical Output 38) | 14E10
907 | LOGIC3 | Logical Out38 Off (Logical Output 38) | 14E11
908 | LOGIC3 | Logical Out39 On (Logical Output 39) | 14E12
909 | LOGIC3 | Logical Out39 Off (Logical Output 39) | 14E13
910 | LOGIC3 | Logical Out40 On (Logical Output 40) | 14E14
911 | LOGIC3 | Logical Out40 Off (Logical Output 40) | 14E15
912 | LOGIC3 | Logical Out41 On (Logical Output 41) | 14E16
913 | LOGIC3 | Logical Out41 Off (Logical Output 41) | 14E17
914 | LOGIC3 | Logical Out42 On (Logical Output 42) | 14E18
915 | LOGIC3 | Logical Out42 Off (Logical Output 42) | 14E19
916 | LOGIC3 | Logical Out43 On (Logical Output 43) | 14E20
917 | LOGIC3 | Logical Out43 Off (Logical Output 43) | 14E21
918 | LOGIC3 | Logical Out44 On (Logical Output 44) | 14E22
919 | LOGIC3 | Logical Out44 Off (Logical Output 44) | 14E23
920 | LOGIC3 | Logical Out45 On (Logical Output 45) | 14E24
921 | LOGIC3 | Logical Out45 Off (Logical Output 45) | 14E25
922 | LOGIC3 | Logical Out46 On (Logical Output 46) | 14E26
923 | LOGIC3 | Logical Out46 Off (Logical Output 46) | 14E27
924 | LOGIC3 | Logical Out47 On (Logical Output 47) | 14E28
925 | LOGIC3 | Logical Out47 Off (Logical Output 47) | 14E29
926 | LOGIC3 | Logical Out48 On (Logical Output 48) | 14E30
927 | LOGIC3 | Logical Out48 Off (Logical Output 48) | 14E31
928 | LOGIC3 | Logical Out49 On (Logical Output 49) | 14E32
929 | LOGIC3 | Logical Out49 Off (Logical Output 49) | 14E33
930 | LOGIC3 | Logical Out50 On (Logical Output 50) | 14E34
931 | LOGIC3 | Logical Out50 Off (Logical Output 50) | 14E35
932 | LOGIC3 | Logical Out51 On (Logical Output 51) | 14E36
933 | LOGIC3 | Logical Out51 Off (Logical Output 51) | 14E37
934 | LOGIC3 | Logical Out52 On (Logical Output 52) | 14E38
935 | LOGIC3 | Logical Out52 Off (Logical Output 52) | 14E39
936 | LOGIC3 | Logical Out53 On (Logical Output 53) | 14E40
937 | LOGIC3 | Logical Out53 Off (Logical Output 53) | 14E41
938 | LOGIC3 | Logical Out54 On (Logical Output 54) | 14E42
939 | LOGIC3 | Logical Out54 Off (Logical Output 54) | 14E43
940 | LOGIC3 | Logical Out55 On (Logical Output 55) | 14E44
941 | LOGIC3 | Logical Out55 Off (Logical Output 55) | 14E45
942 | LOGIC3 | Logical Out56 On (Logical Output 56) | 14E46
943 | LOGIC3 | Logical Out56 Off (Logical Output 56) | 14E47
944 | LOGIC3 | Logical Out57 On (Logical Output 57) | 14E48
945 | LOGIC3 | Logical Out57 Off (Logical Output 57) | 14E49
946 | LOGIC3 | Logical Out58 On (Logical Output 58) | 14E50
947 | LOGIC3 | Logical Out58 Off (Logical Output 58) | 14E51
948 | LOGIC3 | Logical Out59 On (Logical Output 59) | 14E52
949 | LOGIC3 | Logical Out59 Off (Logical Output 59) | 14E53
950 | LOGIC3 | Logical Out60 On (Logical Output 60) | 14E54
951 | LOGIC3 | Logical Out60 Off (Logical Output 60) | 14E55
952 | LOGIC3 | Logical Out61 On (Logical Output 61) | 14E56
953 | LOGIC3 | Logical Out61 Off (Logical Output 61) | 14E57
954 | LOGIC3 | Logical Out62 On (Logical Output 62) | 14E58
955 | LOGIC3 | Logical Out62 Off (Logical Output 62) | 14E59
956 | LOGIC3 | Logical Out63 On (Logical Output 63) | 14E60
957 | LOGIC3 | Logical Out63 Off (Logical Output 63) | 14E61
958 | LOGIC3 | Logical Out64 On (Logical Output 64) | 14E62
959 | LOGIC3 | Logical Out64 Off (Logical Output 64) | 14E63
1024 | GOOSE1 | GOOSE IN1 On (GOOSE IN 1) | 16E0
1025 | GOOSE1 | GOOSE IN1 Off (GOOSE IN 1) | 16E1
1026 | GOOSE1 | GOOSE IN2 On (GOOSE IN 2) | 16E2
1027 | GOOSE1 | GOOSE IN2 Off (GOOSE IN 2) | 16E3
1028 | GOOSE1 | GOOSE IN3 On (GOOSE IN 3) | 16E4
1029 | GOOSE1 | GOOSE IN3 Off (GOOSE IN 3) | 16E5
1030 | GOOSE1 | GOOSE IN4 On (GOOSE IN 4) | 16E6
1031 | GOOSE1 | GOOSE IN4 Off (GOOSE IN 4) | 16E7
1032 | GOOSE1 | GOOSE IN5 On (GOOSE IN 5) | 16E8
1033 | GOOSE1 | GOOSE IN5 Off (GOOSE IN 5) | 16E9
1034 | GOOSE1 | GOOSE IN6 On (GOOSE IN 6) | 16E10
1035 | GOOSE1 | GOOSE IN6 Off (GOOSE IN 6) | 16E11
1036 | GOOSE1 | GOOSE IN7 On (GOOSE IN 7) | 16E12
1037 | GOOSE1 | GOOSE IN7 Off (GOOSE IN 7) | 16E13
1038 | GOOSE1 | GOOSE IN8 On (GOOSE IN 8) | 16E14
1039 | GOOSE1 | GOOSE IN8 Off (GOOSE IN 8) | 16E15
1040 | GOOSE1 | GOOSE IN9 On (GOOSE IN 9) | 16E16
1041 | GOOSE1 | GOOSE IN9 Off (GOOSE IN 9) | 16E17
1042 | GOOSE1 | GOOSE IN10 On (GOOSE IN 10) | 16E18
1043 | GOOSE1 | GOOSE IN10 Off (GOOSE IN 10) | 16E19
1044 | GOOSE1 | GOOSE IN11 On (GOOSE IN 11) | 16E20
1045 | GOOSE1 | GOOSE IN11 Off (GOOSE IN 11) | 16E21
1046 | GOOSE1 | GOOSE IN12 On (GOOSE IN 12) | 16E22
1047 | GOOSE1 | GOOSE IN12 Off (GOOSE IN 12) | 16E23
1048 | GOOSE1 | GOOSE IN13 On (GOOSE IN 13) | 16E24
1049 | GOOSE1 | GOOSE IN13 Off (GOOSE IN 13) | 16E25
1050 | GOOSE1 | GOOSE IN14 On (GOOSE IN 14) | 16E26
1051 | GOOSE1 | GOOSE IN14 Off (GOOSE IN 14) | 16E27
1052 | GOOSE1 | GOOSE IN15 On (GOOSE IN 15) | 16E28
1053 | GOOSE1 | GOOSE IN15 Off (GOOSE IN 15) | 16E29
1054 | GOOSE1 | GOOSE IN16 On (GOOSE IN 16) | 16E30
1055 | GOOSE1 | GOOSE IN16 Off (GOOSE IN 16) | 16E31
1056 | GOOSE1 | GOOSE IN17 On (GOOSE IN 17) | 16E32
1057 | GOOSE1 | GOOSE IN17 Off (GOOSE IN 17) | 16E33
1058 | GOOSE1 | GOOSE IN18 On (GOOSE IN 18) | 16E34
1059 | GOOSE1 | GOOSE IN18 Off (GOOSE IN 18) | 16E35
1060 | GOOSE1 | GOOSE IN19 On (GOOSE IN 19) | 16E36
1061 | GOOSE1 | GOOSE IN19 Off (GOOSE IN 19) | 16E37
1062 | GOOSE1 | GOOSE IN20 On (GOOSE IN 20) | 16E38
1063 | GOOSE1 | GOOSE IN20 Off (GOOSE IN 20) | 16E39
1064 | GOOSE1 | GOOSE IN21 On (GOOSE IN 21) | 16E40
1065 | GOOSE1 | GOOSE IN21 Off (GOOSE IN 21) | 16E41
1066 | GOOSE1 | GOOSE IN22 On (GOOSE IN 22) | 16E42
1067 | GOOSE1 | GOOSE IN22 Off (GOOSE IN 22) | 16E43
1068 | GOOSE1 | GOOSE IN23 On (GOOSE IN 23) | 16E44
1069 | GOOSE1 | GOOSE IN23 Off (GOOSE IN 23) | 16E45
1070 | GOOSE1 | GOOSE IN24 On (GOOSE IN 24) | 16E46
1071 | GOOSE1 | GOOSE IN24 Off (GOOSE IN 24) | 16E47
1072 | GOOSE1 | GOOSE IN25 On (GOOSE IN 25) | 16E48
1073 | GOOSE1 | GOOSE IN25 Off (GOOSE IN 25) | 16E49
1074 | GOOSE1 | GOOSE IN26 On (GOOSE IN 26) | 16E50
1075 | GOOSE1 | GOOSE IN26 Off (GOOSE IN 26) | 16E51
1076 | GOOSE1 | GOOSE IN27 On (GOOSE IN 27) | 16E52
1077 | GOOSE1 | GOOSE IN27 Off (GOOSE IN 27) | 16E53
1078 | GOOSE1 | GOOSE IN28 On (GOOSE IN 28) | 16E54
1079 | GOOSE1 | GOOSE IN28 Off (GOOSE IN 28) | 16E55
1080 | GOOSE1 | GOOSE IN29 On (GOOSE IN 29) | 16E56
1081 | GOOSE1 | GOOSE IN29 Off (GOOSE IN 29) | 16E57
1082 | GOOSE1 | GOOSE IN30 On (GOOSE IN 30) | 16E58
1083 | GOOSE1 | GOOSE IN30 Off (GOOSE IN 30) | 16E59
1084 | GOOSE1 | GOOSE IN31 On (GOOSE IN 31) | 16E60
1085 | GOOSE1 | GOOSE IN31 Off (GOOSE IN 31) | 16E61
1086 | GOOSE1 | GOOSE IN32 On (GOOSE IN 32) | 16E62
1087 | GOOSE1 | GOOSE IN32 Off (GOOSE IN 32) | 16E63
1088 | GOOSE2 | GOOSE IN33 On (GOOSE IN 33) | 17E0
1089 | GOOSE2 | GOOSE IN33 Off (GOOSE IN 33) | 17E1
1090 | GOOSE2 | GOOSE IN34 On (GOOSE IN 34) | 17E2
1091 | GOOSE2 | GOOSE IN34 Off (GOOSE IN 34) | 17E3
1092 | GOOSE2 | GOOSE IN35 On (GOOSE IN 35) | 17E4
1093 | GOOSE2 | GOOSE IN35 Off (GOOSE IN 35) | 17E5
1094 | GOOSE2 | GOOSE IN36 On (GOOSE IN 36) | 17E6
1095 | GOOSE2 | GOOSE IN36 Off (GOOSE IN 36) | 17E7
1096 | GOOSE2 | GOOSE IN37 On (GOOSE IN 37) | 17E8
1097 | GOOSE2 | GOOSE IN37 Off (GOOSE IN 37) | 17E9
1098 | GOOSE2 | GOOSE IN38 On (GOOSE IN 38) | 17E10
1099 | GOOSE2 | GOOSE IN38 Off (GOOSE IN 38) | 17E11
1100 | GOOSE2 | GOOSE IN39 On (GOOSE IN 39) | 17E12
1101 | GOOSE2 | GOOSE IN39 Off (GOOSE IN 39) | 17E13
1102 | GOOSE2 | GOOSE IN40 On (GOOSE IN 40) | 17E14
1103 | GOOSE2 | GOOSE IN40 Off (GOOSE IN 40) | 17E15
1104 | GOOSE2 | GOOSE IN41 On (GOOSE IN 41) | 17E16
1105 | GOOSE2 | GOOSE IN41 Off (GOOSE IN 41) | 17E17
1106 | GOOSE2 | GOOSE IN42 On (GOOSE IN 42) | 17E18
1107 | GOOSE2 | GOOSE IN42 Off (GOOSE IN 42) | 17E19
1108 | GOOSE2 | GOOSE IN43 On (GOOSE IN 43) | 17E20
1109 | GOOSE2 | GOOSE IN43 Off (GOOSE IN 43) | 17E21
1110 | GOOSE2 | GOOSE IN44 On (GOOSE IN 44) | 17E22
1111 | GOOSE2 | GOOSE IN44 Off (GOOSE IN 44) | 17E23
1112 | GOOSE2 | GOOSE IN45 On (GOOSE IN 45) | 17E24
1113 | GOOSE2 | GOOSE IN45 Off (GOOSE IN 45) | 17E25
1114 | GOOSE2 | GOOSE IN46 On (GOOSE IN 46) | 17E26
1115 | GOOSE2 | GOOSE IN46 Off (GOOSE IN 46) | 17E27
1116 | GOOSE2 | GOOSE IN47 On (GOOSE IN 47) | 17E28
1117 | GOOSE2 | GOOSE IN47 Off (GOOSE IN 47) | 17E29
1118 | GOOSE2 | GOOSE IN48 On (GOOSE IN 48) | 17E30
1119 | GOOSE2 | GOOSE IN48 Off (GOOSE IN 48) | 17E31
1120 | GOOSE2 | GOOSE IN49 On (GOOSE IN 49) | 17E32
1121 | GOOSE2 | GOOSE IN49 Off (GOOSE IN 49) | 17E33
1122 | GOOSE2 | GOOSE IN50 On (GOOSE IN 50) | 17E34
1123 | GOOSE2 | GOOSE IN50 Off (GOOSE IN 50) | 17E35
1124 | GOOSE2 | GOOSE IN51 On (GOOSE IN 51) | 17E36
1125 | GOOSE2 | GOOSE IN51 Off (GOOSE IN 51) | 17E37
1126 | GOOSE2 | GOOSE IN52 On (GOOSE IN 52) | 17E38
1127 | GOOSE2 | GOOSE IN52 Off (GOOSE IN 52) | 17E39
1128 | GOOSE2 | GOOSE IN53 On (GOOSE IN 53) | 17E40
1129 | GOOSE2 | GOOSE IN53 Off (GOOSE IN 53) | 17E41
1130 | GOOSE2 | GOOSE IN54 On (GOOSE IN 54) | 17E42
1131 | GOOSE2 | GOOSE IN54 Off (GOOSE IN 54) | 17E43
1132 | GOOSE2 | GOOSE IN55 On (GOOSE IN 55) | 17E44
1133 | GOOSE2 | GOOSE IN55 Off (GOOSE IN 55) | 17E45
1134 | GOOSE2 | GOOSE IN56 On (GOOSE IN 56) | 17E46
1135 | GOOSE2 | GOOSE IN56 Off (GOOSE IN 56) | 17E47
1136 | GOOSE2 | GOOSE IN57 On (GOOSE IN 57) | 17E48
1137 | GOOSE2 | GOOSE IN57 Off (GOOSE IN 57) | 17E49
1138 | GOOSE2 | GOOSE IN58 On (GOOSE IN 58) | 17E50
1139 | GOOSE2 | GOOSE IN58 Off (GOOSE IN 58) | 17E51
1140 | GOOSE2 | GOOSE IN59 On (GOOSE IN 59) | 17E52
1141 | GOOSE2 | GOOSE IN59 Off (GOOSE IN 59) | 17E53
1142 | GOOSE2 | GOOSE IN60 On (GOOSE IN 60) | 17E54
1143 | GOOSE2 | GOOSE IN60 Off (GOOSE IN 60) | 17E55
1144 | GOOSE2 | GOOSE IN61 On (GOOSE IN 61) | 17E56
1145 | GOOSE2 | GOOSE IN61 Off (GOOSE IN 61) | 17E57
1146 | GOOSE2 | GOOSE IN62 On (GOOSE IN 62) | 17E58
1147 | GOOSE2 | GOOSE IN62 Off (GOOSE IN 62) | 17E59
1148 | GOOSE2 | GOOSE IN63 On (GOOSE IN 63) | 17E60
1149 | GOOSE2 | GOOSE IN63 Off (GOOSE IN 63) | 17E61
1150 | GOOSE2 | GOOSE IN64 On (GOOSE IN 64) | 17E62
1151 | GOOSE2 | GOOSE IN64 Off (GOOSE IN 64) | 17E63
1152 | GOOSE3 | GOOSE IN1 Quality Good (GOOSE IN 1) | 18E0
1153 | GOOSE3 | GOOSE IN1 Quality Bad (GOOSE IN 1) | 18E1
1154 | GOOSE3 | GOOSE IN2 Quality Good (GOOSE IN 2) | 18E2
1155 | GOOSE3 | GOOSE IN2 Quality Bad (GOOSE IN 2) | 18E3
1156 | GOOSE3 | GOOSE IN3 Quality Good (GOOSE IN 3) | 18E4
1157 | GOOSE3 | GOOSE IN3 Quality Bad (GOOSE IN 3) | 18E5
1158 | GOOSE3 | GOOSE IN4 Quality Good (GOOSE IN 4) | 18E6
1159 | GOOSE3 | GOOSE IN4 Quality Bad (GOOSE IN 4) | 18E7
1160 | GOOSE3 | GOOSE IN5 Quality Good (GOOSE IN 5) | 18E8
1161 | GOOSE3 | GOOSE IN5 Quality Bad (GOOSE IN 5) | 18E9
1162 | GOOSE3 | GOOSE IN6 Quality Good (GOOSE IN 6) | 18E10
1163 | GOOSE3 | GOOSE IN6 Quality Bad (GOOSE IN 6) | 18E11
1164 | GOOSE3 | GOOSE IN7 Quality Good (GOOSE IN 7) | 18E12
1165 | GOOSE3 | GOOSE IN7 Quality Bad (GOOSE IN 7) | 18E13
1166 | GOOSE3 | GOOSE IN8 Quality Good (GOOSE IN 8) | 18E14
1167 | GOOSE3 | GOOSE IN8 Quality Bad (GOOSE IN 8) | 18E15
1168 | GOOSE3 | GOOSE IN9 Quality Good (GOOSE IN 9) | 18E16
1169 | GOOSE3 | GOOSE IN9 Quality Bad (GOOSE IN 9) | 18E17
1170 | GOOSE3 | GOOSE IN10 Quality Good (GOOSE IN 10) | 18E18
1171 | GOOSE3 | GOOSE IN10 Quality Bad (GOOSE IN 10) | 18E19
1172 | GOOSE3 | GOOSE IN11 Quality Good (GOOSE IN 11) | 18E20
1173 | GOOSE3 | GOOSE IN11 Quality Bad (GOOSE IN 11) | 18E21
1174 | GOOSE3 | GOOSE IN12 Quality Good (GOOSE IN 12) | 18E22
1175 | GOOSE3 | GOOSE IN12 Quality Bad (GOOSE IN 12) | 18E23
1176 | GOOSE3 | GOOSE IN13 Quality Good (GOOSE IN 13) | 18E24
1177 | GOOSE3 | GOOSE IN13 Quality Bad (GOOSE IN 13) | 18E25
1178 | GOOSE3 | GOOSE IN14 Quality Good (GOOSE IN 14) | 18E26
1179 | GOOSE3 | GOOSE IN14 Quality Bad (GOOSE IN 14) | 18E27
1180 | GOOSE3 | GOOSE IN15 Quality Good (GOOSE IN 15) | 18E28
1181 | GOOSE3 | GOOSE IN15 Quality Bad (GOOSE IN 15) | 18E29
1182 | GOOSE3 | GOOSE IN16 Quality Good (GOOSE IN 16) | 18E30
1183 | GOOSE3 | GOOSE IN16 Quality Bad (GOOSE IN 16) | 18E31
1184 | GOOSE3 | GOOSE IN17 Quality Good (GOOSE IN 17) | 18E32
1185 | GOOSE3 | GOOSE IN17 Quality Bad (GOOSE IN 17) | 18E33
1186 | GOOSE3 | GOOSE IN18 Quality Good (GOOSE IN 18) | 18E34
1187 | GOOSE3 | GOOSE IN18 Quality Bad (GOOSE IN 18) | 18E35
1188 | GOOSE3 | GOOSE IN19 Quality Good (GOOSE IN 19) | 18E36
1189 | GOOSE3 | GOOSE IN19 Quality Bad (GOOSE IN 19) | 18E37
1190 | GOOSE3 | GOOSE IN20 Quality Good (GOOSE IN 20) | 18E38
1191 | GOOSE3 | GOOSE IN20 Quality Bad (GOOSE IN 20) | 18E39
1192 | GOOSE3 | GOOSE IN21 Quality Good (GOOSE IN 21) | 18E40
1193 | GOOSE3 | GOOSE IN21 Quality Bad (GOOSE IN 21) | 18E41
1194 | GOOSE3 | GOOSE IN22 Quality Good (GOOSE IN 22) | 18E42
1195 | GOOSE3 | GOOSE IN22 Quality Bad (GOOSE IN 22) | 18E43
1196 | GOOSE3 | GOOSE IN23 Quality Good (GOOSE IN 23) | 18E44
1197 | GOOSE3 | GOOSE IN23 Quality Bad (GOOSE IN 23) | 18E45
1198 | GOOSE3 | GOOSE IN24 Quality Good (GOOSE IN 24) | 18E46
1199 | GOOSE3 | GOOSE IN24 Quality Bad (GOOSE IN 24) | 18E47
1200 | GOOSE3 | GOOSE IN25 Quality Good (GOOSE IN 25) | 18E48
1201 | GOOSE3 | GOOSE IN25 Quality Bad (GOOSE IN 25) | 18E49
1202 | GOOSE3 | GOOSE IN26 Quality Good (GOOSE IN 26) | 18E50
1203 | GOOSE3 | GOOSE IN26 Quality Bad (GOOSE IN 26) | 18E51
1204 | GOOSE3 | GOOSE IN27 Quality Good (GOOSE IN 27) | 18E52
1205 | GOOSE3 | GOOSE IN27 Quality Bad (GOOSE IN 27) | 18E53
1206 | GOOSE3 | GOOSE IN28 Quality Good (GOOSE IN 28) | 18E54
1207 | GOOSE3 | GOOSE IN28 Quality Bad (GOOSE IN 28) | 18E55
1208 | GOOSE3 | GOOSE IN29 Quality Good (GOOSE IN 29) | 18E56
1209 | GOOSE3 | GOOSE IN29 Quality Bad (GOOSE IN 29) | 18E57
1210 | GOOSE3 | GOOSE IN30 Quality Good (GOOSE IN 30) | 18E58
1211 | GOOSE3 | GOOSE IN30 Quality Bad (GOOSE IN 30) | 18E59
1212 | GOOSE3 | GOOSE IN31 Quality Good (GOOSE IN 31) | 18E60
1213 | GOOSE3 | GOOSE IN31 Quality Bad (GOOSE IN 31) | 18E61
1214 | GOOSE3 | GOOSE IN32 Quality Good (GOOSE IN 32) | 18E62
1215 | GOOSE3 | GOOSE IN32 Quality Bad (GOOSE IN 32) | 18E63
1216 | GOOSE4 | GOOSE IN33 Quality Good (GOOSE IN 33) | 19E0
1217 | GOOSE4 | GOOSE IN33 Quality Bad (GOOSE IN 33) | 19E1
1218 | GOOSE4 | GOOSE IN34 Quality Good (GOOSE IN 34) | 19E2
1219 | GOOSE4 | GOOSE IN34 Quality Bad (GOOSE IN 34) | 19E3
1220 | GOOSE4 | GOOSE IN35 Quality Good (GOOSE IN 35) | 19E4
1221 | GOOSE4 | GOOSE IN35 Quality Bad (GOOSE IN 35) | 19E5
1222 | GOOSE4 | GOOSE IN36 Quality Good (GOOSE IN 36) | 19E6
1223 | GOOSE4 | GOOSE IN36 Quality Bad (GOOSE IN 36) | 19E7
1224 | GOOSE4 | GOOSE IN37 Quality Good (GOOSE IN 37) | 19E8
1225 | GOOSE4 | GOOSE IN37 Quality Bad (GOOSE IN 37) | 19E9
1226 | GOOSE4 | GOOSE IN38 Quality Good (GOOSE IN 38) | 19E10
1227 | GOOSE4 | GOOSE IN38 Quality Bad (GOOSE IN 38) | 19E11
1228 | GOOSE4 | GOOSE IN39 Quality Good (GOOSE IN 39) | 19E12
1229 | GOOSE4 | GOOSE IN39 Quality Bad (GOOSE IN 39) | 19E13
1230 | GOOSE4 | GOOSE IN40 Quality Good (GOOSE IN 40) | 19E14
1231 | GOOSE4 | GOOSE IN40 Quality Bad (GOOSE IN 40) | 19E15
1232 | GOOSE4 | GOOSE IN41 Quality Good (GOOSE IN 41) | 19E16
1233 | GOOSE4 | GOOSE IN41 Quality Bad (GOOSE IN 41) | 19E17
1234 | GOOSE4 | GOOSE IN42 Quality Good (GOOSE IN 42) | 19E18
1235 | GOOSE4 | GOOSE IN42 Quality Bad (GOOSE IN 42) | 19E19
1236 | GOOSE4 | GOOSE IN43 Quality Good (GOOSE IN 43) | 19E20
1237 | GOOSE4 | GOOSE IN43 Quality Bad (GOOSE IN 43) | 19E21
1238 | GOOSE4 | GOOSE IN44 Quality Good (GOOSE IN 44) | 19E22
1239 | GOOSE4 | GOOSE IN44 Quality Bad (GOOSE IN 44) | 19E23
1240 | GOOSE4 | GOOSE IN45 Quality Good (GOOSE IN 45) | 19E24
1241 | GOOSE4 | GOOSE IN45 Quality Bad (GOOSE IN 45) | 19E25
1242 | GOOSE4 | GOOSE IN46 Quality Good (GOOSE IN 46) | 19E26
1243 | GOOSE4 | GOOSE IN46 Quality Bad (GOOSE IN 46) | 19E27
1244 | GOOSE4 | GOOSE IN47 Quality Good (GOOSE IN 47) | 19E28
1245 | GOOSE4 | GOOSE IN47 Quality Bad (GOOSE IN 47) | 19E29
1246 | GOOSE4 | GOOSE IN48 Quality Good (GOOSE IN 48) | 19E30
1247 | GOOSE4 | GOOSE IN48 Quality Bad (GOOSE IN 48) | 19E31
1248 | GOOSE4 | GOOSE IN49 Quality Good (GOOSE IN 49) | 19E32
1249 | GOOSE4 | GOOSE IN49 Quality Bad (GOOSE IN 49) | 19E33
1250 | GOOSE4 | GOOSE IN50 Quality Good (GOOSE IN 50) | 19E34
1251 | GOOSE4 | GOOSE IN50 Quality Bad (GOOSE IN 50) | 19E35
1252 | GOOSE4 | GOOSE IN51 Quality Good (GOOSE IN 51) | 19E36
1253 | GOOSE4 | GOOSE IN51 Quality Bad (GOOSE IN 51) | 19E37
1254 | GOOSE4 | GOOSE IN52 Quality Good (GOOSE IN 52) | 19E38
1255 | GOOSE4 | GOOSE IN52 Quality Bad (GOOSE IN 52) | 19E39
1256 | GOOSE4 | GOOSE IN53 Quality Good (GOOSE IN 53) | 19E40
1257 | GOOSE4 | GOOSE IN53 Quality Bad (GOOSE IN 53) | 19E41
1258 | GOOSE4 | GOOSE IN54 Quality Good (GOOSE IN 54) | 19E42
1259 | GOOSE4 | GOOSE IN54 Quality Bad (GOOSE IN 54) | 19E43
1260 | GOOSE4 | GOOSE IN55 Quality Good (GOOSE IN 55) | 19E44
1261 | GOOSE4 | GOOSE IN55 Quality Bad (GOOSE IN 55) | 19E45
1262 | GOOSE4 | GOOSE IN56 Quality Good (GOOSE IN 56) | 19E46
1263 | GOOSE4 | GOOSE IN56 Quality Bad (GOOSE IN 56) | 19E47
1264 | GOOSE4 | GOOSE IN57 Quality Good (GOOSE IN 57) | 19E48
1265 | GOOSE4 | GOOSE IN57 Quality Bad (GOOSE IN 57) | 19E49
1266 | GOOSE4 | GOOSE IN58 Quality Good (GOOSE IN 58) | 19E50
1267 | GOOSE4 | GOOSE IN58 Quality Bad (GOOSE IN 58) | 19E51
1268 | GOOSE4 | GOOSE IN59 Quality Good (GOOSE IN 59) | 19E52
1269 | GOOSE4 | GOOSE IN59 Quality Bad (GOOSE IN 59) | 19E53
1270 | GOOSE4 | GOOSE IN60 Quality Good (GOOSE IN 60) | 19E54
1271 | GOOSE4 | GOOSE IN60 Quality Bad (GOOSE IN 60) | 19E55
1272 | GOOSE4 | GOOSE IN61 Quality Good (GOOSE IN 61) | 19E56
1273 | GOOSE4 | GOOSE IN61 Quality Bad (GOOSE IN 61) | 19E57
1274 | GOOSE4 | GOOSE IN62 Quality Good (GOOSE IN 62) | 19E58
1275 | GOOSE4 | GOOSE IN62 Quality Bad (GOOSE IN 62) | 19E59
1276 | GOOSE4 | GOOSE IN63 Quality Good (GOOSE IN 63) | 19E60
1277 | GOOSE4 | GOOSE IN63 Quality Bad (GOOSE IN 63) | 19E61
1278 | GOOSE4 | GOOSE IN64 Quality Good (GOOSE IN 64) | 19E62
1279 | GOOSE4 | GOOSE IN64 Quality Bad (GOOSE IN 64) | 19E63
1280 | NOC1 | Start On | 20E0
1281 | NOC1 | Start Off | 20E1
1282 | NOC1 | Trip On | 20E2
1283 | NOC1 | Trip Off | 20E3
1284 | NOC1 | Block On | 20E4
1285 | NOC1 | Block Off | 20E5
1286 | NOC1 | Phase A Start On | 20E6
1287 | NOC1 | Phase A Start Off | 20E7
1288 | NOC1 | Phase B Start On | 20E8
1289 | NOC1 | Phase B Start Off | 20E9
1290 | NOC1 | Phase C Start On | 20E10
1291 | NOC1 | Phase C Start Off | 20E11
1292 | NOC1 | Phase A Trip On | 20E12
1293 | NOC1 | Phase A Trip Off | 20E13
1294 | NOC1 | Phase B Trip On | 20E14
1295 | NOC1 | Phase B Trip Off | 20E15
1296 | NOC1 | Phase C Trip On | 20E16
1297 | NOC1 | Phase C Trip Off | 20E17
1298 | NOC1 | Block input active On | 20E18
1299 | NOC1 | Block input active Off | 20E19
1344 | NOC2 | Start On | 21E0
1345 | NOC2 | Start Off | 21E1
1346 | NOC2 | Trip On | 21E2
1347 | NOC2 | Trip Off | 21E3
1348 | NOC2 | Block On | 21E4
1349 | NOC2 | Block Off | 21E5
1350 | NOC2 | Phase A Start On | 21E6
1351 | NOC2 | Phase A Start Off | 21E7
1352 | NOC2 | Phase B Start On | 21E8
1353 | NOC2 | Phase B Start Off | 21E9
1354 | NOC2 | Phase C Start On | 21E10
1355 | NOC2 | Phase C Start Off | 21E11
1356 | NOC2 | Phase A Trip On | 21E12
1357 | NOC2 | Phase A Trip Off | 21E13
1358 | NOC2 | Phase B Trip On | 21E14
1359 | NOC2 | Phase B Trip Off | 21E15
1360 | NOC2 | Phase C Trip On | 21E16
1361 | NOC2 | Phase C Trip Off | 21E17
1362 | NOC2 | Block input active On | 21E18
1363 | NOC2 | Block input active Off | 21E19
1408 | NOC3 | Start On | 22E0
1409 | NOC3 | Start Off | 22E1
1410 | NOC3 | Trip On | 22E2
1411 | NOC3 | Trip Off | 22E3
1412 | NOC3 | Block On | 22E4
1413 | NOC3 | Block Off | 22E5
1414 | NOC3 | Phase A Start On | 22E6
1415 | NOC3 | Phase A Start Off | 22E7
1416 | NOC3 | Phase B Start On | 22E8
1417 | NOC3 | Phase B Start Off | 22E9
1418 | NOC3 | Phase C Start On | 22E10
1419 | NOC3 | Phase C Start Off | 22E11
1420 | NOC3 | Phase A Trip On | 22E12
1421 | NOC3 | Phase A Trip Off | 22E13
1422 | NOC3 | Phase B Trip On | 22E14
1423 | NOC3 | Phase B Trip Off | 22E15
1424 | NOC3 | Phase C Trip On | 22E16
1425 | NOC3 | Phase C Trip Off | 22E17
1426 | NOC3 | Block input active On | 22E18
1427 | NOC3 | Block input active Off | 22E19
1472 | NOC4 | Start On | 23E0
1473 | NOC4 | Start Off | 23E1
1474 | NOC4 | Trip On | 23E2
1475 | NOC4 | Trip Off | 23E3
1476 | NOC4 | Block On | 23E4
1477 | NOC4 | Block Off | 23E5
1478 | NOC4 | Phase A Start On | 23E6
1479 | NOC4 | Phase A Start Off | 23E7
1480 | NOC4 | Phase B Start On | 23E8
1481 | NOC4 | Phase B Start Off | 23E9
1482 | NOC4 | Phase C Start On | 23E10
1483 | NOC4 | Phase C Start Off | 23E11
1484 | NOC4 | Phase A Trip On | 23E12
1485 | NOC4 | Phase A Trip Off | 23E13
1486 | NOC4 | Phase B Trip On | 23E14
1487 | NOC4 | Phase B Trip Off | 23E15
1488 | NOC4 | Phase C Trip On | 23E16
1489 | NOC4 | Phase C Trip Off | 23E17
1490 | NOC4 | Block input active On | 23E18
1491 | NOC4 | Block input active Off | 23E19
1536 | LOGIC4 | Logical Out1 00 On | 24E0
1537 | LOGIC4 | Logical Out1 01 On | 24E1
1538 | LOGIC4 | Logical Out1 10 On | 24E2
1539 | LOGIC4 | Logical Out1 11 On | 24E3
1540 | LOGIC4 | Logical Out2 00 On | 24E4
1541 | LOGIC4 | Logical Out2 01 On | 24E5
1542 | LOGIC4 | Logical Out2 10 On | 24E6
1543 | LOGIC4 | Logical Out2 11 On | 24E7
1544 | LOGIC4 | Logical Out3 00 On | 24E8
1545 | LOGIC4 | Logical Out3 01 On | 24E9
1546 | LOGIC4 | Logical Out3 10 On | 24E10
1547 | LOGIC4 | Logical Out3 11 On | 24E11
1548 | LOGIC4 | Logical Out4 00 On | 24E12
1549 | LOGIC4 | Logical Out4 01 On | 24E13
1550 | LOGIC4 | Logical Out4 10 On | 24E14
1551 | LOGIC4 | Logical Out4 11 On | 24E15
1552 | LOGIC4 | Logical Out5 00 On | 24E16
1553 | LOGIC4 | Logical Out5 01 On | 24E17
1554 | LOGIC4 | Logical Out5 10 On | 24E18
1555 | LOGIC4 | Logical Out5 11 On | 24E19
1556 | LOGIC4 | Logical Out6 00 On | 24E20
1557 | LOGIC4 | Logical Out6 01 On | 24E21
1558 | LOGIC4 | Logical Out6 10 On | 24E22
1559 | LOGIC4 | Logical Out6 11 On | 24E23
1560 | LOGIC4 | Logical Out7 00 On | 24E24
1561 | LOGIC4 | Logical Out7 01 On | 24E25
1562 | LOGIC4 | Logical Out7 10 On | 24E26
1563 | LOGIC4 | Logical Out7 11 On | 24E27
1564 | LOGIC4 | Logical Out8 00 On | 24E28
1565 | LOGIC4 | Logical Out8 01 On | 24E29
1566 | LOGIC4 | Logical Out8 10 On | 24E30
1567 | LOGIC4 | Logical Out8 11 On | 24E31
1568 | LOGIC4 | Logical Out9 00 On | 24E32
1569 | LOGIC4 | Logical Out9 01 On | 24E33
1570 | LOGIC4 | Logical Out9 10 On | 24E34
1571 | LOGIC4 | Logical Out9 11 On | 24E35
1572 | LOGIC4 | Logical Out10 00 On | 24E36
1573 | LOGIC4 | Logical Out10 01 On | 24E37
1574 | LOGIC4 | Logical Out10 10 On | 24E38
1575 | LOGIC4 | Logical Out10 11 On | 24E39
1576 | LOGIC4 | Logical TC1 Lower On | 24E40
1577 | LOGIC4 | Logical TC1 Lower Off | 24E41
1578 | LOGIC4 | Logical TC1 Higher On | 24E42
1579 | LOGIC4 | Logical TC1 Higher Off | 24E43
1580 | LOGIC4 | Logical TC2 Lower On | 24E44
1581 | LOGIC4 | Logical TC2 Lower Off | 24E45
1582 | LOGIC4 | Logical TC2 Higher On | 24E46
1583 | LOGIC4 | Logical TC2 Higher Off | 24E47
1584 | LOGIC4 | Logical TC3 Lower On | 24E48
1585 | LOGIC4 | Logical TC3 Lower Off | 24E49
1586 | LOGIC4 | Logical TC3 Higher On | 24E50
1587 | LOGIC4 | Logical TC3 Higher Off | 24E51
1664 | NEF1 | Start On | 26E0
1665 | NEF1 | Start Off | 26E1
1666 | NEF1 | Trip On | 26E2
1667 | NEF1 | Trip Off | 26E3
1668 | NEF1 | Block On | 26E4
1669 | NEF1 | Block Off | 26E5
1728 | NEF2 | Start On | 27E0
1729 | NEF2 | Start Off | 27E1
1730 | NEF2 | Trip On | 27E2
1731 | NEF2 | Trip Off | 27E3
1732 | NEF2 | Block On | 27E4
1733 | NEF2 | Block Off | 27E5
1792 | NEF3 | Start On | 28E0
1793 | NEF3 | Start Off | 28E1
1794 | NEF3 | Trip On | 28E2
1795 | NEF3 | Trip Off | 28E3
1796 | NEF3 | Block On | 28E4
1797 | NEF3 | Block Off | 28E5
1856 | NEF4 | Start On | 29E0
1857 | NEF4 | Start Off | 29E1
1858 | NEF4 | Trip On | 29E2
1859 | NEF4 | Trip Off | 29E3
1860 | NEF4 | Block On | 29E4
1861 | NEF4 | Block Off | 29E5
2048 | CUB1 | Start On | 32E0
2049 | CUB1 | Start Off | 32E1
2050 | CUB1 | Trip On | 32E2
2051 | CUB1 | Trip Off | 32E3
2052 | CUB1 | Block On | 32E4
2053 | CUB1 | Block Off | 32E5
2112 | CUB2 | Start On | 33E0
2113 | CUB2 | Start Off | 33E1
2114 | CUB2 | Trip On | 33E2
2115 | CUB2 | Trip Off | 33E3
2116 | CUB2 | Block On | 33E4
2117 | CUB2 | Block Off | 33E5
2176 | CUB3 | Start On | 34E0
2177 | CUB3 | Start Off | 34E1
2178 | CUB3 | Trip On | 34E2
2179 | CUB3 | Trip Off | 34E3
2180 | CUB3 | Block On | 34E4
2181 | CUB3 | Block Off | 34E5
2240 | CUB4 | Start On | 35E0
2241 | CUB4 | Start Off | 35E1
2242 | CUB4 | Trip On | 35E2
2243 | CUB4 | Trip Off | 35E3
2244 | CUB4 | Block On | 35E4
2245 | CUB4 | Block Off | 35E5
2368 | HOC1 | Start On | 37E0
2369 | HOC1 | Start Off | 37E1
2370 | HOC1 | Trip On | 37E2
2371 | HOC1 | Trip Off | 37E3
2372 | HOC1 | Block On | 37E4
2373 | HOC1 | Block Off | 37E5
2432 | HOC2 | Start On | 38E0
2433 | HOC2 | Start Off | 38E1
2434 | HOC2 | Trip On | 38E2
2435 | HOC2 | Trip Off | 38E3
2436 | HOC2 | Block On | 38E4
2437 | HOC2 | Block Off | 38E5
2496 | HOC3 | Start On | 39E0
2497 | HOC3 | Start Off | 39E1
2498 | HOC3 | Trip On | 39E2
2499 | HOC3 | Trip Off | 39E3
2500 | HOC3 | Block On | 39E4
2501 | HOC3 | Block Off | 39E5
2560 | HOC4 | Start On | 40E0
2561 | HOC4 | Start Off | 40E1
2562 | HOC4 | Trip On | 40E2
2563 | HOC4 | Trip Off | 40E3
2564 | HOC4 | Block On | 40E4
2565 | HOC4 | Block Off | 40E5
2688 | CLP1 | LowStart On | 42E0
2689 | CLP1 | LowStart Off | 42E1
2690 | CLP1 | HighStart On | 42E2
2691 | CLP1 | HighStart Off | 42E3
2692 | CLP1 | LoadNormal On | 42E4
2693 | CLP1 | LoadNormal Off | 42E5
2694 | CLP1 | Overcurrent On | 42E6
2695 | CLP1 | Overcurrent Off | 42E7
2696 | CLP1 | CLPUActivated On | 42E8
2697 | CLP1 | CLPUActivated Off | 42E9
2698 | CLP1 | Block On | 42E10
2699 | CLP1 | Block Off | 42E11
2752 | FLX1 | Flocator triggered On | 43E0
2753 | FLX1 | Flocator triggered Off | 43E1
2754 | FLX1 | Flocator Calculation On | 43E2
2755 | FLX1 | Flocator Calculation Off | 43E3
2816 | CBF1 | Start On | 44E0
2817 | CBF1 | Start Off | 44E1
2818 | CBF1 | Retrip On | 44E2
2819 | CBF1 | Retrip Off | 44E3
2820 | CBF1 | CBFP On | 44E4
2821 | CBF1 | CBFP Off | 44E5
2822 | CBF1 | Block On | 44E6
2823 | CBF1 | Block Off | 44E7
2824 | CBF1 | DO monitor On | 44E8
2825 | CBF1 | DO monitor Off | 44E9
2826 | CBF1 | Signal On | 44E10
2827 | CBF1 | Signal Off | 44E11
2828 | CBF1 | Phase current On | 44E12
2829 | CBF1 | Phase current Off | 44E13
2830 | CBF1 | Res current On | 44E14
2831 | CBF1 | Res current Off | 44E15
2880 | SYN1 | SYN1 Blocked On | 45E0
2881 | SYN1 | SYN1 Blocked Off | 45E1
2882 | SYN1 | SYN1 Ok On | 45E2
2883 | SYN1 | SYN1 Ok Off | 45E3
2884 | SYN1 | SYN1 Bypass On | 45E4
2885 | SYN1 | SYN1 Bypass Off | 45E5
2886 | SYN1 | SYN1 Volt condition OK | 45E6
2887 | SYN1 | SYN1 Volt cond not match | 45E7
2888 | SYN1 | SYN1 Volt diff Ok | 45E8
2889 | SYN1 | SYN1 Volt diff out of setting | 45E9
2890 | SYN1 | SYN1 Angle diff Ok | 45E10
2891 | SYN1 | SYN1 Angle diff out of setting | 45E11
2892 | SYN1 | SYN1 Frequency diff Ok | 45E12
2893 | SYN1 | SYN1 Frequency diff out of setting | 45E13
2894 | SYN1 | SYN2 Blocked On | 45E14
2895 | SYN1 | SYN2 Blocked Off | 45E15
2896 | SYN1 | SYN2 Ok On | 45E16
2897 | SYN1 | SYN2 Ok Off | 45E17
2898 | SYN1 | SYN2 Bypass On | 45E18
2899 | SYN1 | SYN2 Bypass Off | 45E19
2900 | SYN1 | SYN2 Volt condition OK | 45E20
2901 | SYN1 | SYN2 Volt cond not match | 45E21
2902 | SYN1 | SYN2 Volt diff Ok | 45E22
2903 | SYN1 | SYN2 Volt diff out of setting | 45E23
2904 | SYN1 | SYN2 Angle diff Ok | 45E24
2905 | SYN1 | SYN2 Angle diff out of setting | 45E25
2906 | SYN1 | SYN2 Frequency diff Ok | 45E26
2907 | SYN1 | SYN2 Frequency diff out of setting | 45E27
2908 | SYN1 | SYN3 Blocked On | 45E28
2909 | SYN1 | SYN3 Blocked Off | 45E29
2910 | SYN1 | SYN3 Ok On | 45E30
2911 | SYN1 | SYN3 Ok Off | 45E31
2912 | SYN1 | SYN3 Bypass On | 45E32
2913 | SYN1 | SYN3 Bypass Off | 45E33
2914 | SYN1 | SYN3 Volt condition OK | 45E34
2915 | SYN1 | SYN3 Volt cond not match | 45E35
2916 | SYN1 | SYN3 Volt diff Ok | 45E36
2917 | SYN1 | SYN3 Volt diff out of setting | 45E37
2918 | SYN1 | SYN3 Angle diff Ok | 45E38
2919 | SYN1 | SYN3 Angle diff out of setting | 45E39
2920 | SYN1 | SYN3 Frequency diff Ok | 45E40
2921 | SYN1 | SYN3 Frequency diff out of setting | 45E41
2922 | SYN1 | SYN1 Switch On | 45E42
2923 | SYN1 | SYN1 Switch Off | 45E43
2924 | SYN1 | SYN2 Switch On | 45E44
2925 | SYN1 | SYN2 Switch Off | 45E45
2926 | SYN1 | SYN3 Switch On | 45E46
2927 | SYN1 | SYN3 Switch Off | 45E47
2928 | SYN1 | SYN1 Block input active On | 45E48
2929 | SYN1 | SYN1 Block input active Off | 45E49
2930 | SYN1 | SYN2 Block input active On | 45E50
2931 | SYN1 | SYN2 Block input active Off | 45E51
2932 | SYN1 | SYN3 Block input active On | 45E52
2933 | SYN1 | SYN3 Block input active Off | 45E53
2944 | OBJ1 | Object Intermediate | 46E0
2945 | OBJ1 | Object Open | 46E1
2946 | OBJ1 | Object Close | 46E2
2947 | OBJ1 | Object Bad | 46E3
2948 | OBJ1 | WD Intermediate | 46E4
2949 | OBJ1 | WD Out | 46E5
2950 | OBJ1 | WD In | 46E6
2951 | OBJ1 | WD Bad | 46E7
2952 | OBJ1 | Open Request On | 46E8
2953 | OBJ1 | Open Request Off | 46E9
2954 | OBJ1 | Open Command On | 46E10
2955 | OBJ1 | Open Command Off | 46E11
2956 | OBJ1 | Close Request On | 46E12
2957 | OBJ1 | Close Request Off | 46E13
2958 | OBJ1 | Close Command On | 46E14
2959 | OBJ1 | Close Command Off | 46E15
2960 | OBJ1 | Open Blocked On | 46E16
2961 | OBJ1 | Open Blocked Off | 46E17
2962 | OBJ1 | Close Blocked On | 46E18
2963 | OBJ1 | Close Blocked Off | 46E19
2964 | OBJ1 | Object Ready | 46E20
2965 | OBJ1 | Object Not Ready | 46E21
2966 | OBJ1 | Sync Ok | 46E22
2967 | OBJ1 | Sync Not Ok | 46E23
2968 | OBJ1 | Open Command Fail | 46E24
2969 | OBJ1 | Close Command Fail | 46E25
2970 | OBJ1 | Final Trip On | 46E26
2971 | OBJ1 | Final Trip Off | 46E27
2972 | OBJ1 | Contact Abrasion Alarm On | 46E28
2973 | OBJ1 | Contact Abrasion Alarm Off | 46E29
2974 | OBJ1 | Switch Operating Time Exceeded On | 46E30
2975 | OBJ1 | Switch Operating Time Exceeded Off | 46E31
2976 | OBJ1 | XCBR Loc On | 46E32
2977 | OBJ1 | XCBR Loc Off | 46E33
2978 | OBJ1 | XSWI Loc On | 46E34
2979 | OBJ1 | XSWI Loc Off | 46E35
2980 | OBJ1 | OBJ1 Cond monitoring Alarm 1 On | 46E36
2981 | OBJ1 | OBJ1 Cond monitoring Alarm 1 Off | 46E37
2982 | OBJ1 | OBJ1 Cond monitoring Alarm 2 On | 46E38
2983 | OBJ1 | OBJ1 Cond monitoring Alarm 2 Off | 46E39
2984 | OBJ1 | OBJ1 Trip Circuit Supervision On | 46E40
2985 | OBJ1 | OBJ1 Trip Circuit Supervision Off | 46E41
3008 | OBJ2 | Object Intermediate | 47E0
3009 | OBJ2 | Object Open | 47E1
3010 | OBJ2 | Object Close | 47E2
3011 | OBJ2 | Object Bad | 47E3
3012 | OBJ2 | WD Intermediate | 47E4
3013 | OBJ2 | WD Out | 47E5
3014 | OBJ2 | WD In | 47E6
3015 | OBJ2 | WD Bad | 47E7
3016 | OBJ2 | Open Request On | 47E8
3017 | OBJ2 | Open Request Off | 47E9
3018 | OBJ2 | Open Command On | 47E10
3019 | OBJ2 | Open Command Off | 47E11
3020 | OBJ2 | Close Request On | 47E12
3021 | OBJ2 | Close Request Off | 47E13
3022 | OBJ2 | Close Command On | 47E14
3023 | OBJ2 | Close Command Off | 47E15
3024 | OBJ2 | Open Blocked On | 47E16
3025 | OBJ2 | Open Blocked Off | 47E17
3026 | OBJ2 | Close Blocked On | 47E18
3027 | OBJ2 | Close Blocked Off | 47E19
3028 | OBJ2 | Object Ready | 47E20
3029 | OBJ2 | Object Not Ready | 47E21
3030 | OBJ2 | Sync Ok | 47E22
3031 | OBJ2 | Sync Not Ok | 47E23
3032 | OBJ2 | Open Command Fail | 47E24
3033 | OBJ2 | Close Command Fail | 47E25
3034 | OBJ2 | Final Trip On | 47E26
3035 | OBJ2 | Final Trip Off | 47E27
3036 | OBJ2 | Contact Abrasion Alarm On | 47E28
3037 | OBJ2 | Contact Abrasion Alarm Off | 47E29
3038 | OBJ2 | Switch Operating Time Exceeded On | 47E30
3039 | OBJ2 | Switch Operating Time Exceeded Off | 47E31
3040 | OBJ2 | XCBR Loc On | 47E32
3041 | OBJ2 | XCBR Loc Off | 47E33
3042 | OBJ2 | XSWI Loc On | 47E34
3043 | OBJ2 | XSWI Loc Off | 47E35
3044 | OBJ2 | OBJ2 Cond monitoring Alarm 1 On | 47E36
3045 | OBJ2 | OBJ2 Cond monitoring Alarm 1 Off | 47E37
3046 | OBJ2 | OBJ2 Cond monitoring Alarm 2 On | 47E38
3047 | OBJ2 | OBJ2 Cond monitoring Alarm 2 Off | 47E39
3048 | OBJ2 | OBJ2 Trip Circuit Supervision On | 47E40
3049 | OBJ2 | OBJ2 Trip Circuit Supervision Off | 47E41
3072 | OBJ3 | Object Intermediate | 48E0
3073 | OBJ3 | Object Open | 48E1
3074 | OBJ3 | Object Close | 48E2
3075 | OBJ3 | Object Bad | 48E3
3076 | OBJ3 | WD Intermediate | 48E4
3077 | OBJ3 | WD Out | 48E5
3078 | OBJ3 | WD In | 48E6
3079 | OBJ3 | WD Bad | 48E7
3080 | OBJ3 | Open Request On | 48E8
3081 | OBJ3 | Open Request Off | 48E9
3082 | OBJ3 | Open Command On | 48E10
3083 | OBJ3 | Open Command Off | 48E11
3084 | OBJ3 | Close Request On | 48E12
3085 | OBJ3 | Close Request Off | 48E13
3086 | OBJ3 | Close Command On | 48E14
3087 | OBJ3 | Close Command Off | 48E15
3088 | OBJ3 | Open Blocked On | 48E16
3089 | OBJ3 | Open Blocked Off | 48E17
3090 | OBJ3 | Close Blocked On | 48E18
3091 | OBJ3 | Close Blocked Off | 48E19
3092 | OBJ3 | Object Ready | 48E20
3093 | OBJ3 | Object Not Ready | 48E21
3094 | OBJ3 | Sync Ok | 48E22
3095 | OBJ3 | Sync Not Ok | 48E23
3096 | OBJ3 | Open Command Fail | 48E24
3097 | OBJ3 | Close Command Fail | 48E25
3098 | OBJ3 | Final Trip On | 48E26
3099 | OBJ3 | Final Trip Off | 48E27
3100 | OBJ3 | Contact Abrasion Alarm On | 48E28
3101 | OBJ3 | Contact Abrasion Alarm Off | 48E29
3102 | OBJ3 | Switch Operating Time Exceeded On | 48E30
3103 | OBJ3 | Switch Operating Time Exceeded Off | 48E31
3104 | OBJ3 | XCBR Loc On | 48E32
3105 | OBJ3 | XCBR Loc Off | 48E33
3106 | OBJ3 | XSWI Loc On | 48E34
3107 | OBJ3 | XSWI Loc Off | 48E35
3108 | OBJ3 | OBJ3 Cond monitoring Alarm 1 On | 48E36
3109 | OBJ3 | OBJ3 Cond monitoring Alarm 1 Off | 48E37
3110 | OBJ3 | OBJ3 Cond monitoring Alarm 2 On | 48E38
3111 | OBJ3 | OBJ3 Cond monitoring Alarm 2 Off | 48E39
3112 | OBJ3 | OBJ3 Trip Circuit Supervision On | 48E40
3113 | OBJ3 | OBJ3 Trip Circuit Supervision Off | 48E41
3136 | OBJ4 | Object Intermediate | 49E0
3137 | OBJ4 | Object Open | 49E1
3138 | OBJ4 | Object Close | 49E2
3139 | OBJ4 | Object Bad | 49E3
3140 | OBJ4 | WD Intermediate | 49E4
3141 | OBJ4 | WD Out | 49E5
3142 | OBJ4 | WD In | 49E6
3143 | OBJ4 | WD Bad | 49E7
3144 | OBJ4 | Open Request On | 49E8
3145 | OBJ4 | Open Request Off | 49E9
3146 | OBJ4 | Open Command On | 49E10
3147 | OBJ4 | Open Command Off | 49E11
3148 | OBJ4 | Close Request On | 49E12
3149 | OBJ4 | Close Request Off | 49E13
3150 | OBJ4 | Close Command On | 49E14
3151 | OBJ4 | Close Command Off | 49E15
3152 | OBJ4 | Open Blocked On | 49E16
3153 | OBJ4 | Open Blocked Off | 49E17
3154 | OBJ4 | Close Blocked On | 49E18
3155 | OBJ4 | Close Blocked Off | 49E19
3156 | OBJ4 | Object Ready | 49E20
3157 | OBJ4 | Object Not Ready | 49E21
3158 | OBJ4 | Sync Ok | 49E22
3159 | OBJ4 | Sync Not Ok | 49E23
3160 | OBJ4 | Open Command Fail | 49E24
3161 | OBJ4 | Close Command Fail | 49E25
3162 | OBJ4 | Final Trip On | 49E26
3163 | OBJ4 | Final Trip Off | 49E27
3164 | OBJ4 | Contact Abrasion Alarm On | 49E28
3165 | OBJ4 | Contact Abrasion Alarm Off | 49E29
3166 | OBJ4 | Switch Operating Time Exceeded On | 49E30
3167 | OBJ4 | Switch Operating Time Exceeded Off | 49E31
3168 | OBJ4 | XCBR Loc On | 49E32
3169 | OBJ4 | XCBR Loc Off | 49E33
3170 | OBJ4 | XSWI Loc On | 49E34
3171 | OBJ4 | XSWI Loc Off | 49E35
3172 | OBJ4 | OBJ4 Cond monitoring Alarm 1 On | 49E36
3173 | OBJ4 | OBJ4 Cond monitoring Alarm 1 Off | 49E37
3174 | OBJ4 | OBJ4 Cond monitoring Alarm 2 On | 49E38
3175 | OBJ4 | OBJ4 Cond monitoring Alarm 2 Off | 49E39
3176 | OBJ4 | OBJ4 Trip Circuit Supervision On | 49E40
3177 | OBJ4 | OBJ4 Trip Circuit Supervision Off | 49E41
3200 | OBJ5 | Object Intermediate | 50E0
3201 | OBJ5 | Object Open | 50E1
3202 | OBJ5 | Object Close | 50E2
3203 | OBJ5 | Object Bad | 50E3
3204 | OBJ5 | WD Intermediate | 50E4
3205 | OBJ5 | WD Out | 50E5
3206 | OBJ5 | WD In | 50E6
3207 | OBJ5 | WD Bad | 50E7
3208 | OBJ5 | Open Request On | 50E8
3209 | OBJ5 | Open Request Off | 50E9
3210 | OBJ5 | Open Command On | 50E10
3211 | OBJ5 | Open Command Off | 50E11
3212 | OBJ5 | Close Request On | 50E12
3213 | OBJ5 | Close Request Off | 50E13
3214 | OBJ5 | Close Command On | 50E14
3215 | OBJ5 | Close Command Off | 50E15
3216 | OBJ5 | Open Blocked On | 50E16
3217 | OBJ5 | Open Blocked Off | 50E17
3218 | OBJ5 | Close Blocked On | 50E18
3219 | OBJ5 | Close Blocked Off | 50E19
3220 | OBJ5 | Object Ready | 50E20
3221 | OBJ5 | Object Not Ready | 50E21
3222 | OBJ5 | Sync Ok | 50E22
3223 | OBJ5 | Sync Not Ok | 50E23
3224 | OBJ5 | Open Command Fail | 50E24
3225 | OBJ5 | Close Command Fail | 50E25
3226 | OBJ5 | Final Trip On | 50E26
3227 | OBJ5 | Final Trip Off | 50E27
3228 | OBJ5 | Contact Abrasion Alarm On | 50E28
3229 | OBJ5 | Contact Abrasion Alarm Off | 50E29
3230 | OBJ5 | Switch Operating Time Exceeded On | 50E30
3231 | OBJ5 | Switch Operating Time Exceeded Off | 50E31
3232 | OBJ5 | XCBR Loc On | 50E32
3233 | OBJ5 | XCBR Loc Off | 50E33
3234 | OBJ5 | XSWI Loc On | 50E34
3235 | OBJ5 | XSWI Loc Off | 50E35
3236 | OBJ5 | OBJ5 Cond monitoring Alarm 1 On | 50E36
3237 | OBJ5 | OBJ5 Cond monitoring Alarm 1 Off | 50E37
3238 | OBJ5 | OBJ5 Cond monitoring Alarm 2 On | 50E38
3239 | OBJ5 | OBJ5 Cond monitoring Alarm 2 Off | 50E39
3240 | OBJ5 | OBJ5 Trip Circuit Supervision On | 50E40
3241 | OBJ5 | OBJ5 Trip Circuit Supervision Off | 50E41
3264 | HSHC | HSO1 TCS Input On (HSO1 TCS In) | 51E0
3265 | HSHC | HSO1 TCS Input Off (HSO1 TCS In) | 51E1
3266 | HSHC | HSO2 TCS Input On (HSO2 TCS In) | 51E2
3267 | HSHC | HSO2 TCS Input Off (HSO2 TCS In) | 51E3
3268 | HSHC | HSO3 TCS Input On (HSO3 TCS In) | 51E4
3269 | HSHC | HSO3 TCS Input Off (HSO3 TCS In) | 51E5
3270 | HSHC | HSO4 TCS Input On (HSO4 TCS In) | 51E6
3271 | HSHC | HSO4 TCS Input Off (HSO4 TCS In) | 51E7
3272 | HSHC | HSO5 TCS Input On (HSO5 TCS In) | 51E8
3273 | HSHC | HSO5 TCS Input Off (HSO5 TCS In) | 51E9
3274 | HSHC | HSO6 TCS Input On (HSO6 TCS In) | 51E10
3275 | HSHC | HSO6 TCS Input Off (HSO6 TCS In) | 51E11
3276 | HSHC | HSO7 TCS Input On (HSO7 TCS In) | 51E12
3277 | HSHC | HSO7 TCS Input Off (HSO7 TCS In) | 51E13
3278 | HSHC | HSO8 TCS Input On (HSO8 TCS In) | 51E14
3279 | HSHC | HSO8 TCS Input Off (HSO8 TCS In) | 51E15
3280 | HSHC | HSO9 TCS Input On (HSO9 TCS In) | 51E16
3281 | HSHC | HSO9 TCS Input Off (HSO9 TCS In) | 51E17
3328 | CTS1 | Alarm On | 52E0
3329 | CTS1 | Alarm Off | 52E1
3330 | CTS1 | Block On | 52E2
3331 | CTS1 | Block Off | 52E3
3392 | VTS1 | Bus VT fail Start On | 53E0
3393 | VTS1 | Bus VT fail Start Off | 53E1
3394 | VTS1 | Bus VT fail Trip On | 53E2
3395 | VTS1 | Bus VT fail Trip Off | 53E3
3396 | VTS1 | Bus VT fail Block On | 53E4
3397 | VTS1 | Bus VT fail Block Off | 53E5
3398 | VTS1 | Line VT fail On | 53E6
3399 | VTS1 | Line VT fail Off | 53E7
3400 | VTS1 | Bus Fuse fail On | 53E8
3401 | VTS1 | Bus Fuse fail Off | 53E9
3402 | VTS1 | Line Fuse fail On | 53E10
3403 | VTS1 | Line Fuse fail Off | 53E11
3456 | CTS2 | Alarm On | 54E0
3457 | CTS2 | Alarm Off | 54E1
3458 | CTS2 | Block On | 54E2
3459 | CTS2 | Block Off | 54E3
3520 | THD1 | THD Start Phase On | 55E0
3521 | THD1 | THD Start Phase Off | 55E1
3522 | THD1 | THD Start I01 On | 55E2
3523 | THD1 | THD Start I01 Off | 55E3
3524 | THD1 | THD Start I02 On | 55E4
3525 | THD1 | THD Start I02 Off | 55E5
3526 | THD1 | THD Alarm Phase On | 55E6
3527 | THD1 | THD Alarm Phase Off | 55E7
3528 | THD1 | THD Alarm I01 On | 55E8
3529 | THD1 | THD Alarm I01 Off | 55E9
3530 | THD1 | THD Alarm I02 On | 55E10
3531 | THD1 | THD Alarm I02 Off | 55E11
3532 | THD1 | Blocked On | 55E12
3533 | THD1 | Blocked Off | 55E13
3584 | FSP1 | Alarm On | 56E0
3585 | FSP1 | Alarm Off | 56E1
3586 | FSP1 | Inhibit On | 56E2
3587 | FSP1 | Inhibit Off | 56E3
3588 | FSP1 | Blocked On | 56E4
3589 | FSP1 | Blocked Off | 56E5
3648 | LCR1 | Max.Start time exceed On | 57E0
3649 | LCR1 | Max.Start time exceed Off | 57E1
3650 | LCR1 | Set start time exceed On | 57E2
3651 | LCR1 | Set start time exceed Off | 57E3
3652 | LCR1 | Speed Switch not received On | 57E4
3653 | LCR1 | Speed Switch not received Off | 57E5
3654 | LCR1 | Start On | 57E6
3655 | LCR1 | Start Off | 57E7
3656 | LCR1 | Set time Trip On | 57E8
3657 | LCR1 | Set time Trip Off | 57E9
3658 | LCR1 | Max cap Trip On | 57E10
3659 | LCR1 | Max cap Trip Off | 57E11
3660 | LCR1 | Blocked On | 57E12
3661 | LCR1 | Blocked Off | 57E13
3712 | CBW1 | CBWEAR1 Triggered | 58E0
3713 | CBW1 | CBWEAR1 Alarm1 On | 58E1
3714 | CBW1 | CBWEAR1 Alarm1 Off | 58E2
3715 | CBW1 | CBWEAR1 Alarm2 On | 58E3
3716 | CBW1 | CBWEAR1 Alarm2 Off | 58E4
3776 | MJP1 | Start On | 59E0
3777 | MJP1 | Start Off | 59E1
3778 | MJP1 | Trip On | 59E2
3779 | MJP1 | Trip Off | 59E3
3780 | MJP1 | Block On | 59E4
3781 | MJP1 | Block Off | 59E5
3840 | NUC1 | Start On | 60E0
3841 | NUC1 | Start Off | 60E1
3842 | NUC1 | Trip On | 60E2
3843 | NUC1 | Trip Off | 60E3
3844 | NUC1 | Block On | 60E4
3845 | NUC1 | Block Off | 60E5
3904 | SOF1 | SOTF Init On | 61E0
3905 | SOF1 | SOTF Init Off | 61E1
3906 | SOF1 | SOTF Block On | 61E2
3907 | SOF1 | SOTF Block Off | 61E3
3908 | SOF1 | SOTF Active On | 61E4
3909 | SOF1 | SOTF Active Off | 61E5
3910 | SOF1 | SOTF Trip On | 61E6
3911 | SOF1 | SOTF Trip Off | 61E7
3968 | MST1 | Motor Stopped On | 62E0
3969 | MST1 | Motor Stopped Off | 62E1
3970 | MST1 | Motor Starting On | 62E2
3971 | MST1 | Motor Starting Off | 62E3
3972 | MST1 | Motor Running On | 62E4
3973 | MST1 | Motor Running Off | 62E5
3974 | MST1 | Motor Stalled On | 62E6
3975 | MST1 | Motor Stalled Off | 62E7
3976 | MST1 | Load not symm On | 62E8
3977 | MST1 | Load not symm Off | 62E9
3978 | MST1 | Load normal On | 62E10
3979 | MST1 | Load normal Off | 62E11
3980 | MST1 | Overload On | 62E12
3981 | MST1 | Overload Off | 62E13
3982 | MST1 | High Overcurrent On | 62E14
3983 | MST1 | High Overcurrent Off | 62E15
4032 | AR1 | AR Ready On | 63E0
4033 | AR1 | AR Ready Off | 63E1
4034 | AR1 | AR Locked Reset | 63E2
4035 | AR1 | AR Reclosing request rejected On | 63E3
4036 | AR1 | AR Reclosing request rejected Off | 63E4
4037 | AR1 | AR Reclosing request On | 63E5
4038 | AR1 | AR Reclosing request Off | 63E6
4039 | AR1 | User Operated Obj AR halted and reset | 63E7
4040 | AR1 | Object failure, AR locked | 63E8
4041 | AR1 | Shot Failed | 63E9
4042 | AR1 | AR cycle end due to Discr request | 63E10
4043 | AR1 | AR Shot Clear | 63E11
4044 | AR1 | Object Close Request On | 63E12
4045 | AR1 | Object Open Request | 63E13
4046 | AR1 | Inhibit condition On | 63E14
4047 | AR1 | Inhibit condition Off | 63E15
4048 | AR1 | Locking condition On | 63E16
4049 | AR1 | Locking condition Off | 63E17
4050 | AR1 | Reserved | 63E18
4051 | AR1 | AR1 Request On | 63E19
4052 | AR1 | AR1 Request Off | 63E20
4053 | AR1 | AR2 Request On | 63E21
4054 | AR1 | AR2 Request Off | 63E22
4055 | AR1 | AR3 Request On | 63E23
4056 | AR1 | AR3 Request Off | 63E24
4057 | AR1 | AR4 Request On | 63E25
4058 | AR1 | AR4 Request Off | 63E26
4059 | AR1 | AR5 Request On | 63E27
4060 | AR1 | AR5 Request Off | 63E28
4061 | AR1 | Critical Request On | 63E29
4062 | AR1 | Critical Request Off | 63E30
4063 | AR1 | AR Running On | 63E31
4064 | AR1 | AR Running Off | 63E32
4065 | AR1 | Shot 1 Execute On | 63E33
4066 | AR1 | Shot 1 Execute Off | 63E34
4067 | AR1 | Shot 2 Execute On | 63E35
4068 | AR1 | Shot 2 Execute Off | 63E36
4069 | AR1 | Shot 3 Execute On | 63E37
4070 | AR1 | Shot 3 Execute Off | 63E38
4071 | AR1 | Shot 4 Execute On | 63E39
4072 | AR1 | Shot 4 Execute Off | 63E40
4073 | AR1 | Shot 5 Execute On | 63E41
4074 | AR1 | Shot 5 Execute Off | 63E42
4075 | AR1 | Seq Finished Final Trip Armed On | 63E43
4076 | AR1 | Final Trip Executed | 63E44
4077 | AR1 | Lock Out Time On | 63E45
4078 | AR1 | Lock Out Time Off | 63E46
4079 | AR1 | General Reclaim time On | 63E47
4080 | AR1 | General Reclaim time Off | 63E48
4081 | AR1 | Shot Start Time On | 63E49
4082 | AR1 | Shot Start Time Off | 63E50
4083 | AR1 | Dead Time On | 63E51
4084 | AR1 | Dead Time Off | 63E52
4085 | AR1 | Arc Discr Time On | 63E53
4086 | AR1 | Arc Discr Time Off | 63E54
4087 | AR1 | Shot Reclaim Time On | 63E55
4088 | AR1 | Shot Reclaim Time Off | 63E56
4089 | AR1 | Seq. finished Off | 63E57
4090 | AR1 | Final Trip Executed Off | 63E58
4091 | AR1 | Object Close Request Off | 63E59
4092 | AR1 | AR On | 63E60
4093 | AR1 | AR Off | 63E61
4094 | AR1 | AR Running (DT) On | 63E62
4095 | AR1 | AR Running (DT) Off | 63E63
4096 | DR1 | Recorder triggered On | 64E0
4097 | DR1 | Recorder triggered Off | 64E1
4098 | DR1 | Recorder memory cleared | 64E2
4099 | DR1 | Oldest record cleared | 64E3
4100 | DR1 | Recorder memory full On | 64E4
4101 | DR1 | Recorder memory full Off | 64E5
4102 | DR1 | Recording On | 64E6
4103 | DR1 | Recording Off | 64E7
4104 | DR1 | Storing recording On | 64E8
4105 | DR1 | Storing recording Off | 64E9
4106 | DR1 | Newest record cleared | 64E10
4160 | SGS | SG2 Enabled | 65E0
4161 | SGS | SG2 Disabled | 65E1
4162 | SGS | SG3 Enabled | 65E2
4163 | SGS | SG3 Disabled | 65E3
4164 | SGS | SG4 Enabled | 65E4
4165 | SGS | SG4 Disabled | 65E5
4166 | SGS | SG5 Enabled | 65E6
4167 | SGS | SG5 Disabled | 65E7
4168 | SGS | SG6 Enabled | 65E8
4169 | SGS | SG6 Disabled | 65E9
4170 | SGS | SG7 Enabled | 65E10
4171 | SGS | SG7 Disabled | 65E11
4172 | SGS | SG8 Enabled | 65E12
4173 | SGS | SG8 Disabled | 65E13
4174 | SGS | SG1 Request On | 65E14
4175 | SGS | SG1 Request Off | 65E15
4176 | SGS | SG2 Request On | 65E16
4177 | SGS | SG2 Request Off | 65E17
4178 | SGS | SG3 Request On | 65E18
4179 | SGS | SG3 Request Off | 65E19
4180 | SGS | SG4 Request On | 65E20
4181 | SGS | SG4 Request Off | 65E21
4182 | SGS | SG5 Request On | 65E22
4183 | SGS | SG5 Request Off | 65E23
4184 | SGS | SG6 Request On | 65E24
4185 | SGS | SG6 Request Off | 65E25
4186 | SGS | SG7 Request On | 65E26
4187 | SGS | SG7 Request Off | 65E27
4188 | SGS | SG8 Request On | 65E28
4189 | SGS | SG8 Request Off | 65E29
4190 | SGS | Remote Change SG Req On | 65E30
4191 | SGS | Remote Change SG Req Off | 65E31
4192 | SGS | Local Change SG Req On | 65E32
4193 | SGS | Local Change SG Req On | 65E33
4194 | SGS | Force Change SG On | 65E34
4195 | SGS | Force Change SG Off | 65E35
4196 | SGS | SG Req. Fail Not configured SG On | 65E36
4197 | SGS | SG Req. Fail Not configured SG On | 65E37
4198 | SGS | Force Req. Fail Force not On | 65E38
4199 | SGS | Force Req. Fail Off | 65E39
4200 | SGS | SG Req. Fail Lower priority Req. On | 65E40
4201 | SGS | SG Req. Fail Lower priority Req. Off | 65E41
4202 | SGS | SG1 Active On | 65E42
4203 | SGS | SG1 Active Off | 65E43
4204 | SGS | SG2 Active On | 65E44
4205 | SGS | SG2 Active Off | 65E45
4206 | SGS | SG3 Active On | 65E46
4207 | SGS | SG3 Active Off | 65E47
4208 | SGS | SG4 Active On | 65E48
4209 | SGS | SG4 Active Off | 65E49
4210 | SGS | SG5 Active On | 65E50
4211 | SGS | SG5 Active Off | 65E51
4212 | SGS | SG6 Active On | 65E52
4213 | SGS | SG6 Active Off | 65E53
4214 | SGS | SG7 Active On | 65E54
4215 | SGS | SG7 Active Off | 65E55
4216 | SGS | SG8 Active On | 65E56
4217 | SGS | SG8 Active Off | 65E57
4224 | REF1 | REF Trip On | 66E0
4225 | REF1 | REF Trip Off | 66E1
4226 | REF1 | REF Block On | 66E2
4227 | REF1 | REF Block Off | 66E3
4288 | TOLF1 | Alarm1 On | 67E0
4289 | TOLF1 | Alarm1 Off | 67E1
4290 | TOLF1 | Alarm2 On | 67E2
4291 | TOLF1 | Alarm2 Off | 67E3
4292 | TOLF1 | Inhibit On | 67E4
4293 | TOLF1 | Inhibit Off | 67E5
4294 | TOLF1 | Trip On | 67E6
4295 | TOLF1 | Trip Off | 67E7
4296 | TOLF1 | Block On | 67E8
4297 | TOLF1 | Block Off | 67E9
4352 | TOLM1 | Alarm1 On | 68E0
4353 | TOLM1 | Alarm1 Off | 68E1
4354 | TOLM1 | Alarm2 On | 68E2
4355 | TOLM1 | Alarm2 Off | 68E3
4356 | TOLM1 | Inhibit On | 68E4
4357 | TOLM1 | Inhibit Off | 68E5
4358 | TOLM1 | Trip On | 68E6
4359 | TOLM1 | Trip Off | 68E7
4360 | TOLM1 | Block On | 68E8
4361 | TOLM1 | Block Off | 68E9
4416 | RTD1 | S1 Alarm1 On | 69E0
4417 | RTD1 | S1 Alarm1 Off | 69E1
4418 | RTD1 | S1 Alarm2 On | 69E2
4419 | RTD1 | S1 Alarm2 Off | 69E3
4420 | RTD1 | S2 Alarm1 On | 69E4
4421 | RTD1 | S2 Alarm1 Off | 69E5
4422 | RTD1 | S2 Alarm2 On | 69E6
4423 | RTD1 | S2 Alarm2 Off | 69E7
4424 | RTD1 | S3 Alarm1 On | 69E8
4425 | RTD1 | S3 Alarm1 Off | 69E9
4426 | RTD1 | S3 Alarm2 On | 69E10
4427 | RTD1 | S3 Alarm2 Off | 69E11
4428 | RTD1 | S4 Alarm1 On | 69E12
4429 | RTD1 | S4 Alarm1 Off | 69E13
4430 | RTD1 | S4 Alarm2 On | 69E14
4431 | RTD1 | S4 Alarm2 Off | 69E15
4432 | RTD1 | S5 Alarm1 On | 69E16
4433 | RTD1 | S5 Alarm1 Off | 69E17
4434 | RTD1 | S5 Alarm2 On | 69E18
4435 | RTD1 | S5 Alarm2 Off | 69E19
4436 | RTD1 | S6 Alarm1 On | 69E20
4437 | RTD1 | S6 Alarm1 Off | 69E21
4438 | RTD1 | S6 Alarm2 On | 69E22
4439 | RTD1 | S6 Alarm2 Off | 69E23
4440 | RTD1 | S7 Alarm1 On | 69E24
4441 | RTD1 | S7 Alarm1 Off | 69E25
4442 | RTD1 | S7 Alarm2 On | 69E26
4443 | RTD1 | S7 Alarm2 Off | 69E27
4444 | RTD1 | S8 Alarm1 On | 69E28
4445 | RTD1 | S8 Alarm1 Off | 69E29
4446 | RTD1 | S8 Alarm2 On | 69E30
4447 | RTD1 | S8 Alarm2 Off | 69E31
4448 | RTD1 | S9 Alarm1 On | 69E32
4449 | RTD1 | S9 Alarm1 Off | 69E33
4450 | RTD1 | S9 Alarm2 On | 69E34
4451 | RTD1 | S9 Alarm2 Off | 69E35
4452 | RTD1 | S10 Alarm1 On | 69E36
4453 | RTD1 | S10 Alarm1 Off | 69E37
4454 | RTD1 | S10 Alarm2 On | 69E38
4455 | RTD1 | S10 Alarm2 Off | 69E39
4456 | RTD1 | S11 Alarm1 On | 69E40
4457 | RTD1 | S11 Alarm1 Off | 69E41
4458 | RTD1 | S11 Alarm2 On | 69E42
4459 | RTD1 | S11 Alarm2 Off | 69E43
4460 | RTD1 | S12 Alarm1 On | 69E44
4461 | RTD1 | S12 Alarm1 Off | 69E45
4462 | RTD1 | S12 Alarm2 On | 69E46
4463 | RTD1 | S12 Alarm2 Off | 69E47
4464 | RTD1 | S13 Alarm1 On | 69E48
4465 | RTD1 | S13 Alarm1 Off | 69E49
4466 | RTD1 | S13 Alarm2 On | 69E50
4467 | RTD1 | S13 Alarm2 Off | 69E51
4468 | RTD1 | S14 Alarm1 On | 69E52
4469 | RTD1 | S14 Alarm1 Off | 69E53
4470 | RTD1 | S14 Alarm2 On | 69E54
4471 | RTD1 | S14 Alarm2 Off | 69E55
4472 | RTD1 | S15 Alarm1 On | 69E56
4473 | RTD1 | S15 Alarm1 Off | 69E57
4474 | RTD1 | S15 Alarm2 On | 69E58
4475 | RTD1 | S15 Alarm2 Off | 69E59
4476 | RTD1 | S16 Alarm1 On | 69E60
4477 | RTD1 | S16 Alarm1 Off | 69E61
4478 | RTD1 | S16 Alarm2 On | 69E62
4479 | RTD1 | S16 Alarm2 Off | 69E63
4480 | RTD2 | S1 Meas Ok | 70E0
4481 | RTD2 | S1 Meas Invalid | 70E1
4482 | RTD2 | S2 Meas Ok | 70E2
4483 | RTD2 | S2 Meas Invalid | 70E3
4484 | RTD2 | S3 Meas Ok | 70E4
4485 | RTD2 | S3 Meas Invalid | 70E5
4486 | RTD2 | S4 Meas Ok | 70E6
4487 | RTD2 | S4 Meas Invalid | 70E7
4488 | RTD2 | S5 Meas Ok | 70E8
4489 | RTD2 | S5 Meas Invalid | 70E9
4490 | RTD2 | S6 Meas Ok | 70E10
4491 | RTD2 | S6 Meas Invalid | 70E11
4492 | RTD2 | S7 Meas Ok | 70E12
4493 | RTD2 | S7 Meas Invalid | 70E13
4494 | RTD2 | S8 Meas Ok | 70E14
4495 | RTD2 | S8 Meas Invalid | 70E15
4496 | RTD2 | S9 Meas Ok | 70E16
4497 | RTD2 | S9 Meas Invalid | 70E17
4498 | RTD2 | S10 Meas Ok | 70E18
4499 | RTD2 | S10 Meas Invalid | 70E19
4500 | RTD2 | S11 Meas Ok | 70E20
4501 | RTD2 | S11 Meas Invalid | 70E21
4502 | RTD2 | S12 Meas Ok | 70E22
4503 | RTD2 | S12 Meas Invalid | 70E23
4504 | RTD2 | S13 Meas Ok | 70E24
4505 | RTD2 | S13 Meas Invalid | 70E25
4506 | RTD2 | S14 Meas Ok | 70E26
4507 | RTD2 | S14 Meas Invalid | 70E27
4508 | RTD2 | S15 Meas Ok | 70E28
4509 | RTD2 | S15 Meas Invalid | 70E29
4510 | RTD2 | S16 Meas Ok | 70E30
4511 | RTD2 | S16 Meas Invalid | 70E31
4544 | DIF1 | Idb> Trip On | 71E0
4545 | DIF1 | Idb> Trip Off | 71E1
4546 | DIF1 | Idb> Blocked (ext) On | 71E2
4547 | DIF1 | Idb> Blocked (ext) Off | 71E3
4548 | DIF1 | Idi> Trip On | 71E4
4549 | DIF1 | Idi> Trip Off | 71E5
4550 | DIF1 | Idi> Blocked (ext) On | 71E6
4551 | DIF1 | Idi> Blocked (ext) Off | 71E7
4552 | DIF1 | 2.nd Harmonic Block On | 71E8
4553 | DIF1 | 2.nd Harmonic Block Off | 71E9
4554 | DIF1 | 5.th Harmonic Block On | 71E10
4555 | DIF1 | 5.th Harmonic Block Off | 71E11
4556 | DIF1 | L1 2.nd harm On | 71E12
4557 | DIF1 | L1 2.nd harm Off | 71E13
4558 | DIF1 | L2 2.nd harm On | 71E14
4559 | DIF1 | L2 2.nd harm Off | 71E15
4560 | DIF1 | L3 2.nd harm On | 71E16
4561 | DIF1 | L3 2.nd harm Off | 71E17
4562 | DIF1 | L1 5.th harm On | 71E18
4563 | DIF1 | L1 5.th harm Off | 71E19
4564 | DIF1 | L2 5.th harm On | 71E20
4565 | DIF1 | L2 5.th harm Off | 71E21
4566 | DIF1 | L3 5.th harm On | 71E22
4567 | DIF1 | L3 5.th harm Off | 71E23
4568 | DIF1 | HV I0d> Block On | 71E24
4569 | DIF1 | HV I0d> Block Off | 71E25
4570 | DIF1 | HV I0d> Trip On | 71E26
4571 | DIF1 | HV I0d> Trip Off | 71E27
4572 | DIF1 | LV I0d> Block On | 71E28
4573 | DIF1 | LV I0d> Block Off | 71E29
4574 | DIF1 | LV I0d> Trip On | 71E30
4575 | DIF1 | LV I0d> Trip Off | 71E31
4608 | TRF1 | Light/No load On | 72E0
4609 | TRF1 | Light/No load Off | 72E1
4610 | TRF1 | HV side inrush On | 72E2
4611 | TRF1 | HV side inrush Off | 72E3
4612 | TRF1 | LV side inrush On | 72E4
4613 | TRF1 | LV side inrush Off | 72E5
4614 | TRF1 | Load normal On | 72E6
4615 | TRF1 | Load normal Off | 72E7
4616 | TRF1 | Overloading On | 72E8
4617 | TRF1 | Overloading Off | 72E9
4618 | TRF1 | High overload On | 72E10
4619 | TRF1 | High overload Off | 72E11
4620 | TRF1 | Setting changes, calculating new trafo data | 72E12
4621 | TRF1 | Calculation finished, possible restart | 72E13
4672 | TOLT1 | Alarm1 On | 73E0
4673 | TOLT1 | Alarm1 Off | 73E1
4674 | TOLT1 | Alarm2 On | 73E2
4675 | TOLT1 | Alarm2 Off | 73E3
4676 | TOLT1 | Inhibit On | 73E4
4677 | TOLT1 | Inhibit Off | 73E5
4678 | TOLT1 | Trip On | 73E6
4679 | TOLT1 | Trip Off | 73E7
4680 | TOLT1 | Block On | 73E8
4681 | TOLT1 | Block Off | 73E9
4736 | ARC1 | Zone1 Trip On | 74E0
4737 | ARC1 | Zone1 Trip Off | 74E1
4738 | ARC1 | Zone1 Block On | 74E2
4739 | ARC1 | Zone1 Block Off | 74E3
4740 | ARC1 | Zone2 Trip On | 74E4
4741 | ARC1 | Zone2 Trip Off | 74E5
4742 | ARC1 | Zone2 Block On | 74E6
4743 | ARC1 | Zone2 Block Off | 74E7
4744 | ARC1 | Zone3 Trip On | 74E8
4745 | ARC1 | Zone3 Trip Off | 74E9
4746 | ARC1 | Zone3 Block On | 74E10
4747 | ARC1 | Zone3 Block Off | 74E11
4748 | ARC1 | Zone4 Trip On | 74E12
4749 | ARC1 | Zone4 Trip Off | 74E13
4750 | ARC1 | Zone4 Block On | 74E14
4751 | ARC1 | Zone4 Block Off | 74E15
4752 | ARC1 | Ph Current Blocked On | 74E16
4753 | ARC1 | Ph Current Blocked Off | 74E17
4754 | ARC1 | Ph Current Start On | 74E18
4755 | ARC1 | Ph Current Start Off | 74E19
4756 | ARC1 | Res Current Blocked On | 74E20
4757 | ARC1 | Res Current Blocked Off | 74E21
4758 | ARC1 | Res Current Start On | 74E22
4759 | ARC1 | Res Current Start Off | 74E23
4760 | ARC1 | Channel 1 Light On | 74E24
4761 | ARC1 | Channel 1 Light Off | 74E25
4762 | ARC1 | Reserved 1 On | 74E26
4763 | ARC1 | Reserved 1 Off | 74E27
4764 | ARC1 | Channel 2 Light On | 74E28
4765 | ARC1 | Channel 2 Light Off | 74E29
4766 | ARC1 | Reserved 2 On | 74E30
4767 | ARC1 | Reserved 2 Off | 74E31
4768 | ARC1 | Channel 3 Light On | 74E32
4769 | ARC1 | Channel 3 Light Off | 74E33
4770 | ARC1 | Reserved 3 On | 74E34
4771 | ARC1 | Reserved 3 Off | 74E35
4772 | ARC1 | Channel 4 Light On | 74E36
4773 | ARC1 | Channel 4 Light Off | 74E37
4774 | ARC1 | Reserved 4 On | 74E38
4775 | ARC1 | Reserved 4 Off | 74E39
4776 | ARC1 | DI Signal On | 74E40
4777 | ARC1 | DI Signal Off | 74E41
4778 | ARC1 | S1 Sensor fault On | 74E42
4779 | ARC1 | S1 Sensor fault Off | 74E43
4780 | ARC1 | S2 Sensor fault On | 74E44
4781 | ARC1 | S2 Sensor fault Off | 74E45
4782 | ARC1 | S3 Sensor fault On | 74E46
4783 | ARC1 | S3 Sensor fault Off | 74E47
4784 | ARC1 | S4 Sensor fault On | 74E48
4785 | ARC1 | S4 Sensor fault Off | 74E49
4786 | ARC1 | Sub-unit count error On | 74E50
4787 | ARC1 | Sub-unit count error Off | 74E51
4800 | DOC1 | Start On | 75E0
4801 | DOC1 | Start Off | 75E1
4802 | DOC1 | Trip On | 75E2
4803 | DOC1 | Trip Off | 75E3
4804 | DOC1 | Block On | 75E4
4805 | DOC1 | Block Off | 75E5
4806 | DOC1 | No voltage, Protection locked On | 75E6
4807 | DOC1 | Voltage measurable, Protection locked Off | 75E7
4808 | DOC1 | Measuring live angle On | 75E8
4809 | DOC1 | Measuring live angle Off | 75E9
4810 | DOC1 | Using voltmem On | 75E10
4811 | DOC1 | Using voltmem Off | 75E11
4813 | DOC1 | Voltage mem Off Emergency non dir On | 75E13
4814 | DOC1 | Voltage mem Off Emergency non dir Off | 75E14
4864 | DOC2 | Start On | 76E0
4865 | DOC2 | Start Off | 76E1
4866 | DOC2 | Trip On | 76E2
4867 | DOC2 | Trip Off | 76E3
4868 | DOC2 | Block On | 76E4
4869 | DOC2 | Block Off | 76E5
4870 | DOC2 | No voltage, Protection locked On | 76E6
4871 | DOC2 | Voltage measurable, Protection locked Off | 76E7
4872 | DOC2 | Measuring live angle On | 76E8
4873 | DOC2 | Measuring live angle Off | 76E9
4874 | DOC2 | Using voltmem On | 76E10
4875 | DOC2 | Using voltmem Off | 76E11
4877 | DOC2 | Voltage mem Off Emergency non dir On | 76E13
4878 | DOC2 | Voltage mem Off Emergency non dir Off | 76E14
4928 | DOC3 | Start On | 77E0
4929 | DOC3 | Start Off | 77E1
4930 | DOC3 | Trip On | 77E2
4931 | DOC3 | Trip Off | 77E3
4932 | DOC3 | Block On | 77E4
4933 | DOC3 | Block Off | 77E5
4934 | DOC3 | No voltage, Protection locked On | 77E6
4935 | DOC3 | Voltage measurable, Protection locked Off | 77E7
4936 | DOC3 | Measuring live angle On | 77E8
4937 | DOC3 | Measuring live angle Off | 77E9
4938 | DOC3 | Using voltmem On | 77E10
4939 | DOC3 | Using voltmem Off | 77E11
4941 | DOC3 | Voltage mem Off Emergency non dir On | 77E13
4942 | DOC3 | Voltage mem Off Emergency non dir Off | 77E14
4992 | DOC4 | Start On | 78E0
4993 | DOC4 | Start Off | 78E1
4994 | DOC4 | Trip On | 78E2
4995 | DOC4 | Trip Off | 78E3
4996 | DOC4 | Block On | 78E4
4997 | DOC4 | Block Off | 78E5
4998 | DOC4 | No voltage, Protection locked On | 78E6
4999 | DOC4 | Voltage measurable, Protection locked Off | 78E7
5000 | DOC4 | Measuring live angle On | 78E8
5001 | DOC4 | Measuring live angle Off | 78E9
5002 | DOC4 | Using voltmem On | 78E10
5003 | DOC4 | Using voltmem Off | 78E11
5005 | DOC4 | Voltage mem Off Emergency non dir On | 78E13
5006 | DOC4 | Voltage mem Off Emergency non dir Off | 78E14
5184 | DEF1 | Start On | 81E0
5185 | DEF1 | Start Off | 81E1
5186 | DEF1 | Trip On | 81E2
5187 | DEF1 | Trip Off | 81E3
5188 | DEF1 | Block On | 81E4
5189 | DEF1 | Block Off | 81E5
5190 | DEF1 | I0Cosfi Start On | 81E6
5191 | DEF1 | I0Cosfi Start Off | 81E7
5192 | DEF1 | I0Sinfi Start On | 81E8
5193 | DEF1 | I0Sinfi Start Off | 81E9
5194 | DEF1 | I0Cosfi Trip On | 81E10
5195 | DEF1 | I0Cosfi Trip Off | 81E11
5196 | DEF1 | I0Sinfi Trip On | 81E12
5197 | DEF1 | I0Sinfi Trip Off | 81E13
5248 | DEF2 | Start On | 82E0
5249 | DEF2 | Start Off | 82E1
5250 | DEF2 | Trip On | 82E2
5251 | DEF2 | Trip Off | 82E3
5252 | DEF2 | Block On | 82E4
5253 | DEF2 | Block Off | 82E5
5254 | DEF2 | I0Cosfi Start On | 82E6
5255 | DEF2 | I0Cosfi Start Off | 82E7
5256 | DEF2 | I0Sinfi Start On | 82E8
5257 | DEF2 | I0Sinfi Start Off | 82E9
5258 | DEF2 | I0Cosfi Trip On | 82E10
5259 | DEF2 | I0Cosfi Trip Off | 82E11
5260 | DEF2 | I0Sinfi Trip On | 82E12
5261 | DEF2 | I0Sinfi Trip Off | 82E13
5312 | DEF3 | Start On | 83E0
5313 | DEF3 | Start Off | 83E1
5314 | DEF3 | Trip On | 83E2
5315 | DEF3 | Trip Off | 83E3
5316 | DEF3 | Block On | 83E4
5317 | DEF3 | Block Off | 83E5
5318 | DEF3 | I0Cosfi Start On | 83E6
5319 | DEF3 | I0Cosfi Start Off | 83E7
5320 | DEF3 | I0Sinfi Start On | 83E8
5321 | DEF3 | I0Sinfi Start Off | 83E9
5322 | DEF3 | I0Cosfi Trip On | 83E10
5323 | DEF3 | I0Cosfi Trip Off | 83E11
5324 | DEF3 | I0Sinfi Trip On | 83E12
5325 | DEF3 | I0Sinfi Trip Off | 83E13
5376 | DEF4 | Start On | 84E0
5377 | DEF4 | Start Off | 84E1
5378 | DEF4 | Trip On | 84E2
5379 | DEF4 | Trip Off | 84E3
5380 | DEF4 | Block On | 84E4
5381 | DEF4 | Block Off | 84E5
5382 | DEF4 | I0Cosfi Start On | 84E6
5383 | DEF4 | I0Cosfi Start Off | 84E7
5384 | DEF4 | I0Sinfi Start On | 84E8
5385 | DEF4 | I0Sinfi Start Off | 84E9
5386 | DEF4 | I0Cosfi Trip On | 84E10
5387 | DEF4 | I0Cosfi Trip Off | 84E11
5388 | DEF4 | I0Sinfi Trip On | 84E12
5389 | DEF4 | I0Sinfi Trip Off | 84E13
5440 | OV1 | Start On | 85E0
5441 | OV1 | Start Off | 85E1
5442 | OV1 | Trip On | 85E2
5443 | OV1 | Trip Off | 85E3
5444 | OV1 | Block On | 85E4
5445 | OV1 | Block Off | 85E5
5446 | OV1 | Block input active On | 85E6
5447 | OV1 | Block input active Off | 85E7
5504 | OV2 | Start On | 86E0
5505 | OV2 | Start Off | 86E1
5506 | OV2 | Trip On | 86E2
5507 | OV2 | Trip Off | 86E3
5508 | OV2 | Block On | 86E4
5509 | OV2 | Block Off | 86E5
5510 | OV2 | Block input active On | 86E6
5511 | OV2 | Block input active Off | 86E7
5568 | OV3 | Start On | 87E0
5569 | OV3 | Start Off | 87E1
5570 | OV3 | Trip On | 87E2
5571 | OV3 | Trip Off | 87E3
5572 | OV3 | Block On | 87E4
5573 | OV3 | Block Off | 87E5
5574 | OV3 | Block input active On | 87E6
5575 | OV3 | Block input active Off | 87E7
5632 | OV4 | Start On | 88E0
5633 | OV4 | Start Off | 88E1
5634 | OV4 | Trip On | 88E2
5635 | OV4 | Trip Off | 88E3
5636 | OV4 | Block On | 88E4
5637 | OV4 | Block Off | 88E5
5638 | OV4 | Block input active On | 88E6
5639 | OV4 | Block input active Off | 88E7
5696 | UV1 | Start On | 89E0
5697 | UV1 | Start Off | 89E1
5698 | UV1 | Trip On | 89E2
5699 | UV1 | Trip Off | 89E3
5700 | UV1 | Block On | 89E4
5701 | UV1 | Block Off | 89E5
5702 | UV1 | Undervoltage Block On | 89E6
5703 | UV1 | Undervoltage Block Off | 89E7
5704 | UV1 | Block input active On | 89E8
5705 | UV1 | Block input active Off | 89E9
5760 | UV2 | Start On | 90E0
5761 | UV2 | Start Off | 90E1
5762 | UV2 | Trip On | 90E2
5763 | UV2 | Trip Off | 90E3
5764 | UV2 | Block On | 90E4
5765 | UV2 | Block Off | 90E5
5766 | UV2 | Undervoltage Block On | 90E6
5767 | UV2 | Undervoltage Block Off | 90E7
5768 | UV2 | Block input active On | 90E8
5769 | UV2 | Block input active Off | 90E9
5824 | UV3 | Start On | 91E0
5825 | UV3 | Start Off | 91E1
5826 | UV3 | Trip On | 91E2
5827 | UV3 | Trip Off | 91E3
5828 | UV3 | Block On | 91E4
5829 | UV3 | Block Off | 91E5
5830 | UV3 | Undervoltage Block On | 91E6
5831 | UV3 | Undervoltage Block Off | 91E7
5832 | UV3 | Block input active On | 91E8
5833 | UV3 | Block input active Off | 91E9
5888 | UV4 | Start On | 92E0
5889 | UV4 | Start Off | 92E1
5890 | UV4 | Trip On | 92E2
5891 | UV4 | Trip Off | 92E3
5892 | UV4 | Block On | 92E4
5893 | UV4 | Block Off | 92E5
5894 | UV4 | Undervoltage Block On | 92E6
5895 | UV4 | Undervoltage Block Off | 92E7
5896 | UV4 | Block input active On | 92E8
5897 | UV4 | Block input active Off | 92E9
5952 | NOV1 | Start On | 93E0
5953 | NOV1 | Start Off | 93E1
5954 | NOV1 | Trip On | 93E2
5955 | NOV1 | Trip Off | 93E3
5956 | NOV1 | Block On | 93E4
5957 | NOV1 | Block Off | 93E5
6016 | NOV2 | Start On | 94E0
6017 | NOV2 | Start Off | 94E1
6018 | NOV2 | Trip On | 94E2
6019 | NOV2 | Trip Off | 94E3
6020 | NOV2 | Block On | 94E4
6021 | NOV2 | Block Off | 94E5
6080 | NOV3 | Start On | 95E0
6081 | NOV3 | Start Off | 95E1
6082 | NOV3 | Trip On | 95E2
6083 | NOV3 | Trip Off | 95E3
6084 | NOV3 | Block On | 95E4
6085 | NOV3 | Block Off | 95E5
6144 | NOV4 | Start On | 96E0
6145 | NOV4 | Start Off | 96E1
6146 | NOV4 | Trip On | 96E2
6147 | NOV4 | Trip Off | 96E3
6148 | NOV4 | Block On | 96E4
6149 | NOV4 | Block Off | 96E5
6208 | NJK1 | U0RECL Request On | 97E0
6209 | NJK1 | U0RECL Request Off | 97E1
6210 | NJK1 | U0RECL Blocked On | 97E2
6211 | NJK1 | U0RECL Blocked Off | 97E3
6212 | NJK1 | U0RECL Active On | 97E4
6213 | NJK1 | U0RECL Active Off | 97E5
6214 | NJK1 | U0RECL Breaker close request On | 97E6
6215 | NJK1 | U0RECL Breaker close request Off | 97E7
6216 | NJK1 | U0RECL U0 Blocking On | 97E8
6217 | NJK1 | U0RECL U0 Blocking Off | 97E9
6272 | FRQC1 | f> [Curr] Start On | 98E0
6273 | FRQC1 | f> [Curr] Start Off | 98E1
6274 | FRQC1 | f> [Curr] Trip On | 98E2
6275 | FRQC1 | f> [Curr] Trip Off | 98E3
6276 | FRQC1 | f>>[Curr] Start On | 98E4
6277 | FRQC1 | f>> [Curr] Start Off | 98E5
6278 | FRQC1 | f>> [Curr] Trip On | 98E6
6279 | FRQC1 | f>> [Curr] Trip Off | 98E7
6280 | FRQC1 | f>>> [Curr] Start On | 98E8
6281 | FRQC1 | f>>> [Curr] Start Off | 98E9
6282 | FRQC1 | f>>> [Curr] Trip On | 98E10
6283 | FRQC1 | f>>> [Curr] Trip Off | 98E11
6284 | FRQC1 | f>>>> [Curr] Start On | 98E12
6285 | FRQC1 | f>>>> [Curr] Start Off | 98E13
6286 | FRQC1 | f>>>> [Curr] Trip On | 98E14
6287 | FRQC1 | f>>>> [Curr] Trip Off | 98E15
6288 | FRQC1 | f< [Curr] Start On | 98E16
6289 | FRQC1 | f< [Curr] Start Off | 98E17
6290 | FRQC1 | f< [Curr] Trip On | 98E18
6291 | FRQC1 | f< [Curr] Trip Off | 98E19
6292 | FRQC1 | f<< [Curr] Start On | 98E20
6293 | FRQC1 | f<< [Curr] Start Off | 98E21
6294 | FRQC1 | f<< [Curr] Trip On | 98E22
6295 | FRQC1 | f<< [Curr] Trip Off | 98E23
6296 | FRQC1 | f<<< [Curr] Start On | 98E24
6297 | FRQC1 | f<<< [Curr] Start Off | 98E25
6298 | FRQC1 | f<<< [Curr] Trip On | 98E26
6299 | FRQC1 | f<<< [Curr] Trip Off | 98E27
6300 | FRQC1 | f<<<< [Curr] Start On | 98E28
6301 | FRQC1 | f<<<< [Curr] Start Off | 98E29
6302 | FRQC1 | f<<<< [Curr] Trip On | 98E30
6303 | FRQC1 | f<<<< [Curr] Trip Off | 98E31
6304 | FRQC1 | f> [Curr] Block On | 98E32
6305 | FRQC1 | f> [Curr] Block Off | 98E33
6306 | FRQC1 | f>> [Curr] Block On | 98E34
6307 | FRQC1 | f>> [Curr] Block Off | 98E35
6308 | FRQC1 | f>>> [Curr] Block On | 98E36
6309 | FRQC1 | f>>> [Curr] Block Off | 98E37
6310 | FRQC1 | f>>>> [Curr] Block On | 98E38
6311 | FRQC1 | f>>>> [Curr] Block Off | 98E39
6312 | FRQC1 | f< [Curr] Block On | 98E40
6313 | FRQC1 | f< [Curr] Block Off | 98E41
6314 | FRQC1 | f<< [Curr] Block On | 98E42
6315 | FRQC1 | f<< [Curr] Block Off | 98E43
6316 | FRQC1 | f<<< [Curr] Block On | 98E44
6317 | FRQC1 | f<<< [Curr] Block Off | 98E45
6318 | FRQC1 | f<<<< [Curr] Block On | 98E46
6319 | FRQC1 | f<<<< [Curr] Block Off | 98E47
6320 | FRQC1 | Meas Curr Ok for f [curr] | 98E48
6321 | FRQC1 | Meas Curr too low, f [curr] blocked | 98E49
6336 | FRQV1 | f> Start On | 99E0
6337 | FRQV1 | f> Start Off | 99E1
6338 | FRQV1 | f> Trip On | 99E2
6339 | FRQV1 | f> Trip Off | 99E3
6340 | FRQV1 | f>> Start On | 99E4
6341 | FRQV1 | f>> Start Off | 99E5
6342 | FRQV1 | f>> Trip On | 99E6
6343 | FRQV1 | f>> Trip Off | 99E7
6344 | FRQV1 | f>>> Start On | 99E8
6345 | FRQV1 | f>>> Start Off | 99E9
6346 | FRQV1 | f>>> Trip On | 99E10
6347 | FRQV1 | f>>> Trip Off | 99E11
6348 | FRQV1 | f>>>> Start On | 99E12
6349 | FRQV1 | f>>>> Start Off | 99E13
6350 | FRQV1 | f>>>> Trip On | 99E14
6351 | FRQV1 | f>>>> Trip Off | 99E15
6352 | FRQV1 | f< Start On | 99E16
6353 | FRQV1 | f< Start Off | 99E17
6354 | FRQV1 | f< Trip On | 99E18
6355 | FRQV1 | f< Trip Off | 99E19
6356 | FRQV1 | f<< Start On | 99E20
6357 | FRQV1 | f<< Start Off | 99E21
6358 | FRQV1 | f<< Trip On | 99E22
6359 | FRQV1 | f<< Trip Off | 99E23
6360 | FRQV1 | f<<< Start On | 99E24
6361 | FRQV1 | f<<< Start Off | 99E25
6362 | FRQV1 | f<<< Trip On | 99E26
6363 | FRQV1 | f<<< Trip Off | 99E27
6364 | FRQV1 | f<<<< Start On | 99E28
6365 | FRQV1 | f<<<< Start Off | 99E29
6366 | FRQV1 | f<<<< Trip On | 99E30
6367 | FRQV1 | f<<<< Trip Off | 99E31
6368 | FRQV1 | f> Block On | 99E32
6369 | FRQV1 | f> Block Off | 99E33
6370 | FRQV1 | f>> Block On | 99E34
6371 | FRQV1 | f>> Block Off | 99E35
6372 | FRQV1 | f>>> Block On | 99E36
6373 | FRQV1 | f>>> Block Off | 99E37
6374 | FRQV1 | f>>>> Block On | 99E38
6375 | FRQV1 | f>>>> Block Off | 99E39
6376 | FRQV1 | f< Block On | 99E40
6377 | FRQV1 | f< Block Off | 99E41
6378 | FRQV1 | f<< Block On | 99E42
6379 | FRQV1 | f<< Block Off | 99E43
6380 | FRQV1 | f<<< Block On | 99E44
6381 | FRQV1 | f<<< Block Off | 99E45
6382 | FRQV1 | f<<<< Block On | 99E46
6383 | FRQV1 | f<<<< Block Off | 99E47
6384 | FRQV1 | f< Undervoltage Block On | 99E48
6385 | FRQV1 | f< Undervoltage Block Off | 99E49
6386 | FRQV1 | f<< Undervoltage Block On | 99E50
6387 | FRQV1 | f<< Undervoltage Block Off | 99E51
6388 | FRQV1 | f<<< Undervoltage Block On | 99E52
6389 | FRQV1 | f<<< Undervoltage Block Off | 99E53
6390 | FRQV1 | f<<<< Undervoltage Block On | 99E54
6391 | FRQV1 | f<<<< Undervoltage Block Off | 99E55
6392 | FRQV1 | f< Block input active On | 99E56
6393 | FRQV1 | f< Block input active Off | 99E57
6394 | FRQV1 | f<< Block input active On | 99E58
6395 | FRQV1 | f<< Block input active Off | 99E59
6396 | FRQV1 | f<<< Block input active On | 99E60
6397 | FRQV1 | f<<< Block input active Off | 99E61
6398 | FRQV1 | f<<<< Block input active On | 99E62
6399 | FRQV1 | f<<<< Block input active Off | 99E63
6400 | OPW1 | Start On | 100E0
6401 | OPW1 | Start Off | 100E1
6402 | OPW1 | Trip On | 100E2
6403 | OPW1 | Trip Off | 100E3
6404 | OPW1 | Block On | 100E4
6405 | OPW1 | Block Off | 100E5
6464 | UPW1 | Start On | 101E0
6465 | UPW1 | Start Off | 101E1
6466 | UPW1 | Trip On | 101E2
6467 | UPW1 | Trip Off | 101E3
6468 | UPW1 | Block On | 101E4
6469 | UPW1 | Block Off | 101E5
6528 | RPW1 | Start On | 102E0
6529 | RPW1 | Start Off | 102E1
6530 | RPW1 | Trip On | 102E2
6531 | RPW1 | Trip Off | 102E3
6532 | RPW1 | Block On | 102E4
6533 | RPW1 | Block Off | 102E5
6592 | DFT1 | df/dt </> (1) Start On | 103E0
6593 | DFT1 | df/dt </> (1) Start Off | 103E1
6594 | DFT1 | df/dt </> (1) Trip On | 103E2
6595 | DFT1 | df/dt </> (1) Trip Off | 103E3
6596 | DFT1 | df/dt </> (2) Start On | 103E4
6597 | DFT1 | df/dt </> (2) Start Off | 103E5
6598 | DFT1 | df/dt </> (2) Trip On | 103E6
6599 | DFT1 | df/dt </> (2) Trip Off | 103E7
6600 | DFT1 | df/dt </> (3) Start On | 103E8
6601 | DFT1 | df/dt </> (3) Start Off | 103E9
6602 | DFT1 | df/dt </> (3) Trip On | 103E10
6603 | DFT1 | df/dt </> (3) Trip Off | 103E11
6604 | DFT1 | df/dt </> (4) Start On | 103E12
6605 | DFT1 | df/dt </> (4) Start Off | 103E13
6606 | DFT1 | df/dt </> (4) Trip On | 103E14
6607 | DFT1 | df/dt </> (4) Trip Off | 103E15
6608 | DFT1 | df/dt </> (5) Start On | 103E16
6609 | DFT1 | df/dt </> (5) Start Off | 103E17
6610 | DFT1 | df/dt </> (5) Trip On | 103E18
6611 | DFT1 | df/dt </> (5) Trip Off | 103E19
6612 | DFT1 | df/dt </> (6) Start On | 103E20
6613 | DFT1 | df/dt </> (6) Start Off | 103E21
6614 | DFT1 | df/dt </> (6) Trip On | 103E22
6615 | DFT1 | df/dt </> (6) Trip Off | 103E23
6616 | DFT1 | df/dt </> (7) Start On | 103E24
6617 | DFT1 | df/dt </> (7) Start Off | 103E25
6618 | DFT1 | df/dt </> (7) Trip On | 103E26
6619 | DFT1 | df/dt </> (7) Trip Off | 103E27
6620 | DFT1 | df/dt </> (8) Start On | 103E28
6621 | DFT1 | df/dt </> (8) Start Off | 103E29
6622 | DFT1 | df/dt </> (8) Trip On | 103E30
6623 | DFT1 | df/dt </> (8) Trip Off | 103E31
6624 | DFT1 | df/dt </> (1) Block On | 103E32
6625 | DFT1 | df/dt </> (1) Block Off | 103E33
6626 | DFT1 | df/dt </> (2) Block On | 103E34
6627 | DFT1 | df/dt </> (2) Block Off | 103E35
6628 | DFT1 | df/dt </> (3) Block On | 103E36
6629 | DFT1 | df/dt </> (3) Block Off | 103E37
6630 | DFT1 | df/dt </> (4) Block On | 103E38
6631 | DFT1 | df/dt </> (4) Block Off | 103E39
6632 | DFT1 | df/dt </> (5) Block On | 103E40
6633 | DFT1 | df/dt </> (5) Block Off | 103E41
6634 | DFT1 | df/dt </> (6) Block On | 103E42
6635 | DFT1 | df/dt </> (6) Block Off | 103E43
6636 | DFT1 | df/dt </> (7) Block On | 103E44
6637 | DFT1 | df/dt </> (7) Block Off | 103E45
6638 | DFT1 | df/dt </> (8) Block On | 103E46
6639 | DFT1 | df/dt </> (8) Block Off | 103E47
6656 | CIN1 | Intermediate | 104E0
6657 | CIN1 | Open | 104E1
6658 | CIN1 | Close | 104E2
6659 | CIN1 | Bad | 104E3
6720 | CIN2 | Intermediate | 105E0
6721 | CIN2 | Open | 105E1
6722 | CIN2 | Close | 105E2
6723 | CIN2 | Bad | 105E3
6784 | CIN3 | Intermediate | 106E0
6785 | CIN3 | Open | 106E1
6786 | CIN3 | Close | 106E2
6787 | CIN3 | Bad | 106E3
6848 | CIN4 | Intermediate | 107E0
6849 | CIN4 | Open | 107E1
6850 | CIN4 | Close | 107E2
6851 | CIN4 | Bad | 107E3
6912 | CIN5 | Intermediate | 108E0
6913 | CIN5 | Open | 108E1
6914 | CIN5 | Close | 108E2
6915 | CIN5 | Bad | 108E3
6976 | UEX1 | Start On | 109E0
6977 | UEX1 | Start Off | 109E1
6978 | UEX1 | Trip On | 109E2
6979 | UEX1 | Trip Off | 109E3
6980 | UEX1 | Block On | 109E4
6981 | UEX1 | Block Off | 109E5
7040 | SEF1 | Start On | 110E0
7041 | SEF1 | Start Off | 110E1
7042 | SEF1 | Trip On | 110E2
7043 | SEF1 | Trip Off | 110E3
7044 | SEF1 | Block On | 110E4
7045 | SEF1 | Block Off | 110E5
7104 | UIM1 | Start On | 111E0
7105 | UIM1 | Start Off | 111E1
7106 | UIM1 | Trip On | 111E2
7107 | UIM1 | Trip Off | 111E3
7108 | UIM1 | Block On | 111E4
7109 | UIM1 | Block Off | 111E5
7168 | VOC1 | Start On | 112E0
7169 | VOC1 | Start Off | 112E1
7170 | VOC1 | Trip On | 112E2
7171 | VOC1 | Trip Off | 112E3
7172 | VOC1 | Block On | 112E4
7173 | VOC1 | Block Off | 112E5
7232 | GST1 | Light/No load On | 113E0
7233 | GST1 | Light/No load Off | 113E1
7234 | GST1 | HV side inrush On | 113E2
7235 | GST1 | HV side inrush Off | 113E3
7236 | GST1 | LV side inrush On | 113E4
7237 | GST1 | LV side inrush Off | 113E5
7238 | GST1 | Load normal On | 113E6
7239 | GST1 | Load normal Off | 113E7
7240 | GST1 | Overloading On | 113E8
7241 | GST1 | Overloading Off | 113E9
7242 | GST1 | High overload On | 113E10
7243 | GST1 | High overload Off | 113E11
7244 | GST1 | Setting changes, calculating new trafo data | 113E12
7245 | GST1 | Calculation finished, possible restart | 113E13
7296 | IEF1 | Start FWD On | 114E0
7297 | IEF1 | Start FWD Off | 114E1
7298 | IEF1 | Start REV On | 114E2
7299 | IEF1 | Start REV Off | 114E3
7300 | IEF1 | Trip On | 114E4
7301 | IEF1 | Trip Off | 114E5
7302 | IEF1 | Block On | 114E6
7303 | IEF1 | Block Off | 114E7
7304 | IEF1 | Intermittent EF detected On | 114E8
7305 | IEF1 | Intermittent EF detected Off | 114E9
7306 | IEF1 | Normal earthfault detected | 114E10
7307 | IEF1 | Intermittent EF Locked | 114E11
7360 | VRG1 | Tap Raise command On | 115E0
7361 | VRG1 | Tap Raise command Off | 115E1
7362 | VRG1 | Tap Lower command On | 115E2
7363 | VRG1 | Tap Lower command Off | 115E3
7364 | VRG1 | Block operation On | 115E4
7365 | VRG1 | Block Operation Off | 115E5
7366 | VRG1 | Block Output commands On | 115E6
7367 | VRG1 | Block Output commands Off | 115E7
7368 | VRG1 | Low voltage blocking On | 115E8
7369 | VRG1 | Low voltage blocking Off | 115E9
7370 | VRG1 | Overcurrent blocking On | 115E10
7371 | VRG1 | Overcurrent blocking Off | 115E11
7372 | VRG1 | Tap on highlimit On | 115E12
7373 | VRG1 | Tap on highlimit Off | 115E13
7374 | VRG1 | Tap on lowlimit On | 115E14
7375 | VRG1 | Tap on lowlimit Off | 115E15
7376 | VRG1 | Operation blocked On | 115E16
7377 | VRG1 | Operation blocked Off | 115E17
7378 | VRG1 | U>/< Start On | 115E18
7379 | VRG1 | U>/< Start Off | 115E19
7380 | VRG1 | U>>/<< Start On | 115E20
7381 | VRG1 | U>>/<< Start Off | 115E21
7382 | VRG1 | Control wait time On | 115E22
7383 | VRG1 | Control wait time Off | 115E23
7384 | VRG1 | Manual control On | 115E24
7385 | VRG1 | Automatic control On | 115E25
7386 | VRG1 | Tap raise requested On | 115E26
7387 | VRG1 | Tap raise requested Off | 115E27
7388 | VRG1 | Tap lower requested On | 115E28
7389 | VRG1 | Tap lower requested Off | 115E29
7390 | VRG1 | Transformer independent control | 115E30
7391 | VRG1 | Transformer parallel control | 115E31
7392 | VRG1 | Tranformer operates as Master | 115E32
7393 | VRG1 | Tranformer operates as follower | 115E33
7394 | VRG1 | Circulating reactive current mode | 115E34
7395 | VRG1 | Master and follower mode | 115E35
7396 | VRG1 | Parallel communication failure On | 115E36
7397 | VRG1 | Parallel communication failure Off | 115E37
7398 | VRG1 | Tap control circuit failure On | 115E38
7399 | VRG1 | Tap control circuit failure Off | 115E39
7400 | VRG1 | Tap difference failure On | 115E40
7401 | VRG1 | Tap difference failure Off | 115E41
7402 | VRG1 | Tap position changed | 115E42
8192 | VHZ1 | (1)Start On | 128E0
8193 | VHZ1 | (1)Start Off | 128E1
8194 | VHZ1 | (1)Alarm On | 128E2
8195 | VHZ1 | (1)Alarm Off | 128E3
8196 | VHZ1 | (1)Trip On | 128E4
8197 | VHZ1 | (1)Trip Off | 128E5
8198 | VHZ1 | (1)Block On | 128E6
8199 | VHZ1 | (1)Block Off | 128E7
8200 | VHZ1 | (2)Start On | 128E8
8201 | VHZ1 | (2)Start Off | 128E9
8202 | VHZ1 | (2)Alarm On | 128E10
8203 | VHZ1 | (2)Alarm Off | 128E11
8204 | VHZ1 | (2)Trip On | 128E12
8205 | VHZ1 | (2)Trip Off | 128E13
8206 | VHZ1 | (2)Block On | 128E14
8207 | VHZ1 | (2)Block Off | 128E15
8256 | UPF1 | Block On | 129E0
8257 | UPF1 | Block Off | 129E1
8258 | UPF1 | Start On | 129E2
8259 | UPF1 | Start Off | 129E3
8260 | UPF1 | Trip On | 129E4
8261 | UPF1 | Trip Off | 129E5
8262 | UPF1 | Alarm Start On | 129E6
8263 | UPF1 | Alarm Start Off | 129E7
8264 | UPF1 | Alarm On | 129E8
8265 | UPF1 | Alarm Off | 129E9
8320 | VUB1 | Start On | 130E0
8321 | VUB1 | Start Off | 130E1
8322 | VUB1 | Trip On | 130E2
8323 | VUB1 | Trip Off | 130E3
8324 | VUB1 | Block On | 130E4
8325 | VUB1 | Block Off | 130E5
8384 | VUB2 | Start On | 131E0
8385 | VUB2 | Start Off | 131E1
8386 | VUB2 | Trip On | 131E2
8387 | VUB2 | Trip Off | 131E3
8388 | VUB2 | Block On | 131E4
8389 | VUB2 | Block Off | 131E5
8448 | VUB3 | Start On | 132E0
8449 | VUB3 | Start Off | 132E1
8450 | VUB3 | Trip On | 132E2
8451 | VUB3 | Trip Off | 132E3
8452 | VUB3 | Block On | 132E4
8453 | VUB3 | Block Off | 132E5
8512 | VUB4 | Start On | 133E0
8513 | VUB4 | Start Off | 133E1
8514 | VUB4 | Trip On | 133E2
8515 | VUB4 | Trip Off | 133E3
8516 | VUB4 | Block On | 133E4
8517 | VUB4 | Block Off | 133E5
8576 | PGS1 | PS1 >/< Start On | 134E0
8577 | PGS1 | PS1 >/< Start Off | 134E1
8578 | PGS1 | PS1 >/< Trip On | 134E2
8579 | PGS1 | PS1 >/< Trip Off | 134E3
8580 | PGS1 | PS1 >/< Block On | 134E4
8581 | PGS1 | PS1 >/< Block Off | 134E5
8582 | PGS1 | PS2 >/< Start On | 134E6
8583 | PGS1 | PS2 >/< Start Off | 134E7
8584 | PGS1 | PS2 >/< Trip On | 134E8
8585 | PGS1 | PS2 >/< Trip Off | 134E9
8586 | PGS1 | PS2 >/< Block On | 134E10
8587 | PGS1 | PS2 >/< Block Off | 134E11
8588 | PGS1 | PS3 >/< Start On | 134E12
8589 | PGS1 | PS3 >/< Start Off | 134E13
8590 | PGS1 | PS3 >/< Trip On | 134E14
8591 | PGS1 | PS3 >/< Trip Off | 134E15
8592 | PGS1 | PS3 >/< Block On | 134E16
8593 | PGS1 | PS3 >/< Block Off | 134E17
8594 | PGS1 | PS4 >/< Start On | 134E18
8595 | PGS1 | PS4 >/< Start Off | 134E19
8596 | PGS1 | PS4 >/< Trip On | 134E20
8597 | PGS1 | PS4 >/< Trip Off | 134E21
8598 | PGS1 | PS4 >/< Block On | 134E22
8599 | PGS1 | PS4 >/< Block Off | 134E23
8600 | PGS1 | PS5 >/< Start On | 134E24
8601 | PGS1 | PS5 >/< Start Off | 134E25
8602 | PGS1 | PS5 >/< Trip On | 134E26
8603 | PGS1 | PS5 >/< Trip Off | 134E27
8604 | PGS1 | PS5 >/< Block On | 134E28
8605 | PGS1 | PS5 >/< Block Off | 134E29
8606 | PGS1 | Reserved | 134E30
8607 | PGS1 | Reserved | 134E31
8608 | PGS1 | PS6 >/< Start On | 134E32
8609 | PGS1 | PS6 >/< Start Off | 134E33
8610 | PGS1 | PS6 >/< Trip On | 134E34
8611 | PGS1 | PS6 >/< Trip Off | 134E35
8612 | PGS1 | PS6 >/< Block On | 134E36
8613 | PGS1 | PS6 >/< Block Off | 134E37
8614 | PGS1 | PS7 >/< Start On | 134E38
8615 | PGS1 | PS7 >/< Start Off | 134E39
8616 | PGS1 | PS7 >/< Trip On | 134E40
8617 | PGS1 | PS7 >/< Trip Off | 134E41
8618 | PGS1 | PS7 >/< Block On | 134E42
8619 | PGS1 | PS7 >/< Block Off | 134E43
8620 | PGS1 | PS8 >/< Start On | 134E44
8621 | PGS1 | PS8 >/< Start Off | 134E45
8622 | PGS1 | PS8 >/< Trip On | 134E46
8623 | PGS1 | PS8 >/< Trip Off | 134E47
8624 | PGS1 | PS8 >/< Block On | 134E48
8625 | PGS1 | PS8 >/< Block Off | 134E49
8626 | PGS1 | PS9 >/< Start On | 134E50
8627 | PGS1 | PS9 >/< Start Off | 134E51
8628 | PGS1 | PS9 >/< Trip On | 134E52
8629 | PGS1 | PS9 >/< Trip Off | 134E53
8630 | PGS1 | PS9 >/< Block On | 134E54
8631 | PGS1 | PS9 >/< Block Off | 134E55
8632 | PGS1 | PS10 >/< Start On | 134E56
8633 | PGS1 | PS10 >/< Start Off | 134E57
8634 | PGS1 | PS10 >/< Trip On | 134E58
8635 | PGS1 | PS10 >/< Trip Off | 134E59
8636 | PGS1 | PS10 >/< Block On | 134E60
8637 | PGS1 | PS10 >/< Block Off | 134E61
8640 | EMON1 | I> (50) Detect On | 135E0
8641 | EMON1 | I> (50) Detect Off | 135E1
8642 | EMON1 | I0> (50N) Detect On | 135E2
8643 | EMON1 | I0> (50N) Detect Off | 135E3
8644 | EMON1 | Idir> (67) Detect On | 135E4
8645 | EMON1 | Idir> (67) Detect Off | 135E5
8646 | EMON1 | I0dir> (67N) Detect On | 135E6
8647 | EMON1 | I0dir> (67N) Detect Off | 135E7
8648 | EMON1 | I0Int> (67NT) Detect FWD On | 135E8
8649 | EMON1 | I0Int> (67NT) Detect FWD Off | 135E9
8650 | EMON1 | I0Int> (67NT) Detect REV On | 135E10
8651 | EMON1 | I0Int> (67NT) Detect REV Off | 135E11
8652 | EMON1 | U< (27) Undervoltage detected On | 135E12
8653 | EMON1 | U< (27) Undervoltage detected Off | 135E13
8654 | EMON1 | U< (27) No voltage detected On | 135E14
8655 | EMON1 | U< (27) No voltage detected Off | 135E15
8656 | EMON1 | U0> (59N) Overvoltage detected On | 135E16
8657 | EMON1 | U0> (59N) Overvoltage detected Off | 135E17
8658 | EMON1 | FL (21FL) Triggered On | 135E18
8659 | EMON1 | FL (21FL) Triggered On | 135E19
8832 | MBIO | ModuleA Ch1 Invalid On | 138E0
8833 | MBIO | ModuleA Ch1 Invalid Off | 138E1
8834 | MBIO | ModuleA Ch2 Invalid On | 138E2
8835 | MBIO | ModuleA Ch2 Invalid Off | 138E3
8836 | MBIO | ModuleA Ch3 Invalid On | 138E4
8837 | MBIO | ModuleA Ch3 Invalid Off | 138E5
8838 | MBIO | ModuleA Ch4 Invalid On | 138E6
8839 | MBIO | ModuleA Ch4 Invalid Off | 138E7
8840 | MBIO | ModuleA Ch5 Invalid On | 138E8
8841 | MBIO | ModuleA Ch5 Invalid Off | 138E9
8842 | MBIO | ModuleA Ch6 Invalid On | 138E10
8843 | MBIO | ModuleA Ch6 Invalid Off | 138E11
8844 | MBIO | ModuleA Ch7 Invalid On | 138E12
8845 | MBIO | ModuleA Ch7 Invalid Off | 138E13
8846 | MBIO | ModuleA Ch8 Invalid On | 138E14
8847 | MBIO | ModuleA Ch8 Invalid Off | 138E15
8848 | MBIO | ModuleB Ch1 Invalid On | 138E16
8849 | MBIO | ModuleB Ch1 Invalid Off | 138E17
8850 | MBIO | ModuleB Ch2 Invalid On | 138E18
8851 | MBIO | ModuleB Ch2 Invalid Off | 138E19
8852 | MBIO | ModuleB Ch3 Invalid On | 138E20
8853 | MBIO | ModuleB Ch3 Invalid Off | 138E21
8854 | MBIO | ModuleB Ch4 Invalid On | 138E22
8855 | MBIO | ModuleB Ch4 Invalid Off | 138E23
8856 | MBIO | ModuleB Ch5 Invalid On | 138E24
8857 | MBIO | ModuleB Ch5 Invalid Off | 138E25
8858 | MBIO | ModuleB Ch6 Invalid On | 138E26
8859 | MBIO | ModuleB Ch6 Invalid Off | 138E27
8860 | MBIO | ModuleB Ch7 Invalid On | 138E28
8861 | MBIO | ModuleB Ch7 Invalid Off | 138E29
8862 | MBIO | ModuleB Ch8 Invalid On | 138E30
8863 | MBIO | ModuleB Ch8 Invalid Off | 138E31
8864 | MBIO | ModuleC Ch1 Invalid On | 138E32
8865 | MBIO | ModuleC Ch1 Invalid Off | 138E33
8866 | MBIO | ModuleC Ch2 Invalid On | 138E34
8867 | MBIO | ModuleC Ch2 Invalid Off | 138E35
8868 | MBIO | ModuleC Ch3 Invalid On | 138E36
8869 | MBIO | ModuleC Ch3 Invalid Off | 138E37
8870 | MBIO | ModuleC Ch4 Invalid On | 138E38
8871 | MBIO | ModuleC Ch4 Invalid Off | 138E39
8872 | MBIO | ModuleC Ch5 Invalid On | 138E40
8873 | MBIO | ModuleC Ch5 Invalid Off | 138E41
8874 | MBIO | ModuleC Ch6 Invalid On | 138E42
8875 | MBIO | ModuleC Ch6 Invalid Off | 138E43
8876 | MBIO | ModuleC Ch7 Invalid On | 138E44
8877 | MBIO | ModuleC Ch7 Invalid Off | 138E45
8878 | MBIO | ModuleC Ch8 Invalid On | 138E46
8879 | MBIO | ModuleC Ch8 Invalid Off | 138E47
9536 | UIM2 | Start On | 149E0
9537 | UIM2 | Start Off | 149E1
9538 | UIM2 | Trip On | 149E2
9539 | UIM2 | Trip Off | 149E3
9540 | UIM2 | Block On | 149E4
9541 | UIM2 | Block Off | 149E5
9600 | OBJ6 | Object Intermediate | 150E0
9601 | OBJ6 | Object Open | 150E1
9602 | OBJ6 | Object Close | 150E2
9603 | OBJ6 | Object Bad | 150E3
9604 | OBJ6 | WD Intermediate | 150E4
9605 | OBJ6 | WD Out | 150E5
9606 | OBJ6 | WD In | 150E6
9607 | OBJ6 | WD Bad | 150E7
9608 | OBJ6 | Open Request On | 150E8
9609 | OBJ6 | Open Request Off | 150E9
9610 | OBJ6 | Open Command On | 150E10
9611 | OBJ6 | Open Command Off | 150E11
9612 | OBJ6 | Close Request On | 150E12
9613 | OBJ6 | Close Request Off | 150E13
9614 | OBJ6 | Close Command On | 150E14
9615 | OBJ6 | Close Command Off | 150E15
9616 | OBJ6 | Open Blocked On | 150E16
9617 | OBJ6 | Open Blocked Off | 150E17
9618 | OBJ6 | Close Blocked On | 150E18
9619 | OBJ6 | Close Blocked Off | 150E19
9620 | OBJ6 | Object Ready | 150E20
9621 | OBJ6 | Object Not Ready | 150E21
9622 | OBJ6 | Sync Ok | 150E22
9623 | OBJ6 | Sync Not Ok | 150E23
9624 | OBJ6 | Open Command Fail | 150E24
9625 | OBJ6 | Close Command Fail | 150E25
9626 | OBJ6 | Final Trip On | 150E26
9627 | OBJ6 | Final Trip Off | 150E27
9628 | OBJ6 | Contact Abrasion Alarm On | 150E28
9629 | OBJ6 | Contact Abrasion Alarm Off | 150E29
9630 | OBJ6 | Switch Operating Time Exceeded On | 150E30
9631 | OBJ6 | Switch Operating Time Exceeded Off | 150E31
9632 | OBJ6 | XCBR Loc On | 150E32
9633 | OBJ6 | XCBR Loc Off | 150E33
9634 | OBJ6 | XSWI Loc On | 150E34
9635 | OBJ6 | XSWI Loc Off | 150E35
9636 | OBJ6 | OBJ6 Cond monitoring Alarm 1 On | 150E36
9637 | OBJ6 | OBJ6 Cond monitoring Alarm 1 Off | 150E37
9638 | OBJ6 | OBJ6 Cond monitoring Alarm 2 On | 150E38
9639 | OBJ6 | OBJ6 Cond monitoring Alarm 2 Off | 150E39
9640 | OBJ6 | OBJ6 Trip Circuit Supervision On | 150E40
9641 | OBJ6 | OBJ6 Trip Circuit Supervision Off | 150E41
9664 | OBJ7 | Object Intermediate | 151E0
9665 | OBJ7 | Object Open | 151E1
9666 | OBJ7 | Object Close | 151E2
9667 | OBJ7 | Object Bad | 151E3
9668 | OBJ7 | WD Intermediate | 151E4
9669 | OBJ7 | WD Out | 151E5
9670 | OBJ7 | WD In | 151E6
9671 | OBJ7 | WD Bad | 151E7
9672 | OBJ7 | Open Request On | 151E8
9673 | OBJ7 | Open Request Off | 151E9
9674 | OBJ7 | Open Command On | 151E10
9675 | OBJ7 | Open Command Off | 151E11
9676 | OBJ7 | Close Request On | 151E12
9677 | OBJ7 | Close Request Off | 151E13
9678 | OBJ7 | Close Command On | 151E14
9679 | OBJ7 | Close Command Off | 151E15
9680 | OBJ7 | Open Blocked On | 151E16
9681 | OBJ7 | Open Blocked Off | 151E17
9682 | OBJ7 | Close Blocked On | 151E18
9683 | OBJ7 | Close Blocked Off | 151E19
9684 | OBJ7 | Object Ready | 151E20
9685 | OBJ7 | Object Not Ready | 151E21
9686 | OBJ7 | Sync Ok | 151E22
9687 | OBJ7 | Sync Not Ok | 151E23
9688 | OBJ7 | Open Command Fail | 151E24
9689 | OBJ7 | Close Command Fail | 151E25
9690 | OBJ7 | Final Trip On | 151E26
9691 | OBJ7 | Final Trip Off | 151E27
9692 | OBJ7 | Contact Abrasion Alarm On | 151E28
9693 | OBJ7 | Contact Abrasion Alarm Off | 151E29
9694 | OBJ7 | Switch Operating Time Exceeded On | 151E30
9695 | OBJ7 | Switch Operating Time Exceeded Off | 151E31
9696 | OBJ7 | XCBR Loc On | 151E32
9697 | OBJ7 | XCBR Loc Off | 151E33
9698 | OBJ7 | XSWI Loc On | 151E34
9699 | OBJ7 | XSWI Loc Off | 151E35
9700 | OBJ7 | OBJ7 Cond monitoring Alarm 1 On | 151E36
9701 | OBJ7 | OBJ7 Cond monitoring Alarm 1 Off | 151E37
9702 | OBJ7 | OBJ7 Cond monitoring Alarm 2 On | 151E38
9703 | OBJ7 | OBJ7 Cond monitoring Alarm 2 Off | 151E39
9704 | OBJ7 | OBJ7 Trip Circuit Supervision On | 151E40
9705 | OBJ7 | OBJ7 Trip Circuit Supervision Off | 151E41
9728 | OBJ8 | Object Intermediate | 152E0
9729 | OBJ8 | Object Open | 152E1
9730 | OBJ8 | Object Close | 152E2
9731 | OBJ8 | Object Bad | 152E3
9732 | OBJ8 | WD Intermediate | 152E4
9733 | OBJ8 | WD Out | 152E5
9734 | OBJ8 | WD In | 152E6
9735 | OBJ8 | WD Bad | 152E7
9736 | OBJ8 | Open Request On | 152E8
9737 | OBJ8 | Open Request Off | 152E9
9738 | OBJ8 | Open Command On | 152E10
9739 | OBJ8 | Open Command Off | 152E11
9740 | OBJ8 | Close Request On | 152E12
9741 | OBJ8 | Close Request Off | 152E13
9742 | OBJ8 | Close Command On | 152E14
9743 | OBJ8 | Close Command Off | 152E15
9744 | OBJ8 | Open Blocked On | 152E16
9745 | OBJ8 | Open Blocked Off | 152E17
9746 | OBJ8 | Close Blocked On | 152E18
9747 | OBJ8 | Close Blocked Off | 152E19
9748 | OBJ8 | Object Ready | 152E20
9749 | OBJ8 | Object Not Ready | 152E21
9750 | OBJ8 | Sync Ok | 152E22
9751 | OBJ8 | Sync Not Ok | 152E23
9752 | OBJ8 | Open Command Fail | 152E24
9753 | OBJ8 | Close Command Fail | 152E25
9754 | OBJ8 | Final Trip On | 152E26
9755 | OBJ8 | Final Trip Off | 152E27
9756 | OBJ8 | Contact Abrasion Alarm On | 152E28
9757 | OBJ8 | Contact Abrasion Alarm Off | 152E29
9758 | OBJ8 | Switch Operating Time Exceeded On | 152E30
9759 | OBJ8 | Switch Operating Time Exceeded Off | 152E31
9760 | OBJ8 | XCBR Loc On | 152E32
9761 | OBJ8 | XCBR Loc Off | 152E33
9762 | OBJ8 | XSWI Loc On | 152E34
9763 | OBJ8 | XSWI Loc Off | 152E35
9764 | OBJ8 | OBJ8 Cond monitoring Alarm 1 On | 152E36
9765 | OBJ8 | OBJ8 Cond monitoring Alarm 1 Off | 152E37
9766 | OBJ8 | OBJ8 Cond monitoring Alarm 2 On | 152E38
9767 | OBJ8 | OBJ8 Cond monitoring Alarm 2 Off | 152E39
9768 | OBJ8 | OBJ8 Trip Circuit Supervision On | 152E40
9769 | OBJ8 | OBJ8 Trip Circuit Supervision Off | 152E41
9792 | OBJ9 | Object Intermediate | 153E0
9793 | OBJ9 | Object Open | 153E1
9794 | OBJ9 | Object Close | 153E2
9795 | OBJ9 | Object Bad | 153E3
9796 | OBJ9 | WD Intermediate | 153E4
9797 | OBJ9 | WD Out | 153E5
9798 | OBJ9 | WD In | 153E6
9799 | OBJ9 | WD Bad | 153E7
9800 | OBJ9 | Open Request On | 153E8
9801 | OBJ9 | Open Request Off | 153E9
9802 | OBJ9 | Open Command On | 153E10
9803 | OBJ9 | Open Command Off | 153E11
9804 | OBJ9 | Close Request On | 153E12
9805 | OBJ9 | Close Request Off | 153E13
9806 | OBJ9 | Close Command On | 153E14
9807 | OBJ9 | Close Command Off | 153E15
9808 | OBJ9 | Open Blocked On | 153E16
9809 | OBJ9 | Open Blocked Off | 153E17
9810 | OBJ9 | Close Blocked On | 153E18
9811 | OBJ9 | Close Blocked Off | 153E19
9812 | OBJ9 | Object Ready | 153E20
9813 | OBJ9 | Object Not Ready | 153E21
9814 | OBJ9 | Sync Ok | 153E22
9815 | OBJ9 | Sync Not Ok | 153E23
9816 | OBJ9 | Open Command Fail | 153E24
9817 | OBJ9 | Close Command Fail | 153E25
9818 | OBJ9 | Final Trip On | 153E26
9819 | OBJ9 | Final Trip Off | 153E27
9820 | OBJ9 | Contact Abrasion Alarm On | 153E28
9821 | OBJ9 | Contact Abrasion Alarm Off | 153E29
9822 | OBJ9 | Switch Operating Time Exceeded On | 153E30
9823 | OBJ9 | Switch Operating Time Exceeded Off | 153E31
9824 | OBJ9 | XCBR Loc On | 153E32
9825 | OBJ9 | XCBR Loc Off | 153E33
9826 | OBJ9 | XSWI Loc On | 153E34
9827 | OBJ9 | XSWI Loc Off | 153E35
9828 | OBJ9 | OBJ9 Cond monitoring Alarm 1 On | 153E36
9829 | OBJ9 | OBJ9 Cond monitoring Alarm 1 Off | 153E37
9830 | OBJ9 | OBJ9 Cond monitoring Alarm 2 On | 153E38
9831 | OBJ9 | OBJ9 Cond monitoring Alarm 2 Off | 153E39
9832 | OBJ9 | OBJ9 Trip Circuit Supervision On | 153E40
9833 | OBJ9 | OBJ9 Trip Circuit Supervision Off | 153E41
9856 | OBJ10 | Object Intermediate | 154E0
9857 | OBJ10 | Object Open | 154E1
9858 | OBJ10 | Object Close | 154E2
9859 | OBJ10 | Object Bad | 154E3
9860 | OBJ10 | WD Intermediate | 154E4
9861 | OBJ10 | WD Out | 154E5
9862 | OBJ10 | WD In | 154E6
9863 | OBJ10 | WD Bad | 154E7
9864 | OBJ10 | Open Request On | 154E8
9865 | OBJ10 | Open Request Off | 154E9
9866 | OBJ10 | Open Command On | 154E10
9867 | OBJ10 | Open Command Off | 154E11
9868 | OBJ10 | Close Request On | 154E12
9869 | OBJ10 | Close Request Off | 154E13
9870 | OBJ10 | Close Command On | 154E14
9871 | OBJ10 | Close Command Off | 154E15
9872 | OBJ10 | Open Blocked On | 154E16
9873 | OBJ10 | Open Blocked Off | 154E17
9874 | OBJ10 | Close Blocked On | 154E18
9875 | OBJ10 | Close Blocked Off | 154E19
9876 | OBJ10 | Object Ready | 154E20
9877 | OBJ10 | Object Not Ready | 154E21
9878 | OBJ10 | Sync Ok | 154E22
9879 | OBJ10 | Sync Not Ok | 154E23
9880 | OBJ10 | Open Command Fail | 154E24
9881 | OBJ10 | Close Command Fail | 154E25
9882 | OBJ10 | Final Trip On | 154E26
9883 | OBJ10 | Final Trip Off | 154E27
9884 | OBJ10 | Contact Abrasion Alarm On | 154E28
9885 | OBJ10 | Contact Abrasion Alarm Off | 154E29
9886 | OBJ10 | Switch Operating Time Exceeded On | 154E30
9887 | OBJ10 | Switch Operating Time Exceeded Off | 154E31
9888 | OBJ10 | XCBR Loc On | 154E32
9889 | OBJ10 | XCBR Loc Off | 154E33
9890 | OBJ10 | XSWI Loc On | 154E34
9891 | OBJ10 | XSWI Loc Off | 154E35
9892 | OBJ10 | OBJ10 Cond monitoring Alarm 1 On | 154E36
9893 | OBJ10 | OBJ10 Cond monitoring Alarm 1 Off | 154E37
9894 | OBJ10 | OBJ10 Cond monitoring Alarm 2 On | 154E38
9895 | OBJ10 | OBJ10 Cond monitoring Alarm 2 Off | 154E39
9896 | OBJ10 | OBJ10 Trip Circuit Supervision On | 154E40
9897 | OBJ10 | OBJ10 Trip Circuit Supervision Off | 154E41
9920 | VJP1 | Block On | 155E0
9921 | VJP1 | Block Off | 155E1
9922 | VJP1 | Trip On | 155E2
9923 | VJP1 | Trip Off | 155E3
9924 | VJP1 | Alarm On | 155E4
9925 | VJP1 | Alarm Off | 155E5
9984 | GMAG | FCL on limit On | 156E0
9985 | GMAG | FCL on limit Off | 156E1
9986 | GMAG | UEL in operation On | 156E2
9987 | GMAG | UEL in operation Off | 156E3
9988 | GMAG | SCL Overexcitation On | 156E4
9989 | GMAG | SCL Overexcitation Off | 156E5
9990 | GMAG | SCL Underexcitation On | 156E6
9991 | GMAG | SCL Underexcitation Off | 156E7
9992 | GMAG | High IP On | 156E8
9993 | GMAG | High IP Off | 156E9
9994 | GMAG | Inst FCL On | 156E10
9995 | GMAG | Inst FCL Off | 156E11
9996 | GMAG | Low supply voltage On | 156E12
9997 | GMAG | Low supply voltage Off | 156E13
9998 | GMAG | FCR Mode On | 156E14
9999 | GMAG | FCR Mode Off | 156E15
10000 | GMAG | AVR Mode On | 156E16
10001 | GMAG | AVR Mode Off | 156E17
10002 | GMAG | Low meas volt On | 156E18
10003 | GMAG | Low meas volt Off | 156E19
10004 | GMAG | IGBT Shorted On | 156E20
10005 | GMAG | IGBT Shorted Off | 156E21
10006 | GMAG | PWM Enable On | 156E22
10007 | GMAG | PWM Enable Off | 156E23
10008 | GMAG | PWM DO1 On | 156E24
10009 | GMAG | PWM DO1 Off | 156E25
10010 | GMAG | PWM DO2 On | 156E26
10011 | GMAG | PWM DO2 Off | 156E27
10012 | GMAG | Rectifier trip On | 156E28
10013 | GMAG | Rectifier trip Off | 156E29
10014 | GMAG | Temp high breaker 1 On | 156E30
10015 | GMAG | Temp high breaker 1 Off | 156E31
10016 | GMAG | Temp high breaker 2 On | 156E32
10017 | GMAG | Temp high breaker 2 Off | 156E33
10018 | GMAG | Excitation On | 156E34
10019 | GMAG | Exc On Cmd Off | 156E35
10020 | GMAG | Excitation Off | 156E36
10021 | GMAG | Exc Off Cmd Off | 156E37
10022 | GMAG | Diode fault On | 156E38
10023 | GMAG | Diode fault Off | 156E39
10024 | GMAG | Overcurrent On | 156E40
10025 | GMAG | Overcurrent Off | 156E41
10026 | GMAG | PWM DI1 On | 156E42
10027 | GMAG | PWM DI1 Off | 156E43
10028 | GMAG | PWM DI2 On | 156E44
10029 | GMAG | PWM DI2 Off | 156E45
10030 | GMAG | PWM DI3 On | 156E46
10031 | GMAG | PWM DI3 Off | 156E47
10032 | GMAG | PWM DI4 On | 156E48
10033 | GMAG | PWM DI4 Off | 156E49
10034 | GMAG | PWM DI5 On | 156E50
10035 | GMAG | PWM DI5 Off | 156E51
10036 | GMAG | PWM DI6 On | 156E52
10037 | GMAG | PWM DI6 Off | 156E53
10038 | GMAG | PWM DI7 On | 156E54
10039 | GMAG | PWM DI7 Off | 156E55
10040 | GMAG | PWM DI8 On | 156E56
10041 | GMAG | PWM DI8 Off | 156E57
10048 | GMAG1 | Synchronised On | 157E0
10049 | GMAG1 | Synchronised Off | 157E1
10050 | GMAG1 | Islandmode On | 157E2
10051 | GMAG1 | Islandmode Off | 157E3
10052 | GMAG1 | FB is Open On | 157E4
10053 | GMAG1 | FB is Open Off | 157E5
10054 | GMAG1 | FB is Closed On | 157E6
10055 | GMAG1 | FB is Closed Off | 157E7
10056 | GMAG1 | Field flashing On | 157E8
10057 | GMAG1 | Field flashing Off | 157E9
10058 | GMAG1 | Long field flashing On | 157E10
10059 | GMAG1 | Long field flashing Off | 157E11
10060 | GMAG1 | Test mode On | 157E12
10061 | GMAG1 | Test mode Off | 157E13
10062 | GMAG1 | Phase retard On | 157E14
10063 | GMAG1 | Phase retard Off | 157E15
10064 | GMAG1 | Reset On | 157E16
10065 | GMAG1 | Reset Off | 157E17
10066 | GMAG1 | Command AVR On | 157E18
10067 | GMAG1 | Command AVR Off | 157E19
10068 | GMAG1 | Command FCR On | 157E20
10069 | GMAG1 | Command FCR Off | 157E21
10070 | GMAG1 | Command MVar On | 157E22
10071 | GMAG1 | Command MVar Off | 157E23
10072 | GMAG1 | Command PF On | 157E24
10073 | GMAG1 | Command PF Off | 157E25
10074 | GMAG1 | Excitation run order On | 157E26
10075 | GMAG1 | Excitation run order Off | 157E27
10076 | GMAG1 | Increase On | 157E28
10077 | GMAG1 | Increase Off | 157E29
10078 | GMAG1 | Decrease On | 157E30
10079 | GMAG1 | Decrease Off | 157E31
10080 | GMAG1 | AVR Bus On | 157E32
10081 | GMAG1 | AVR Bus Off | 157E33
10082 | GMAG1 | FCR Bus On | 157E34
10083 | GMAG1 | FCR Bus Off | 157E35
10084 | GMAG1 | MVar Bus On | 157E36
10085 | GMAG1 | MVar Bus Off | 157E37
10086 | GMAG1 | PF Bus On | 157E38
10087 | GMAG1 | PF Bus Off | 157E39
10088 | GMAG1 | Overriding control On | 157E40
10089 | GMAG1 | Overriding control Off | 157E41
10090 | GMAG1 | Increase MVAR/PF On | 157E42
10091 | GMAG1 | Increase MVAR/PF Off | 157E43
10092 | GMAG1 | Decrease MVAR/PF On | 157E44
10093 | GMAG1 | Decrease MVAR/PF Off | 157E45
10094 | GMAG1 | Low Q error On | 157E46
10095 | GMAG1 | Low Q error Off | 157E47
10096 | GMAG1 | AVR ref on lowlim On | 157E48
10097 | GMAG1 | AVR ref on lowlim Off | 157E49
10098 | GMAG1 | AVR ref on highlim On | 157E50
10099 | GMAG1 | AVR ref on highlim Off | 157E51
10100 | GMAG1 | FCR ref on lowlim On | 157E52
10101 | GMAG1 | FCR ref on lowlim Off | 157E53
10102 | GMAG1 | FCR ref on highlim On | 157E54
10103 | GMAG1 | FCR ref on highlim Off | 157E55
10104 | GMAG1 | VHZ limit active On | 157E56
10105 | GMAG1 | VHZ limit active Off | 157E57
10106 | GMAG1 | Process panel activated On | 157E58
10107 | GMAG1 | Process panel activated Off | 157E59
10108 | GMAG1 | Parameters active On | 157E60
10109 | GMAG1 | Parameters active Off | 157E61
10110 | GMAG1 | Bus activated On | 157E62
10111 | GMAG1 | Bus activated Off | 157E63
10112 | GMAG2 | Reset and excitation off On | 158E0
10113 | GMAG2 | Reset and excitation off Off | 158E1
10114 | GMAG2 | Field breaker does not open On | 158E2
10115 | GMAG2 | Field breaker does not open Off | 158E3
10116 | GMAG2 | New reference start On | 158E4
10117 | GMAG2 | New reference start Off | 158E5
10118 | GMAG2 | GB is closed On | 158E6
10119 | GMAG2 | GB is closed Off | 158E7
10120 | GMAG2 | FB off GB on On | 158E8
10121 | GMAG2 | FB off GB on Off | 158E9
10122 | GMAG2 | Disturbed mode On | 158E10
10123 | GMAG2 | Disturbed mode Off | 158E11
10124 | GMAG2 | Disturbed mode pulse On | 158E12
10125 | GMAG2 | Disturbed mode pulse Off | 158E13
10126 | GMAG2 | Following line voltage On | 158E14
10127 | GMAG2 | Following line voltage Off | 158E15
10128 | GMAG2 | Test Square enable On | 158E16
10129 | GMAG2 | Test Square enable Off | 158E17
10130 | GMAG2 | Order open FB On | 158E18
10131 | GMAG2 | Order open FB Off | 158E19
10132 | GMAG2 | Order close FB On | 158E20
10133 | GMAG2 | Order close FB Off | 158E21
10134 | GMAG2 | Q unloaded On | 158E22
10135 | GMAG2 | Q unloaded Off | 158E23
10136 | GMAG2 | MVAR ref on high On | 158E24
10137 | GMAG2 | MVAR ref on high Off | 158E25
10138 | GMAG2 | MVAR ref on low On | 158E26
10139 | GMAG2 | MVAR ref on low Off | 158E27
10140 | GMAG2 | PF ref on high On | 158E28
10141 | GMAG2 | PF ref on high Off | 158E29
10142 | GMAG2 | PF ref on low On | 158E30
10143 | GMAG2 | PF ref on low Off | 158E31
10144 | GMAG2 | AVR start Ref On | 158E32
10145 | GMAG2 | AVR start Ref Off | 158E33
10146 | GMAG2 | FCR start Ref On | 158E34
10147 | GMAG2 | FCR start Ref Off | 158E35
10148 | GMAG2 | Unload MVAR On | 158E36
10149 | GMAG2 | Unload MVAR Off | 158E37
10150 | GMAG2 | PWM DO3 On | 158E38
10151 | GMAG2 | PWM DO3 Off | 158E39
10152 | GMAG2 | PWM DO4 On | 158E40
10153 | GMAG2 | PWM DO4 Off | 158E41
10154 | GMAG2 | MVAR Mode On | 158E42
10155 | GMAG2 | MVAR Mode Off | 158E43
10156 | GMAG2 | PF Mode On | 158E44
10157 | GMAG2 | PF Mode Off | 158E45
10158 | GMAG2 | PSS Enabled On | 158E46
10159 | GMAG2 | PSS Enabled Off | 158E47
10160 | GMAG2 | PSS Blocked On | 158E48
10161 | GMAG2 | PSS Blocked Off | 158E49
10176 | ALARM1 | Alarm 1 On (Alarm 1) | 159E0
10177 | ALARM1 | Alarm 1 Off (Alarm 1) | 159E1
10178 | ALARM1 | Alarm 2 On (Alarm 2) | 159E2
10179 | ALARM1 | Alarm 2 Off (Alarm 2) | 159E3
10180 | ALARM1 | Alarm 3 On (Alarm 3) | 159E4
10181 | ALARM1 | Alarm 3 Off (Alarm 3) | 159E5
10182 | ALARM1 | Alarm 4 On (Alarm 4) | 159E6
10183 | ALARM1 | Alarm 4 Off (Alarm 4) | 159E7
10184 | ALARM1 | Alarm 5 On (Alarm 5) | 159E8
10185 | ALARM1 | Alarm 5 Off (Alarm 5) | 159E9
10186 | ALARM1 | Alarm 6 On (Alarm 6) | 159E10
10187 | ALARM1 | Alarm 6 Off (Alarm 6) | 159E11
10188 | ALARM1 | Alarm 7 On (Alarm 7) | 159E12
10189 | ALARM1 | Alarm 7 Off (Alarm 7) | 159E13
10190 | ALARM1 | Alarm 8 On (Alarm 8) | 159E14
10191 | ALARM1 | Alarm 8 Off (Alarm 8) | 159E15
10192 | ALARM1 | Alarm 9 On (Alarm 9) | 159E16
10193 | ALARM1 | Alarm 9 Off (Alarm 9) | 159E17
10194 | ALARM1 | Alarm 10 On (Alarm 10) | 159E18
10195 | ALARM1 | Alarm 10 Off (Alarm 10) | 159E19
10196 | ALARM1 | Alarm 11 On (Alarm 11) | 159E20
10197 | ALARM1 | Alarm 11 Off (Alarm 11) | 159E21
10198 | ALARM1 | Alarm 12 On (Alarm 12) | 159E22
10199 | ALARM1 | Alarm 12 Off (Alarm 12) | 159E23
10200 | ALARM1 | Alarm 13 On (Alarm 13) | 159E24
10201 | ALARM1 | Alarm 13 Off (Alarm 13) | 159E25
10202 | ALARM1 | Alarm 14 On (Alarm 14) | 159E26
10203 | ALARM1 | Alarm 14 Off (Alarm 14) | 159E27
10204 | ALARM1 | Alarm 15 On (Alarm 15) | 159E28
10205 | ALARM1 | Alarm 15 Off (Alarm 15) | 159E29
10206 | ALARM1 | Alarm 16 On (Alarm 16) | 159E30
10207 | ALARM1 | Alarm 16 Off (Alarm 16) | 159E31
10208 | ALARM1 | Alarm 17 On (Alarm 17) | 159E32
10209 | ALARM1 | Alarm 17 Off (Alarm 17) | 159E33
10210 | ALARM1 | Alarm 18 On (Alarm 18) | 159E34
10211 | ALARM1 | Alarm 18 Off (Alarm 18) | 159E35
10212 | ALARM1 | Alarm 19 On (Alarm 19) | 159E36
10213 | ALARM1 | Alarm 19 Off (Alarm 19) | 159E37
10214 | ALARM1 | Alarm 20 On (Alarm 20) | 159E38
10215 | ALARM1 | Alarm 20 Off (Alarm 20) | 159E39
10216 | ALARM1 | Alarm 21 On (Alarm 21) | 159E40
10217 | ALARM1 | Alarm 21 Off (Alarm 21) | 159E41
10218 | ALARM1 | Alarm 22 On (Alarm 22) | 159E42
10219 | ALARM1 | Alarm 22 Off (Alarm 22) | 159E43
10220 | ALARM1 | Alarm 23 On (Alarm 23) | 159E44
10221 | ALARM1 | Alarm 23 Off (Alarm 23) | 159E45
10222 | ALARM1 | Alarm 24 On (Alarm 24) | 159E46
10223 | ALARM1 | Alarm 24 Off (Alarm 24) | 159E47
10224 | ALARM1 | Alarm 25 On (Alarm 25) | 159E48
10225 | ALARM1 | Alarm 25 Off (Alarm 25) | 159E49
10226 | ALARM1 | Alarm 26 On (Alarm 26) | 159E50
10227 | ALARM1 | Alarm 26 Off (Alarm 26) | 159E51
10228 | ALARM1 | Alarm 27 On (Alarm 27) | 159E52
10229 | ALARM1 | Alarm 27 Off (Alarm 27) | 159E53
10230 | ALARM1 | Alarm 28 On (Alarm 28) | 159E54
10231 | ALARM1 | Alarm 28 Off (Alarm 28) | 159E55
10232 | ALARM1 | Alarm 29 On (Alarm 29) | 159E56
10233 | ALARM1 | Alarm 29 Off (Alarm 29) | 159E57
10234 | ALARM1 | Alarm 30 On (Alarm 30) | 159E58
10235 | ALARM1 | Alarm 30 Off (Alarm 30) | 159E59
10236 | ALARM1 | Alarm 31 On (Alarm 31) | 159E60
10237 | ALARM1 | Alarm 31 Off (Alarm 31) | 159E61
10238 | ALARM1 | Alarm 32 On (Alarm 32) | 159E62
10239 | ALARM1 | Alarm 32 Off (Alarm 32) | 159E63
10240 | ALARM2 | Alarm 33 On (Alarm 33) | 160E0
10241 | ALARM2 | Alarm 33 Off (Alarm 33) | 160E1
10242 | ALARM2 | Alarm 34 On (Alarm 34) | 160E2
10243 | ALARM2 | Alarm 34 Off (Alarm 34) | 160E3
10244 | ALARM2 | Alarm 35 On (Alarm 35) | 160E4
10245 | ALARM2 | Alarm 35 Off (Alarm 35) | 160E5
10246 | ALARM2 | Alarm 36 On (Alarm 36) | 160E6
10247 | ALARM2 | Alarm 36 Off (Alarm 36) | 160E7
10248 | ALARM2 | Alarm 37 On (Alarm 37) | 160E8
10249 | ALARM2 | Alarm 37 Off (Alarm 37) | 160E9
10250 | ALARM2 | Alarm 38 On (Alarm 38) | 160E10
10251 | ALARM2 | Alarm 38 Off (Alarm 38) | 160E11
10252 | ALARM2 | Alarm 39 On (Alarm 39) | 160E12
10253 | ALARM2 | Alarm 39 Off (Alarm 39) | 160E13
10254 | ALARM2 | Alarm 40 On (Alarm 40) | 160E14
10255 | ALARM2 | Alarm 40 Off (Alarm 40) | 160E15
10256 | ALARM2 | Alarm 41 On (Alarm 41) | 160E16
10257 | ALARM2 | Alarm 41 Off (Alarm 41) | 160E17
10258 | ALARM2 | Alarm 42 On (Alarm 42) | 160E18
10259 | ALARM2 | Alarm 42 Off (Alarm 42) | 160E19
10260 | ALARM2 | Alarm 43 On (Alarm 43) | 160E20
10261 | ALARM2 | Alarm 43 Off (Alarm 43) | 160E21
10262 | ALARM2 | Alarm 44 On (Alarm 44) | 160E22
10263 | ALARM2 | Alarm 44 Off (Alarm 44) | 160E23
10264 | ALARM2 | Alarm 45 On (Alarm 45) | 160E24
10265 | ALARM2 | Alarm 45 Off (Alarm 45) | 160E25
10266 | ALARM2 | Alarm 46 On (Alarm 46) | 160E26
10267 | ALARM2 | Alarm 46 Off (Alarm 46) | 160E27
10268 | ALARM2 | Alarm 47 On (Alarm 47) | 160E28
10269 | ALARM2 | Alarm 47 Off (Alarm 47) | 160E29
10270 | ALARM2 | Alarm 48 On (Alarm 48) | 160E30
10271 | ALARM2 | Alarm 48 Off (Alarm 48) | 160E31
10272 | ALARM2 | Alarm 49 On (Alarm 49) | 160E32
10273 | ALARM2 | Alarm 49 Off (Alarm 49) | 160E33
10274 | ALARM2 | Alarm 50 On (Alarm 50) | 160E34
10275 | ALARM2 | Alarm 50 Off (Alarm 50) | 160E35
10276 | ALARM2 | Alarm 51 On (Alarm 51) | 160E36
10277 | ALARM2 | Alarm 51 Off (Alarm 51) | 160E37
10278 | ALARM2 | Alarm 52 On (Alarm 52) | 160E38
10279 | ALARM2 | Alarm 52 Off (Alarm 52) | 160E39
10280 | ALARM2 | Alarm 53 On (Alarm 53) | 160E40
10281 | ALARM2 | Alarm 53 Off (Alarm 53) | 160E41
10282 | ALARM2 | Alarm 54 On (Alarm 54) | 160E42
10283 | ALARM2 | Alarm 54 Off (Alarm 54) | 160E43
10284 | ALARM2 | Alarm 55 On (Alarm 55) | 160E44
10285 | ALARM2 | Alarm 55 Off (Alarm 55) | 160E45
10286 | ALARM2 | Alarm 56 On (Alarm 56) | 160E46
10287 | ALARM2 | Alarm 56 Off (Alarm 56) | 160E47
10288 | ALARM2 | Alarm 57 On (Alarm 57) | 160E48
10289 | ALARM2 | Alarm 57 Off (Alarm 57) | 160E49
10290 | ALARM2 | Alarm 58 On (Alarm 58) | 160E50
10291 | ALARM2 | Alarm 58 Off (Alarm 58) | 160E51
10292 | ALARM2 | Alarm 59 On (Alarm 59) | 160E52
10293 | ALARM2 | Alarm 59 Off (Alarm 59) | 160E53
10294 | ALARM2 | Alarm 60 On (Alarm 60) | 160E54
10295 | ALARM2 | Alarm 60 Off (Alarm 60) | 160E55
10296 | ALARM2 | Alarm 61 On (Alarm 61) | 160E56
10297 | ALARM2 | Alarm 61 Off (Alarm 61) | 160E57
10298 | ALARM2 | Alarm 62 On (Alarm 62) | 160E58
10299 | ALARM2 | Alarm 62 Off (Alarm 62) | 160E59
10300 | ALARM2 | Alarm 63 On (Alarm 63) | 160E60
10301 | ALARM2 | Alarm 63 Off (Alarm 63) | 160E61
10302 | ALARM2 | Alarm 64 On (Alarm 64) | 160E62
10303 | ALARM2 | Alarm 64 Off (Alarm 64) | 160E63
10304 | IAE1 | Start On | 161E0
10305 | IAE1 | Start Off | 161E1
10306 | IAE1 | Trip On | 161E2
10307 | IAE1 | Trip Off | 161E3
10308 | IAE1 | Block On | 161E4
10309 | IAE1 | Block Off | 161E5
10310 | IAE1 | Low Current On | 161E6
10311 | IAE1 | Low Current Off | 161E7
10312 | IAE1 | Low Voltage On | 161E8
10313 | IAE1 | Low Voltage On | 161E9
10368 | GSYN | Synchronizing Blocked On | 162E0
10369 | GSYN | Synchronizing Blocked Off | 162E1
10370 | GSYN | Synchronizing Running On | 162E2
10371 | GSYN | Synchronizing Running Off | 162E3
10372 | GSYN | Synchr. Increase Voltage On | 162E4
10373 | GSYN | Synchr. Increase Voltage Off | 162E5
10374 | GSYN | Synchr. Decrease Voltage On | 162E6
10375 | GSYN | Synchr. Decrease Voltage Off | 162E7
10376 | GSYN | Synchr. Increase Frequency On | 162E8
10377 | GSYN | Synchr. Increase Frequency Off | 162E9
10378 | GSYN | Synchr. Decrease Frequency On | 162E10
10379 | GSYN | Synchr. Decrease Frequency Off | 162E11
10380 | GSYN | Synchronizer BRK Close On | 162E12
10381 | GSYN | Synchronizer BRK Close Off | 162E13
10382 | GSYN | Synchronizer Long Sync. Time On | 162E14
10383 | GSYN | Synchronizer Long Sync. Time Off | 162E15
10384 | GSYN | Synchroswitch Close fail Re-init On | 162E16
10385 | GSYN | Synchroswitch Close fail Re-init Off | 162E17
10386 | GSYN | Synchroswitching requested On | 162E18
10387 | GSYN | Synchroswitching requested Off | 162E19
10388 | GSYN | GSYN Voltage Mag.Difference Ok | 162E20
10389 | GSYN | GSYN Voltage Mag.Difference Not Ok | 162E21
10390 | GSYN | GSYN Voltage Freq.Difference Ok | 162E22
10391 | GSYN | GSYN Voltage Freq.Difference Not Ok | 162E23
10392 | GSYN | GSYN Voltage Ang.Difference Ok | 162E24
10393 | GSYN | GSYN Voltage Ang.Difference Not Ok | 162E25
10394 | GSYN | GSYN Nets Standstill On | 162E26
10395 | GSYN | GSYN Nets Standstill Off | 162E27
10396 | GSYN | GSYN Nets Departing On | 162E28
10397 | GSYN | GSYN Nets Departing Off | 162E29
10398 | GSYN | GSYN Nets Enclosing On | 162E30
10399 | GSYN | GSYN Nets Enclosing Off | 162E31
10432 | VREC | Trigger On | 163E0
10433 | VREC | Trigger Off | 163E1
10496 | PWR1 | Start On | 164E0
10497 | PWR1 | Start Off | 164E1
10498 | PWR1 | Trip On | 164E2
10499 | PWR1 | Trip Off | 164E3
10500 | PWR1 | Block On | 164E4
10501 | PWR1 | Block Off | 164E5
10560 | PWR2 | Start On | 165E0
10561 | PWR2 | Start Off | 165E1
10562 | PWR2 | Trip On | 165E2
10563 | PWR2 | Trip Off | 165E3
10564 | PWR2 | Block On | 165E4
10565 | PWR2 | Block Off | 165E5
10624 | PWR3 | Start On | 166E0
10625 | PWR3 | Start Off | 166E1
10626 | PWR3 | Trip On | 166E2
10627 | PWR3 | Trip Off | 166E3
10628 | PWR3 | Block On | 166E4
10629 | PWR3 | Block Off | 166E5
10688 | PWR4 | Start On | 167E0
10689 | PWR4 | Start Off | 167E1
10690 | PWR4 | Trip On | 167E2
10691 | PWR4 | Trip Off | 167E3
10692 | PWR4 | Block On | 167E4
10693 | PWR4 | Block Off | 167E5
10752 | CIN6 | Intermediate | 168E0
10753 | CIN6 | Open | 168E1
10754 | CIN6 | Close | 168E2
10755 | CIN6 | Bad | 168E3
10816 | CIN7 | Intermediate | 169E0
10817 | CIN7 | Open | 169E1
10818 | CIN7 | Close | 169E2
10819 | CIN7 | Bad | 169E3
10880 | CIN8 | Intermediate | 170E0
10881 | CIN8 | Open | 170E1
10882 | CIN8 | Close | 170E2
10883 | CIN8 | Bad | 170E3
10944 | CIN9 | Intermediate | 171E0
10945 | CIN9 | Open | 171E1
10946 | CIN9 | Close | 171E2
10947 | CIN9 | Bad | 171E3
11008 | CIN10 | Intermediate | 172E0
11009 | CIN10 | Open | 172E1
11010 | CIN10 | Close | 172E2
11011 | CIN10 | Bad | 172E3
11072 | CIN11 | Intermediate | 173E0
11073 | CIN11 | Open | 173E1
11074 | CIN11 | Close | 173E2
11075 | CIN11 | Bad | 173E3
11136 | CIN12 | Intermediate | 174E0
11137 | CIN12 | Open | 174E1
11138 | CIN12 | Close | 174E2
11139 | CIN12 | Bad | 174E3
11200 | CIN13 | Intermediate | 175E0
11201 | CIN13 | Open | 175E1
11202 | CIN13 | Close | 175E2
11203 | CIN13 | Bad | 175E3
11264 | CIN14 | Intermediate | 176E0
11265 | CIN14 | Open | 176E1
11266 | CIN14 | Close | 176E2
11267 | CIN14 | Bad | 176E3
11328 | CIN15 | Intermediate | 177E0
11329 | CIN15 | Open | 177E1
11330 | CIN15 | Close | 177E2
11331 | CIN15 | Bad | 177E3
11392 | CIN16 | Intermediate | 178E0
11393 | CIN16 | Open | 178E1
11394 | CIN16 | Close | 178E2
11395 | CIN16 | Bad | 178E3
11456 | CIN17 | Intermediate | 179E0
11457 | CIN17 | Open | 179E1
11458 | CIN17 | Close | 179E2
11459 | CIN17 | Bad | 179E3
11520 | CIN18 | Intermediate | 180E0
11521 | CIN18 | Open | 180E1
11522 | CIN18 | Close | 180E2
11523 | CIN18 | Bad | 180E3
11584 | CIN19 | Intermediate | 181E0
11585 | CIN19 | Open | 181E1
11586 | CIN19 | Close | 181E2
11587 | CIN19 | Bad | 181E3
11648 | CIN20 | Intermediate | 182E0
11649 | CIN20 | Open | 182E1
11650 | CIN20 | Close | 182E2
11651 | CIN20 | Bad | 182E3
11712 | RHC1 | Running hour counter On | 183E0
11713 | RHC1 | Running hour counter Off | 183E1
11714 | RHC1 | Running hour counter cleared On | 183E2
11715 | RHC1 | Running hour counter cleared Off | 183E3
11776 | ALARM3 | Alarm 65 On (Alarm 65) | 184E0
11777 | ALARM3 | Alarm 65 Off (Alarm 65) | 184E1
11778 | ALARM3 | Alarm 66 On (Alarm 66) | 184E2
11779 | ALARM3 | Alarm 66 Off (Alarm 66) | 184E3
11780 | ALARM3 | Alarm 67 On (Alarm 67) | 184E4
11781 | ALARM3 | Alarm 67 Off (Alarm 67) | 184E5
11782 | ALARM3 | Alarm 68 On (Alarm 68) | 184E6
11783 | ALARM3 | Alarm 68 Off (Alarm 68) | 184E7
11784 | ALARM3 | Alarm 69 On (Alarm 69) | 184E8
11785 | ALARM3 | Alarm 69 Off (Alarm 69) | 184E9
11786 | ALARM3 | Alarm 70 On (Alarm 70) | 184E10
11787 | ALARM3 | Alarm 70 Off (Alarm 70) | 184E11
11788 | ALARM3 | Alarm 71 On (Alarm 71) | 184E12
11789 | ALARM3 | Alarm 71 Off (Alarm 71) | 184E13
11790 | ALARM3 | Alarm 72 On (Alarm 72) | 184E14
11791 | ALARM3 | Alarm 72 Off (Alarm 72) | 184E15
11792 | ALARM3 | Alarm 73 On (Alarm 73) | 184E16
11793 | ALARM3 | Alarm 73 Off (Alarm 73) | 184E17
11794 | ALARM3 | Alarm 74 On (Alarm 74) | 184E18
11795 | ALARM3 | Alarm 74 Off (Alarm 74) | 184E19
11796 | ALARM3 | Alarm 75 On (Alarm 75) | 184E20
11797 | ALARM3 | Alarm 75 Off (Alarm 75) | 184E21
11798 | ALARM3 | Alarm 76 On (Alarm 76) | 184E22
11799 | ALARM3 | Alarm 76 Off (Alarm 76) | 184E23
11800 | ALARM3 | Alarm 77 On (Alarm 77) | 184E24
11801 | ALARM3 | Alarm 77 Off (Alarm 77) | 184E25
11802 | ALARM3 | Alarm 78 On (Alarm 78) | 184E26
11803 | ALARM3 | Alarm 78 Off (Alarm 78) | 184E27
11804 | ALARM3 | Alarm 79 On (Alarm 79) | 184E28
11805 | ALARM3 | Alarm 79 Off (Alarm 79) | 184E29
11806 | ALARM3 | Alarm 80 On (Alarm 80) | 184E30
11807 | ALARM3 | Alarm 80 Off (Alarm 80) | 184E31
11808 | ALARM3 | Alarm 81 On (Alarm 81) | 184E32
11809 | ALARM3 | Alarm 81 Off (Alarm 81) | 184E33
11810 | ALARM3 | Alarm 82 On (Alarm 82) | 184E34
11811 | ALARM3 | Alarm 82 Off (Alarm 82) | 184E35
11812 | ALARM3 | Alarm 83 On (Alarm 83) | 184E36
11813 | ALARM3 | Alarm 83 Off (Alarm 83) | 184E37
11814 | ALARM3 | Alarm 84 On (Alarm 84) | 184E38
11815 | ALARM3 | Alarm 84 Off (Alarm 84) | 184E39
11816 | ALARM3 | Alarm 85 On (Alarm 85) | 184E40
11817 | ALARM3 | Alarm 85 Off (Alarm 85) | 184E41
11818 | ALARM3 | Alarm 86 On (Alarm 86) | 184E42
11819 | ALARM3 | Alarm 86 Off (Alarm 86) | 184E43
11820 | ALARM3 | Alarm 87 On (Alarm 87) | 184E44
11821 | ALARM3 | Alarm 87 Off (Alarm 87) | 184E45
11822 | ALARM3 | Alarm 88 On (Alarm 88) | 184E46
11823 | ALARM3 | Alarm 88 Off (Alarm 88) | 184E47
11824 | ALARM3 | Alarm 89 On (Alarm 89) | 184E48
11825 | ALARM3 | Alarm 89 Off (Alarm 89) | 184E49
11826 | ALARM3 | Alarm 90 On (Alarm 90) | 184E50
11827 | ALARM3 | Alarm 90 Off (Alarm 90) | 184E51
11828 | ALARM3 | Alarm 91 On (Alarm 91) | 184E52
11829 | ALARM3 | Alarm 91 Off (Alarm 91) | 184E53
11830 | ALARM3 | Alarm 92 On (Alarm 92) | 184E54
11831 | ALARM3 | Alarm 92 Off (Alarm 92) | 184E55
11832 | ALARM3 | Alarm 93 On (Alarm 93) | 184E56
11833 | ALARM3 | Alarm 93 Off (Alarm 93) | 184E57
11834 | ALARM3 | Alarm 94 On (Alarm 94) | 184E58
11835 | ALARM3 | Alarm 94 Off (Alarm 94) | 184E59
11836 | ALARM3 | Alarm 95 On (Alarm 95) | 184E60
11837 | ALARM3 | Alarm 95 Off (Alarm 95) | 184E61
11838 | ALARM3 | Alarm 96 On (Alarm 96) | 184E62
11839 | ALARM3 | Alarm 96 Off (Alarm 96) | 184E63
11840 | ALARM4 | Alarm 97 On (Alarm 97) | 185E0
11841 | ALARM4 | Alarm 97 Off (Alarm 97) | 185E1
11842 | ALARM4 | Alarm 98 On (Alarm 98) | 185E2
11843 | ALARM4 | Alarm 98 Off (Alarm 98) | 185E3
11844 | ALARM4 | Alarm 99 On (Alarm 99) | 185E4
11845 | ALARM4 | Alarm 99 Off (Alarm 99) | 185E5
11846 | ALARM4 | Alarm 100 On (Alarm 100) | 185E6
11847 | ALARM4 | Alarm 100 Off (Alarm 100) | 185E7
11848 | ALARM4 | Alarm 101 On (Alarm 101) | 185E8
11849 | ALARM4 | Alarm 101 Off (Alarm 101) | 185E9
11850 | ALARM4 | Alarm 102 On (Alarm 102) | 185E10
11851 | ALARM4 | Alarm 102 Off (Alarm 102) | 185E11
11852 | ALARM4 | Alarm 103 On (Alarm 103) | 185E12
11853 | ALARM4 | Alarm 103 Off (Alarm 103) | 185E13
11854 | ALARM4 | Alarm 104 On (Alarm 104) | 185E14
11855 | ALARM4 | Alarm 104 Off (Alarm 104) | 185E15
11856 | ALARM4 | Alarm 105 On (Alarm 105) | 185E16
11857 | ALARM4 | Alarm 105 Off (Alarm 105) | 185E17
11858 | ALARM4 | Alarm 106 On (Alarm 106) | 185E18
11859 | ALARM4 | Alarm 106 Off (Alarm 106) | 185E19
11860 | ALARM4 | Alarm 107 On (Alarm 107) | 185E20
11861 | ALARM4 | Alarm 107 Off (Alarm 107) | 185E21
11862 | ALARM4 | Alarm 108 On (Alarm 108) | 185E22
11863 | ALARM4 | Alarm 108 Off (Alarm 108) | 185E23
11864 | ALARM4 | Alarm 109 On (Alarm 109) | 185E24
11865 | ALARM4 | Alarm 109 Off (Alarm 109) | 185E25
11866 | ALARM4 | Alarm 110 On (Alarm 110) | 185E26
11867 | ALARM4 | Alarm 110 Off (Alarm 110) | 185E27
11868 | ALARM4 | Alarm 111 On (Alarm 111) | 185E28
11869 | ALARM4 | Alarm 111 Off (Alarm 111) | 185E29
11870 | ALARM4 | Alarm 112 On (Alarm 112) | 185E30
11871 | ALARM4 | Alarm 112 Off (Alarm 112) | 185E31
11872 | ALARM4 | Alarm 113 On (Alarm 113) | 185E32
11873 | ALARM4 | Alarm 113 Off (Alarm 113) | 185E33
11874 | ALARM4 | Alarm 114 On (Alarm 114) | 185E34
11875 | ALARM4 | Alarm 114 Off (Alarm 114) | 185E35
11876 | ALARM4 | Alarm 115 On (Alarm 115) | 185E36
11877 | ALARM4 | Alarm 115 Off (Alarm 115) | 185E37
11878 | ALARM4 | Alarm 116 On (Alarm 116) | 185E38
11879 | ALARM4 | Alarm 116 Off (Alarm 116) | 185E39
11880 | ALARM4 | Alarm 117 On (Alarm 117) | 185E40
11881 | ALARM4 | Alarm 117 Off (Alarm 117) | 185E41
11882 | ALARM4 | Alarm 118 On (Alarm 118) | 185E42
11883 | ALARM4 | Alarm 118 Off (Alarm 118) | 185E43
11884 | ALARM4 | Alarm 119 On (Alarm 119) | 185E44
11885 | ALARM4 | Alarm 119 Off (Alarm 119) | 185E45
11886 | ALARM4 | Alarm 120 On (Alarm 120) | 185E46
11887 | ALARM4 | Alarm 120 Off (Alarm 120) | 185E47
11888 | ALARM4 | Alarm 121 On (Alarm 121) | 185E48
11889 | ALARM4 | Alarm 121 Off (Alarm 121) | 185E49
11890 | ALARM4 | Alarm 122 On (Alarm 122) | 185E50
11891 | ALARM4 | Alarm 122 Off (Alarm 122) | 185E51
11892 | ALARM4 | Alarm 123 On (Alarm 123) | 185E52
11893 | ALARM4 | Alarm 123 Off (Alarm 123) | 185E53
11894 | ALARM4 | Alarm 124 On (Alarm 124) | 185E54
11895 | ALARM4 | Alarm 124 Off (Alarm 124) | 185E55
11896 | ALARM4 | Alarm 125 On (Alarm 125) | 185E56
11897 | ALARM4 | Alarm 125 Off (Alarm 125) | 185E57
11898 | ALARM4 | Alarm 126 On (Alarm 126) | 185E58
11899 | ALARM4 | Alarm 126 Off (Alarm 126) | 185E59
11900 | ALARM4 | Alarm 127 On (Alarm 127) | 185E60
11901 | ALARM4 | Alarm 127 Off (Alarm 127) | 185E61
11902 | ALARM4 | Alarm 128 On (Alarm 128) | 185E62
11903 | ALARM4 | Alarm 128 Off (Alarm 128) | 185E63
12096 | LDIF1 | Idb> Trip On | 189E0
12097 | LDIF1 | Idb> Trip Off | 189E1
12098 | LDIF1 | Idb> Blocked (ext) On | 189E2
12099 | LDIF1 | Idb> Blocked (ext) Off | 189E3
12100 | LDIF1 | Idi> Trip On | 189E4
12101 | LDIF1 | Idi> Trip Off | 189E5
12102 | LDIF1 | Idi> Blocked (ext) On | 189E6
12103 | LDIF1 | Idi> Blocked (ext) Off | 189E7
12104 | LDIF1 | 2.nd Harmonic Block On | 189E8
12105 | LDIF1 | 2.nd Harmonic Block Off | 189E9
12106 | LDIF1 | 5.th Harmonic Block On | 189E10
12107 | LDIF1 | 5.th Harmonic Block Off | 189E11
12108 | LDIF1 | L1 2.nd harm On | 189E12
12109 | LDIF1 | L1 2.nd harm Off | 189E13
12110 | LDIF1 | L2 2.nd harm On | 189E14
12111 | LDIF1 | L2 2.nd harm Off | 189E15
12112 | LDIF1 | L3 2.nd harm On | 189E16
12113 | LDIF1 | L3 2.nd harm Off | 189E17
12114 | LDIF1 | L1 5.th harm On | 189E18
12115 | LDIF1 | L1 5.th harm Off | 189E19
12116 | LDIF1 | L2 5.th harm On | 189E20
12117 | LDIF1 | L2 5.th harm Off | 189E21
12118 | LDIF1 | L3 5.th harm On | 189E22
12119 | LDIF1 | L3 5.th harm Off | 189E23
12160 | M1VT1 | Voltage memory enabled | 190E0
12161 | M1VT1 | Voltage memory disabled | 190E1
12162 | M1VT1 | Voltage low detected On | 190E2
12163 | M1VT1 | Voltage low detected Off | 190E3
12164 | M1VT1 | Current high detected On | 190E4
12165 | M1VT1 | Current high detected Off | 190E5
12166 | M1VT1 | Frequency tracked from CT On | 190E6
12167 | M1VT1 | Frequency tracked from CT Off | 190E7
12168 | M1VT1 | Using Voltage memory On | 190E8
12169 | M1VT1 | Using Voltage memory Off | 190E9
12170 | M1VT1 | Voltage memory blocked On | 190E10
12171 | M1VT1 | Voltage memory blocked Off | 190E11
12288 | NOCS1 | Start On | 192E0
12289 | NOCS1 | Start Off | 192E1
12290 | NOCS1 | Trip On | 192E2
12291 | NOCS1 | Trip Off | 192E3
12292 | NOCS1 | Block On | 192E4
12293 | NOCS1 | Block Off | 192E5
12294 | NOCS1 | L1 Start On | 192E6
12295 | NOCS1 | L1 Start Off | 192E7
12296 | NOCS1 | L2 Start On | 192E8
12297 | NOCS1 | L2 Start Off | 192E9
12298 | NOCS1 | L3 Start On | 192E10
12299 | NOCS1 | L3 Start Off | 192E11
12300 | NOCS1 | L1 Trip On | 192E12
12301 | NOCS1 | L1 Trip Off | 192E13
12302 | NOCS1 | L2 Trip On | 192E14
12303 | NOCS1 | L2 Trip Off | 192E15
12304 | NOCS1 | L3 Trip On | 192E16
12305 | NOCS1 | L3 Trip Off | 192E17
12352 | OBJS1 | Object A(L1) Intermediate | 193E0
12353 | OBJS1 | Object A(L1) Open | 193E1
12354 | OBJS1 | Object A(L1) Close | 193E2
12355 | OBJS1 | Object A(L1) Bad | 193E3
12356 | OBJS1 | Object B(L2) Open | 193E4
12357 | OBJS1 | Object B(L2) Close | 193E5
12358 | OBJS1 | Object B(L2) Bad | 193E6
12359 | OBJS1 | Object B(L2) Intermediate | 193E7
12360 | OBJS1 | Object C(L3) Open | 193E8
12361 | OBJS1 | Object C(L3) Close | 193E9
12362 | OBJS1 | Object C(L3) Bad | 193E10
12363 | OBJS1 | Object C(L3) Intermediate | 193E11
12364 | OBJS1 | WD Cart Intermediate | 193E12
12365 | OBJS1 | WD Cart Open | 193E13
12366 | OBJS1 | WD Cart Close | 193E14
12367 | OBJS1 | WD Cart Bad | 193E15
12368 | OBJS1 | Object A(L1) Open Command On | 193E16
12369 | OBJS1 | Object A(L1) Open Command Off | 193E17
12370 | OBJS1 | Object B(L2) Open Command On | 193E18
12371 | OBJS1 | Object B(L2) Open Command Off | 193E19
12372 | OBJS1 | Object C(L3) Open Command On | 193E20
12373 | OBJS1 | Object C(L3) Open Command Off | 193E21
12374 | OBJS1 | Close Command On | 193E22
12375 | OBJS1 | Close Command Off | 193E23
12376 | OBJS1 | Open Commands Blocked | 193E24
12377 | OBJS1 | Open Commands Allowed | 193E25
12378 | OBJS1 | Close Commands Blocked | 193E26
12379 | OBJS1 | Close Commands Allowed | 193E27
12380 | OBJS1 | Object Is Ready | 193E28
12381 | OBJS1 | Object Not Ready, Wait for Ready | 193E29
12382 | OBJS1 | Sync Is Ok | 193E30
12383 | OBJS1 | Sync Not Ok Wait for sync | 193E31
12384 | OBJS1 | Final Trip On | 193E32
12385 | OBJS1 | Final Trip Off | 193E33
12386 | OBJS1 | Open Command Fail On | 193E34
12387 | OBJS1 | Open Command Fail Off | 193E35
12388 | OBJS1 | Close Command Fail On | 193E36
12389 | OBJS1 | Close Command Fail Off | 193E37
12390 | OBJS1 | L1 Open Command Timeout On | 193E38
12391 | OBJS1 | L1 Open Command Timeout On | 193E39
12392 | OBJS1 | L2 Open Command Timeout On | 193E40
12393 | OBJS1 | L2 Open Command Timeout On | 193E41
12394 | OBJS1 | L3 Open Command Timeout On | 193E42
12395 | OBJS1 | L3 Open Command Timeout On | 193E43
12396 | OBJS1 | Close Command Timeout On | 193E44
12397 | OBJS1 | Close Command Timeout On | 193E45
12416 | NOCS2 | Start On | 194E0
12417 | NOCS2 | Start Off | 194E1
12418 | NOCS2 | Trip On | 194E2
12419 | NOCS2 | Trip Off | 194E3
12420 | NOCS2 | Block On | 194E4
12421 | NOCS2 | Block Off | 194E5
12422 | NOCS2 | L1 Start On | 194E6
12423 | NOCS2 | L1 Start Off | 194E7
12424 | NOCS2 | L2 Start On | 194E8
12425 | NOCS2 | L2 Start Off | 194E9
12426 | NOCS2 | L3 Start On | 194E10
12427 | NOCS2 | L3 Start Off | 194E11
12428 | NOCS2 | L1 Trip On | 194E12
12429 | NOCS2 | L1 Trip Off | 194E13
12430 | NOCS2 | L2 Trip On | 194E14
12431 | NOCS2 | L2 Trip Off | 194E15
12432 | NOCS2 | L3 Trip On | 194E16
12433 | NOCS2 | L3 Trip Off | 194E17
12480 | SGS2 | SG2 Enabled | 195E0
12481 | SGS2 | SG2 Disabled | 195E1
12482 | SGS2 | SG3 Enabled | 195E2
12483 | SGS2 | SG3 Disabled | 195E3
12484 | SGS2 | SG4 Enabled | 195E4
12485 | SGS2 | SG4 Disabled | 195E5
12486 | SGS2 | SG5 Enabled | 195E6
12487 | SGS2 | SG5 Disabled | 195E7
12488 | SGS2 | SG6 Enabled | 195E8
12489 | SGS2 | SG6 Disabled | 195E9
12490 | SGS2 | SG7 Enabled | 195E10
12491 | SGS2 | SG7 Disabled | 195E11
12492 | SGS2 | SG8 Enabled | 195E12
12493 | SGS2 | SG8 Disabled | 195E13
12494 | SGS2 | SG1 Request On | 195E14
12495 | SGS2 | SG1 Request Off | 195E15
12496 | SGS2 | SG2 Request On | 195E16
12497 | SGS2 | SG2 Request Off | 195E17
12498 | SGS2 | SG3 Request On | 195E18
12499 | SGS2 | SG3 Request Off | 195E19
12500 | SGS2 | SG4 Request On | 195E20
12501 | SGS2 | SG4 Request Off | 195E21
12502 | SGS2 | SG5 Request On | 195E22
12503 | SGS2 | SG5 Request Off | 195E23
12504 | SGS2 | SG6 Request On | 195E24
12505 | SGS2 | SG6 Request Off | 195E25
12506 | SGS2 | SG7 Request On | 195E26
12507 | SGS2 | SG7 Request Off | 195E27
12508 | SGS2 | SG8 Request On | 195E28
12509 | SGS2 | SG8 Request Off | 195E29
12510 | SGS2 | Remote Change SG Req On | 195E30
12511 | SGS2 | Remote Change SG Req Off | 195E31
12512 | SGS2 | Local Change SG Req On | 195E32
12513 | SGS2 | Local Change SG Req On | 195E33
12514 | SGS2 | Force Change SG On | 195E34
12515 | SGS2 | Force Change SG Off | 195E35
12516 | SGS2 | SG Req. Fail Not configured SG On | 195E36
12517 | SGS2 | SG Req. Fail Not configured SG On | 195E37
12518 | SGS2 | Force Req. Fail Force not On | 195E38
12519 | SGS2 | Force Req. Fail Off | 195E39
12520 | SGS2 | SG Req. Fail Lower priority Req. On | 195E40
12521 | SGS2 | SG Req. Fail Lower priority Req. Off | 195E41
12522 | SGS2 | SG1 Active On | 195E42
12523 | SGS2 | SG1 Active Off | 195E43
12524 | SGS2 | SG2 Active On | 195E44
12525 | SGS2 | SG2 Active Off | 195E45
12526 | SGS2 | SG3 Active On | 195E46
12527 | SGS2 | SG3 Active Off | 195E47
12528 | SGS2 | SG4 Active On | 195E48
12529 | SGS2 | SG4 Active Off | 195E49
12530 | SGS2 | SG5 Active On | 195E50
12531 | SGS2 | SG5 Active Off | 195E51
12532 | SGS2 | SG6 Active On | 195E52
12533 | SGS2 | SG6 Active Off | 195E53
12534 | SGS2 | SG7 Active On | 195E54
12535 | SGS2 | SG7 Active Off | 195E55
12536 | SGS2 | SG8 Active On | 195E56
12537 | SGS2 | SG8 Active Off | 195E57
12544 | URX1 | Start On | 196E0
12545 | URX1 | Start Off | 196E1
12546 | URX1 | Trip On | 196E2
12547 | URX1 | Trip Off | 196E3
12548 | URX1 | Block On | 196E4
12549 | URX1 | Block Off | 196E5
12608 | URX2 | Start On | 197E0
12609 | URX2 | Start Off | 197E1
12610 | URX2 | Trip On | 197E2
12611 | URX2 | Trip Off | 197E3
12612 | URX2 | Block On | 197E4
12613 | URX2 | Block Off | 197E5
12736 | MGWB1 | On Bit 1 (Acq.Bit.1) | 199E0
12737 | MGWB1 | Off Bit 1 (Acq.Bit.1) | 199E1
12738 | MGWB1 | On Bit 2 (Acq.Bit.2) | 199E2
12739 | MGWB1 | Off Bit 2 (Acq.Bit.2) | 199E3
12740 | MGWB1 | On Bit 3 (Acq.Bit.3) | 199E4
12741 | MGWB1 | Off Bit 3 (Acq.Bit.3) | 199E5
12742 | MGWB1 | On Bit 4 (Acq.Bit.4) | 199E6
12743 | MGWB1 | Off Bit 4 (Acq.Bit.4) | 199E7
12744 | MGWB1 | On Bit 5 (Acq.Bit.5) | 199E8
12745 | MGWB1 | Off Bit 5 (Acq.Bit.5) | 199E9
12746 | MGWB1 | On Bit 6 (Acq.Bit.6) | 199E10
12747 | MGWB1 | Off Bit 6 (Acq.Bit.6) | 199E11
12748 | MGWB1 | On Bit 7 (Acq.Bit.7) | 199E12
12749 | MGWB1 | Off Bit 7 (Acq.Bit.7) | 199E13
12750 | MGWB1 | On Bit 8 (Acq.Bit.8) | 199E14
12751 | MGWB1 | Off Bit 8 (Acq.Bit.8) | 199E15
12752 | MGWB1 | On Bit 9 (Acq.Bit.9) | 199E16
12753 | MGWB1 | Off Bit 9 (Acq.Bit.9) | 199E17
12754 | MGWB1 | On Bit 10 (Acq.Bit.10) | 199E18
12755 | MGWB1 | Off Bit 10 (Acq.Bit.10) | 199E19
12756 | MGWB1 | On Bit 11 (Acq.Bit.11) | 199E20
12757 | MGWB1 | Off Bit 11 (Acq.Bit.11) | 199E21
12758 | MGWB1 | On Bit 12 (Acq.Bit.12) | 199E22
12759 | MGWB1 | Off Bit 12 (Acq.Bit.12) | 199E23
12760 | MGWB1 | On Bit 13 (Acq.Bit.13) | 199E24
12761 | MGWB1 | Off Bit 13 (Acq.Bit.13) | 199E25
12762 | MGWB1 | On Bit 14 (Acq.Bit.14) | 199E26
12763 | MGWB1 | Off Bit 14 (Acq.Bit.14) | 199E27
12764 | MGWB1 | On Bit 15 (Acq.Bit.15) | 199E28
12765 | MGWB1 | Off Bit 15 (Acq.Bit.15) | 199E29
12766 | MGWB1 | On Bit 16 (Acq.Bit.16) | 199E30
12767 | MGWB1 | Off Bit 16 (Acq.Bit.16) | 199E31
12768 | MGWB1 | On Bit 17 (Acq.Bit.17) | 199E32
12769 | MGWB1 | Off Bit 17 (Acq.Bit.17) | 199E33
12770 | MGWB1 | On Bit 18 (Acq.Bit.18) | 199E34
12771 | MGWB1 | Off Bit 18 (Acq.Bit.18) | 199E35
12772 | MGWB1 | On Bit 19 (Acq.Bit.19) | 199E36
12773 | MGWB1 | Off Bit 19 (Acq.Bit.19) | 199E37
12774 | MGWB1 | On Bit 20 (Acq.Bit.20) | 199E38
12775 | MGWB1 | Off Bit 20 (Acq.Bit.20) | 199E39
12776 | MGWB1 | On Bit 21 (Acq.Bit.21) | 199E40
12777 | MGWB1 | Off Bit 21 (Acq.Bit.21) | 199E41
12778 | MGWB1 | On Bit 22 (Acq.Bit.22) | 199E42
12779 | MGWB1 | Off Bit 22 (Acq.Bit.22) | 199E43
12780 | MGWB1 | On Bit 23 (Acq.Bit.23) | 199E44
12781 | MGWB1 | Off Bit 23 (Acq.Bit.23) | 199E45
12782 | MGWB1 | On Bit 24 (Acq.Bit.24) | 199E46
12783 | MGWB1 | Off Bit 24 (Acq.Bit.24) | 199E47
12784 | MGWB1 | On Bit 25 (Acq.Bit.25) | 199E48
12785 | MGWB1 | Off Bit 25 (Acq.Bit.25) | 199E49
12786 | MGWB1 | On Bit 26 (Acq.Bit.26) | 199E50
12787 | MGWB1 | Off Bit 26 (Acq.Bit.26) | 199E51
12788 | MGWB1 | On Bit 27 (Acq.Bit.27) | 199E52
12789 | MGWB1 | Off Bit 27 (Acq.Bit.27) | 199E53
12790 | MGWB1 | On Bit 28 (Acq.Bit.28) | 199E54
12791 | MGWB1 | Off Bit 28 (Acq.Bit.28) | 199E55
12792 | MGWB1 | On Bit 29 (Acq.Bit.29) | 199E56
12793 | MGWB1 | Off Bit 29 (Acq.Bit.29) | 199E57
12794 | MGWB1 | On Bit 30 (Acq.Bit.30) | 199E58
12795 | MGWB1 | Off Bit 30 (Acq.Bit.30) | 199E59
12796 | MGWB1 | On Bit 31 (Acq.Bit.31) | 199E60
12797 | MGWB1 | Off Bit 31 (Acq.Bit.31) | 199E61
12798 | MGWB1 | On Bit 32 (Acq.Bit.32) | 199E62
12799 | MGWB1 | Off Bit 32 (Acq.Bit.32) | 199E63
12800 | MGWB2 | On Bit 33 (Acq.Bit.33) | 200E0
12801 | MGWB2 | Off Bit 33 (Acq.Bit.33) | 200E1
12802 | MGWB2 | On Bit 34 (Acq.Bit.34) | 200E2
12803 | MGWB2 | Off Bit 34 (Acq.Bit.34) | 200E3
12804 | MGWB2 | On Bit 35 (Acq.Bit.35) | 200E4
12805 | MGWB2 | Off Bit 35 (Acq.Bit.35) | 200E5
12806 | MGWB2 | On Bit 36 (Acq.Bit.36) | 200E6
12807 | MGWB2 | Off Bit 36 (Acq.Bit.36) | 200E7
12808 | MGWB2 | On Bit 37 (Acq.Bit.37) | 200E8
12809 | MGWB2 | Off Bit 37 (Acq.Bit.37) | 200E9
12810 | MGWB2 | On Bit 38 (Acq.Bit.38) | 200E10
12811 | MGWB2 | Off Bit 38 (Acq.Bit.38) | 200E11
12812 | MGWB2 | On Bit 39 (Acq.Bit.39) | 200E12
12813 | MGWB2 | Off Bit 39 (Acq.Bit.39) | 200E13
12814 | MGWB2 | On Bit 40 (Acq.Bit.40) | 200E14
12815 | MGWB2 | Off Bit 40 (Acq.Bit.40) | 200E15
12816 | MGWB2 | On Bit 41 (Acq.Bit.41) | 200E16
12817 | MGWB2 | Off Bit 41 (Acq.Bit.41) | 200E17
12818 | MGWB2 | On Bit 42 (Acq.Bit.42) | 200E18
12819 | MGWB2 | Off Bit 42 (Acq.Bit.42) | 200E19
12820 | MGWB2 | On Bit 43 (Acq.Bit.43) | 200E20
12821 | MGWB2 | Off Bit 43 (Acq.Bit.43) | 200E21
12822 | MGWB2 | On Bit 44 (Acq.Bit.44) | 200E22
12823 | MGWB2 | Off Bit 44 (Acq.Bit.44) | 200E23
12824 | MGWB2 | On Bit 45 (Acq.Bit.45) | 200E24
12825 | MGWB2 | Off Bit 45 (Acq.Bit.45) | 200E25
12826 | MGWB2 | On Bit 46 (Acq.Bit.46) | 200E26
12827 | MGWB2 | Off Bit 46 (Acq.Bit.46) | 200E27
12828 | MGWB2 | On Bit 47 (Acq.Bit.47) | 200E28
12829 | MGWB2 | Off Bit 47 (Acq.Bit.47) | 200E29
12830 | MGWB2 | On Bit 48 (Acq.Bit.48) | 200E30
12831 | MGWB2 | Off Bit 48 (Acq.Bit.48) | 200E31
12832 | MGWB2 | On Bit 49 (Acq.Bit.49) | 200E32
12833 | MGWB2 | Off Bit 49 (Acq.Bit.49) | 200E33
12834 | MGWB2 | On Bit 50 (Acq.Bit.50) | 200E34
12835 | MGWB2 | Off Bit 50 (Acq.Bit.50) | 200E35
12836 | MGWB2 | On Bit 51 (Acq.Bit.51) | 200E36
12837 | MGWB2 | Off Bit 51 (Acq.Bit.51) | 200E37
12838 | MGWB2 | On Bit 52 (Acq.Bit.52) | 200E38
12839 | MGWB2 | Off Bit 52 (Acq.Bit.52) | 200E39
12840 | MGWB2 | On Bit 53 (Acq.Bit.53) | 200E40
12841 | MGWB2 | Off Bit 53 (Acq.Bit.53) | 200E41
12842 | MGWB2 | On Bit 54 (Acq.Bit.54) | 200E42
12843 | MGWB2 | Off Bit 54 (Acq.Bit.54) | 200E43
12844 | MGWB2 | On Bit 55 (Acq.Bit.55) | 200E44
12845 | MGWB2 | Off Bit 55 (Acq.Bit.55) | 200E45
12846 | MGWB2 | On Bit 56 (Acq.Bit.56) | 200E46
12847 | MGWB2 | Off Bit 56 (Acq.Bit.56) | 200E47
12848 | MGWB2 | On Bit 57 (Acq.Bit.57) | 200E48
12849 | MGWB2 | Off Bit 57 (Acq.Bit.57) | 200E49
12850 | MGWB2 | On Bit 58 (Acq.Bit.58) | 200E50
12851 | MGWB2 | Off Bit 58 (Acq.Bit.58) | 200E51
12852 | MGWB2 | On Bit 59 (Acq.Bit.59) | 200E52
12853 | MGWB2 | Off Bit 59 (Acq.Bit.59) | 200E53
12854 | MGWB2 | On Bit 60 (Acq.Bit.60) | 200E54
12855 | MGWB2 | Off Bit 60 (Acq.Bit.60) | 200E55
12856 | MGWB2 | On Bit 61 (Acq.Bit.61) | 200E56
12857 | MGWB2 | Off Bit 61 (Acq.Bit.61) | 200E57
12858 | MGWB2 | On Bit 62 (Acq.Bit.62) | 200E58
12859 | MGWB2 | Off Bit 62 (Acq.Bit.62) | 200E59
12860 | MGWB2 | On Bit 63 (Acq.Bit.63) | 200E60
12861 | MGWB2 | Off Bit 63 (Acq.Bit.63) | 200E61
12862 | MGWB2 | On Bit 64 (Acq.Bit.64) | 200E62
12863 | MGWB2 | Off Bit 64 (Acq.Bit.64) | 200E63
12864 | MGWB3 | On Bit 65 (Acq.Bit.65) | 201E0
12865 | MGWB3 | Off Bit 65 (Acq.Bit.65) | 201E1
12866 | MGWB3 | On Bit 66 (Acq.Bit.66) | 201E2
12867 | MGWB3 | Off Bit 66 (Acq.Bit.66) | 201E3
12868 | MGWB3 | On Bit 67 (Acq.Bit.67) | 201E4
12869 | MGWB3 | Off Bit 67 (Acq.Bit.67) | 201E5
12870 | MGWB3 | On Bit 68 (Acq.Bit.68) | 201E6
12871 | MGWB3 | Off Bit 68 (Acq.Bit.68) | 201E7
12872 | MGWB3 | On Bit 69 (Acq.Bit.69) | 201E8
12873 | MGWB3 | Off Bit 69 (Acq.Bit.69) | 201E9
12874 | MGWB3 | On Bit 70 (Acq.Bit.70) | 201E10
12875 | MGWB3 | Off Bit 70 (Acq.Bit.70) | 201E11
12876 | MGWB3 | On Bit 71 (Acq.Bit.71) | 201E12
12877 | MGWB3 | Off Bit 71 (Acq.Bit.71) | 201E13
12878 | MGWB3 | On Bit 72 (Acq.Bit.72) | 201E14
12879 | MGWB3 | Off Bit 72 (Acq.Bit.72) | 201E15
12880 | MGWB3 | On Bit 73 (Acq.Bit.73) | 201E16
12881 | MGWB3 | Off Bit 73 (Acq.Bit.73) | 201E17
12882 | MGWB3 | On Bit 74 (Acq.Bit.74) | 201E18
12883 | MGWB3 | Off Bit 74 (Acq.Bit.74) | 201E19
12884 | MGWB3 | On Bit 75 (Acq.Bit.75) | 201E20
12885 | MGWB3 | Off Bit 75 (Acq.Bit.75) | 201E21
12886 | MGWB3 | On Bit 76 (Acq.Bit.76) | 201E22
12887 | MGWB3 | Off Bit 76 (Acq.Bit.76) | 201E23
12888 | MGWB3 | On Bit 77 (Acq.Bit.77) | 201E24
12889 | MGWB3 | Off Bit 77 (Acq.Bit.77) | 201E25
12890 | MGWB3 | On Bit 78 (Acq.Bit.78) | 201E26
12891 | MGWB3 | Off Bit 78 (Acq.Bit.78) | 201E27
12892 | MGWB3 | On Bit 79 (Acq.Bit.79) | 201E28
12893 | MGWB3 | Off Bit 79 (Acq.Bit.79) | 201E29
12894 | MGWB3 | On Bit 80 (Acq.Bit.80) | 201E30
12895 | MGWB3 | Off Bit 80 (Acq.Bit.80) | 201E31
12896 | MGWB3 | On Bit 81 (Acq.Bit.81) | 201E32
12897 | MGWB3 | Off Bit 81 (Acq.Bit.81) | 201E33
12898 | MGWB3 | On Bit 82 (Acq.Bit.82) | 201E34
12899 | MGWB3 | Off Bit 82 (Acq.Bit.82) | 201E35
12900 | MGWB3 | On Bit 83 (Acq.Bit.83) | 201E36
12901 | MGWB3 | Off Bit 83 (Acq.Bit.83) | 201E37
12902 | MGWB3 | On Bit 84 (Acq.Bit.84) | 201E38
12903 | MGWB3 | Off Bit 84 (Acq.Bit.84) | 201E39
12904 | MGWB3 | On Bit 85 (Acq.Bit.85) | 201E40
12905 | MGWB3 | Off Bit 85 (Acq.Bit.85) | 201E41
12906 | MGWB3 | On Bit 86 (Acq.Bit.86) | 201E42
12907 | MGWB3 | Off Bit 86 (Acq.Bit.86) | 201E43
12908 | MGWB3 | On Bit 87 (Acq.Bit.87) | 201E44
12909 | MGWB3 | Off Bit 87 (Acq.Bit.87) | 201E45
12910 | MGWB3 | On Bit 88 (Acq.Bit.88) | 201E46
12911 | MGWB3 | Off Bit 88 (Acq.Bit.88) | 201E47
12912 | MGWB3 | On Bit 89 (Acq.Bit.89) | 201E48
12913 | MGWB3 | Off Bit 89 (Acq.Bit.89) | 201E49
12914 | MGWB3 | On Bit 90 (Acq.Bit.90) | 201E50
12915 | MGWB3 | Off Bit 90 (Acq.Bit.90) | 201E51
12916 | MGWB3 | On Bit 91 (Acq.Bit.91) | 201E52
12917 | MGWB3 | Off Bit 91 (Acq.Bit.91) | 201E53
12918 | MGWB3 | On Bit 92 (Acq.Bit.92) | 201E54
12919 | MGWB3 | Off Bit 92 (Acq.Bit.92) | 201E55
12920 | MGWB3 | On Bit 93 (Acq.Bit.93) | 201E56
12921 | MGWB3 | Off Bit 93 (Acq.Bit.93) | 201E57
12922 | MGWB3 | On Bit 94 (Acq.Bit.94) | 201E58
12923 | MGWB3 | Off Bit 94 (Acq.Bit.94) | 201E59
12924 | MGWB3 | On Bit 95 (Acq.Bit.95) | 201E60
12925 | MGWB3 | Off Bit 95 (Acq.Bit.95) | 201E61
12926 | MGWB3 | On Bit 96 (Acq.Bit.96) | 201E62
12927 | MGWB3 | Off Bit 96 (Acq.Bit.96) | 201E63
12928 | MGWB4 | On Bit 97 (Acq.Bit.97) | 202E0
12929 | MGWB4 | Off Bit 97 (Acq.Bit.97) | 202E1
12930 | MGWB4 | On Bit 98 (Acq.Bit.98) | 202E2
12931 | MGWB4 | Off Bit 98 (Acq.Bit.98) | 202E3
12932 | MGWB4 | On Bit 99 (Acq.Bit.99) | 202E4
12933 | MGWB4 | Off Bit 99 (Acq.Bit.99) | 202E5
12934 | MGWB4 | On Bit 100 (Acq.Bit.100) | 202E6
12935 | MGWB4 | Off Bit 100 (Acq.Bit.100) | 202E7
12936 | MGWB4 | On Bit 101 (Acq.Bit.101) | 202E8
12937 | MGWB4 | Off Bit 101 (Acq.Bit.101) | 202E9
12938 | MGWB4 | On Bit 102 (Acq.Bit.102) | 202E10
12939 | MGWB4 | Off Bit 102 (Acq.Bit.102) | 202E11
12940 | MGWB4 | On Bit 103 (Acq.Bit.103) | 202E12
12941 | MGWB4 | Off Bit 103 (Acq.Bit.103) | 202E13
12942 | MGWB4 | On Bit 104 (Acq.Bit.104) | 202E14
12943 | MGWB4 | Off Bit 104 (Acq.Bit.104) | 202E15
12944 | MGWB4 | On Bit 105 (Acq.Bit.105) | 202E16
12945 | MGWB4 | Off Bit 105 (Acq.Bit.105) | 202E17
12946 | MGWB4 | On Bit 106 (Acq.Bit.106) | 202E18
12947 | MGWB4 | Off Bit 106 (Acq.Bit.106) | 202E19
12948 | MGWB4 | On Bit 107 (Acq.Bit.107) | 202E20
12949 | MGWB4 | Off Bit 107 (Acq.Bit.107) | 202E21
12950 | MGWB4 | On Bit 108 (Acq.Bit.108) | 202E22
12951 | MGWB4 | Off Bit 108 (Acq.Bit.108) | 202E23
12952 | MGWB4 | On Bit 109 (Acq.Bit.109) | 202E24
12953 | MGWB4 | Off Bit 109 (Acq.Bit.109) | 202E25
12954 | MGWB4 | On Bit 110 (Acq.Bit.110) | 202E26
12955 | MGWB4 | Off Bit 110 (Acq.Bit.110) | 202E27
12956 | MGWB4 | On Bit 111 (Acq.Bit.111) | 202E28
12957 | MGWB4 | Off Bit 111 (Acq.Bit.111) | 202E29
12958 | MGWB4 | On Bit 112 (Acq.Bit.112) | 202E30
12959 | MGWB4 | Off Bit 112 (Acq.Bit.112) | 202E31
12960 | MGWB4 | On Bit 113 (Acq.Bit.113) | 202E32
12961 | MGWB4 | Off Bit 113 (Acq.Bit.113) | 202E33
12962 | MGWB4 | On Bit 114 (Acq.Bit.114) | 202E34
12963 | MGWB4 | Off Bit 114 (Acq.Bit.114) | 202E35
12964 | MGWB4 | On Bit 115 (Acq.Bit.115) | 202E36
12965 | MGWB4 | Off Bit 115 (Acq.Bit.115) | 202E37
12966 | MGWB4 | On Bit 116 (Acq.Bit.116) | 202E38
12967 | MGWB4 | Off Bit 116 (Acq.Bit.116) | 202E39
12968 | MGWB4 | On Bit 117 (Acq.Bit.117) | 202E40
12969 | MGWB4 | Off Bit 117 (Acq.Bit.117) | 202E41
12970 | MGWB4 | On Bit 118 (Acq.Bit.118) | 202E42
12971 | MGWB4 | Off Bit 118 (Acq.Bit.118) | 202E43
12972 | MGWB4 | On Bit 119 (Acq.Bit.119) | 202E44
12973 | MGWB4 | Off Bit 119 (Acq.Bit.119) | 202E45
12974 | MGWB4 | On Bit 120 (Acq.Bit.120) | 202E46
12975 | MGWB4 | Off Bit 120 (Acq.Bit.120) | 202E47
12976 | MGWB4 | On Bit 121 (Acq.Bit.121) | 202E48
12977 | MGWB4 | Off Bit 121 (Acq.Bit.121) | 202E49
12978 | MGWB4 | On Bit 122 (Acq.Bit.122) | 202E50
12979 | MGWB4 | Off Bit 122 (Acq.Bit.122) | 202E51
12980 | MGWB4 | On Bit 123 (Acq.Bit.123) | 202E52
12981 | MGWB4 | Off Bit 123 (Acq.Bit.123) | 202E53
12982 | MGWB4 | On Bit 124 (Acq.Bit.124) | 202E54
12983 | MGWB4 | Off Bit 124 (Acq.Bit.124) | 202E55
12984 | MGWB4 | On Bit 125 (Acq.Bit.125) | 202E56
12985 | MGWB4 | Off Bit 125 (Acq.Bit.125) | 202E57
12986 | MGWB4 | On Bit 126 (Acq.Bit.126) | 202E58
12987 | MGWB4 | Off Bit 126 (Acq.Bit.126) | 202E59
12988 | MGWB4 | On Bit 127 (Acq.Bit.127) | 202E60
12989 | MGWB4 | Off Bit 127 (Acq.Bit.127) | 202E61
12990 | MGWB4 | On Bit 128 (Acq.Bit.128) | 202E62
12991 | MGWB4 | Off Bit 128 (Acq.Bit.128) | 202E63
12992 | MGWD1 | Off Off Double Bit 1 (Acq.Binary.1) | 203E0
12993 | MGWD1 | On Off Double Bit 1 (Acq.Binary.1) | 203E1
12994 | MGWD1 | Off On Double Bit 1 (Acq.Binary.1) | 203E2
12995 | MGWD1 | On On Double Bit 1 (Acq.Binary.1) | 203E3
12996 | MGWD1 | Off Off Double Bit 2 (Acq.Binary.2) | 203E4
12997 | MGWD1 | On Off Double Bit 2 (Acq.Binary.2) | 203E5
12998 | MGWD1 | Off On Double Bit 2 (Acq.Binary.2) | 203E6
12999 | MGWD1 | On On Double Bit 2 (Acq.Binary.2) | 203E7
13000 | MGWD1 | Off Off Double Bit 3 (Acq.Binary.3) | 203E8
13001 | MGWD1 | On Off Double Bit 3 (Acq.Binary.3) | 203E9
13002 | MGWD1 | Off On Double Bit 3 (Acq.Binary.3) | 203E10
13003 | MGWD1 | On On Double Bit 3 (Acq.Binary.3) | 203E11
13004 | MGWD1 | Off Off Double Bit 4 (Acq.Binary.4) | 203E12
13005 | MGWD1 | On Off Double Bit 4 (Acq.Binary.4) | 203E13
13006 | MGWD1 | Off On Double Bit 4 (Acq.Binary.4) | 203E14
13007 | MGWD1 | On On Double Bit 4 (Acq.Binary.4) | 203E15
13008 | MGWD1 | Off Off Double Bit 5 (Acq.Binary.5) | 203E16
13009 | MGWD1 | On Off Double Bit 5 (Acq.Binary.5) | 203E17
13010 | MGWD1 | Off On Double Bit 5 (Acq.Binary.5) | 203E18
13011 | MGWD1 | On On Double Bit 5 (Acq.Binary.5) | 203E19
13012 | MGWD1 | Off Off Double Bit 6 (Acq.Binary.6) | 203E20
13013 | MGWD1 | On Off Double Bit 6 (Acq.Binary.6) | 203E21
13014 | MGWD1 | Off On Double Bit 6 (Acq.Binary.6) | 203E22
13015 | MGWD1 | On On Double Bit 6 (Acq.Binary.6) | 203E23
13016 | MGWD1 | Off Off Double Bit 7 (Acq.Binary.7) | 203E24
13017 | MGWD1 | On Off Double Bit 7 (Acq.Binary.7) | 203E25
13018 | MGWD1 | Off On Double Bit 7 (Acq.Binary.7) | 203E26
13019 | MGWD1 | On On Double Bit 7 (Acq.Binary.7) | 203E27
13020 | MGWD1 | Off Off Double Bit 8 (Acq.Binary.8) | 203E28
13021 | MGWD1 | On Off Double Bit 8 (Acq.Binary.8) | 203E29
13022 | MGWD1 | Off On Double Bit 8 (Acq.Binary.8) | 203E30
13023 | MGWD1 | On On Double Bit 8 (Acq.Binary.8) | 203E31
13024 | MGWD1 | Off Off Double Bit 9 (Acq.Binary.9) | 203E32
13025 | MGWD1 | On Off Double Bit 9 (Acq.Binary.9) | 203E33
13026 | MGWD1 | Off On Double Bit 9 (Acq.Binary.9) | 203E34
13027 | MGWD1 | On On Double Bit 9 (Acq.Binary.9) | 203E35
13028 | MGWD1 | Off Off Double Bit 10 (Acq.Binary.10) | 203E36
13029 | MGWD1 | On Off Double Bit 10 (Acq.Binary.10) | 203E37
13030 | MGWD1 | Off On Double Bit 10 (Acq.Binary.10) | 203E38
13031 | MGWD1 | On On Double Bit 10 (Acq.Binary.10) | 203E39
13032 | MGWD1 | Off Off Double Bit 11 (Acq.Binary.11) | 203E40
13033 | MGWD1 | On Off Double Bit 11 (Acq.Binary.11) | 203E41
13034 | MGWD1 | Off On Double Bit 11 (Acq.Binary.11) | 203E42
13035 | MGWD1 | On On Double Bit 11 (Acq.Binary.11) | 203E43
13036 | MGWD1 | Off Off Double Bit 12 (Acq.Binary.12) | 203E44
13037 | MGWD1 | On Off Double Bit 12 (Acq.Binary.12) | 203E45
13038 | MGWD1 | Off On Double Bit 12 (Acq.Binary.12) | 203E46
13039 | MGWD1 | On On Double Bit 12 (Acq.Binary.12) | 203E47
13040 | MGWD1 | Off Off Double Bit 13 (Acq.Binary.13) | 203E48
13041 | MGWD1 | On Off Double Bit 13 (Acq.Binary.13) | 203E49
13042 | MGWD1 | Off On Double Bit 13 (Acq.Binary.13) | 203E50
13043 | MGWD1 | On On Double Bit 13 (Acq.Binary.13) | 203E51
13044 | MGWD1 | Off Off Double Bit 14 (Acq.Binary.14) | 203E52
13045 | MGWD1 | On Off Double Bit 14 (Acq.Binary.14) | 203E53
13046 | MGWD1 | Off On Double Bit 14 (Acq.Binary.14) | 203E54
13047 | MGWD1 | On On Double Bit 14 (Acq.Binary.14) | 203E55
13048 | MGWD1 | Off Off Double Bit 15 (Acq.Binary.15) | 203E56
13049 | MGWD1 | On Off Double Bit 15 (Acq.Binary.15) | 203E57
13050 | MGWD1 | Off On Double Bit 15 (Acq.Binary.15) | 203E58
13051 | MGWD1 | On On Double Bit 15 (Acq.Binary.15) | 203E59
13052 | MGWD1 | Off Off Double Bit 16 (Acq.Binary.16) | 203E60
13053 | MGWD1 | On Off Double Bit 16 (Acq.Binary.16) | 203E61
13054 | MGWD1 | Off On Double Bit 16 (Acq.Binary.16) | 203E62
13055 | MGWD1 | On On Double Bit 16 (Acq.Binary.16) | 203E63
13056 | MGWD2 | Off Off Double Bit 17 (Acq.Binary.17) | 204E0
13057 | MGWD2 | On Off Double Bit 17 (Acq.Binary.17) | 204E1
13058 | MGWD2 | Off On Double Bit 17 (Acq.Binary.17) | 204E2
13059 | MGWD2 | On On Double Bit 17 (Acq.Binary.17) | 204E3
13060 | MGWD2 | Off Off Double Bit 18 (Acq.Binary.18) | 204E4
13061 | MGWD2 | On Off Double Bit 18 (Acq.Binary.18) | 204E5
13062 | MGWD2 | Off On Double Bit 18 (Acq.Binary.18) | 204E6
13063 | MGWD2 | On On Double Bit 18 (Acq.Binary.18) | 204E7
13064 | MGWD2 | Off Off Double Bit 19 (Acq.Binary.19) | 204E8
13065 | MGWD2 | On Off Double Bit 19 (Acq.Binary.19) | 204E9
13066 | MGWD2 | Off On Double Bit 19 (Acq.Binary.19) | 204E10
13067 | MGWD2 | On On Double Bit 19 (Acq.Binary.19) | 204E11
13068 | MGWD2 | Off Off Double Bit 20 (Acq.Binary.20) | 204E12
13069 | MGWD2 | On Off Double Bit 20 (Acq.Binary.20) | 204E13
13070 | MGWD2 | Off On Double Bit 20 (Acq.Binary.20) | 204E14
13071 | MGWD2 | On On Double Bit 20 (Acq.Binary.20) | 204E15
13072 | MGWD2 | Off Off Double Bit 21 (Acq.Binary.21) | 204E16
13073 | MGWD2 | On Off Double Bit 21 (Acq.Binary.21) | 204E17
13074 | MGWD2 | Off On Double Bit 21 (Acq.Binary.21) | 204E18
13075 | MGWD2 | On On Double Bit 21 (Acq.Binary.21) | 204E19
13076 | MGWD2 | Off Off Double Bit 22 (Acq.Binary.22) | 204E20
13077 | MGWD2 | On Off Double Bit 22 (Acq.Binary.22) | 204E21
13078 | MGWD2 | Off On Double Bit 22 (Acq.Binary.22) | 204E22
13079 | MGWD2 | On On Double Bit 22 (Acq.Binary.22) | 204E23
13080 | MGWD2 | Off Off Double Bit 23 (Acq.Binary.23) | 204E24
13081 | MGWD2 | On Off Double Bit 23 (Acq.Binary.23) | 204E25
13082 | MGWD2 | Off On Double Bit 23 (Acq.Binary.23) | 204E26
13083 | MGWD2 | On On Double Bit 23 (Acq.Binary.23) | 204E27
13084 | MGWD2 | Off Off Double Bit 24 (Acq.Binary.24) | 204E28
13085 | MGWD2 | On Off Double Bit 24 (Acq.Binary.24) | 204E29
13086 | MGWD2 | Off On Double Bit 24 (Acq.Binary.24) | 204E30
13087 | MGWD2 | On On Double Bit 24 (Acq.Binary.24) | 204E31
13088 | MGWD2 | Off Off Double Bit 25 (Acq.Binary.25) | 204E32
13089 | MGWD2 | On Off Double Bit 25 (Acq.Binary.25) | 204E33
13090 | MGWD2 | Off On Double Bit 25 (Acq.Binary.25) | 204E34
13091 | MGWD2 | On On Double Bit 25 (Acq.Binary.25) | 204E35
13092 | MGWD2 | Off Off Double Bit 26 (Acq.Binary.26) | 204E36
13093 | MGWD2 | On Off Double Bit 26 (Acq.Binary.26) | 204E37
13094 | MGWD2 | Off On Double Bit 26 (Acq.Binary.26) | 204E38
13095 | MGWD2 | On On Double Bit 26 (Acq.Binary.26) | 204E39
13096 | MGWD2 | Off Off Double Bit 27 (Acq.Binary.27) | 204E40
13097 | MGWD2 | On Off Double Bit 27 (Acq.Binary.27) | 204E41
13098 | MGWD2 | Off On Double Bit 27 (Acq.Binary.27) | 204E42
13099 | MGWD2 | On On Double Bit 27 (Acq.Binary.27) | 204E43
13100 | MGWD2 | Off Off Double Bit 28 (Acq.Binary.28) | 204E44
13101 | MGWD2 | On Off Double Bit 28 (Acq.Binary.28) | 204E45
13102 | MGWD2 | Off On Double Bit 28 (Acq.Binary.28) | 204E46
13103 | MGWD2 | On On Double Bit 28 (Acq.Binary.28) | 204E47
13104 | MGWD2 | Off Off Double Bit 29 (Acq.Binary.29) | 204E48
13105 | MGWD2 | On Off Double Bit 29 (Acq.Binary.29) | 204E49
13106 | MGWD2 | Off On Double Bit 29 (Acq.Binary.29) | 204E50
13107 | MGWD2 | On On Double Bit 29 (Acq.Binary.29) | 204E51
13108 | MGWD2 | Off Off Double Bit 30 (Acq.Binary.30) | 204E52
13109 | MGWD2 | On Off Double Bit 30 (Acq.Binary.30) | 204E53
13110 | MGWD2 | Off On Double Bit 30 (Acq.Binary.30) | 204E54
13111 | MGWD2 | On On Double Bit 30 (Acq.Binary.30) | 204E55
13112 | MGWD2 | Off Off Double Bit 31 (Acq.Binary.31) | 204E56
13113 | MGWD2 | On Off Double Bit 31 (Acq.Binary.31) | 204E57
13114 | MGWD2 | Off On Double Bit 31 (Acq.Binary.31) | 204E58
13115 | MGWD2 | On On Double Bit 31 (Acq.Binary.31) | 204E59
13116 | MGWD2 | Off Off Double Bit 32 (Acq.Binary.32) | 204E60
13117 | MGWD2 | On Off Double Bit 32 (Acq.Binary.32) | 204E61
13118 | MGWD2 | Off On Double Bit 32 (Acq.Binary.32) | 204E62
13119 | MGWD2 | On On Double Bit 32 (Acq.Binary.32) | 204E63
13120 | CPB1 | Capacitor disconnected On | 205E0
13121 | CPB1 | Capacitor disconnected Off | 205E1
13122 | CPB1 | Capacitor connected On | 205E2
13123 | CPB1 | Capacitor connected Off | 205E3
13124 | CPB1 | Capacitor discharging On | 205E4
13125 | CPB1 | Capacitor discharging Off | 205E5
13126 | CPB1 | Capacitor overvoltage On | 205E6
13127 | CPB1 | Capacitor overvoltage Off | 205E7
13184 | COL1 | Start On | 206E0
13185 | COL1 | Start Off | 206E1
13186 | COL1 | Trip On | 206E2
13187 | COL1 | Trip Off | 206E3
13188 | COL1 | Block On | 206E4
13189 | COL1 | Block Off | 206E5
13248 | COL2 | Start On | 207E0
13249 | COL2 | Start Off | 207E1
13250 | COL2 | Trip On | 207E2
13251 | COL2 | Trip Off | 207E3
13252 | COL2 | Block On | 207E4
13253 | COL2 | Block Off | 207E5
13312 | CNU1 | Alarm Start On | 208E0
13313 | CNU1 | Alarm Start Off | 208E1
13314 | CNU1 | Alarm On | 208E2
13315 | CNU1 | Alarm Off | 208E3
13316 | CNU1 | Trip Start On | 208E4
13317 | CNU1 | Trip Start Off | 208E5
13318 | CNU1 | Trip On | 208E6
13319 | CNU1 | Trip Off | 208E7
13320 | CNU1 | Blocked On | 208E8
13321 | CNU1 | Blocked Off | 208E9
13322 | CNU1 | Unbalance detected On | 208E10
13323 | CNU1 | Unbalance detected Off | 208E11
13324 | CNU1 | Compensating natural unbalance On | 208E12
13325 | CNU1 | Compensating natural unbalance Off | 208E13
13376 | CRF1 | Dummy event for SPA | 209E0
13440 | OOS1 | Pole Slip detection Start On | 210E0
13441 | OOS1 | Pole Slip detection Start Off | 210E1
13442 | OOS1 | Pole Slip detected Trip On | 210E2
13443 | OOS1 | Pole Slip detected Trip Off | 210E3
13444 | OOS1 | Pole Slip detection Blocked On | 210E4
13445 | OOS1 | Pole Slip detection Blocked Off | 210E5
13446 | OOS1 | Pole Slip Z locus entered chacacteristics | 210E6
13447 | OOS1 | Pole Slip Z locus exit chacacteristics | 210E7
13448 | OOS1 | Pole Slip Z locus outside R+ Blinder On | 210E8
13449 | OOS1 | Pole Slip Z locus outside R+ Blinder Off | 210E9
13450 | OOS1 | Pole Slip Z locus Inside R+ Blinder On | 210E10
13451 | OOS1 | Pole Slip Z locus Inside R+ Blinder Off | 210E11
13452 | OOS1 | Pole Slip Z locus outside R- Blinder On | 210E12
13453 | OOS1 | Pole Slip Z locus outside R- Blinder Off | 210E13
13454 | OOS1 | Pole Slip Z locus Inside R- Blinder On | 210E14
13455 | OOS1 | Pole Slip Z locus Inside R- Blinder Off | 210E15
13456 | OOS1 | Pole Slip Z locus between R Blinders On | 210E16
13457 | OOS1 | Pole Slip Z locus between R Blinders Off | 210E17
13458 | OOS1 | Pole Slip Z locus travel time criteria On | 210E18
13459 | OOS1 | Pole Slip Z locus travel time criteria Off | 210E19
13460 | OOS1 | Pole Slip Detected On | 210E20
13461 | OOS1 | Pole Slip Detected Off | 210E21
13462 | OOS1 | Reset time finished On | 210E22
13463 | OOS1 | Reset time finished, slip counters reset Off | 210E23
13504 | THDV1 | Voltage THD Start On | 211E0
13505 | THDV1 | Voltage THD Start Off | 211E1
13506 | THDV1 | Voltage THD Alarm On | 211E2
13507 | THDV1 | Voltage THD Alarm Off | 211E3
13508 | THDV1 | Voltage THD Alarm Blocked On | 211E4
13509 | THDV1 | Voltage THD Alarm Blocked Off | 211E5
13568 | GOOSE5 | GOOSE Subscription status 1 Active | 212E0
13569 | GOOSE5 | GOOSE Subscription status 1 Not active | 212E1
13570 | GOOSE5 | GOOSE Subscription status 2 Active | 212E2
13571 | GOOSE5 | GOOSE Subscription status 2 Not active | 212E3
13572 | GOOSE5 | GOOSE Subscription status 3 Active | 212E4
13573 | GOOSE5 | GOOSE Subscription status 3 Not active | 212E5
13574 | GOOSE5 | GOOSE Subscription status 4 Active | 212E6
13575 | GOOSE5 | GOOSE Subscription status 4 Not active | 212E7
13576 | GOOSE5 | GOOSE Subscription status 5 Active | 212E8
13577 | GOOSE5 | GOOSE Subscription status 5 Not active | 212E9
13578 | GOOSE5 | GOOSE Subscription status 6 Active | 212E10
13579 | GOOSE5 | GOOSE Subscription status 6 Not active | 212E11
13580 | GOOSE5 | GOOSE Subscription status 7 Active | 212E12
13581 | GOOSE5 | GOOSE Subscription status 7 Not active | 212E13
13582 | GOOSE5 | GOOSE Subscription status 8 Active | 212E14
13583 | GOOSE5 | GOOSE Subscription status 8 Not active | 212E15
13584 | GOOSE5 | GOOSE Subscription status 9 Active | 212E16
13585 | GOOSE5 | GOOSE Subscription status 9 Not active | 212E17
13586 | GOOSE5 | GOOSE Subscription status 10 Active | 212E18
13587 | GOOSE5 | GOOSE Subscription status 10 Not active | 212E19
13588 | GOOSE5 | GOOSE Subscription status 11 Active | 212E20
13589 | GOOSE5 | GOOSE Subscription status 11 Not active | 212E21
13590 | GOOSE5 | GOOSE Subscription status 12 Active | 212E22
13591 | GOOSE5 | GOOSE Subscription status 12 Not active | 212E23
13592 | GOOSE5 | GOOSE Subscription status 13 Active | 212E24
13593 | GOOSE5 | GOOSE Subscription status 13 Not active | 212E25
13594 | GOOSE5 | GOOSE Subscription status 14 Active | 212E26
13595 | GOOSE5 | GOOSE Subscription status 14 Not active | 212E27
13596 | GOOSE5 | GOOSE Subscription status 15 Active | 212E28
13597 | GOOSE5 | GOOSE Subscription status 15 Not active | 212E29
13598 | GOOSE5 | GOOSE Subscription status 16 Active | 212E30
13599 | GOOSE5 | GOOSE Subscription status 16 Not active | 212E31
13600 | GOOSE5 | GOOSE Subscription status 17 Active | 212E32
13601 | GOOSE5 | GOOSE Subscription status 17 Not active | 212E33
13602 | GOOSE5 | GOOSE Subscription status 18 Active | 212E34
13603 | GOOSE5 | GOOSE Subscription status 18 Not active | 212E35
13604 | GOOSE5 | GOOSE Subscription status 19 Active | 212E36
13605 | GOOSE5 | GOOSE Subscription status 19 Not active | 212E37
13606 | GOOSE5 | GOOSE Subscription status 20 Active | 212E38
13607 | GOOSE5 | GOOSE Subscription status 20 Not active | 212E39
13608 | GOOSE5 | GOOSE Subscription status 21 Active | 212E40
13609 | GOOSE5 | GOOSE Subscription status 21 Not active | 212E41
13610 | GOOSE5 | GOOSE Subscription status 22 Active | 212E42
13611 | GOOSE5 | GOOSE Subscription status 22 Not active | 212E43
13612 | GOOSE5 | GOOSE Subscription status 23 Active | 212E44
13613 | GOOSE5 | GOOSE Subscription status 23 Not active | 212E45
13614 | GOOSE5 | GOOSE Subscription status 24 Active | 212E46
13615 | GOOSE5 | GOOSE Subscription status 24 Not active | 212E47
13616 | GOOSE5 | GOOSE Subscription status 25 Active | 212E48
13617 | GOOSE5 | GOOSE Subscription status 25 Not active | 212E49
13618 | GOOSE5 | GOOSE Subscription status 26 Active | 212E50
13619 | GOOSE5 | GOOSE Subscription status 26 Not active | 212E51
13620 | GOOSE5 | GOOSE Subscription status 27 Active | 212E52
13621 | GOOSE5 | GOOSE Subscription status 27 Not active | 212E53
13622 | GOOSE5 | GOOSE Subscription status 28 Active | 212E54
13623 | GOOSE5 | GOOSE Subscription status 28 Not active | 212E55
13624 | GOOSE5 | GOOSE Subscription status 29 Active | 212E56
13625 | GOOSE5 | GOOSE Subscription status 29 Not active | 212E57
13626 | GOOSE5 | GOOSE Subscription status 30 Active | 212E58
13627 | GOOSE5 | GOOSE Subscription status 30 Not active | 212E59
13628 | GOOSE5 | GOOSE Subscription status 31 Active | 212E60
13629 | GOOSE5 | GOOSE Subscription status 31 Not active | 212E61
13630 | GOOSE5 | GOOSE Subscription status 32 Active | 212E62
13631 | GOOSE5 | GOOSE Subscription status 32 Not active | 212E63
13632 | GOOSE6 | GOOSE Subscription status 33 Active | 213E0
13633 | GOOSE6 | GOOSE Subscription status 33 Not active | 213E1
13634 | GOOSE6 | GOOSE Subscription status 34 Active | 213E2
13635 | GOOSE6 | GOOSE Subscription status 34 Not active | 213E3
13636 | GOOSE6 | GOOSE Subscription status 35 Active | 213E4
13637 | GOOSE6 | GOOSE Subscription status 35 Not active | 213E5
13638 | GOOSE6 | GOOSE Subscription status 36 Active | 213E6
13639 | GOOSE6 | GOOSE Subscription status 36 Not active | 213E7
13640 | GOOSE6 | GOOSE Subscription status 37 Active | 213E8
13641 | GOOSE6 | GOOSE Subscription status 37 Not active | 213E9
13642 | GOOSE6 | GOOSE Subscription status 38 Active | 213E10
13643 | GOOSE6 | GOOSE Subscription status 38 Not active | 213E11
13644 | GOOSE6 | GOOSE Subscription status 39 Active | 213E12
13645 | GOOSE6 | GOOSE Subscription status 39 Not active | 213E13
13646 | GOOSE6 | GOOSE Subscription status 40 Active | 213E14
13647 | GOOSE6 | GOOSE Subscription status 40 Not active | 213E15
13648 | GOOSE6 | GOOSE Subscription status 41 Active | 213E16
13649 | GOOSE6 | GOOSE Subscription status 41 Not active | 213E17
13650 | GOOSE6 | GOOSE Subscription status 42 Active | 213E18
13651 | GOOSE6 | GOOSE Subscription status 42 Not active | 213E19
13652 | GOOSE6 | GOOSE Subscription status 43 Active | 213E20
13653 | GOOSE6 | GOOSE Subscription status 43 Not active | 213E21
13654 | GOOSE6 | GOOSE Subscription status 44 Active | 213E22
13655 | GOOSE6 | GOOSE Subscription status 44 Not active | 213E23
13656 | GOOSE6 | GOOSE Subscription status 45 Active | 213E24
13657 | GOOSE6 | GOOSE Subscription status 45 Not active | 213E25
13658 | GOOSE6 | GOOSE Subscription status 46 Active | 213E26
13659 | GOOSE6 | GOOSE Subscription status 46 Not active | 213E27
13660 | GOOSE6 | GOOSE Subscription status 47 Active | 213E28
13661 | GOOSE6 | GOOSE Subscription status 47 Not active | 213E29
13662 | GOOSE6 | GOOSE Subscription status 48 Active | 213E30
13663 | GOOSE6 | GOOSE Subscription status 48 Not active | 213E31
13664 | GOOSE6 | GOOSE Subscription status 49 Active | 213E32
13665 | GOOSE6 | GOOSE Subscription status 49 Not active | 213E33
13666 | GOOSE6 | GOOSE Subscription status 50 Active | 213E34
13667 | GOOSE6 | GOOSE Subscription status 50 Not active | 213E35
13668 | GOOSE6 | GOOSE Subscription status 51 Active | 213E36
13669 | GOOSE6 | GOOSE Subscription status 51 Not active | 213E37
13670 | GOOSE6 | GOOSE Subscription status 52 Active | 213E38
13671 | GOOSE6 | GOOSE Subscription status 52 Not active | 213E39
13672 | GOOSE6 | GOOSE Subscription status 53 Active | 213E40
13673 | GOOSE6 | GOOSE Subscription status 53 Not active | 213E41
13674 | GOOSE6 | GOOSE Subscription status 54 Active | 213E42
13675 | GOOSE6 | GOOSE Subscription status 54 Not active | 213E43
13676 | GOOSE6 | GOOSE Subscription status 55 Active | 213E44
13677 | GOOSE6 | GOOSE Subscription status 55 Not active | 213E45
13678 | GOOSE6 | GOOSE Subscription status 56 Active | 213E46
13679 | GOOSE6 | GOOSE Subscription status 56 Not active | 213E47
13680 | GOOSE6 | GOOSE Subscription status 57 Active | 213E48
13681 | GOOSE6 | GOOSE Subscription status 57 Not active | 213E49
13682 | GOOSE6 | GOOSE Subscription status 58 Active | 213E50
13683 | GOOSE6 | GOOSE Subscription status 58 Not active | 213E51
13684 | GOOSE6 | GOOSE Subscription status 59 Active | 213E52
13685 | GOOSE6 | GOOSE Subscription status 59 Not active | 213E53
13686 | GOOSE6 | GOOSE Subscription status 60 Active | 213E54
13687 | GOOSE6 | GOOSE Subscription status 60 Not active | 213E55
13688 | GOOSE6 | GOOSE Subscription status 61 Active | 213E56
13689 | GOOSE6 | GOOSE Subscription status 61 Not active | 213E57
13690 | GOOSE6 | GOOSE Subscription status 62 Active | 213E58
13691 | GOOSE6 | GOOSE Subscription status 62 Not active | 213E59
13692 | GOOSE6 | GOOSE Subscription status 63 Active | 213E60
13693 | GOOSE6 | GOOSE Subscription status 63 Not active | 213E61
13694 | GOOSE6 | GOOSE Subscription status 64 Active | 213E62
13695 | GOOSE6 | GOOSE Subscription status 64 Not active | 213E63
13696 | GOOSE7 | GOOSE Processing simulated messages 1 True | 214E0
13697 | GOOSE7 | GOOSE Processing simulated messages 1 False | 214E1
13698 | GOOSE7 | GOOSE Processing simulated messages 2 True | 214E2
13699 | GOOSE7 | GOOSE Processing simulated messages 2 False | 214E3
13700 | GOOSE7 | GOOSE Processing simulated messages 3 True | 214E4
13701 | GOOSE7 | GOOSE Processing simulated messages 3 False | 214E5
13702 | GOOSE7 | GOOSE Processing simulated messages 4 True | 214E6
13703 | GOOSE7 | GOOSE Processing simulated messages 4 False | 214E7
13704 | GOOSE7 | GOOSE Processing simulated messages 5 True | 214E8
13705 | GOOSE7 | GOOSE Processing simulated messages 5 False | 214E9
13706 | GOOSE7 | GOOSE Processing simulated messages 6 True | 214E10
13707 | GOOSE7 | GOOSE Processing simulated messages 6 False | 214E11
13708 | GOOSE7 | GOOSE Processing simulated messages 7 True | 214E12
13709 | GOOSE7 | GOOSE Processing simulated messages 7 False | 214E13
13710 | GOOSE7 | GOOSE Processing simulated messages 8 True | 214E14
13711 | GOOSE7 | GOOSE Processing simulated messages 8 False | 214E15
13712 | GOOSE7 | GOOSE Processing simulated messages 9 True | 214E16
13713 | GOOSE7 | GOOSE Processing simulated messages 9 False | 214E17
13714 | GOOSE7 | GOOSE Processing simulated messages 10 True | 214E18
13715 | GOOSE7 | GOOSE Processing simulated messages 10 False | 214E19
13716 | GOOSE7 | GOOSE Processing simulated messages 11 True | 214E20
13717 | GOOSE7 | GOOSE Processing simulated messages 11 False | 214E21
13718 | GOOSE7 | GOOSE Processing simulated messages 12 True | 214E22
13719 | GOOSE7 | GOOSE Processing simulated messages 12 False | 214E23
13720 | GOOSE7 | GOOSE Processing simulated messages 13 True | 214E24
13721 | GOOSE7 | GOOSE Processing simulated messages 13 False | 214E25
13722 | GOOSE7 | GOOSE Processing simulated messages 14 True | 214E26
13723 | GOOSE7 | GOOSE Processing simulated messages 14 False | 214E27
13724 | GOOSE7 | GOOSE Processing simulated messages 15 True | 214E28
13725 | GOOSE7 | GOOSE Processing simulated messages 15 False | 214E29
13726 | GOOSE7 | GOOSE Processing simulated messages 16 True | 214E30
13727 | GOOSE7 | GOOSE Processing simulated messages 16 False | 214E31
13728 | GOOSE7 | GOOSE Processing simulated messages 17 True | 214E32
13729 | GOOSE7 | GOOSE Processing simulated messages 17 False | 214E33
13730 | GOOSE7 | GOOSE Processing simulated messages 18 True | 214E34
13731 | GOOSE7 | GOOSE Processing simulated messages 18 False | 214E35
13732 | GOOSE7 | GOOSE Processing simulated messages 19 True | 214E36
13733 | GOOSE7 | GOOSE Processing simulated messages 19 False | 214E37
13734 | GOOSE7 | GOOSE Processing simulated messages 20 True | 214E38
13735 | GOOSE7 | GOOSE Processing simulated messages 20 False | 214E39
13736 | GOOSE7 | GOOSE Processing simulated messages 21 True | 214E40
13737 | GOOSE7 | GOOSE Processing simulated messages 21 False | 214E41
13738 | GOOSE7 | GOOSE Processing simulated messages 22 True | 214E42
13739 | GOOSE7 | GOOSE Processing simulated messages 22 False | 214E43
13740 | GOOSE7 | GOOSE Processing simulated messages 23 True | 214E44
13741 | GOOSE7 | GOOSE Processing simulated messages 23 False | 214E45
13742 | GOOSE7 | GOOSE Processing simulated messages 24 True | 214E46
13743 | GOOSE7 | GOOSE Processing simulated messages 24 False | 214E47
13744 | GOOSE7 | GOOSE Processing simulated messages 25 True | 214E48
13745 | GOOSE7 | GOOSE Processing simulated messages 25 False | 214E49
13746 | GOOSE7 | GOOSE Processing simulated messages 26 True | 214E50
13747 | GOOSE7 | GOOSE Processing simulated messages 26 False | 214E51
13748 | GOOSE7 | GOOSE Processing simulated messages 27 True | 214E52
13749 | GOOSE7 | GOOSE Processing simulated messages 27 False | 214E53
13750 | GOOSE7 | GOOSE Processing simulated messages 28 True | 214E54
13751 | GOOSE7 | GOOSE Processing simulated messages 28 False | 214E55
13752 | GOOSE7 | GOOSE Processing simulated messages 29 True | 214E56
13753 | GOOSE7 | GOOSE Processing simulated messages 29 False | 214E57
13754 | GOOSE7 | GOOSE Processing simulated messages 30 True | 214E58
13755 | GOOSE7 | GOOSE Processing simulated messages 30 False | 214E59
13756 | GOOSE7 | GOOSE Processing simulated messages 31 True | 214E60
13757 | GOOSE7 | GOOSE Processing simulated messages 31 False | 214E61
13758 | GOOSE7 | GOOSE Processing simulated messages 32 True | 214E62
13759 | GOOSE7 | GOOSE Processing simulated messages 32 False | 214E63
13760 | GOOSE8 | GOOSE Processing simulated messages 33 True | 215E0
13761 | GOOSE8 | GOOSE Processing simulated messages 33 False | 215E1
13762 | GOOSE8 | GOOSE Processing simulated messages 34 True | 215E2
13763 | GOOSE8 | GOOSE Processing simulated messages 34 False | 215E3
13764 | GOOSE8 | GOOSE Processing simulated messages 35 True | 215E4
13765 | GOOSE8 | GOOSE Processing simulated messages 35 False | 215E5
13766 | GOOSE8 | GOOSE Processing simulated messages 36 True | 215E6
13767 | GOOSE8 | GOOSE Processing simulated messages 36 False | 215E7
13768 | GOOSE8 | GOOSE Processing simulated messages 37 True | 215E8
13769 | GOOSE8 | GOOSE Processing simulated messages 37 False | 215E9
13770 | GOOSE8 | GOOSE Processing simulated messages 38 True | 215E10
13771 | GOOSE8 | GOOSE Processing simulated messages 38 False | 215E11
13772 | GOOSE8 | GOOSE Processing simulated messages 39 True | 215E12
13773 | GOOSE8 | GOOSE Processing simulated messages 39 False | 215E13
13774 | GOOSE8 | GOOSE Processing simulated messages 40 True | 215E14
13775 | GOOSE8 | GOOSE Processing simulated messages 40 False | 215E15
13776 | GOOSE8 | GOOSE Processing simulated messages 41 True | 215E16
13777 | GOOSE8 | GOOSE Processing simulated messages 41 False | 215E17
13778 | GOOSE8 | GOOSE Processing simulated messages 42 True | 215E18
13779 | GOOSE8 | GOOSE Processing simulated messages 42 False | 215E19
13780 | GOOSE8 | GOOSE Processing simulated messages 43 True | 215E20
13781 | GOOSE8 | GOOSE Processing simulated messages 43 False | 215E21
13782 | GOOSE8 | GOOSE Processing simulated messages 44 True | 215E22
13783 | GOOSE8 | GOOSE Processing simulated messages 44 False | 215E23
13784 | GOOSE8 | GOOSE Processing simulated messages 45 True | 215E24
13785 | GOOSE8 | GOOSE Processing simulated messages 45 False | 215E25
13786 | GOOSE8 | GOOSE Processing simulated messages 46 True | 215E26
13787 | GOOSE8 | GOOSE Processing simulated messages 46 False | 215E27
13788 | GOOSE8 | GOOSE Processing simulated messages 47 True | 215E28
13789 | GOOSE8 | GOOSE Processing simulated messages 47 False | 215E29
13790 | GOOSE8 | GOOSE Processing simulated messages 48 True | 215E30
13791 | GOOSE8 | GOOSE Processing simulated messages 48 False | 215E31
13792 | GOOSE8 | GOOSE Processing simulated messages 49 True | 215E32
13793 | GOOSE8 | GOOSE Processing simulated messages 49 False | 215E33
13794 | GOOSE8 | GOOSE Processing simulated messages 50 True | 215E34
13795 | GOOSE8 | GOOSE Processing simulated messages 50 False | 215E35
13796 | GOOSE8 | GOOSE Processing simulated messages 51 True | 215E36
13797 | GOOSE8 | GOOSE Processing simulated messages 51 False | 215E37
13798 | GOOSE8 | GOOSE Processing simulated messages 52 True | 215E38
13799 | GOOSE8 | GOOSE Processing simulated messages 52 False | 215E39
13800 | GOOSE8 | GOOSE Processing simulated messages 53 True | 215E40
13801 | GOOSE8 | GOOSE Processing simulated messages 53 False | 215E41
13802 | GOOSE8 | GOOSE Processing simulated messages 54 True | 215E42
13803 | GOOSE8 | GOOSE Processing simulated messages 54 False | 215E43
13804 | GOOSE8 | GOOSE Processing simulated messages 55 True | 215E44
13805 | GOOSE8 | GOOSE Processing simulated messages 55 False | 215E45
13806 | GOOSE8 | GOOSE Processing simulated messages 56 True | 215E46
13807 | GOOSE8 | GOOSE Processing simulated messages 56 False | 215E47
13808 | GOOSE8 | GOOSE Processing simulated messages 57 True | 215E48
13809 | GOOSE8 | GOOSE Processing simulated messages 57 False | 215E49
13810 | GOOSE8 | GOOSE Processing simulated messages 58 True | 215E50
13811 | GOOSE8 | GOOSE Processing simulated messages 58 False | 215E51
13812 | GOOSE8 | GOOSE Processing simulated messages 59 True | 215E52
13813 | GOOSE8 | GOOSE Processing simulated messages 59 False | 215E53
13814 | GOOSE8 | GOOSE Processing simulated messages 60 True | 215E54
13815 | GOOSE8 | GOOSE Processing simulated messages 60 False | 215E55
13816 | GOOSE8 | GOOSE Processing simulated messages 61 True | 215E56
13817 | GOOSE8 | GOOSE Processing simulated messages 61 False | 215E57
13818 | GOOSE8 | GOOSE Processing simulated messages 62 True | 215E58
13819 | GOOSE8 | GOOSE Processing simulated messages 62 False | 215E59
13820 | GOOSE8 | GOOSE Processing simulated messages 63 True | 215E60
13821 | GOOSE8 | GOOSE Processing simulated messages 63 False | 215E61
13822 | GOOSE8 | GOOSE Processing simulated messages 64 True | 215E62
13823 | GOOSE8 | GOOSE Processing simulated messages 64 False | 215E63
13888 | UCP1 | Alarm Start On | 217E0
13889 | UCP1 | Alarm Start Off | 217E1
13890 | UCP1 | Alarm On | 217E2
13891 | UCP1 | Alarm Off | 217E3
13892 | UCP1 | Start On | 217E4
13893 | UCP1 | Start Off | 217E5
13894 | UCP1 | Trip On | 217E6
13895 | UCP1 | Trip Off | 217E7
13896 | UCP1 | Block On | 217E8
13897 | UCP1 | Block Off | 217E9
13898 | UCP1 | Harmonic block On | 217E10
13899 | UCP1 | Harmonic block Off | 217E11
13952 | PGS1B | PS6 >/< Start On | 218E0
13953 | PGS1B | PS6 >/< Start Off | 218E1
13954 | PGS1B | PS6 >/< Trip On | 218E2
13955 | PGS1B | PS6 >/< Trip Off | 218E3
13956 | PGS1B | PS6 >/< Block On | 218E4
13957 | PGS1B | PS6 >/< Block Off | 218E5
13958 | PGS1B | PS7 >/< Start On | 218E6
13959 | PGS1B | PS7 >/< Start Off | 218E7
13960 | PGS1B | PS7 >/< Trip On | 218E8
13961 | PGS1B | PS7 >/< Trip Off | 218E9
13962 | PGS1B | PS7 >/< Block On | 218E10
13963 | PGS1B | PS7 >/< Block Off | 218E11
13964 | PGS1B | PS8 >/< Start On | 218E12
13965 | PGS1B | PS8 >/< Start Off | 218E13
13966 | PGS1B | PS8 >/< Trip On | 218E14
13967 | PGS1B | PS8 >/< Trip Off | 218E15
13968 | PGS1B | PS8 >/< Block On | 218E16
13969 | PGS1B | PS8 >/< Block Off | 218E17
13970 | PGS1B | PS9 >/< Start On | 218E18
13971 | PGS1B | PS9 >/< Start Off | 218E19
13972 | PGS1B | PS9 >/< Trip On | 218E20
13973 | PGS1B | PS9 >/< Trip Off | 218E21
13974 | PGS1B | PS9 >/< Block On | 218E22
13975 | PGS1B | PS9 >/< Block Off | 218E23
13976 | PGS1B | PS10 >/< Start On | 218E24
13977 | PGS1B | PS10 >/< Start Off | 218E25
13978 | PGS1B | PS10 >/< Trip On | 218E26
13979 | PGS1B | PS10 >/< Trip Off | 218E27
13980 | PGS1B | PS10 >/< Block On | 218E28
13981 | PGS1B | PS10 >/< Block Off | 218E29
14016 | GOOSE9 | GOOSE Receive needs commissioning 1 True | 219E0
14017 | GOOSE9 | GOOSE Receive needs commissioning 1 False | 219E1
14018 | GOOSE9 | GOOSE Receive needs commissioning 2 True | 219E2
14019 | GOOSE9 | GOOSE Receive needs commissioning 2 False | 219E3
14020 | GOOSE9 | GOOSE Receive needs commissioning 3 True | 219E4
14021 | GOOSE9 | GOOSE Receive needs commissioning 3 False | 219E5
14022 | GOOSE9 | GOOSE Receive needs commissioning 4 True | 219E6
14023 | GOOSE9 | GOOSE Receive needs commissioning 4 False | 219E7
14024 | GOOSE9 | GOOSE Receive needs commissioning 5 True | 219E8
14025 | GOOSE9 | GOOSE Receive needs commissioning 5 False | 219E9
14026 | GOOSE9 | GOOSE Receive needs commissioning 6 True | 219E10
14027 | GOOSE9 | GOOSE Receive needs commissioning 6 False | 219E11
14028 | GOOSE9 | GOOSE Receive needs commissioning 7 True | 219E12
14029 | GOOSE9 | GOOSE Receive needs commissioning 7 False | 219E13
14030 | GOOSE9 | GOOSE Receive needs commissioning 8 True | 219E14
14031 | GOOSE9 | GOOSE Receive needs commissioning 8 False | 219E15
14032 | GOOSE9 | GOOSE Receive needs commissioning 9 True | 219E16
14033 | GOOSE9 | GOOSE Receive needs commissioning 9 False | 219E17
14034 | GOOSE9 | GOOSE Receive needs commissioning 10 True | 219E18
14035 | GOOSE9 | GOOSE Receive needs commissioning 10 False | 219E19
14036 | GOOSE9 | GOOSE Receive needs commissioning 11 True | 219E20
14037 | GOOSE9 | GOOSE Receive needs commissioning 11 False | 219E21
14038 | GOOSE9 | GOOSE Receive needs commissioning 12 True | 219E22
14039 | GOOSE9 | GOOSE Receive needs commissioning 12 False | 219E23
14040 | GOOSE9 | GOOSE Receive needs commissioning 13 True | 219E24
14041 | GOOSE9 | GOOSE Receive needs commissioning 13 False | 219E25
14042 | GOOSE9 | GOOSE Receive needs commissioning 14 True | 219E26
14043 | GOOSE9 | GOOSE Receive needs commissioning 14 False | 219E27
14044 | GOOSE9 | GOOSE Receive needs commissioning 15 True | 219E28
14045 | GOOSE9 | GOOSE Receive needs commissioning 15 False | 219E29
14046 | GOOSE9 | GOOSE Receive needs commissioning 16 True | 219E30
14047 | GOOSE9 | GOOSE Receive needs commissioning 16 False | 219E31
14048 | GOOSE9 | GOOSE Receive needs commissioning 17 True | 219E32
14049 | GOOSE9 | GOOSE Receive needs commissioning 17 False | 219E33
14050 | GOOSE9 | GOOSE Receive needs commissioning 18 True | 219E34
14051 | GOOSE9 | GOOSE Receive needs commissioning 18 False | 219E35
14052 | GOOSE9 | GOOSE Receive needs commissioning 19 True | 219E36
14053 | GOOSE9 | GOOSE Receive needs commissioning 19 False | 219E37
14054 | GOOSE9 | GOOSE Receive needs commissioning 20 True | 219E38
14055 | GOOSE9 | GOOSE Receive needs commissioning 20 False | 219E39
14056 | GOOSE9 | GOOSE Receive needs commissioning 21 True | 219E40
14057 | GOOSE9 | GOOSE Receive needs commissioning 21 False | 219E41
14058 | GOOSE9 | GOOSE Receive needs commissioning 22 True | 219E42
14059 | GOOSE9 | GOOSE Receive needs commissioning 22 False | 219E43
14060 | GOOSE9 | GOOSE Receive needs commissioning 23 True | 219E44
14061 | GOOSE9 | GOOSE Receive needs commissioning 23 False | 219E45
14062 | GOOSE9 | GOOSE Receive needs commissioning 24 True | 219E46
14063 | GOOSE9 | GOOSE Receive needs commissioning 24 False | 219E47
14064 | GOOSE9 | GOOSE Receive needs commissioning 25 True | 219E48
14065 | GOOSE9 | GOOSE Receive needs commissioning 25 False | 219E49
14066 | GOOSE9 | GOOSE Receive needs commissioning 26 True | 219E50
14067 | GOOSE9 | GOOSE Receive needs commissioning 26 False | 219E51
14068 | GOOSE9 | GOOSE Receive needs commissioning 27 True | 219E52
14069 | GOOSE9 | GOOSE Receive needs commissioning 27 False | 219E53
14070 | GOOSE9 | GOOSE Receive needs commissioning 28 True | 219E54
14071 | GOOSE9 | GOOSE Receive needs commissioning 28 False | 219E55
14072 | GOOSE9 | GOOSE Receive needs commissioning 29 True | 219E56
14073 | GOOSE9 | GOOSE Receive needs commissioning 29 False | 219E57
14074 | GOOSE9 | GOOSE Receive needs commissioning 30 True | 219E58
14075 | GOOSE9 | GOOSE Receive needs commissioning 30 False | 219E59
14076 | GOOSE9 | GOOSE Receive needs commissioning 31 True | 219E60
14077 | GOOSE9 | GOOSE Receive needs commissioning 31 False | 219E61
14078 | GOOSE9 | GOOSE Receive needs commissioning 32 True | 219E62
14079 | GOOSE9 | GOOSE Receive needs commissioning 32 False | 219E63
14080 | GOOSE10 | GOOSE Receive needs commissioning 33 True | 220E0
14081 | GOOSE10 | GOOSE Receive needs commissioning 33 False | 220E1
14082 | GOOSE10 | GOOSE Receive needs commissioning 34 True | 220E2
14083 | GOOSE10 | GOOSE Receive needs commissioning 34 False | 220E3
14084 | GOOSE10 | GOOSE Receive needs commissioning 35 True | 220E4
14085 | GOOSE10 | GOOSE Receive needs commissioning 35 False | 220E5
14086 | GOOSE10 | GOOSE Receive needs commissioning 36 True | 220E6
14087 | GOOSE10 | GOOSE Receive needs commissioning 36 False | 220E7
14088 | GOOSE10 | GOOSE Receive needs commissioning 37 True | 220E8
14089 | GOOSE10 | GOOSE Receive needs commissioning 37 False | 220E9
14090 | GOOSE10 | GOOSE Receive needs commissioning 38 True | 220E10
14091 | GOOSE10 | GOOSE Receive needs commissioning 38 False | 220E11
14092 | GOOSE10 | GOOSE Receive needs commissioning 39 True | 220E12
14093 | GOOSE10 | GOOSE Receive needs commissioning 39 False | 220E13
14094 | GOOSE10 | GOOSE Receive needs commissioning 40 True | 220E14
14095 | GOOSE10 | GOOSE Receive needs commissioning 40 False | 220E15
14096 | GOOSE10 | GOOSE Receive needs commissioning 41 True | 220E16
14097 | GOOSE10 | GOOSE Receive needs commissioning 41 False | 220E17
14098 | GOOSE10 | GOOSE Receive needs commissioning 42 True | 220E18
14099 | GOOSE10 | GOOSE Receive needs commissioning 42 False | 220E19
14100 | GOOSE10 | GOOSE Receive needs commissioning 43 True | 220E20
14101 | GOOSE10 | GOOSE Receive needs commissioning 43 False | 220E21
14102 | GOOSE10 | GOOSE Receive needs commissioning 44 True | 220E22
14103 | GOOSE10 | GOOSE Receive needs commissioning 44 False | 220E23
14104 | GOOSE10 | GOOSE Receive needs commissioning 45 True | 220E24
14105 | GOOSE10 | GOOSE Receive needs commissioning 45 False | 220E25
14106 | GOOSE10 | GOOSE Receive needs commissioning 46 True | 220E26
14107 | GOOSE10 | GOOSE Receive needs commissioning 46 False | 220E27
14108 | GOOSE10 | GOOSE Receive needs commissioning 47 True | 220E28
14109 | GOOSE10 | GOOSE Receive needs commissioning 47 False | 220E29
14110 | GOOSE10 | GOOSE Receive needs commissioning 48 True | 220E30
14111 | GOOSE10 | GOOSE Receive needs commissioning 48 False | 220E31
14112 | GOOSE10 | GOOSE Receive needs commissioning 49 True | 220E32
14113 | GOOSE10 | GOOSE Receive needs commissioning 49 False | 220E33
14114 | GOOSE10 | GOOSE Receive needs commissioning 50 True | 220E34
14115 | GOOSE10 | GOOSE Receive needs commissioning 50 False | 220E35
14116 | GOOSE10 | GOOSE Receive needs commissioning 51 True | 220E36
14117 | GOOSE10 | GOOSE Receive needs commissioning 51 False | 220E37
14118 | GOOSE10 | GOOSE Receive needs commissioning 52 True | 220E38
14119 | GOOSE10 | GOOSE Receive needs commissioning 52 False | 220E39
14120 | GOOSE10 | GOOSE Receive needs commissioning 53 True | 220E40
14121 | GOOSE10 | GOOSE Receive needs commissioning 53 False | 220E41
14122 | GOOSE10 | GOOSE Receive needs commissioning 54 True | 220E42
14123 | GOOSE10 | GOOSE Receive needs commissioning 54 False | 220E43
14124 | GOOSE10 | GOOSE Receive needs commissioning 55 True | 220E44
14125 | GOOSE10 | GOOSE Receive needs commissioning 55 False | 220E45
14126 | GOOSE10 | GOOSE Receive needs commissioning 56 True | 220E46
14127 | GOOSE10 | GOOSE Receive needs commissioning 56 False | 220E47
14128 | GOOSE10 | GOOSE Receive needs commissioning 57 True | 220E48
14129 | GOOSE10 | GOOSE Receive needs commissioning 57 False | 220E49
14130 | GOOSE10 | GOOSE Receive needs commissioning 58 True | 220E50
14131 | GOOSE10 | GOOSE Receive needs commissioning 58 False | 220E51
14132 | GOOSE10 | GOOSE Receive needs commissioning 59 True | 220E52
14133 | GOOSE10 | GOOSE Receive needs commissioning 59 False | 220E53
14134 | GOOSE10 | GOOSE Receive needs commissioning 60 True | 220E54
14135 | GOOSE10 | GOOSE Receive needs commissioning 60 False | 220E55
14136 | GOOSE10 | GOOSE Receive needs commissioning 61 True | 220E56
14137 | GOOSE10 | GOOSE Receive needs commissioning 61 False | 220E57
14138 | GOOSE10 | GOOSE Receive needs commissioning 62 True | 220E58
14139 | GOOSE10 | GOOSE Receive needs commissioning 62 False | 220E59
14140 | GOOSE10 | GOOSE Receive needs commissioning 63 True | 220E60
14141 | GOOSE10 | GOOSE Receive needs commissioning 63 False | 220E61
14142 | GOOSE10 | GOOSE Receive needs commissioning 64 True | 220E62
14143 | GOOSE10 | GOOSE Receive needs commissioning 64 False | 220E63
14144 | EFX1 | Start forward On | 221E0
14145 | EFX1 | Start forward Off | 221E1
14146 | EFX1 | Trip forward On | 221E2
14147 | EFX1 | Trip forward Off | 221E3
14148 | EFX1 | Start reverse On | 221E4
14149 | EFX1 | Start reverse Off | 221E5
14150 | EFX1 | Trip reverse On | 221E6
14151 | EFX1 | Trip reverse Off | 221E7
14152 | EFX1 | Block On | 221E8
14153 | EFX1 | Block Off | 221E9
14208 | EFX2 | Start forward On | 222E0
14209 | EFX2 | Start forward Off | 222E1
14210 | EFX2 | Trip forward On | 222E2
14211 | EFX2 | Trip forward Off | 222E3
14212 | EFX2 | Start reverse On | 222E4
14213 | EFX2 | Start reverse Off | 222E5
14214 | EFX2 | Trip reverse On | 222E6
14215 | EFX2 | Trip reverse Off | 222E7
14216 | EFX2 | Block On | 222E8
14217 | EFX2 | Block Off | 222E9
14272 | EFX3 | Start forward On | 223E0
14273 | EFX3 | Start forward Off | 223E1
14274 | EFX3 | Trip forward On | 223E2
14275 | EFX3 | Trip forward Off | 223E3
14276 | EFX3 | Start reverse On | 223E4
14277 | EFX3 | Start reverse Off | 223E5
14278 | EFX3 | Trip reverse On | 223E6
14279 | EFX3 | Trip reverse Off | 223E7
14280 | EFX3 | Block On | 223E8
14281 | EFX3 | Block Off | 223E9
14336 | EFX4 | Start forward On | 224E0
14337 | EFX4 | Start forward Off | 224E1
14338 | EFX4 | Trip forward On | 224E2
14339 | EFX4 | Trip forward Off | 224E3
14340 | EFX4 | Start reverse On | 224E4
14341 | EFX4 | Start reverse Off | 224E5
14342 | EFX4 | Trip reverse On | 224E6
14343 | EFX4 | Trip reverse Off | 224E7
14344 | EFX4 | Block On | 224E8
14345 | EFX4 | Block Off | 224E9
14400 | ARCS1 | Arc Channel 1 On | 225E0
14401 | ARCS1 | Arc Channel 1 Off | 225E1
14402 | ARCS1 | Arc Channel 2 On | 225E2
14403 | ARCS1 | Arc Channel 2 Off | 225E3
14404 | ARCS1 | Arc Channel 3 On | 225E4
14405 | ARCS1 | Arc Channel 3 Off | 225E5
14406 | ARCS1 | Arc Channel 4 On | 225E6
14407 | ARCS1 | Arc Channel 4 Off | 225E7
14408 | ARCS1 | Arc Channel 5 On | 225E8
14409 | ARCS1 | Arc Channel 5 Off | 225E9
14410 | ARCS1 | Arc Channel 6 On | 225E10
14411 | ARCS1 | Arc Channel 6 Off | 225E11
14412 | ARCS1 | Arc Channel 7 On | 225E12
14413 | ARCS1 | Arc Channel 7 Off | 225E13
14414 | ARCS1 | Arc Channel 8 On | 225E14
14415 | ARCS1 | Arc Channel 8 Off | 225E15
14416 | ARCS1 | Arc Channel 9 On | 225E16
14417 | ARCS1 | Arc Channel 9 Off | 225E17
14418 | ARCS1 | Arc Channel 10 On | 225E18
14419 | ARCS1 | Arc Channel 10 Off | 225E19
14420 | ARCS1 | Arc Channel 11 On | 225E20
14421 | ARCS1 | Arc Channel 11 Off | 225E21
14422 | ARCS1 | Arc Channel 12 On | 225E22
14423 | ARCS1 | Arc Channel 12 Off | 225E23
14424 | ARCS1 | Arc Channel 13 On | 225E24
14425 | ARCS1 | Arc Channel 13 Off | 225E25
14426 | ARCS1 | Arc Channel 14 On | 225E26
14427 | ARCS1 | Arc Channel 14 Off | 225E27
14428 | ARCS1 | Arc Channel 15 On | 225E28
14429 | ARCS1 | Arc Channel 15 Off | 225E29
14430 | ARCS1 | Arc Channel 16 On | 225E30
14431 | ARCS1 | Arc Channel 16 Off | 225E31
14432 | ARCS1 | Arc Channel 17 On | 225E32
14433 | ARCS1 | Arc Channel 17 Off | 225E33
14434 | ARCS1 | Arc Channel 18 On | 225E34
14435 | ARCS1 | Arc Channel 18 Off | 225E35
14436 | ARCS1 | Arc Channel 19 On | 225E36
14437 | ARCS1 | Arc Channel 19 Off | 225E37
14438 | ARCS1 | Arc Channel 20 On | 225E38
14439 | ARCS1 | Arc Channel 20 Off | 225E39
14440 | ARCS1 | Arc Channel 21 On | 225E40
14441 | ARCS1 | Arc Channel 21 Off | 225E41
14442 | ARCS1 | Arc Channel 22 On | 225E42
14443 | ARCS1 | Arc Channel 22 Off | 225E43
14444 | ARCS1 | Arc Channel 23 On | 225E44
14445 | ARCS1 | Arc Channel 23 Off | 225E45
14446 | ARCS1 | Arc Channel 24 On | 225E46
14447 | ARCS1 | Arc Channel 24 Off | 225E47
14464 | ARCS2 | Arc Fiber 1 On | 226E0
14465 | ARCS2 | Arc fiber 1 Off | 226E1
14466 | ARCS2 | Arc Fiber 2 On | 226E2
14467 | ARCS2 | Arc fiber 2 Off | 226E3
14468 | ARCS2 | Arc Fiber 3 On | 226E4
14469 | ARCS2 | Arc fiber 3 Off | 226E5
14470 | ARCS2 | Arc Fiber 4 On | 226E6
14471 | ARCS2 | Arc fiber 4 Off | 226E7
14472 | ARCS2 | Arc Fiber 5 On | 226E8
14473 | ARCS2 | Arc fiber 5 Off | 226E9
14474 | ARCS2 | Arc Fiber 6 On | 226E10
14475 | ARCS2 | Arc fiber 6 Off | 226E11
14476 | ARCS2 | Arc Fiber 7 On | 226E12
14477 | ARCS2 | Arc fiber 7 Off | 226E13
14478 | ARCS2 | Arc Fiber 8 On | 226E14
14479 | ARCS2 | Arc fiber 8 Off | 226E15
14480 | ARCS2 | Arc Fiber 9 On | 226E16
14481 | ARCS2 | Arc fiber 9 Off | 226E17
14482 | ARCS2 | Arc Fiber 10 On | 226E18
14483 | ARCS2 | Arc fiber 10 Off | 226E19
14484 | ARCS2 | Arc Fiber 11 On | 226E20
14485 | ARCS2 | Arc fiber 11 Off | 226E21
14486 | ARCS2 | Arc Fiber 12 On | 226E22
14487 | ARCS2 | Arc fiber 12 Off | 226E23
14488 | ARCS2 | Arc Fiber 13 On | 226E24
14489 | ARCS2 | Arc fiber 13 Off | 226E25
14490 | ARCS2 | Arc Fiber 14 On | 226E26
14491 | ARCS2 | Arc fiber 14 Off | 226E27
14492 | ARCS2 | Arc Fiber 15 On | 226E28
14493 | ARCS2 | Arc fiber 15 Off | 226E29
14494 | ARCS2 | Arc Fiber 16 On | 226E30
14495 | ARCS2 | Arc fiber 16 Off | 226E31
14496 | ARCS2 | Arc Fiber 17 On | 226E32
14497 | ARCS2 | Arc fiber 17 Off | 226E33
14498 | ARCS2 | Arc Fiber 18 On | 226E34
14499 | ARCS2 | Arc fiber 18 Off | 226E35
14528 | ARCSE1 | Arc Channel 1 Error On | 227E0
14529 | ARCSE1 | Arc Channel 1 Error Off | 227E1
14530 | ARCSE1 | Arc Channel 2 Error On | 227E2
14531 | ARCSE1 | Arc Channel 2 Error Off | 227E3
14532 | ARCSE1 | Arc Channel 3 Error On | 227E4
14533 | ARCSE1 | Arc Channel 3 Error Off | 227E5
14534 | ARCSE1 | Arc Channel 4 Error On | 227E6
14535 | ARCSE1 | Arc Channel 4 Error Off | 227E7
14536 | ARCSE1 | Arc Channel 5 Error On | 227E8
14537 | ARCSE1 | Arc Channel 5 Error Off | 227E9
14538 | ARCSE1 | Arc Channel 6 Error On | 227E10
14539 | ARCSE1 | Arc Channel 6 Error Off | 227E11
14540 | ARCSE1 | Arc Channel 7 Error On | 227E12
14541 | ARCSE1 | Arc Channel 7 Error Off | 227E13
14542 | ARCSE1 | Arc Channel 8 Error On | 227E14
14543 | ARCSE1 | Arc Channel 8 Error Off | 227E15
14544 | ARCSE1 | Arc Channel 9 Error On | 227E16
14545 | ARCSE1 | Arc Channel 9 Error Off | 227E17
14546 | ARCSE1 | Arc Channel 10 Error On | 227E18
14547 | ARCSE1 | Arc Channel 10 Error Off | 227E19
14548 | ARCSE1 | Arc Channel 11 Error On | 227E20
14549 | ARCSE1 | Arc Channel 11 Error Off | 227E21
14550 | ARCSE1 | Arc Channel 12 Error On | 227E22
14551 | ARCSE1 | Arc Channel 12 Error Off | 227E23
14552 | ARCSE1 | Arc Channel 13 Error On | 227E24
14553 | ARCSE1 | Arc Channel 13 Error Off | 227E25
14554 | ARCSE1 | Arc Channel 14 Error On | 227E26
14555 | ARCSE1 | Arc Channel 14 Error Off | 227E27
14556 | ARCSE1 | Arc Channel 15 Error On | 227E28
14557 | ARCSE1 | Arc Channel 15 Error Off | 227E29
14558 | ARCSE1 | Arc Channel 16 Error On | 227E30
14559 | ARCSE1 | Arc Channel 16 Error Off | 227E31
14560 | ARCSE1 | Arc Channel 17 Error On | 227E32
14561 | ARCSE1 | Arc Channel 17 Error Off | 227E33
14562 | ARCSE1 | Arc Channel 18 Error On | 227E34
14563 | ARCSE1 | Arc Channel 18 Error Off | 227E35
14564 | ARCSE1 | Arc Channel 19 Error On | 227E36
14565 | ARCSE1 | Arc Channel 19 Error Off | 227E37
14566 | ARCSE1 | Arc Channel 20 Error On | 227E38
14567 | ARCSE1 | Arc Channel 20 Error Off | 227E39
14568 | ARCSE1 | Arc Channel 21 Error On | 227E40
14569 | ARCSE1 | Arc Channel 21 Error Off | 227E41
14570 | ARCSE1 | Arc Channel 22 Error On | 227E42
14571 | ARCSE1 | Arc Channel 22 Error Off | 227E43
14572 | ARCSE1 | Arc Channel 23 Error On | 227E44
14573 | ARCSE1 | Arc Channel 23 Error Off | 227E45
14574 | ARCSE1 | Arc Channel 24 Error On | 227E46
14575 | ARCSE1 | Arc Channel 24 Error Off | 227E47
14592 | ARCSE2 | Arc Fiber 1 Error On | 228E0
14593 | ARCSE2 | Arc Fiber 1 Error Off | 228E1
14594 | ARCSE2 | Arc Fiber 2 Error On | 228E2
14595 | ARCSE2 | Arc Fiber 2 Error Off | 228E3
14596 | ARCSE2 | Arc Fiber 3 Error On | 228E4
14597 | ARCSE2 | Arc Fiber 3 Error Off | 228E5
14598 | ARCSE2 | Arc Fiber 4 Error On | 228E6
14599 | ARCSE2 | Arc Fiber 4 Error Off | 228E7
14600 | ARCSE2 | Arc Fiber 5 Error On | 228E8
14601 | ARCSE2 | Arc Fiber 5 Error Off | 228E9
14602 | ARCSE2 | Arc Fiber 6 Error On | 228E10
14603 | ARCSE2 | Arc Fiber 6 Error Off | 228E11
14604 | ARCSE2 | Arc Fiber 7 Error On | 228E12
14605 | ARCSE2 | Arc Fiber 7 Error Off | 228E13
14606 | ARCSE2 | Arc Fiber 8 Error On | 228E14
14607 | ARCSE2 | Arc Fiber 8 Error Off | 228E15
14608 | ARCSE2 | Arc Fiber 9 Error On | 228E16
14609 | ARCSE2 | Arc Fiber 9 Error Off | 228E17
14610 | ARCSE2 | Arc Fiber 10 Error On | 228E18
14611 | ARCSE2 | Arc Fiber 10 Error Off | 228E19
14612 | ARCSE2 | Arc Fiber 11 Error On | 228E20
14613 | ARCSE2 | Arc Fiber 11 Error Off | 228E21
14614 | ARCSE2 | Arc Fiber 12 Error On | 228E22
14615 | ARCSE2 | Arc Fiber 12 Error Off | 228E23
14616 | ARCSE2 | Arc Fiber 13 Error On | 228E24
14617 | ARCSE2 | Arc Fiber 13 Error Off | 228E25
14618 | ARCSE2 | Arc Fiber 14 Error On | 228E26
14619 | ARCSE2 | Arc Fiber 14 Error Off | 228E27
14620 | ARCSE2 | Arc Fiber 15 Error On | 228E28
14621 | ARCSE2 | Arc Fiber 15 Error Off | 228E29
14622 | ARCSE2 | Arc Fiber 16 Error On | 228E30
14623 | ARCSE2 | Arc Fiber 16 Error Off | 228E31
14624 | ARCSE2 | Arc Fiber 17 Error On | 228E32
14625 | ARCSE2 | Arc Fiber 17 Error Off | 228E33
14626 | ARCSE2 | Arc Fiber 18 Error On | 228E34
14627 | ARCSE2 | Arc Fiber 18 Error Off | 228E35
14656 | ARCOE1 | Arc HSO 1 On | 229E0
14657 | ARCOE1 | Arc HSO 1 Off | 229E1
14658 | ARCOE1 | Arc HSO 2 On | 229E2
14659 | ARCOE1 | Arc HSO 2 Off | 229E3
14660 | ARCOE1 | Arc HSO 3 On | 229E4
14661 | ARCOE1 | Arc HSO 3 Off | 229E5
14662 | ARCOE1 | Arc HSO 4 On | 229E6
14663 | ARCOE1 | Arc HSO 4 Off | 229E7
14664 | ARCOE1 | Arc HSO 5 On | 229E8
14665 | ARCOE1 | Arc HSO 5 Off | 229E9
14666 | ARCOE1 | Arc HSO 6 On | 229E10
14667 | ARCOE1 | Arc HSO 6 Off | 229E11
14668 | ARCOE1 | Arc HSO 7 On | 229E12
14669 | ARCOE1 | Arc HSO 7 Off | 229E13
14670 | ARCOE1 | Arc HSO 8 On | 229E14
14671 | ARCOE1 | Arc HSO 8 Off | 229E15
14672 | ARCOE1 | Arc HSO 9 On | 229E16
14673 | ARCOE1 | Arc HSO 9 Off | 229E17
14674 | ARCOE1 | Arc HSO 10 On | 229E18
14675 | ARCOE1 | Arc HSO 10 Off | 229E19
14676 | ARCOE1 | Arc HSO 11 On | 229E20
14677 | ARCOE1 | Arc HSO 11 Off | 229E21
14678 | ARCOE1 | Arc HSO 12 On | 229E22
14679 | ARCOE1 | Arc HSO 12 Off | 229E23
14720 | ARCOE2 | Arc QD 1 On | 230E0
14721 | ARCOE2 | Arc QD 1 Off | 230E1
14722 | ARCOE2 | Arc QD 2 On | 230E2
14723 | ARCOE2 | Arc QD 2 Off | 230E3
14724 | ARCOE2 | Arc QD 3 On | 230E4
14725 | ARCOE2 | Arc QD 3 Off | 230E5
14726 | ARCOE2 | Arc QD 4 On | 230E6
14727 | ARCOE2 | Arc QD 4 Off | 230E7
14728 | ARCOE2 | Arc QD 5 On | 230E8
14729 | ARCOE2 | Arc QD 5 Off | 230E9
14730 | ARCOE2 | Arc QD 6 On | 230E10
14731 | ARCOE2 | Arc QD 6 Off | 230E11
14784 | PFC1 | Increase capacitance request On | 231E0
14785 | PFC1 | Increase capacitance request Off | 231E1
14786 | PFC1 | Decrease capacitance request On | 231E2
14787 | PFC1 | Decrease capacitance request Off | 231E3
14788 | PFC1 | Switching time On | 231E4
14789 | PFC1 | Switching time Off | 231E5
14790 | PFC1 | Manual control mode On | 231E6
14791 | PFC1 | Manual control mode Off | 231E7
14792 | PFC1 | PFC block On | 231E8
14793 | PFC1 | PFC block Off | 231E9
14794 | PFC1 | Bank 1 discharging On | 231E10
14795 | PFC1 | Bank 1 discharging Off | 231E11
14796 | PFC1 | Bank 2 discharging On | 231E12
14797 | PFC1 | Bank 2 discharging Off | 231E13
14798 | PFC1 | Bank 3 discharging On | 231E14
14799 | PFC1 | Bank 3 discharging Off | 231E15
14800 | PFC1 | Bank 4 discharging On | 231E16
14801 | PFC1 | Bank 4 discharging Off | 231E17
14802 | PFC1 | Bank 5 discharging On | 231E18
14803 | PFC1 | Bank 5 discharging Off | 231E19
14804 | PFC1 | Switching failure On | 231E20
14805 | PFC1 | Switching failure Off | 231E21
14806 | PFC1 | Starting increase capacitance On | 231E22
14807 | PFC1 | Starting increase capacitance Off | 231E23
14808 | PFC1 | Starting decrease capacitance On | 231E24
14809 | PFC1 | Starting decrease capacitance Off | 231E25
14848 | SYNX1 | SYN1 Voltage difference Ok On | 232E0
14849 | SYNX1 | SYN1 Voltage difference Ok Off | 232E1
14850 | SYNX1 | SYN1 Angle difference Ok On | 232E2
14851 | SYNX1 | SYN1 Angle difference Ok Off | 232E3
14852 | SYNX1 | SYN1 Frequency difference Ok On | 232E4
14853 | SYNX1 | SYN1 Frequency difference Ok On | 232E5
14854 | SYNX1 | SYN1 Live Live Condition On | 232E6
14855 | SYNX1 | SYN1 Live Live Condition Off | 232E7
14856 | SYNX1 | SYN1 Live Dead Condition On | 232E8
14857 | SYNX1 | SYN1 Live Dead Condition Off | 232E9
14858 | SYNX1 | SYN1 Dead Live Condition On | 232E10
14859 | SYNX1 | SYN1 Dead Live Condition Off | 232E11
14860 | SYNX1 | SYN1 Dead Dead Condition On | 232E12
14861 | SYNX1 | SYN1 Dead Dead Condition On | 232E13
14862 | SYNX1 | SYN1 Voltage Difference too high Vbus > Vline On | 232E14
14863 | SYNX1 | SYN1 Voltage Difference too high Vbus > Vline Off | 232E15
14864 | SYNX1 | SYN1 Voltage Difference too high Vline > Vbus On | 232E16
14865 | SYNX1 | SYN1 Voltage Difference too high Vline > Vbus Off | 232E17
14866 | SYNX1 | SYN1 Frequency Difference too high fbus > fline On | 232E18
14867 | SYNX1 | SYN1 Frequency Difference too high fbus > fline Off | 232E19
14868 | SYNX1 | SYN1 Frequency Difference too high fline > fbus On | 232E20
14869 | SYNX1 | SYN1 Frequency Difference too high fline > fbus Off | 232E21
14870 | SYNX1 | SYN1 Angle Difference too high a bus leads a line On | 232E22
14871 | SYNX1 | SYN1 Angle Difference too high a bus leads a line Off | 232E23
14872 | SYNX1 | SYN1 Angle Difference too high a line leads a bus On | 232E24
14873 | SYNX1 | SYN1 Angle Difference too high a line leads a bus Off | 232E25
14874 | SYNX1 | SYN1 Bus voltage Live On | 232E26
14875 | SYNX1 | SYN1 Bus voltage Live Off | 232E27
14876 | SYNX1 | SYN1 Bus voltage Dead On | 232E28
14877 | SYNX1 | SYN1 Bus voltage Dead Off | 232E29
14878 | SYNX1 | SYN1 Line voltage Live On | 232E30
14879 | SYNX1 | SYN1 Line voltage Live Off | 232E31
14880 | SYNX1 | SYN1 Line voltage Dead On | 232E32
14881 | SYNX1 | SYN1 Line voltage Dead Off | 232E33
14912 | SYNX2 | SYN2 Voltage difference Ok On | 233E0
14913 | SYNX2 | SYN2 Voltage difference Ok Off | 233E1
14914 | SYNX2 | SYN2 Angle difference Ok On | 233E2
14915 | SYNX2 | SYN2 Angle difference Ok Off | 233E3
14916 | SYNX2 | SYN2 Frequency difference Ok On | 233E4
14917 | SYNX2 | SYN2 Frequency difference Ok On | 233E5
14918 | SYNX2 | SYN2 Live Live Condition On | 233E6
14919 | SYNX2 | SYN2 Live Live Condition Off | 233E7
14920 | SYNX2 | SYN2 Live Dead Condition On | 233E8
14921 | SYNX2 | SYN2 Live Dead Condition Off | 233E9
14922 | SYNX2 | SYN2 Dead Live Condition On | 233E10
14923 | SYNX2 | SYN2 Dead Live Condition Off | 233E11
14924 | SYNX2 | SYN2 Dead Dead Condition On | 233E12
14925 | SYNX2 | SYN2 Dead Dead Condition On | 233E13
14926 | SYNX2 | SYN2 Voltage Difference too high Vbus > Vline On | 233E14
14927 | SYNX2 | SYN2 Voltage Difference too high Vbus > Vline Off | 233E15
14928 | SYNX2 | SYN2 Voltage Difference too high Vline > Vbus On | 233E16
14929 | SYNX2 | SYN2 Voltage Difference too high Vline > Vbus Off | 233E17
14930 | SYNX2 | SYN2 Frequency Difference too high fbus > fline On | 233E18
14931 | SYNX2 | SYN2 Frequency Difference too high fbus > fline Off | 233E19
14932 | SYNX2 | SYN2 Frequency Difference too high fline > fbus On | 233E20
14933 | SYNX2 | SYN2 Frequency Difference too high fline > fbus Off | 233E21
14934 | SYNX2 | SYN2 Angle Difference too high a bus leads a line On | 233E22
14935 | SYNX2 | SYN2 Angle Difference too high a bus leads a line Off | 233E23
14936 | SYNX2 | SYN2 Angle Difference too high a line leads a bus On | 233E24
14937 | SYNX2 | SYN2 Angle Difference too high a line leads a bus Off | 233E25
14938 | SYNX2 | SYN2 Bus voltage Live On | 233E26
14939 | SYNX2 | SYN2 Bus voltage Live Off | 233E27
14940 | SYNX2 | SYN2 Bus voltage Dead On | 233E28
14941 | SYNX2 | SYN2 Bus voltage Dead Off | 233E29
14942 | SYNX2 | SYN2 Line voltage Live On | 233E30
14943 | SYNX2 | SYN2 Line voltage Live Off | 233E31
14944 | SYNX2 | SYN2 Line voltage Dead On | 233E32
14945 | SYNX2 | SYN2 Line voltage Dead Off | 233E33
14976 | SYNX3 | SYN3 Voltage difference Ok On | 234E0
14977 | SYNX3 | SYN3 Voltage difference Ok Off | 234E1
14978 | SYNX3 | SYN3 Angle difference Ok On | 234E2
14979 | SYNX3 | SYN3 Angle difference Ok Off | 234E3
14980 | SYNX3 | SYN3 Frequency difference Ok On | 234E4
14981 | SYNX3 | SYN3 Frequency difference Ok On | 234E5
14982 | SYNX3 | SYN3 Live Live Condition On | 234E6
14983 | SYNX3 | SYN3 Live Live Condition Off | 234E7
14984 | SYNX3 | SYN3 Live Dead Condition On | 234E8
14985 | SYNX3 | SYN3 Live Dead Condition Off | 234E9
14986 | SYNX3 | SYN3 Dead Live Condition On | 234E10
14987 | SYNX3 | SYN3 Dead Live Condition Off | 234E11
14988 | SYNX3 | SYN3 Dead Dead Condition On | 234E12
14989 | SYNX3 | SYN3 Dead Dead Condition On | 234E13
14990 | SYNX3 | SYN3 Voltage Difference too high Vbus > Vline On | 234E14
14991 | SYNX3 | SYN3 Voltage Difference too high Vbus > Vline Off | 234E15
14992 | SYNX3 | SYN3 Voltage Difference too high Vline > Vbus On | 234E16
14993 | SYNX3 | SYN3 Voltage Difference too high Vline > Vbus Off | 234E17
14994 | SYNX3 | SYN3 Frequency Difference too high fbus > fline On | 234E18
14995 | SYNX3 | SYN3 Frequency Difference too high fbus > fline Off | 234E19
14996 | SYNX3 | SYN3 Frequency Difference too high fline > fbus On | 234E20
14997 | SYNX3 | SYN3 Frequency Difference too high fline > fbus Off | 234E21
14998 | SYNX3 | SYN3 Angle Difference too high a bus leads a line On | 234E22
14999 | SYNX3 | SYN3 Angle Difference too high a bus leads a line Off | 234E23
15000 | SYNX3 | SYN3 Angle Difference too high a line leads a bus On | 234E24
15001 | SYNX3 | SYN3 Angle Difference too high a line leads a bus Off | 234E25
15002 | SYNX3 | SYN3 Bus voltage Live On | 234E26
15003 | SYNX3 | SYN3 Bus voltage Live Off | 234E27
15004 | SYNX3 | SYN3 Bus voltage Dead On | 234E28
15005 | SYNX3 | SYN3 Bus voltage Dead Off | 234E29
15006 | SYNX3 | SYN3 Line voltage Live On | 234E30
15007 | SYNX3 | SYN3 Line voltage Live Off | 234E31
15008 | SYNX3 | SYN3 Line voltage Dead On | 234E32
15009 | SYNX3 | SYN3 Line voltage Dead Off | 234E33
15040 | DMA1 | IL1 demand alarm On | 235E0
15041 | DMA1 | IL1 demand alarm Off | 235E1
15042 | DMA1 | IL2 demand alarm On | 235E2
15043 | DMA1 | IL2 demand alarm Off | 235E3
15044 | DMA1 | IL3 demand alarm On | 235E4
15045 | DMA1 | IL3 demand alarm Off | 235E5
15046 | DMA1 | Apparent power demand alarm On | 235E6
15047 | DMA1 | Apparent power demand alarm Off | 235E7
15048 | DMA1 | Active power demand alarm On | 235E8
15049 | DMA1 | Active power demand alarm Off | 235E9
15050 | DMA1 | Reactive power demand alarm On | 235E10
15051 | DMA1 | Reactive power demand alarm Off | 235E11
15052 | DMA1 | Power factor demand alarm On | 235E12
15053 | DMA1 | Power Factor demand alarm Off | 235E13
15054 | DMA1 | IL1 demand harmonic alarm On | 235E14
15055 | DMA1 | IL1 demand harmonic alarm Off | 235E15
15056 | DMA1 | IL2 demand harmonic alarm On | 235E16
15057 | DMA1 | IL2 demand harmonic alarm Off | 235E17
15058 | DMA1 | IL3 demand harmonic alarm On | 235E18
15059 | DMA1 | IL3 demand harmonic alarm Off | 235E19
15060 | DMA1 | Demand block On | 235E20
15061 | DMA1 | Demand block Off | 235E21
15104 | LPM | Fast CT supervision On | 236E0
15105 | LPM | Fast CT supervision Off | 236E1
15106 | LPM | Load change supervision On | 236E2
15107 | LPM | Load change supervision Off | 236E3
15108 | LPM | Line communication ok On | 236E4
15109 | LPM | Line communication ok Off | 236E5
15110 | LPM | Line communication failure On | 236E6
15111 | LPM | Line communication failure Off | 236E7
15112 | LPM | Any prot. communication failure On | 236E8
15113 | LPM | Any prot. communication failure Off | 236E9
15114 | LPM | Line differential clocks synchronized On | 236E10
15115 | LPM | Line differential clocks synchronized Off | 236E11
15116 | LPM | Line differential clock synchronization lost On | 236E12
15117 | LPM | Line differential clock synchronization lost Off | 236E13
15168 | ARC2 | Zone1 Trip On | 237E0
15169 | ARC2 | Zone1 Trip Off | 237E1
15170 | ARC2 | Zone1 Block On | 237E2
15171 | ARC2 | Zone1 Block Off | 237E3
15172 | ARC2 | Zone2 Trip On | 237E4
15173 | ARC2 | Zone2 Trip Off | 237E5
15174 | ARC2 | Zone2 Block On | 237E6
15175 | ARC2 | Zone2 Block Off | 237E7
15176 | ARC2 | Zone3 Trip On | 237E8
15177 | ARC2 | Zone3 Trip Off | 237E9
15178 | ARC2 | Zone3 Block On | 237E10
15179 | ARC2 | Zone3 Block Off | 237E11
15180 | ARC2 | Zone4 Trip On | 237E12
15181 | ARC2 | Zone4 Trip Off | 237E13
15182 | ARC2 | Zone4 Block On | 237E14
15183 | ARC2 | Zone4 Block Off | 237E15
15184 | ARC2 | Ph Current Blocked On | 237E16
15185 | ARC2 | Ph Current Blocked Off | 237E17
15186 | ARC2 | Ph Current Start On | 237E18
15187 | ARC2 | Ph Current Start Off | 237E19
15188 | ARC2 | Res Current Blocked On | 237E20
15189 | ARC2 | Res Current Blocked Off | 237E21
15190 | ARC2 | Res Current Start On | 237E22
15191 | ARC2 | Res Current Start Off | 237E23
15192 | ARC2 | Channel 1 Light On | 237E24
15193 | ARC2 | Channel 1 Light Off | 237E25
15194 | ARC2 | Channel 1 Pressure On | 237E26
15195 | ARC2 | Channel 1 Pressure Off | 237E27
15196 | ARC2 | Channel 2 Light On | 237E28
15197 | ARC2 | Channel 2 Light Off | 237E29
15198 | ARC2 | Channel 2 Pressure On | 237E30
15199 | ARC2 | Channel 2 Pressure Off | 237E31
15200 | ARC2 | Channel 3 Light On | 237E32
15201 | ARC2 | Channel 3 Light Off | 237E33
15202 | ARC2 | Channel 3 Pressure On | 237E34
15203 | ARC2 | Channel 3 Pressure Off | 237E35
15204 | ARC2 | Channel 4 Light On | 237E36
15205 | ARC2 | Channel 4 Light Off | 237E37
15206 | ARC2 | Channel 4 Pressure On | 237E38
15207 | ARC2 | Channel 4 Pressure Off | 237E39
15208 | ARC2 | DI Signal On | 237E40
15209 | ARC2 | DI Signal Off | 237E41
15232 | LVRT1 | Vstart< On | 238E0
15233 | LVRT1 | Vstart< Off | 238E1
15234 | LVRT1 | Vtrip< On | 238E2
15235 | LVRT1 | Vtrip< Off | 238E3
15236 | LVRT1 | LVRT block On | 238E4
15237 | LVRT1 | LVRT block Off | 238E5
15238 | LVRT1 | LVRT UV Block On | 238E6
15239 | LVRT1 | LVRT UV Block Off | 238E7
15296 | PVPS | No events needed for SPA | 239E0

## AQ-250 SPA map v2.5.7.1-303-AP2
SPA Ch | SPA Data | Ch Name | Description | Type | Access | Range | Settinggroup
46 | V1 | OBJ1 | Open Select | UINT32 | W | 1=Select
46 | V2 | OBJ1 | Close Select | UINT32 | W | 1=Select
46 | V3 | OBJ1 | Execute | UINT32 | W | 1=Execute
46 | V4 | OBJ1 | Cancel | UINT32 | W | 1=Cancel
46 | V5 | OBJ1 | Direct Open | UINT32 | W | 1=Open
46 | V6 | OBJ1 | Direct Close | UINT32 | W | 1=Close
47 | V1 | OBJ2 | Open Select | UINT32 | W | 1=Select
47 | V2 | OBJ2 | Close Select | UINT32 | W | 1=Select
47 | V3 | OBJ2 | Execute | UINT32 | W | 1=Execute
47 | V4 | OBJ2 | Cancel | UINT32 | W | 1=Cancel
47 | V5 | OBJ2 | Direct Open | UINT32 | W | 1=Open
47 | V6 | OBJ2 | Direct Close | UINT32 | W | 1=Close
48 | V1 | OBJ3 | Open Select | UINT32 | W | 1=Select
48 | V2 | OBJ3 | Close Select | UINT32 | W | 1=Select
48 | V3 | OBJ3 | Execute | UINT32 | W | 1=Execute
48 | V4 | OBJ3 | Cancel | UINT32 | W | 1=Cancel
48 | V5 | OBJ3 | Direct Open | UINT32 | W | 1=Open
48 | V6 | OBJ3 | Direct Close | UINT32 | W | 1=Close
49 | V1 | OBJ4 | Open Select | UINT32 | W | 1=Select
49 | V2 | OBJ4 | Close Select | UINT32 | W | 1=Select
49 | V3 | OBJ4 | Execute | UINT32 | W | 1=Execute
49 | V4 | OBJ4 | Cancel | UINT32 | W | 1=Cancel
49 | V5 | OBJ4 | Direct Open | UINT32 | W | 1=Open
49 | V6 | OBJ4 | Direct Close | UINT32 | W | 1=Close
50 | V1 | OBJ5 | Open Select | UINT32 | W | 1=Select
50 | V2 | OBJ5 | Close Select | UINT32 | W | 1=Select
50 | V3 | OBJ5 | Execute | UINT32 | W | 1=Execute
50 | V4 | OBJ5 | Cancel | UINT32 | W | 1=Cancel
50 | V5 | OBJ5 | Direct Open | UINT32 | W | 1=Open
50 | V6 | OBJ5 | Direct Close | UINT32 | W | 1=Close
150 | V1 | OBJ6 | Open Select | UINT32 | W | 1=Select
150 | V2 | OBJ6 | Close Select | UINT32 | W | 1=Select
150 | V3 | OBJ6 | Execute | UINT32 | W | 1=Execute
150 | V4 | OBJ6 | Cancel | UINT32 | W | 1=Cancel
150 | V5 | OBJ6 | Direct Open | UINT32 | W | 1=Open
150 | V6 | OBJ6 | Direct Close | UINT32 | W | 1=Close
151 | V1 | OBJ7 | Open Select | UINT32 | W | 1=Select
151 | V2 | OBJ7 | Close Select | UINT32 | W | 1=Select
151 | V3 | OBJ7 | Execute | UINT32 | W | 1=Execute
151 | V4 | OBJ7 | Cancel | UINT32 | W | 1=Cancel
151 | V5 | OBJ7 | Direct Open | UINT32 | W | 1=Open
151 | V6 | OBJ7 | Direct Close | UINT32 | W | 1=Close
152 | V1 | OBJ8 | Open Select | UINT32 | W | 1=Select
152 | V2 | OBJ8 | Close Select | UINT32 | W | 1=Select
152 | V3 | OBJ8 | Execute | UINT32 | W | 1=Execute
152 | V4 | OBJ8 | Cancel | UINT32 | W | 1=Cancel
152 | V5 | OBJ8 | Direct Open | UINT32 | W | 1=Open
152 | V6 | OBJ8 | Direct Close | UINT32 | W | 1=Close
153 | V1 | OBJ9 | Open Select | UINT32 | W | 1=Select
153 | V2 | OBJ9 | Close Select | UINT32 | W | 1=Select
153 | V3 | OBJ9 | Execute | UINT32 | W | 1=Execute
153 | V4 | OBJ9 | Cancel | UINT32 | W | 1=Cancel
153 | V5 | OBJ9 | Direct Open | UINT32 | W | 1=Open
153 | V6 | OBJ9 | Direct Close | UINT32 | W | 1=Close
154 | V1 | OBJ10 | Open Select | UINT32 | W | 1=Select
154 | V2 | OBJ10 | Close Select | UINT32 | W | 1=Select
154 | V3 | OBJ10 | Execute | UINT32 | W | 1=Execute
154 | V4 | OBJ10 | Cancel | UINT32 | W | 1=Cancel
154 | V5 | OBJ10 | Direct Open | UINT32 | W | 1=Open
154 | V6 | OBJ10 | Direct Close | UINT32 | W | 1=Close
116 | S1 | MEAS1 | Side 1 Current meas update interval | UINT32 | RW | 5...10000
116 | I1 | MEAS1 | Pri.Pha.curr.IL1 | FLOAT | R | 0...100000
116 | I2 | MEAS1 | Pri.Pha.curr.IL2 | FLOAT | R | 0...100000
116 | I3 | MEAS1 | Pri.Pha.curr.IL3 | FLOAT | R | 0...100000
116 | I4 | MEAS1 | Pha.angle IL1 | FLOAT | R | -360...360
116 | I5 | MEAS1 | Pha.angle IL2 | FLOAT | R | -360...360
116 | I6 | MEAS1 | Pha.angle IL3 | FLOAT | R | -360...360
116 | I7 | MEAS1 | Pri.Res.curr.I01 | FLOAT | R | 0...100000
116 | I8 | MEAS1 | Res.curr.angle I01 | FLOAT | R | -360...360
116 | I9 | MEAS1 | Pri.Res.curr.I02 | FLOAT | R | 0...100000
116 | I10 | MEAS1 | Res.curr.angle I02 | FLOAT | R | -360...360
116 | I11 | MEAS1 | Pri.calc.I0 | FLOAT | R | 0...100000
116 | I12 | MEAS1 | Calculated I0 angle | FLOAT | R | -360...360
116 | I13 | MEAS1 | Pha.curr.IL1 TRMS Pri | FLOAT | R | 0...100000
116 | I14 | MEAS1 | Pha.curr.IL2 TRMS Pri | FLOAT | R | 0...100000
116 | I15 | MEAS1 | Pha.curr.IL3 TRMS Pri | FLOAT | R | 0...100000
116 | I16 | MEAS1 | Pri.Positive sequence curr. | FLOAT | R | 0...100000
116 | I17 | MEAS1 | Pri.Negative sequence curr. | FLOAT | R | 0...100000
116 | I18 | MEAS1 | Pri.Zero sequence curr. | FLOAT | R | 0...100000
116 | I19 | MEAS1 | Positive sequence curr.angle | FLOAT | R | -360...360
116 | I20 | MEAS1 | Negative sequence curr.angle | FLOAT | R | -360...360
116 | I21 | MEAS1 | Zero sequence curr.angle | FLOAT | R | -360...360
116 | I22 | MEAS1 | Res.curr.I01 TRMS Pri | FLOAT | R | 0...100000
116 | I23 | MEAS1 | Res.curr.I02 TRMS Pri | FLOAT | R | 0...100000
116 | I24 | MEAS1 | Pha.L1 ampl. THD | FLOAT | R | 0...100
116 | I25 | MEAS1 | Pha.L1 pow. THD | FLOAT | R | 0...100
116 | I26 | MEAS1 | Pha.L2 ampl. THD | FLOAT | R | 0...100
116 | I27 | MEAS1 | Pha.L2 pow. THD | FLOAT | R | 0...100
116 | I28 | MEAS1 | Pha.L3 ampl. THD | FLOAT | R | 0...100
116 | I29 | MEAS1 | Pha.L3 pow. THD | FLOAT | R | 0...100
116 | I30 | MEAS1 | Res.I01 ampl. THD | FLOAT | R | 0...100
116 | I31 | MEAS1 | Res.I01 pow. THD | FLOAT | R | 0...100
116 | I32 | MEAS1 | Res.I02 ampl. THD | FLOAT | R | 0...100
116 | I33 | MEAS1 | Res.I02 pow. THD | FLOAT | R | 0...100
116 | I34 | MEAS1 | Meas1 IL ang. Ref | FLOAT | R | -360...360
117 | S1 | MEAS2 | Side 2 Current meas update interval | UINT32 | RW | 5...10000
117 | I1 | MEAS2 | Pri.Pha.curr.I''L1 | FLOAT | R | 0...100000
117 | I2 | MEAS2 | Pri.Pha.curr.I''L2 | FLOAT | R | 0...100000
117 | I3 | MEAS2 | Pri.Pha.curr.I''L3 | FLOAT | R | 0...100000
117 | I4 | MEAS2 | Pha.angle I''L1 | FLOAT | R | -360...360
117 | I5 | MEAS2 | Pha.angle I''L2 | FLOAT | R | -360...360
117 | I6 | MEAS2 | Pha.angle I''L3 | FLOAT | R | -360...360
117 | I7 | MEAS2 | Pri.Res.curr.I''01 | FLOAT | R | 0...100000
117 | I8 | MEAS2 | Res.curr.angle I''01 | FLOAT | R | -360...360
117 | I9 | MEAS2 | Pri.Res.curr.I''02 | FLOAT | R | 0...100000
117 | I10 | MEAS2 | Res.curr.angle I''02 | FLOAT | R | -360...360
117 | I11 | MEAS2 | Pri.calc.I''0 | FLOAT | R | 0...100000
117 | I12 | MEAS2 | Calculated I''0 angle | FLOAT | R | -360...360
117 | I13 | MEAS2 | Pha.curr.I''L1 TRMS Pri | FLOAT | R | 0...100000
117 | I14 | MEAS2 | Pha.curr.I''L2 TRMS Pri | FLOAT | R | 0...100000
117 | I15 | MEAS2 | Pha.curr.I''L3 TRMS Pri | FLOAT | R | 0...100000
117 | I16 | MEAS2 | I'' Pri.Positive sequence curr. | FLOAT | R | 0...100000
117 | I17 | MEAS2 | I'' Pri.Negative sequence curr. | FLOAT | R | 0...100000
117 | I18 | MEAS2 | I'' Pri.Zero sequence curr. | FLOAT | R | 0...100000
117 | I19 | MEAS2 | I'' Positive sequence curr.angle | FLOAT | R | -360...360
117 | I20 | MEAS2 | I'' Negative sequence curr.angle | FLOAT | R | -360...360
117 | I21 | MEAS2 | I'' Zero sequence curr.angle | FLOAT | R | -360...360
117 | I22 | MEAS2 | Res.curr.I''01 TRMS Pri | FLOAT | R | 0...100000
117 | I23 | MEAS2 | Res.curr.I''02 TRMS Pri | FLOAT | R | 0...100000
117 | I24 | MEAS2 | Pha.I''L1 ampl. THD | FLOAT | R | 0...100
117 | I25 | MEAS2 | Pha.I''L1 pow. THD | FLOAT | R | 0...100
117 | I26 | MEAS2 | Pha.I''L2 ampl. THD | FLOAT | R | 0...100
117 | I27 | MEAS2 | Pha.I''L2 pow. THD | FLOAT | R | 0...100
117 | I28 | MEAS2 | Pha.I''L3 ampl. THD | FLOAT | R | 0...100
117 | I29 | MEAS2 | Pha.I''L3 pow. THD | FLOAT | R | 0...100
117 | I30 | MEAS2 | Res.I''01 ampl. THD | FLOAT | R | 0...100
117 | I31 | MEAS2 | Res.I''01 pow. THD | FLOAT | R | 0...100
117 | I32 | MEAS2 | Res.I''02 ampl. THD | FLOAT | R | 0...100
117 | I33 | MEAS2 | Res.I''02 pow. THD | FLOAT | R | 0...100
117 | I34 | MEAS2 | MEAS2 IL ang. Ref | FLOAT | R | -360...360
118 | S1 | MEAS3 | Voltage meas update interval | UINT32 | RW | 5...10000
118 | I1 | MEAS3 | Positive sequence volt.pri | FLOAT | R | 0...1000000
118 | I2 | MEAS3 | Negative sequence volt.pri | FLOAT | R | 0...1000000
118 | I3 | MEAS3 | Zero sequence Volt.pri | FLOAT | R | 0...1000000
118 | I4 | MEAS3 | Pos.Seq volt.Angle | FLOAT | R | -360...360
118 | I5 | MEAS3 | Negative sequence volt.Angle | FLOAT | R | -360...360
118 | I6 | MEAS3 | Zero sequence volt.Angle | FLOAT | R | -360...360
118 | I7 | MEAS3 | System volt UL12 mag | FLOAT | R | 0...1000000
118 | I8 | MEAS3 | System volt UL12 mag (kV) | FLOAT | R | 0...1000
118 | I9 | MEAS3 | System volt UL12 ang | FLOAT | R | -360...360
118 | I10 | MEAS3 | System volt UL23 mag | FLOAT | R | 0...1000000
118 | I11 | MEAS3 | System volt UL23 mag (kV) | FLOAT | R | 0...1000
118 | I12 | MEAS3 | System volt UL23 ang | FLOAT | R | -360...360
118 | I13 | MEAS3 | System volt UL31 mag | FLOAT | R | 0...1000000
118 | I14 | MEAS3 | System volt UL31 mag (kV) | FLOAT | R | 0...1000
118 | I15 | MEAS3 | System volt UL31 ang | FLOAT | R | -360...360
118 | I16 | MEAS3 | System volt UL1 mag | FLOAT | R | 0...1000000
118 | I17 | MEAS3 | System volt UL1 mag (kV) | FLOAT | R | 0...1000
118 | I18 | MEAS3 | System volt UL1 ang | FLOAT | R | -360...360
118 | I19 | MEAS3 | System volt UL2 mag | FLOAT | R | 0...1000000
118 | I20 | MEAS3 | System volt UL2 mag (kV) | FLOAT | R | 0...1000
118 | I21 | MEAS3 | System volt UL2 ang | FLOAT | R | -360...360
118 | I22 | MEAS3 | System volt UL3 mag | FLOAT | R | 0...1000000
118 | I23 | MEAS3 | System volt UL3 mag (kV) | FLOAT | R | 0...1000
118 | I24 | MEAS3 | System volt UL3 ang | FLOAT | R | -360...360
118 | I25 | MEAS3 | System volt U0 mag | FLOAT | R | 0...1000000
118 | I26 | MEAS3 | System volt U0 mag (kV) | FLOAT | R | 0...1000
118 | I27 | MEAS3 | System volt U0 mag(%) | FLOAT | R | 0...120
118 | I28 | MEAS3 | System volt U0 ang | FLOAT | R | -360...360
118 | I29 | MEAS3 | System volt U3 mag | FLOAT | R | 0...1000000
118 | I30 | MEAS3 | System volt U3 mag (kV) | FLOAT | R | 0...1000
118 | I31 | MEAS3 | System volt U3 ang | FLOAT | R | -360...360
118 | I32 | MEAS3 | System volt U4 mag | FLOAT | R | 0...1000000
118 | I33 | MEAS3 | System volt U4 mag (kV) | FLOAT | R | 0...1000
118 | I34 | MEAS3 | System volt U4 ang | FLOAT | R | -360...360
188 | I1 | IMERX | IL1 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I2 | IMERX | IL1 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I3 | IMERX | IL2 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I4 | IMERX | IL2 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I5 | IMERX | IL3 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I6 | IMERX | IL3 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I7 | IMERX | Positive sequence Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I8 | IMERX | Positive sequence Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I9 | IMERX | I01 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I10 | IMERX | I01 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I11 | IMERX | I02 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I12 | IMERX | I02 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I13 | IMERX | I01 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I14 | IMERX | I01 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
188 | I15 | IMERX | I02 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I16 | IMERX | I02 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
119 | S1 | POW1 | Power meas update interval | UINT32 | RW | 5...10000
119 | S2 | POW1 | Nominal Power kVA | FLOAT | RW | 0.1...500000
119 | I1 | POW1 | PQ Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Ind;2=Q2 Rev Cap;3=Q3 Rev Ind;4=Q4 Fwd Cap
119 | I2 | POW1 | VA Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Cap, AV;2=Q2 Rev Ind AV;3=Q3 Rev Cap VA;4=Q4 Fwd Ind VA
119 | I3 | POW1 | Export Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I4 | POW1 | Export Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I5 | POW1 | Import Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I6 | POW1 | Import Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I7 | POW1 | Active Energy (P) Export/Import balance MWh | INT32 | R | -2147483647...2147483647
119 | I8 | POW1 | Active Energy (P) Export/Import balance kWh | INT32 | R | -2147483647...2147483647
119 | I9 | POW1 | Exported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I10 | POW1 | Exported (Q) while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I11 | POW1 | Imported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I12 | POW1 | Imported (Q) while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I13 | POW1 | Reactive Energy (Q) balance while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I14 | POW1 | Reactive Energy (Q) balance while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I15 | POW1 | Exported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I16 | POW1 | Exported (Q) while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I17 | POW1 | Imported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I18 | POW1 | Imported (Q) while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I19 | POW1 | Reactive Energy (Q) balance while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I20 | POW1 | Reactive Energy (Q) balance while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I21 | POW1 | Apparent Energy (S) while Export (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I22 | POW1 | Apparent Energy (S) while Export (P) kVAh | INT32 | R | -2147483647...2147483647
119 | I23 | POW1 | Apparent Energy (S) while Import (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I24 | POW1 | Apparent Energy (S) while Import (P) kVAh | INT32 | R | -2147483647...2147483647
119 | I25 | POW1 | Apparent Energy (S) Net | INT32 | R | -2147483647...2147483647
119 | I26 | POW1 | Real Energy (P) Net | INT32 | R | -2147483647...2147483647
119 | I27 | POW1 | Reactive Energy (Q) Net | INT32 | R | -2147483647...2147483647
119 | I28 | POW1 | Real Energy (P) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
119 | I29 | POW1 | Reactive Energy (Q) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
119 | I30 | POW1 | Real Energy (P) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
119 | I31 | POW1 | Reactive Energy (Q) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
119 | S3 | POW1 | Reset 3ph energies | UINT32 | RW | 0=-;1=Reset
119 | I32 | POW1 | POW1 L1 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I33 | POW1 | POW1 L1 Active power (P) | FLOAT | R | -1000000...1000000
119 | I34 | POW1 | POW1 L1 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I35 | POW1 | POW1 L1 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I36 | POW1 | POW1 L1 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I37 | POW1 | L1 Power factor | FLOAT | R | -1000000...1000000
119 | I38 | POW1 | POW1 L2 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I39 | POW1 | POW1 L2 Active power (P) | FLOAT | R | -1000000...1000000
119 | I40 | POW1 | POW1 L2 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I41 | POW1 | POW1 L2 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I42 | POW1 | POW1 L2 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I43 | POW1 | L2 Power factor | FLOAT | R | -1000000...1000000
119 | I44 | POW1 | POW1 L3 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I45 | POW1 | POW1 L3 Active power (P) | FLOAT | R | -1000000...1000000
119 | I46 | POW1 | POW1 L3 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I47 | POW1 | POW1 L3 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I48 | POW1 | POW1 L3 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I49 | POW1 | L3 Power factor | FLOAT | R | -1000000...1000000
119 | I50 | POW1 | POW1 3PH Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I51 | POW1 | POW1 3PH Apparent power (S MVA) | FLOAT | R | -1000000...1000000
119 | I52 | POW1 | POW1 3PH Active power (P) | FLOAT | R | -1000000...1000000
119 | I53 | POW1 | POW1 3PH Active power (P MW) | FLOAT | R | -1000000...1000000
119 | I54 | POW1 | POW1 3PH Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I55 | POW1 | POW1 3PH Reactive power (QMVar) | FLOAT | R | -1000000...1000000
119 | I56 | POW1 | POW1 3PH Tan(phi) | FLOAT | R | -1000000...1000000
119 | I57 | POW1 | POW1 3PH Cos(phi) | FLOAT | R | -1000000...1000000
119 | I58 | POW1 | 3PH Power factor | FLOAT | R | -1000000...1000000
187 | S1 | POW2 | Power meas update interval | UINT32 | RW | 5...10000
187 | S2 | POW2 | Nominal Power kVA | FLOAT | RW | 0.1...500000
187 | I1 | POW2 | PQ Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Ind;2=Q2 Rev Cap;3=Q3 Rev Ind;4=Q4 Fwd Cap
187 | I2 | POW2 | VA Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Cap, AV;2=Q2 Rev Ind AV;3=Q3 Rev Cap VA;4=Q4 Fwd Ind VA
187 | I3 | POW2 | Export Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
187 | I4 | POW2 | Export Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
187 | I5 | POW2 | Import Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
187 | I6 | POW2 | Import Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
187 | I7 | POW2 | Active Energy (P) Export/Import balance MWh | INT32 | R | -2147483647...2147483647
187 | I8 | POW2 | Active Energy (P) Export/Import balance kWh | INT32 | R | -2147483647...2147483647
187 | I9 | POW2 | Exported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
187 | I10 | POW2 | Exported (Q) while Export (P) kVarh | INT32 | R | -2147483647...2147483647
187 | I11 | POW2 | Imported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
187 | I12 | POW2 | Imported (Q) while Export (P) kVarh | INT32 | R | -2147483647...2147483647
187 | I13 | POW2 | Reactive Energy (Q) balance while Export (P) MVarh | INT32 | R | -2147483647...2147483647
187 | I14 | POW2 | Reactive Energy (Q) balance while Export (P) kVarh | INT32 | R | -2147483647...2147483647
187 | I15 | POW2 | Exported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
187 | I16 | POW2 | Exported (Q) while Import (P) kVarh | INT32 | R | -2147483647...2147483647
187 | I17 | POW2 | Imported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
187 | I18 | POW2 | Imported (Q) while Import (P) kVarh | INT32 | R | -2147483647...2147483647
187 | I19 | POW2 | Reactive Energy (Q) balance while Import (P) MVarh | INT32 | R | -2147483647...2147483647
187 | I20 | POW2 | Reactive Energy (Q) balance while Import (P) kVarh | INT32 | R | -2147483647...2147483647
187 | I21 | POW2 | Apparent Energy (S) while Export (P) MVAh | INT32 | R | -2147483647...2147483647
187 | I22 | POW2 | Apparent Energy (S) while Export (P) kVAh | INT32 | R | -2147483647...2147483647
187 | I23 | POW2 | Apparent Energy (S) while Import (P) MVAh | INT32 | R | -2147483647...2147483647
187 | I24 | POW2 | Apparent Energy (S) while Import (P) kVAh | INT32 | R | -2147483647...2147483647
187 | I25 | POW2 | Apparent Energy (S) Net | INT32 | R | -2147483647...2147483647
187 | I26 | POW2 | Real Energy (P) Net | INT32 | R | -2147483647...2147483647
187 | I27 | POW2 | Reactive Energy (Q) Net | INT32 | R | -2147483647...2147483647
187 | I28 | POW2 | Real Energy (P) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
187 | I29 | POW2 | Reactive Energy (Q) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
187 | I30 | POW2 | Real Energy (P) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
187 | I31 | POW2 | Reactive Energy (Q) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
187 | S3 | POW2 | Reset 3ph energies | UINT32 | RW | 0=-;1=Reset
187 | I32 | POW2 | POW2 L1 Apparent power (S) | FLOAT | R | -1000000...1000000
187 | I33 | POW2 | POW2 L1 Active power (P) | FLOAT | R | -1000000...1000000
187 | I34 | POW2 | POW2 L1 Reactive power (Q) | FLOAT | R | -1000000...1000000
187 | I35 | POW2 | POW2 L1 Tan(phi) | FLOAT | R | -1000000...1000000
187 | I36 | POW2 | POW2 L1 Cos(phi) | FLOAT | R | -1000000...1000000
187 | I37 | POW2 | L1 Power factor | FLOAT | R | -1000000...1000000
187 | I38 | POW2 | POW2 L2 Apparent power (S) | FLOAT | R | -1000000...1000000
187 | I39 | POW2 | POW2 L2 Active power (P) | FLOAT | R | -1000000...1000000
187 | I40 | POW2 | POW2 L2 Reactive power (Q) | FLOAT | R | -1000000...1000000
187 | I41 | POW2 | POW2 L2 Tan(phi) | FLOAT | R | -1000000...1000000
187 | I42 | POW2 | POW2 L2 Cos(phi) | FLOAT | R | -1000000...1000000
187 | I43 | POW2 | L2 Power factor | FLOAT | R | -1000000...1000000
187 | I44 | POW2 | POW2 L3 Apparent power (S) | FLOAT | R | -1000000...1000000
187 | I45 | POW2 | POW2 L3 Active power (P) | FLOAT | R | -1000000...1000000
187 | I46 | POW2 | POW2 L3 Reactive power (Q) | FLOAT | R | -1000000...1000000
187 | I47 | POW2 | POW2 L3 Tan(phi) | FLOAT | R | -1000000...1000000
187 | I48 | POW2 | POW2 L3 Cos(phi) | FLOAT | R | -1000000...1000000
187 | I49 | POW2 | L3 Power factor | FLOAT | R | -1000000...1000000
187 | I50 | POW2 | POW2 3PH Apparent power (S) | FLOAT | R | -1000000...1000000
187 | I51 | POW2 | POW2 3PH Apparent power (S MVA) | FLOAT | R | -1000000...1000000
187 | I52 | POW2 | POW2 3PH Active power (P) | FLOAT | R | -1000000...1000000
187 | I53 | POW2 | POW2 3PH Active power (P MW) | FLOAT | R | -1000000...1000000
187 | I54 | POW2 | POW2 3PH Reactive power (Q) | FLOAT | R | -1000000...1000000
187 | I55 | POW2 | POW2 3PH Reactive power (QMVar) | FLOAT | R | -1000000...1000000
187 | I56 | POW2 | POW2 3PH Tan(phi) | FLOAT | R | -1000000...1000000
187 | I57 | POW2 | POW2 3PH Cos(phi) | FLOAT | R | -1000000...1000000
187 | I58 | POW2 | 3PH Power factor | FLOAT | R | -1000000...1000000
136 | S1 | IMP1 | Impedance meas. update interval | UINT32 | RW | 5...10000
136 | I1 | IMP1 | Primary Resistance L12 R | FLOAT | R | -1000000...1000000
136 | I2 | IMP1 | Primary Reactance L12 X | FLOAT | R | -1000000...1000000
136 | I3 | IMP1 | Primary Resistance L23 R | FLOAT | R | -1000000...1000000
136 | I4 | IMP1 | Primary Reactance L23 X | FLOAT | R | -1000000...1000000
136 | I5 | IMP1 | Primary Resistance L31 R | FLOAT | R | -1000000...1000000
136 | I6 | IMP1 | Primary Reactance L31 X | FLOAT | R | -1000000...1000000
136 | I7 | IMP1 | Primary Impedance Z12 | FLOAT | R | -1000000...1000000
136 | I8 | IMP1 | Primary Impedance Z23 | FLOAT | R | -1000000...1000000
136 | I9 | IMP1 | Primary Impedance Z31 | FLOAT | R | -1000000...1000000
136 | I10 | IMP1 | Impedance Angle Z12 | FLOAT | R | -360...360
136 | I11 | IMP1 | Impedance Angle Z23 | FLOAT | R | -360...360
136 | I12 | IMP1 | Impedance Angle Z31 | FLOAT | R | -360...360
136 | I13 | IMP1 | Primary Resistance L1 R | FLOAT | R | -1000000...1000000
136 | I14 | IMP1 | Primary Reactance L1 X | FLOAT | R | -1000000...1000000
136 | I15 | IMP1 | Primary Resistance L2 R | FLOAT | R | -1000000...1000000
136 | I16 | IMP1 | Primary Reactance L2 X | FLOAT | R | -1000000...1000000
136 | I17 | IMP1 | Primary Resistance L3 R | FLOAT | R | -1000000...1000000
136 | I18 | IMP1 | Primary Reactance L3 X | FLOAT | R | -1000000...1000000
136 | I19 | IMP1 | Primary Impedance Z1 | FLOAT | R | -1000000...1000000
136 | I20 | IMP1 | Primary Impedance Z2 | FLOAT | R | -1000000...1000000
136 | I21 | IMP1 | Primary Impedance Z3 | FLOAT | R | -1000000...1000000
136 | I22 | IMP1 | Impedance Angle Z1 | FLOAT | R | -360...360
136 | I23 | IMP1 | Impedance Angle Z2 | FLOAT | R | -360...360
136 | I24 | IMP1 | Impedance Angle Z3 | FLOAT | R | -360...360
235 | V1 | DMA1 | Demand condition | UINT32 | R | 0=Normal;1=General alarm;2=Blocked
235 | V2 | DMA1 | Combined status | UINT32 | R | 0b=IL1 alarm;1b=IL2 alarm;2b=IL3 alarm;3b=S 3phase alarm;4b=P 3phase alarm;5b=Q 3phase alarm;6b=PF 3phase alarm;7b=IL1 harmonic alarm;8b=IL2 harmonic alarm;9b=IL3 harmonic alarm;10b=Function blocked
235 | I1 | DMA1 | Out of step slips to trip | UINT32 | R | 0...4294967295
137 | I1 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I2 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I3 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I4 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I5 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I6 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I7 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I8 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I9 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I10 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I11 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I12 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
120 | S1 | FREQS | Sampling mode | UINT32 | RW | 0=Fixed;1=Tracking
120 | S2 | FREQS | Max. Tracking freq. allowed (+Nom f) | FLOAT | RW | 0.001...75
120 | S3 | FREQS | System nominal frequency | FLOAT | RW | 7.000...75.000
120 | S4 | FREQS | Min. Tracking freq. allowed (- Nom f) | FLOAT | RW | 0.001...75
120 | I1 | FREQS | Tracked system frequency | FLOAT | R | 0.000...75.000
120 | I2 | FREQS | f atm. Protections (when not measurable returns to nominal) | FLOAT | R | 0...75
120 | I3 | FREQS | f atm. Display (when not measurable is 0Hz) | FLOAT | R | 0...75
3 | V1 | GNSIG | Common signals condition | UINT32 | R | 0=Normal;1=Start;2=Trip
3 | I1 | GNSIG | Common starts | UINT32 | R | 0...4294967295
3 | I2 | GNSIG | Common trips | UINT32 | R | 0...4294967295
3 | S1 | GNSIG | Clear statistics | UINT32 | W | 0=-;1=Clear
10 | I1 | DIGI | DIs | UINT32 | R | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32
10 | I2 | DIGI | DIs | UINT32 | R | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51;19b=DI52;20b=DI53;21b=DI54;22b=DI55;23b=DI56;24b=DI57;25b=DI58;26b=DI59;27b=DI60;28b=DI61;29b=DI62;30b=DI63;31b=DI64
10 | I3 | DIGI | DIs | UINT32 | R | 0b=DI65;1b=DI66;2b=DI67;3b=DI68;4b=DI69;5b=DI70;6b=DI71;7b=DI72;8b=DI73;9b=DI74;10b=DI75;11b=DI76;12b=DI77;13b=DI78;14b=DI79;15b=DI80;16b=DI81;17b=DI82;18b=DI83;19b=DI84;20b=DI85;21b=DI86;22b=DI87;23b=DI88;24b=DI89;25b=DI90;26b=DI91;27b=DI92;28b=DI93;29b=DI94;30b=DI95;31b=DI96
10 | I4 | DIGI | DIs | UINT32 | R | 0b=DI97;1b=DI98;2b=DI99;3b=DI100;4b=DI101;5b=DI102;6b=DI103;7b=DI104;8b=DI105;9b=DI106;10b=DI107;11b=DI108;12b=DI109;13b=DI110;14b=DI111;15b=DI112;16b=DI113;17b=DI114;18b=DI115;19b=DI116;20b=DI117;21b=DI118;22b=DI119;23b=DI120;24b=DI121;25b=DI122;26b=DI123;27b=DI124;28b=DI125;29b=DI126;30b=DI127;31b=DI128
10 | I5 | DIGI | DI1 | SIGNAL_OUT | RW | 0...4294967295
10 | V1 | DIGI | DI1 Counter | UINT32 | R | 0...4294967295
10 | V2 | DIGI | DI1 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I6 | DIGI | DI2 | SIGNAL_OUT | RW | 0...4294967295
10 | V3 | DIGI | DI2 Counter | UINT32 | R | 0...4294967295
10 | V4 | DIGI | DI2 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I7 | DIGI | DI3 | SIGNAL_OUT | RW | 0...4294967295
10 | V5 | DIGI | DI3 Counter | UINT32 | R | 0...4294967295
10 | V6 | DIGI | DI3 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I8 | DIGI | DI4 | SIGNAL_OUT | RW | 0...4294967295
10 | V7 | DIGI | DI4 Counter | UINT32 | R | 0...4294967295
10 | V8 | DIGI | DI4 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I9 | DIGI | DI5 | SIGNAL_OUT | RW | 0...4294967295
10 | V9 | DIGI | DI5 Counter | UINT32 | R | 0...4294967295
10 | V10 | DIGI | DI5 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I10 | DIGI | DI6 | SIGNAL_OUT | RW | 0...4294967295
10 | V11 | DIGI | DI6 Counter | UINT32 | R | 0...4294967295
10 | V12 | DIGI | DI6 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I11 | DIGI | DI7 | SIGNAL_OUT | RW | 0...4294967295
10 | V13 | DIGI | DI7 Counter | UINT32 | R | 0...4294967295
10 | V14 | DIGI | DI7 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I12 | DIGI | DI8 | SIGNAL_OUT | RW | 0...4294967295
10 | V15 | DIGI | DI8 Counter | UINT32 | R | 0...4294967295
10 | V16 | DIGI | DI8 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I13 | DIGI | DI9 | SIGNAL_OUT | RW | 0...4294967295
10 | V17 | DIGI | DI9 Counter | UINT32 | R | 0...4294967295
10 | V18 | DIGI | DI9 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I14 | DIGI | DI10 | SIGNAL_OUT | RW | 0...4294967295
10 | V19 | DIGI | DI10 Counter | UINT32 | R | 0...4294967295
10 | V20 | DIGI | DI10 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I15 | DIGI | DI11 | SIGNAL_OUT | RW | 0...4294967295
10 | V21 | DIGI | DI11 Counter | UINT32 | R | 0...4294967295
10 | V22 | DIGI | DI11 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I16 | DIGI | DI12 | SIGNAL_OUT | RW | 0...4294967295
10 | V23 | DIGI | DI12 Counter | UINT32 | R | 0...4294967295
10 | V24 | DIGI | DI12 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I17 | DIGI | DI13 | SIGNAL_OUT | RW | 0...4294967295
10 | V25 | DIGI | DI13 Counter | UINT32 | R | 0...4294967295
10 | V26 | DIGI | DI13 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I18 | DIGI | DI14 | SIGNAL_OUT | RW | 0...4294967295
10 | V27 | DIGI | DI14 Counter | UINT32 | R | 0...4294967295
10 | V28 | DIGI | DI14 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I19 | DIGI | DI15 | SIGNAL_OUT | RW | 0...4294967295
10 | V29 | DIGI | DI15 Counter | UINT32 | R | 0...4294967295
10 | V30 | DIGI | DI15 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I20 | DIGI | DI16 | SIGNAL_OUT | RW | 0...4294967295
10 | V31 | DIGI | DI16 Counter | UINT32 | R | 0...4294967295
10 | V32 | DIGI | DI16 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I21 | DIGI | DI17 | SIGNAL_OUT | RW | 0...4294967295
10 | V33 | DIGI | DI17 Counter | UINT32 | R | 0...4294967295
10 | V34 | DIGI | DI17 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I22 | DIGI | DI18 | SIGNAL_OUT | RW | 0...4294967295
10 | V35 | DIGI | DI18 Counter | UINT32 | R | 0...4294967295
10 | V36 | DIGI | DI18 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I23 | DIGI | DI19 | SIGNAL_OUT | RW | 0...4294967295
10 | V37 | DIGI | DI19 Counter | UINT32 | R | 0...4294967295
10 | V38 | DIGI | DI19 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I24 | DIGI | DI20 | SIGNAL_OUT | RW | 0...4294967295
10 | V39 | DIGI | DI20 Counter | UINT32 | R | 0...4294967295
10 | V40 | DIGI | DI20 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I25 | DIGI | DI21 | SIGNAL_OUT | RW | 0...4294967295
10 | V41 | DIGI | DI21 Counter | UINT32 | R | 0...4294967295
10 | V42 | DIGI | DI21 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I26 | DIGI | DI22 | SIGNAL_OUT | RW | 0...4294967295
10 | V43 | DIGI | DI22 Counter | UINT32 | R | 0...4294967295
10 | V44 | DIGI | DI22 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I27 | DIGI | DI23 | SIGNAL_OUT | RW | 0...4294967295
10 | V45 | DIGI | DI23 Counter | UINT32 | R | 0...4294967295
10 | V46 | DIGI | DI23 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I28 | DIGI | DI24 | SIGNAL_OUT | RW | 0...4294967295
10 | V47 | DIGI | DI24 Counter | UINT32 | R | 0...4294967295
10 | V48 | DIGI | DI24 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I29 | DIGI | DI25 | SIGNAL_OUT | RW | 0...4294967295
10 | V49 | DIGI | DI25 Counter | UINT32 | R | 0...4294967295
10 | V50 | DIGI | DI25 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I30 | DIGI | DI26 | SIGNAL_OUT | RW | 0...4294967295
10 | V51 | DIGI | DI26 Counter | UINT32 | R | 0...4294967295
10 | V52 | DIGI | DI26 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I31 | DIGI | DI27 | SIGNAL_OUT | RW | 0...4294967295
10 | V53 | DIGI | DI27 Counter | UINT32 | R | 0...4294967295
10 | V54 | DIGI | DI27 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I32 | DIGI | DI28 | SIGNAL_OUT | RW | 0...4294967295
10 | V55 | DIGI | DI28 Counter | UINT32 | R | 0...4294967295
10 | V56 | DIGI | DI28 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I33 | DIGI | DI29 | SIGNAL_OUT | RW | 0...4294967295
10 | V57 | DIGI | DI29 Counter | UINT32 | R | 0...4294967295
10 | V58 | DIGI | DI29 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I34 | DIGI | DI30 | SIGNAL_OUT | RW | 0...4294967295
10 | V59 | DIGI | DI30 Counter | UINT32 | R | 0...4294967295
10 | V60 | DIGI | DI30 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I35 | DIGI | DI31 | SIGNAL_OUT | RW | 0...4294967295
10 | V61 | DIGI | DI31 Counter | UINT32 | R | 0...4294967295
10 | V62 | DIGI | DI31 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I36 | DIGI | DI32 | SIGNAL_OUT | RW | 0...4294967295
10 | V63 | DIGI | DI32 Counter | UINT32 | R | 0...4294967295
10 | V64 | DIGI | DI32 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I37 | DIGI | DI33 | SIGNAL_OUT | RW | 0...4294967295
10 | V65 | DIGI | DI33 Counter | UINT32 | R | 0...4294967295
10 | V66 | DIGI | DI33 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I38 | DIGI | DI34 | SIGNAL_OUT | RW | 0...4294967295
10 | V67 | DIGI | DI34 Counter | UINT32 | R | 0...4294967295
10 | V68 | DIGI | DI34 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I39 | DIGI | DI35 | SIGNAL_OUT | RW | 0...4294967295
10 | V69 | DIGI | DI35 Counter | UINT32 | R | 0...4294967295
10 | V70 | DIGI | DI35 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I40 | DIGI | DI36 | SIGNAL_OUT | RW | 0...4294967295
10 | V71 | DIGI | DI36 Counter | UINT32 | R | 0...4294967295
10 | V72 | DIGI | DI36 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I41 | DIGI | DI37 | SIGNAL_OUT | RW | 0...4294967295
10 | V73 | DIGI | DI37 Counter | UINT32 | R | 0...4294967295
10 | V74 | DIGI | DI37 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I42 | DIGI | DI38 | SIGNAL_OUT | RW | 0...4294967295
10 | V75 | DIGI | DI38 Counter | UINT32 | R | 0...4294967295
10 | V76 | DIGI | DI38 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I43 | DIGI | DI39 | SIGNAL_OUT | RW | 0...4294967295
10 | V77 | DIGI | DI39 Counter | UINT32 | R | 0...4294967295
10 | V78 | DIGI | DI39 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I44 | DIGI | DI40 | SIGNAL_OUT | RW | 0...4294967295
10 | V79 | DIGI | DI40 Counter | UINT32 | R | 0...4294967295
10 | V80 | DIGI | DI40 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I45 | DIGI | DI41 | SIGNAL_OUT | RW | 0...4294967295
10 | V81 | DIGI | DI41 Counter | UINT32 | R | 0...4294967295
10 | V82 | DIGI | DI41 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I46 | DIGI | DI42 | SIGNAL_OUT | RW | 0...4294967295
10 | V83 | DIGI | DI42 Counter | UINT32 | R | 0...4294967295
10 | V84 | DIGI | DI42 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I47 | DIGI | DI43 | SIGNAL_OUT | RW | 0...4294967295
10 | V85 | DIGI | DI43 Counter | UINT32 | R | 0...4294967295
10 | V86 | DIGI | DI43 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I48 | DIGI | DI44 | SIGNAL_OUT | RW | 0...4294967295
10 | V87 | DIGI | DI44 Counter | UINT32 | R | 0...4294967295
10 | V88 | DIGI | DI44 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I49 | DIGI | DI45 | SIGNAL_OUT | RW | 0...4294967295
10 | V89 | DIGI | DI45 Counter | UINT32 | R | 0...4294967295
10 | V90 | DIGI | DI45 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I50 | DIGI | DI46 | SIGNAL_OUT | RW | 0...4294967295
10 | V91 | DIGI | DI46 Counter | UINT32 | R | 0...4294967295
10 | V92 | DIGI | DI46 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I51 | DIGI | DI47 | SIGNAL_OUT | RW | 0...4294967295
10 | V93 | DIGI | DI47 Counter | UINT32 | R | 0...4294967295
10 | V94 | DIGI | DI47 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I52 | DIGI | DI48 | SIGNAL_OUT | RW | 0...4294967295
10 | V95 | DIGI | DI48 Counter | UINT32 | R | 0...4294967295
10 | V96 | DIGI | DI48 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I53 | DIGI | DI49 | SIGNAL_OUT | RW | 0...4294967295
10 | V97 | DIGI | DI49 Counter | UINT32 | R | 0...4294967295
10 | V98 | DIGI | DI49 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I54 | DIGI | DI50 | SIGNAL_OUT | RW | 0...4294967295
10 | V99 | DIGI | DI50 Counter | UINT32 | R | 0...4294967295
10 | V100 | DIGI | DI50 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I55 | DIGI | DI51 | SIGNAL_OUT | RW | 0...4294967295
10 | V101 | DIGI | DI51 Counter | UINT32 | R | 0...4294967295
10 | V102 | DIGI | DI51 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I56 | DIGI | DI52 | SIGNAL_OUT | RW | 0...4294967295
10 | V103 | DIGI | DI52 Counter | UINT32 | R | 0...4294967295
10 | V104 | DIGI | DI52 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I57 | DIGI | DI53 | SIGNAL_OUT | RW | 0...4294967295
10 | V105 | DIGI | DI53 Counter | UINT32 | R | 0...4294967295
10 | V106 | DIGI | DI53 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I58 | DIGI | DI54 | SIGNAL_OUT | RW | 0...4294967295
10 | V107 | DIGI | DI54 Counter | UINT32 | R | 0...4294967295
10 | V108 | DIGI | DI54 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I59 | DIGI | DI55 | SIGNAL_OUT | RW | 0...4294967295
10 | V109 | DIGI | DI55 Counter | UINT32 | R | 0...4294967295
10 | V110 | DIGI | DI55 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I60 | DIGI | DI56 | SIGNAL_OUT | RW | 0...4294967295
10 | V111 | DIGI | DI56 Counter | UINT32 | R | 0...4294967295
10 | V112 | DIGI | DI56 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I61 | DIGI | DI57 | SIGNAL_OUT | RW | 0...4294967295
10 | V113 | DIGI | DI57 Counter | UINT32 | R | 0...4294967295
10 | V114 | DIGI | DI57 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I62 | DIGI | DI58 | SIGNAL_OUT | RW | 0...4294967295
10 | V115 | DIGI | DI58 Counter | UINT32 | R | 0...4294967295
10 | V116 | DIGI | DI58 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I63 | DIGI | DI59 | SIGNAL_OUT | RW | 0...4294967295
10 | V117 | DIGI | DI59 Counter | UINT32 | R | 0...4294967295
10 | V118 | DIGI | DI59 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I64 | DIGI | DI60 | SIGNAL_OUT | RW | 0...4294967295
10 | V119 | DIGI | DI60 Counter | UINT32 | R | 0...4294967295
10 | V120 | DIGI | DI60 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I65 | DIGI | DI61 | SIGNAL_OUT | RW | 0...4294967295
10 | V121 | DIGI | DI61 Counter | UINT32 | R | 0...4294967295
10 | V122 | DIGI | DI61 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I66 | DIGI | DI62 | SIGNAL_OUT | RW | 0...4294967295
10 | V123 | DIGI | DI62 Counter | UINT32 | R | 0...4294967295
10 | V124 | DIGI | DI62 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I67 | DIGI | DI63 | SIGNAL_OUT | RW | 0...4294967295
10 | V125 | DIGI | DI63 Counter | UINT32 | R | 0...4294967295
10 | V126 | DIGI | DI63 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I68 | DIGI | DI64 | SIGNAL_OUT | RW | 0...4294967295
10 | V127 | DIGI | DI64 Counter | UINT32 | R | 0...4294967295
10 | V128 | DIGI | DI64 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I69 | DIGI | DI65 | SIGNAL_OUT | RW | 0...4294967295
10 | V129 | DIGI | DI65 Counter | UINT32 | R | 0...4294967295
10 | V130 | DIGI | DI65 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I70 | DIGI | DI66 | SIGNAL_OUT | RW | 0...4294967295
10 | V131 | DIGI | DI66 Counter | UINT32 | R | 0...4294967295
10 | V132 | DIGI | DI66 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I71 | DIGI | DI67 | SIGNAL_OUT | RW | 0...4294967295
10 | V133 | DIGI | DI67 Counter | UINT32 | R | 0...4294967295
10 | V134 | DIGI | DI67 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I72 | DIGI | DI68 | SIGNAL_OUT | RW | 0...4294967295
10 | V135 | DIGI | DI68 Counter | UINT32 | R | 0...4294967295
10 | V136 | DIGI | DI68 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I73 | DIGI | DI69 | SIGNAL_OUT | RW | 0...4294967295
10 | V137 | DIGI | DI69 Counter | UINT32 | R | 0...4294967295
10 | V138 | DIGI | DI69 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I74 | DIGI | DI70 | SIGNAL_OUT | RW | 0...4294967295
10 | V139 | DIGI | DI70 Counter | UINT32 | R | 0...4294967295
10 | V140 | DIGI | DI70 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I75 | DIGI | DI71 | SIGNAL_OUT | RW | 0...4294967295
10 | V141 | DIGI | DI71 Counter | UINT32 | R | 0...4294967295
10 | V142 | DIGI | DI71 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I76 | DIGI | DI72 | SIGNAL_OUT | RW | 0...4294967295
10 | V143 | DIGI | DI72 Counter | UINT32 | R | 0...4294967295
10 | V144 | DIGI | DI72 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I77 | DIGI | DI73 | SIGNAL_OUT | RW | 0...4294967295
10 | V145 | DIGI | DI73 Counter | UINT32 | R | 0...4294967295
10 | V146 | DIGI | DI73 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I78 | DIGI | DI74 | SIGNAL_OUT | RW | 0...4294967295
10 | V147 | DIGI | DI74 Counter | UINT32 | R | 0...4294967295
10 | V148 | DIGI | DI74 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I79 | DIGI | DI75 | SIGNAL_OUT | RW | 0...4294967295
10 | V149 | DIGI | DI75 Counter | UINT32 | R | 0...4294967295
10 | V150 | DIGI | DI75 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I80 | DIGI | DI76 | SIGNAL_OUT | RW | 0...4294967295
10 | V151 | DIGI | DI76 Counter | UINT32 | R | 0...4294967295
10 | V152 | DIGI | DI76 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I81 | DIGI | DI77 | SIGNAL_OUT | RW | 0...4294967295
10 | V153 | DIGI | DI77 Counter | UINT32 | R | 0...4294967295
10 | V154 | DIGI | DI77 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I82 | DIGI | DI78 | SIGNAL_OUT | RW | 0...4294967295
10 | V155 | DIGI | DI78 Counter | UINT32 | R | 0...4294967295
10 | V156 | DIGI | DI78 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I83 | DIGI | DI79 | SIGNAL_OUT | RW | 0...4294967295
10 | V157 | DIGI | DI79 Counter | UINT32 | R | 0...4294967295
10 | V158 | DIGI | DI79 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I84 | DIGI | DI80 | SIGNAL_OUT | RW | 0...4294967295
10 | V159 | DIGI | DI80 Counter | UINT32 | R | 0...4294967295
10 | V160 | DIGI | DI80 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I85 | DIGI | DI81 | SIGNAL_OUT | RW | 0...4294967295
10 | V161 | DIGI | DI81 Counter | UINT32 | R | 0...4294967295
10 | V162 | DIGI | DI81 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I86 | DIGI | DI82 | SIGNAL_OUT | RW | 0...4294967295
10 | V163 | DIGI | DI82 Counter | UINT32 | R | 0...4294967295
10 | V164 | DIGI | DI82 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I87 | DIGI | DI83 | SIGNAL_OUT | RW | 0...4294967295
10 | V165 | DIGI | DI83 Counter | UINT32 | R | 0...4294967295
10 | V166 | DIGI | DI83 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I88 | DIGI | DI84 | SIGNAL_OUT | RW | 0...4294967295
10 | V167 | DIGI | DI84 Counter | UINT32 | R | 0...4294967295
10 | V168 | DIGI | DI84 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I89 | DIGI | DI85 | SIGNAL_OUT | RW | 0...4294967295
10 | V169 | DIGI | DI85 Counter | UINT32 | R | 0...4294967295
10 | V170 | DIGI | DI85 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I90 | DIGI | DI86 | SIGNAL_OUT | RW | 0...4294967295
10 | V171 | DIGI | DI86 Counter | UINT32 | R | 0...4294967295
10 | V172 | DIGI | DI86 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I91 | DIGI | DI87 | SIGNAL_OUT | RW | 0...4294967295
10 | V173 | DIGI | DI87 Counter | UINT32 | R | 0...4294967295
10 | V174 | DIGI | DI87 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I92 | DIGI | DI88 | SIGNAL_OUT | RW | 0...4294967295
10 | V175 | DIGI | DI88 Counter | UINT32 | R | 0...4294967295
10 | V176 | DIGI | DI88 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I93 | DIGI | DI89 | SIGNAL_OUT | RW | 0...4294967295
10 | V177 | DIGI | DI89 Counter | UINT32 | R | 0...4294967295
10 | V178 | DIGI | DI89 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I94 | DIGI | DI90 | SIGNAL_OUT | RW | 0...4294967295
10 | V179 | DIGI | DI90 Counter | UINT32 | R | 0...4294967295
10 | V180 | DIGI | DI90 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I95 | DIGI | DI91 | SIGNAL_OUT | RW | 0...4294967295
10 | V181 | DIGI | DI91 Counter | UINT32 | R | 0...4294967295
10 | V182 | DIGI | DI91 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I96 | DIGI | DI92 | SIGNAL_OUT | RW | 0...4294967295
10 | V183 | DIGI | DI92 Counter | UINT32 | R | 0...4294967295
10 | V184 | DIGI | DI92 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I97 | DIGI | DI93 | SIGNAL_OUT | RW | 0...4294967295
10 | V185 | DIGI | DI93 Counter | UINT32 | R | 0...4294967295
10 | V186 | DIGI | DI93 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I98 | DIGI | DI94 | SIGNAL_OUT | RW | 0...4294967295
10 | V187 | DIGI | DI94 Counter | UINT32 | R | 0...4294967295
10 | V188 | DIGI | DI94 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I99 | DIGI | DI95 | SIGNAL_OUT | RW | 0...4294967295
10 | V189 | DIGI | DI95 Counter | UINT32 | R | 0...4294967295
10 | V190 | DIGI | DI95 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I100 | DIGI | DI96 | SIGNAL_OUT | RW | 0...4294967295
10 | V191 | DIGI | DI96 Counter | UINT32 | R | 0...4294967295
10 | V192 | DIGI | DI96 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I101 | DIGI | DI97 | SIGNAL_OUT | RW | 0...4294967295
10 | V193 | DIGI | DI97 Counter | UINT32 | R | 0...4294967295
10 | V194 | DIGI | DI97 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I102 | DIGI | DI98 | SIGNAL_OUT | RW | 0...4294967295
10 | V195 | DIGI | DI98 Counter | UINT32 | R | 0...4294967295
10 | V196 | DIGI | DI98 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I103 | DIGI | DI99 | SIGNAL_OUT | RW | 0...4294967295
10 | V197 | DIGI | DI99 Counter | UINT32 | R | 0...4294967295
10 | V198 | DIGI | DI99 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I104 | DIGI | DI100 | SIGNAL_OUT | RW | 0...4294967295
10 | V199 | DIGI | DI100 Counter | UINT32 | R | 0...4294967295
10 | V200 | DIGI | DI100 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I105 | DIGI | DI101 | SIGNAL_OUT | RW | 0...4294967295
10 | V201 | DIGI | DI101 Counter | UINT32 | R | 0...4294967295
10 | V202 | DIGI | DI101 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I106 | DIGI | DI102 | SIGNAL_OUT | RW | 0...4294967295
10 | V203 | DIGI | DI102 Counter | UINT32 | R | 0...4294967295
10 | V204 | DIGI | DI102 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I107 | DIGI | DI103 | SIGNAL_OUT | RW | 0...4294967295
10 | V205 | DIGI | DI103 Counter | UINT32 | R | 0...4294967295
10 | V206 | DIGI | DI103 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I108 | DIGI | DI104 | SIGNAL_OUT | RW | 0...4294967295
10 | V207 | DIGI | DI104 Counter | UINT32 | R | 0...4294967295
10 | V208 | DIGI | DI104 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I109 | DIGI | DI105 | SIGNAL_OUT | RW | 0...4294967295
10 | V209 | DIGI | DI105 Counter | UINT32 | R | 0...4294967295
10 | V210 | DIGI | DI105 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I110 | DIGI | DI106 | SIGNAL_OUT | RW | 0...4294967295
10 | V211 | DIGI | DI106 Counter | UINT32 | R | 0...4294967295
10 | V212 | DIGI | DI106 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I111 | DIGI | DI107 | SIGNAL_OUT | RW | 0...4294967295
10 | V213 | DIGI | DI107 Counter | UINT32 | R | 0...4294967295
10 | V214 | DIGI | DI107 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I112 | DIGI | DI108 | SIGNAL_OUT | RW | 0...4294967295
10 | V215 | DIGI | DI108 Counter | UINT32 | R | 0...4294967295
10 | V216 | DIGI | DI108 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I113 | DIGI | DI109 | SIGNAL_OUT | RW | 0...4294967295
10 | V217 | DIGI | DI109 Counter | UINT32 | R | 0...4294967295
10 | V218 | DIGI | DI109 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I114 | DIGI | DI110 | SIGNAL_OUT | RW | 0...4294967295
10 | V219 | DIGI | DI110 Counter | UINT32 | R | 0...4294967295
10 | V220 | DIGI | DI110 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I115 | DIGI | DI111 | SIGNAL_OUT | RW | 0...4294967295
10 | V221 | DIGI | DI111 Counter | UINT32 | R | 0...4294967295
10 | V222 | DIGI | DI111 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I116 | DIGI | DI112 | SIGNAL_OUT | RW | 0...4294967295
10 | V223 | DIGI | DI112 Counter | UINT32 | R | 0...4294967295
10 | V224 | DIGI | DI112 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I117 | DIGI | DI113 | SIGNAL_OUT | RW | 0...4294967295
10 | V225 | DIGI | DI113 Counter | UINT32 | R | 0...4294967295
10 | V226 | DIGI | DI113 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I118 | DIGI | DI114 | SIGNAL_OUT | RW | 0...4294967295
10 | V227 | DIGI | DI114 Counter | UINT32 | R | 0...4294967295
10 | V228 | DIGI | DI114 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | I119 | DIGI | DI115 | SIGNAL_OUT | RW | 0...4294967295
10 | V229 | DIGI | DI115 Counter | UINT32 | R | 0...4294967295
10 | V230 | DIGI | DI115 Clear counter | UINT32 | RW | 0=-;1=Clear
10 | S1 | DIGI | EventMaskLo | UINT32 | RW | 0...4294967295
10 | S2 | DIGI | EventMaskHi | UINT32 | RW | 0...4294967295
11 | S1 | DIGI2 | EventMaskLo | UINT32 | RW | 0...4294967295
11 | S2 | DIGI2 | EventMaskHi | UINT32 | RW | 0...4294967295
12 | S1 | DIGI3 | EventMaskLo | UINT32 | RW | 0...4294967295
12 | S2 | DIGI3 | EventMaskHi | UINT32 | RW | 0...4294967295
13 | S1 | DIGI4 | EventMaskLo | UINT32 | RW | 0...4294967295
13 | S2 | DIGI4 | EventMaskHi | UINT32 | RW | 0...4294967295
15 | O1 | RELE | Outputs status | UINT32 | R | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15;15b=O16;16b=O17;17b=O18;18b=O19;19b=O20;20b=O21;21b=O22;22b=O23;23b=O24;24b=O25;25b=O26;26b=O27;27b=O28;28b=O29;29b=O30;30b=O31;31b=O32
15 | O2 | RELE | Outputs status | UINT32 | R | 0b=O33;1b=O34;2b=O35
15 | O3 | RELE | OUT1 | SIGNAL_IN | RW | 0...4294967295
15 | O4 | RELE | OUT2 | SIGNAL_IN | RW | 0...4294967295
15 | O5 | RELE | OUT3 | SIGNAL_IN | RW | 0...4294967295
15 | O6 | RELE | OUT4 | SIGNAL_IN | RW | 0...4294967295
15 | O7 | RELE | OUT5 | SIGNAL_IN | RW | 0...4294967295
15 | O8 | RELE | OUT6 | SIGNAL_IN | RW | 0...4294967295
15 | O9 | RELE | OUT7 | SIGNAL_IN | RW | 0...4294967295
15 | O10 | RELE | OUT8 | SIGNAL_IN | RW | 0...4294967295
15 | O11 | RELE | OUT9 | SIGNAL_IN | RW | 0...4294967295
15 | O12 | RELE | OUT10 | SIGNAL_IN | RW | 0...4294967295
15 | O13 | RELE | OUT11 | SIGNAL_IN | RW | 0...4294967295
15 | O14 | RELE | OUT12 | SIGNAL_IN | RW | 0...4294967295
15 | O15 | RELE | OUT13 | SIGNAL_IN | RW | 0...4294967295
15 | O16 | RELE | OUT14 | SIGNAL_IN | RW | 0...4294967295
15 | O17 | RELE | OUT15 | SIGNAL_IN | RW | 0...4294967295
15 | O18 | RELE | OUT16 | SIGNAL_IN | RW | 0...4294967295
15 | O19 | RELE | OUT17 | SIGNAL_IN | RW | 0...4294967295
15 | O20 | RELE | OUT18 | SIGNAL_IN | RW | 0...4294967295
15 | O21 | RELE | OUT19 | SIGNAL_IN | RW | 0...4294967295
15 | O22 | RELE | OUT20 | SIGNAL_IN | RW | 0...4294967295
15 | O23 | RELE | OUT21 | SIGNAL_IN | RW | 0...4294967295
15 | O24 | RELE | OUT22 | SIGNAL_IN | RW | 0...4294967295
15 | O25 | RELE | OUT23 | SIGNAL_IN | RW | 0...4294967295
15 | O26 | RELE | OUT24 | SIGNAL_IN | RW | 0...4294967295
15 | O27 | RELE | OUT25 | SIGNAL_IN | RW | 0...4294967295
15 | O28 | RELE | OUT26 | SIGNAL_IN | RW | 0...4294967295
15 | O29 | RELE | OUT27 | SIGNAL_IN | RW | 0...4294967295
15 | O30 | RELE | OUT28 | SIGNAL_IN | RW | 0...4294967295
15 | O31 | RELE | OUT29 | SIGNAL_IN | RW | 0...4294967295
15 | O32 | RELE | OUT30 | SIGNAL_IN | RW | 0...4294967295
15 | O33 | RELE | OUT31 | SIGNAL_IN | RW | 0...4294967295
15 | O34 | RELE | OUT32 | SIGNAL_IN | RW | 0...4294967295
15 | O35 | RELE | OUT33 | SIGNAL_IN | RW | 0...4294967295
15 | O36 | RELE | OUT34 | SIGNAL_IN | RW | 0...4294967295
15 | O37 | RELE | OUT35 | SIGNAL_IN | RW | 0...4294967295
51 | O1 | HSHC | HSO1 | SIGNAL_IN | RW | 0...4294967295
51 | O2 | HSHC | HSO2 | SIGNAL_IN | RW | 0...4294967295
51 | O3 | HSHC | HSO3 | SIGNAL_IN | RW | 0...4294967295
51 | O4 | HSHC | HSO4 | SIGNAL_IN | RW | 0...4294967295
51 | O5 | HSHC | HSO5 | SIGNAL_IN | RW | 0...4294967295
51 | O6 | HSHC | HSO6 | SIGNAL_IN | RW | 0...4294967295
51 | O7 | HSHC | HSO7 | SIGNAL_IN | RW | 0...4294967295
51 | O8 | HSHC | HSO8 | SIGNAL_IN | RW | 0...4294967295
51 | O9 | HSHC | HSO9 | SIGNAL_IN | RW | 0...4294967295
51 | I1 | HSHC | HSO1 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I2 | HSHC | HSO2 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I3 | HSHC | HSO3 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I4 | HSHC | HSO4 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I5 | HSHC | HSO5 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I6 | HSHC | HSO6 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I7 | HSHC | HSO7 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I8 | HSHC | HSO8 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I9 | HSHC | HSO9 TCS input | SIGNAL_OUT | RW | 0...4294967295
51 | I10 | HSHC | HSO card inputs | UINT32 | R | 0b=HSO1 TCS In;1b=HSO2 TCS In;2b=HSO3 TCS In;3b=HSO4 TCS In;4b=HSO5 TCS In;5b=HSO6 TCS In;6b=HSO7 TCS In;7b=HSO8 TCS In;8b=HSO9 TCS In
51 | I11 | HSHC | HSO card output status | UINT32 | R | 0b=HSO1;1b=HSO2;2b=HSO3;3b=HSO4;4b=HSO5;5b=HSO6;6b=HSO7;7b=HSO8;8b=HSO9
51 | V1 | HSHC | HSO1 TCS Counter | UINT32 | R | 0...4294967295
51 | V2 | HSHC | HSO1 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V3 | HSHC | HSO2 TCS Counter | UINT32 | R | 0...4294967295
51 | V4 | HSHC | HSO2 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V5 | HSHC | HSO3 TCS Counter | UINT32 | R | 0...4294967295
51 | V6 | HSHC | HSO3 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V7 | HSHC | HSO4 TCS Counter | UINT32 | R | 0...4294967295
51 | V8 | HSHC | HSO4 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V9 | HSHC | HSO5 TCS Counter | UINT32 | R | 0...4294967295
51 | V10 | HSHC | HSO5 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V11 | HSHC | HSO6 TCS Counter | UINT32 | R | 0...4294967295
51 | V12 | HSHC | HSO6 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V13 | HSHC | HSO7 TCS Counter | UINT32 | R | 0...4294967295
51 | V14 | HSHC | HSO7 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V15 | HSHC | HSO8 TCS Counter | UINT32 | R | 0...4294967295
51 | V16 | HSHC | HSO8 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | V17 | HSHC | HSO9 TCS Counter | UINT32 | R | 0...4294967295
51 | V18 | HSHC | HSO9 TCS Clear counter | UINT32 | RW | 0=-;1=Clear
51 | S1 | HSHC | EventMaskLo | UINT32 | RW | 0...4294967295
51 | S2 | HSHC | EventMaskHi | UINT32 | RW | 0...4294967295
121 | O1 | LED | LED START | SIGNAL_IN | RW | 0...4294967295
121 | O2 | LED | LED TRIP | SIGNAL_IN | RW | 0...4294967295
121 | O3 | LED | User LED (Default Green) 1 | SIGNAL_IN | RW | 0...4294967295
121 | O4 | LED | User LED (Default Green) 2 | SIGNAL_IN | RW | 0...4294967295
121 | O5 | LED | User LED (Default Green) 3 | SIGNAL_IN | RW | 0...4294967295
121 | O6 | LED | User LED (Default Green) 4 | SIGNAL_IN | RW | 0...4294967295
121 | O7 | LED | User LED (Default Green) 5 | SIGNAL_IN | RW | 0...4294967295
121 | O8 | LED | User LED (Default Green) 6 | SIGNAL_IN | RW | 0...4294967295
121 | O9 | LED | User LED (Default Green) 7 | SIGNAL_IN | RW | 0...4294967295
121 | O10 | LED | User LED (Default Green) 8 | SIGNAL_IN | RW | 0...4294967295
121 | O11 | LED | User LED (Default Green) 9 | SIGNAL_IN | RW | 0...4294967295
121 | O12 | LED | User LED (Default Green) 10 | SIGNAL_IN | RW | 0...4294967295
121 | O13 | LED | User LED (Default Green) 11 | SIGNAL_IN | RW | 0...4294967295
121 | O14 | LED | User LED (Default Green) 12 | SIGNAL_IN | RW | 0...4294967295
121 | O15 | LED | User LED (Default Green) 13 | SIGNAL_IN | RW | 0...4294967295
121 | O16 | LED | User LED (Default Green) 14 | SIGNAL_IN | RW | 0...4294967295
121 | O17 | LED | User LED (Default Green) 15 | SIGNAL_IN | RW | 0...4294967295
121 | O18 | LED | User LED (Default Green) 16 | SIGNAL_IN | RW | 0...4294967295
121 | O19 | LED | Red User LED 1 | SIGNAL_IN | RW | 0...4294967295
121 | O20 | LED | Red User LED 2 | SIGNAL_IN | RW | 0...4294967295
121 | O21 | LED | Red User LED 3 | SIGNAL_IN | RW | 0...4294967295
121 | O22 | LED | Red User LED 4 | SIGNAL_IN | RW | 0...4294967295
121 | O23 | LED | Red User LED 5 | SIGNAL_IN | RW | 0...4294967295
121 | O24 | LED | Red User LED 6 | SIGNAL_IN | RW | 0...4294967295
121 | O25 | LED | Red User LED 7 | SIGNAL_IN | RW | 0...4294967295
121 | O26 | LED | Red User LED 8 | SIGNAL_IN | RW | 0...4294967295
121 | O27 | LED | Red User LED 9 | SIGNAL_IN | RW | 0...4294967295
121 | O28 | LED | Red User LED 10 | SIGNAL_IN | RW | 0...4294967295
121 | O29 | LED | Red User LED 11 | SIGNAL_IN | RW | 0...4294967295
121 | O30 | LED | Red User LED 12 | SIGNAL_IN | RW | 0...4294967295
121 | O31 | LED | Red User LED 13 | SIGNAL_IN | RW | 0...4294967295
121 | O32 | LED | Red User LED 14 | SIGNAL_IN | RW | 0...4294967295
121 | O33 | LED | Red User LED 15 | SIGNAL_IN | RW | 0...4294967295
121 | O34 | LED | Red User LED 16 | SIGNAL_IN | RW | 0...4294967295
121 | O35 | LED | Orange User LED 1 | SIGNAL_IN | RW | 0...4294967295
121 | O36 | LED | Orange User LED 2 | SIGNAL_IN | RW | 0...4294967295
121 | O37 | LED | Orange User LED 3 | SIGNAL_IN | RW | 0...4294967295
121 | O38 | LED | Orange User LED 4 | SIGNAL_IN | RW | 0...4294967295
121 | O39 | LED | Orange User LED 5 | SIGNAL_IN | RW | 0...4294967295
121 | O40 | LED | Orange User LED 6 | SIGNAL_IN | RW | 0...4294967295
121 | O41 | LED | Orange User LED 7 | SIGNAL_IN | RW | 0...4294967295
121 | O42 | LED | Orange User LED 8 | SIGNAL_IN | RW | 0...4294967295
121 | O43 | LED | Orange User LED 9 | SIGNAL_IN | RW | 0...4294967295
121 | O44 | LED | Orange User LED 10 | SIGNAL_IN | RW | 0...4294967295
121 | O45 | LED | Orange User LED 11 | SIGNAL_IN | RW | 0...4294967295
121 | O46 | LED | Orange User LED 12 | SIGNAL_IN | RW | 0...4294967295
121 | O47 | LED | Orange User LED 13 | SIGNAL_IN | RW | 0...4294967295
121 | O48 | LED | Orange User LED 14 | SIGNAL_IN | RW | 0...4294967295
121 | O49 | LED | Orange User LED 15 | SIGNAL_IN | RW | 0...4294967295
121 | O50 | LED | Orange User LED 16 | SIGNAL_IN | RW | 0...4294967295
122 | O1 | LEDX | User LED 17 | SIGNAL_IN | RW | 0...4294967295
122 | O2 | LEDX | User LED 18 | SIGNAL_IN | RW | 0...4294967295
122 | O3 | LEDX | User LED 19 | SIGNAL_IN | RW | 0...4294967295
122 | O4 | LEDX | User LED 20 | SIGNAL_IN | RW | 0...4294967295
122 | O5 | LEDX | User LED 21 | SIGNAL_IN | RW | 0...4294967295
122 | O6 | LEDX | User LED 22 | SIGNAL_IN | RW | 0...4294967295
122 | O7 | LEDX | User LED 23 | SIGNAL_IN | RW | 0...4294967295
122 | O8 | LEDX | User LED 24 | SIGNAL_IN | RW | 0...4294967295
122 | O9 | LEDX | User LED 25 | SIGNAL_IN | RW | 0...4294967295
122 | O10 | LEDX | User LED 26 | SIGNAL_IN | RW | 0...4294967295
122 | O11 | LEDX | User LED 27 | SIGNAL_IN | RW | 0...4294967295
122 | O12 | LEDX | User LED 28 | SIGNAL_IN | RW | 0...4294967295
122 | O13 | LEDX | User LED 29 | SIGNAL_IN | RW | 0...4294967295
122 | O14 | LEDX | User LED 30 | SIGNAL_IN | RW | 0...4294967295
122 | O15 | LEDX | User LED 31 | SIGNAL_IN | RW | 0...4294967295
122 | O16 | LEDX | User LED 32 | SIGNAL_IN | RW | 0...4294967295
122 | O17 | LEDX | User LED 33 | SIGNAL_IN | RW | 0...4294967295
122 | O18 | LEDX | User LED 34 | SIGNAL_IN | RW | 0...4294967295
122 | O19 | LEDX | User LED 35 | SIGNAL_IN | RW | 0...4294967295
122 | O20 | LEDX | User LED 36 | SIGNAL_IN | RW | 0...4294967295
122 | O21 | LEDX | User LED 37 | SIGNAL_IN | RW | 0...4294967295
122 | O22 | LEDX | User LED 38 | SIGNAL_IN | RW | 0...4294967295
122 | O23 | LEDX | User LED 39 | SIGNAL_IN | RW | 0...4294967295
122 | O24 | LEDX | User LED 40 | SIGNAL_IN | RW | 0...4294967295
122 | O25 | LEDX | User LED 41 | SIGNAL_IN | RW | 0...4294967295
122 | O26 | LEDX | User LED 42 | SIGNAL_IN | RW | 0...4294967295
122 | O27 | LEDX | User LED 43 | SIGNAL_IN | RW | 0...4294967295
122 | O28 | LEDX | User LED 44 | SIGNAL_IN | RW | 0...4294967295
122 | O29 | LEDX | User LED 45 | SIGNAL_IN | RW | 0...4294967295
122 | O30 | LEDX | User LED 46 | SIGNAL_IN | RW | 0...4294967295
122 | O31 | LEDX | User LED 47 | SIGNAL_IN | RW | 0...4294967295
122 | O32 | LEDX | User LED 48 | SIGNAL_IN | RW | 0...4294967295
65 | V1 | SGS | Active setting group | UINT32 | R | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
65 | S1 | SGS | Force setting group | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | S2 | SGS | Force setting group change | UINT32 | RW | 0=Disabled;1=Enabled
65 | S3 | SGS | Used setting groups | UINT32 | RW | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
65 | S4 | SGS | Remote setting group change | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | O1 | SGS | Forced setting group in use | SIGNAL_OUT | RW | 0...4294967295
65 | O2 | SGS | Setting group 1 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O3 | SGS | Setting group 2 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O4 | SGS | Setting group 3 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O5 | SGS | Setting group 4 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O6 | SGS | Setting group 5 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O7 | SGS | Setting group 6 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O8 | SGS | Setting group 7 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O9 | SGS | Setting group 8 Active | SIGNAL_OUT | RW | 0...4294967295
195 | V1 | SGS2 | SGS2 Active setting group | UINT32 | R | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
195 | S1 | SGS2 | SGS2 Force setting group | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
195 | S2 | SGS2 | SGS2 Force setting group change | UINT32 | RW | 0=Disabled;1=Enabled
195 | S3 | SGS2 | SGS2 Used setting groups | UINT32 | RW | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
195 | S4 | SGS2 | SGS2 Remote setting group change | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
195 | O1 | SGS2 | SGS2 Forced setting group in use | SIGNAL_OUT | RW | 0...4294967295
195 | O2 | SGS2 | SGS2 Setting group 1 Active | SIGNAL_OUT | RW | 0...4294967295
195 | O3 | SGS2 | SGS2 Setting group 2 Active | SIGNAL_OUT | RW | 0...4294967295
195 | O4 | SGS2 | SGS2 Setting group 3 Active | SIGNAL_OUT | RW | 0...4294967295
195 | O5 | SGS2 | SGS2 Setting group 4 Active | SIGNAL_OUT | RW | 0...4294967295
195 | O6 | SGS2 | SGS2 Setting group 5 Active | SIGNAL_OUT | RW | 0...4294967295
195 | O7 | SGS2 | SGS2 Setting group 6 Active | SIGNAL_OUT | RW | 0...4294967295
195 | O8 | SGS2 | SGS2 Setting group 7 Active | SIGNAL_OUT | RW | 0...4294967295
195 | O9 | SGS2 | SGS2 Setting group 8 Active | SIGNAL_OUT | RW | 0...4294967295
7 | I1 | CTRL | Local/Remote status | UINT32 | R | 0=Remote;1=Local
7 | I2 | CTRL | Control Authority status | UINT32 | R | 0=Remote Control;1=Station Level Control
123 | V1 | DEV | Serial number | UINT32 | R | 0...4294967295
123 | V2 | DEV | Firmware version | STRING | R | ...32
123 | V3 | DEV | Application package | STRING | R | ...32
123 | O1 | DEV | Ph.Rotating Logic control 0=A-B-C, 1=A-C-B | SIGNAL_OUT | RW | 0...4294967295
124 | S1 | EVENT | Clear events | UINT32 | RW | 0=-;1=Clear
125 | I1 | DIAG | Diagnostic alarm status | UINT32 | R | 0b=Temp. out of range;1b=Voltage out of range;2b=HW configuration invalid;3b=Relay output failure;4b=Option card A alarm;5b=Option card B alarm;6b=Option card C alarm;7b=Option card D alarm;8b=Option card E alarm;9b=Option card F alarm;10b=Safe setting mode active;11b=System overload;12b=GOOSE simulation enabled;13b=Device/LN mode not On;14b=UAC password issue;15b=Audit logging failed;16b=Option card K alarm;17b=Option card L alarm;18b=Option card M alarm;19b=Option card N alarm
125 | S1 | DIAG | Clear diagnostic alarm | UINT32 | W | 0=-;1=Clear
125 | I2 | DIAG | Internal temperature | FLOAT | R | 0...200
125 | I3 | DIAG | Internal voltage 24V | FLOAT | R | 0...50
125 | I4 | DIAG | Internal voltage 24V max | FLOAT | R | 0...50
125 | I5 | DIAG | Internal voltage 24V min | FLOAT | R | 0...50
125 | I6 | DIAG | Internal voltage 24V deviation | FLOAT | R | 0...50
138 | I1 | MBIO | Input value | FLOAT | R | -101...2000
138 | I2 | MBIO | Input value | FLOAT | R | -101...2000
138 | I3 | MBIO | Input value | FLOAT | R | -101...2000
138 | I4 | MBIO | Input value | FLOAT | R | -101...2000
138 | I5 | MBIO | Input value | FLOAT | R | -101...2000
138 | I6 | MBIO | Input value | FLOAT | R | -101...2000
138 | I7 | MBIO | Input value | FLOAT | R | -101...2000
138 | I8 | MBIO | Input value | FLOAT | R | -101...2000
138 | I9 | MBIO | Input value | FLOAT | R | -101...2000
138 | I10 | MBIO | Input value | FLOAT | R | -101...2000
138 | I11 | MBIO | Input value | FLOAT | R | -101...2000
138 | I12 | MBIO | Input value | FLOAT | R | -101...2000
138 | I13 | MBIO | Input value | FLOAT | R | -101...2000
138 | I14 | MBIO | Input value | FLOAT | R | -101...2000
138 | I15 | MBIO | Input value | FLOAT | R | -101...2000
138 | I16 | MBIO | Input value | FLOAT | R | -101...2000
138 | I17 | MBIO | Input value | FLOAT | R | -101...2000
138 | I18 | MBIO | Input value | FLOAT | R | -101...2000
138 | I19 | MBIO | Input value | FLOAT | R | -101...2000
138 | I20 | MBIO | Input value | FLOAT | R | -101...2000
138 | I21 | MBIO | Input value | FLOAT | R | -101...2000
138 | I22 | MBIO | Input value | FLOAT | R | -101...2000
138 | I23 | MBIO | Input value | FLOAT | R | -101...2000
138 | I24 | MBIO | Input value | FLOAT | R | -101...2000
138 | I25 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I26 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I27 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I28 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I29 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I30 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I31 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I32 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I33 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I34 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I35 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I36 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I37 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I38 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I39 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I40 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I41 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I42 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I43 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I44 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I45 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I46 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I47 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I48 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | O1 | MBIO | MBIO ModA Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O2 | MBIO | MBIO ModA Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O3 | MBIO | MBIO ModA Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O4 | MBIO | MBIO ModA Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O5 | MBIO | MBIO ModA Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O6 | MBIO | MBIO ModA Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O7 | MBIO | MBIO ModA Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O8 | MBIO | MBIO ModA Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O9 | MBIO | MBIO ModB Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O10 | MBIO | MBIO ModB Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O11 | MBIO | MBIO ModB Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O12 | MBIO | MBIO ModB Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O13 | MBIO | MBIO ModB Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O14 | MBIO | MBIO ModB Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O15 | MBIO | MBIO ModB Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O16 | MBIO | MBIO ModB Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O17 | MBIO | MBIO ModC Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O18 | MBIO | MBIO ModC Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O19 | MBIO | MBIO ModC Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O20 | MBIO | MBIO ModC Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O21 | MBIO | MBIO ModC Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O22 | MBIO | MBIO ModC Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O23 | MBIO | MBIO ModC Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O24 | MBIO | MBIO ModC Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
139 | V1 | LOGIC | Reset Latches | UINT32 | RW | 0=-;1=Reset
8 | O1 | LOGIC1 | Logic out 1-32 | UINT32 | RW | 0...4294967295
8 | O2 | LOGIC1 | Logic out 33-64 | UINT32 | RW | 0...4294967295
139 | O1 | LOGIC | Logical Output 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O2 | LOGIC | Logical Output 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O3 | LOGIC | Logical Output 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O4 | LOGIC | Logical Output 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O5 | LOGIC | Logical Output 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O6 | LOGIC | Logical Output 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O7 | LOGIC | Logical Output 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O8 | LOGIC | Logical Output 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O9 | LOGIC | Logical Output 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O10 | LOGIC | Logical Output 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O11 | LOGIC | Logical Output 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O12 | LOGIC | Logical Output 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O13 | LOGIC | Logical Output 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O14 | LOGIC | Logical Output 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O15 | LOGIC | Logical Output 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O16 | LOGIC | Logical Output 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O17 | LOGIC | Logical Output 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O18 | LOGIC | Logical Output 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O19 | LOGIC | Logical Output 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O20 | LOGIC | Logical Output 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O21 | LOGIC | Logical Output 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O22 | LOGIC | Logical Output 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O23 | LOGIC | Logical Output 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O24 | LOGIC | Logical Output 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O25 | LOGIC | Logical Output 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O26 | LOGIC | Logical Output 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O27 | LOGIC | Logical Output 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O28 | LOGIC | Logical Output 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O29 | LOGIC | Logical Output 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O30 | LOGIC | Logical Output 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O31 | LOGIC | Logical Output 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O32 | LOGIC | Logical Output 32 | SIGNAL_OUT | RW | 0...4294967295
139 | O33 | LOGIC | Logical Output 33 | SIGNAL_OUT | RW | 0...4294967295
139 | O34 | LOGIC | Logical Output 34 | SIGNAL_OUT | RW | 0...4294967295
139 | O35 | LOGIC | Logical Output 35 | SIGNAL_OUT | RW | 0...4294967295
139 | O36 | LOGIC | Logical Output 36 | SIGNAL_OUT | RW | 0...4294967295
139 | O37 | LOGIC | Logical Output 37 | SIGNAL_OUT | RW | 0...4294967295
139 | O38 | LOGIC | Logical Output 38 | SIGNAL_OUT | RW | 0...4294967295
139 | O39 | LOGIC | Logical Output 39 | SIGNAL_OUT | RW | 0...4294967295
139 | O40 | LOGIC | Logical Output 40 | SIGNAL_OUT | RW | 0...4294967295
139 | O41 | LOGIC | Logical Output 41 | SIGNAL_OUT | RW | 0...4294967295
139 | O42 | LOGIC | Logical Output 42 | SIGNAL_OUT | RW | 0...4294967295
139 | O43 | LOGIC | Logical Output 43 | SIGNAL_OUT | RW | 0...4294967295
139 | O44 | LOGIC | Logical Output 44 | SIGNAL_OUT | RW | 0...4294967295
139 | O45 | LOGIC | Logical Output 45 | SIGNAL_OUT | RW | 0...4294967295
139 | O46 | LOGIC | Logical Output 46 | SIGNAL_OUT | RW | 0...4294967295
139 | O47 | LOGIC | Logical Output 47 | SIGNAL_OUT | RW | 0...4294967295
139 | O48 | LOGIC | Logical Output 48 | SIGNAL_OUT | RW | 0...4294967295
139 | O49 | LOGIC | Logical Output 49 | SIGNAL_OUT | RW | 0...4294967295
139 | O50 | LOGIC | Logical Output 50 | SIGNAL_OUT | RW | 0...4294967295
139 | O51 | LOGIC | Logical Output 51 | SIGNAL_OUT | RW | 0...4294967295
139 | O52 | LOGIC | Logical Output 52 | SIGNAL_OUT | RW | 0...4294967295
139 | O53 | LOGIC | Logical Output 53 | SIGNAL_OUT | RW | 0...4294967295
139 | O54 | LOGIC | Logical Output 54 | SIGNAL_OUT | RW | 0...4294967295
139 | O55 | LOGIC | Logical Output 55 | SIGNAL_OUT | RW | 0...4294967295
139 | O56 | LOGIC | Logical Output 56 | SIGNAL_OUT | RW | 0...4294967295
139 | O57 | LOGIC | Logical Output 57 | SIGNAL_OUT | RW | 0...4294967295
139 | O58 | LOGIC | Logical Output 58 | SIGNAL_OUT | RW | 0...4294967295
139 | O59 | LOGIC | Logical Output 59 | SIGNAL_OUT | RW | 0...4294967295
139 | O60 | LOGIC | Logical Output 60 | SIGNAL_OUT | RW | 0...4294967295
139 | O61 | LOGIC | Logical Output 61 | SIGNAL_OUT | RW | 0...4294967295
139 | O62 | LOGIC | Logical Output 62 | SIGNAL_OUT | RW | 0...4294967295
139 | O63 | LOGIC | Logical Output 63 | SIGNAL_OUT | RW | 0...4294967295
139 | O64 | LOGIC | Logical Output 64 | SIGNAL_OUT | RW | 0...4294967295
139 | O65 | LOGIC | Logical Input 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O66 | LOGIC | Logical Input 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O67 | LOGIC | Logical Input 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O68 | LOGIC | Logical Input 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O69 | LOGIC | Logical Input 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O70 | LOGIC | Logical Input 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O71 | LOGIC | Logical Input 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O72 | LOGIC | Logical Input 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O73 | LOGIC | Logical Input 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O74 | LOGIC | Logical Input 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O75 | LOGIC | Logical Input 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O76 | LOGIC | Logical Input 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O77 | LOGIC | Logical Input 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O78 | LOGIC | Logical Input 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O79 | LOGIC | Logical Input 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O80 | LOGIC | Logical Input 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O81 | LOGIC | Logical Input 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O82 | LOGIC | Logical Input 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O83 | LOGIC | Logical Input 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O84 | LOGIC | Logical Input 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O85 | LOGIC | Logical Input 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O86 | LOGIC | Logical Input 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O87 | LOGIC | Logical Input 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O88 | LOGIC | Logical Input 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O89 | LOGIC | Logical Input 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O90 | LOGIC | Logical Input 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O91 | LOGIC | Logical Input 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O92 | LOGIC | Logical Input 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O93 | LOGIC | Logical Input 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O94 | LOGIC | Logical Input 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O95 | LOGIC | Logical Input 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O96 | LOGIC | Logical Input 32 | SIGNAL_OUT | RW | 0...4294967295
8 | S1 | LOGIC1 | Logical Out 1-16 EventMask | UINT32 | RW | 0...4294967295
8 | S2 | LOGIC1 | Logical Out 17-32 EventMask | UINT32 | RW | 0...4294967295
9 | S1 | LOGIC2 | Logical In 1-16 EventMask | UINT32 | RW | 0...4294967295
9 | S2 | LOGIC2 | Logical In 17-32 EventMask | UINT32 | RW | 0...4294967295
14 | S1 | LOGIC3 | Logical Out 33-48 EventMask | UINT32 | RW | 0...4294967295
14 | S2 | LOGIC3 | Logical Out 49-64 EventMask | UINT32 | RW | 0...4294967295
24 | S1 | LOGIC4 | LIDB & LITC EventMask | UINT32 | RW | 0...4294967295
24 | S2 | LOGIC4 | LIDB & LITC EventMask | UINT32 | RW | 0...4294967295
140 | O1 | TIMER | Timer1 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O2 | TIMER | Timer2 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O3 | TIMER | Timer3 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O4 | TIMER | Timer4 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O5 | TIMER | Timer5 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O6 | TIMER | Timer6 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O7 | TIMER | Timer7 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O8 | TIMER | Timer8 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O9 | TIMER | Timer9 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O10 | TIMER | Timer10 Output | SIGNAL_OUT | RW | 0...4294967295
2 | I1 | IRF | Internal Relay Fault status | UINT32 | R | 0b=Storage error;1b=Logic file missing;2b=Aquisition unit error;3b=Measurement config error;4b=Relay hardware setup error;5b=System overload error;6b=Not configured yet;7b=Firmware upgrade done;8b=Slot supervision error;9b=Software inconsistency error;10b=Event overload;
2 | S1 | IRF | Clear Fault status | UINT32 | W | 0=-;1=Clear
2 | I2 | IRF | Option card health status | UINT32 | R | 0b=Baseboard fault;1b=Card slot A fault;2b=Card slot B fault;3b=Card slot C fault;4b=Card slot D fault;5b=Card slot E fault;6b=Card slot F fault;
206 | V1 | COL1 | ICOL> [49OL] condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
207 | V1 | COL2 | ICOL>> [49OL] condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
208 | I1 | CNU1 | Measured unbalance current | FLOAT | R | 0...50
208 | I2 | CNU1 | Unbalance current angle | FLOAT | R | -360...360
208 | S1 | CNU1 | Natural unbalance compensation | UINT32 | RW | 0=Not used;1=In use
208 | S2 | CNU1 | Compensate natural unbal. | UINT32 | RW | 0=-;1=Comp
208 | I3 | CNU1 | Natural unbalance | FLOAT | R | -50...50
208 | I4 | CNU1 | Natural unbalance ang | FLOAT | R | -360...360
208 | I5 | CNU1 | Compensated magnitude | FLOAT | R | -50...50
208 | I6 | CNU1 | Compensated angle | FLOAT | R | -360...360
208 | V1 | CNU1 | CNU> [50UB] condition | UINT32 | R | 0=Normal;1=Alarm Start;2=Alarm On;3=Trip Start;4=Trip On;5=Blocked On
217 | V1 | UCP1 | IUC> condition | UINT32 | R | 0=Normal;1=Blocked;2=StartOn(Alarm);3=StartOn(Alarm&Trip);4=StartOn(Trip);5=AlarmOn;6=StartOn(Alarm),TripOn;7=StartOn,AlarmOn;8=TripOn;9=AlarmOn,TripOn;10=MultistatusOn
217 | I1 | UCP1 | Current unbalance atm. | FLOAT | R | 0...1250
217 | I2 | UCP1 | Imeas/Iset (ALARM) atm. | FLOAT | R | 0...1250
217 | I3 | UCP1 | Imeas/Iset (TRIP) atm. | FLOAT | R | 0...1250
217 | I4 | UCP1 | IUC> Alarm Starts | UINT32 | R | 0...4294967295
217 | I5 | UCP1 | IUC> Alarms | UINT32 | R | 0...4294967295
217 | I6 | UCP1 | IUC> Starts | UINT32 | R | 0...4294967295
217 | I7 | UCP1 | IUC> Trips | UINT32 | R | 0...4294967295
217 | I8 | UCP1 | IUC> Blocks | UINT32 | R | 0...4294967295
217 | S1 | UCP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
217 | S2 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG1
217 | S3 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG2
217 | S4 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG3
217 | S5 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG4
217 | S6 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG5
217 | S7 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG6
217 | S8 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG7
217 | S9 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50 | SG8
217 | S10 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG1
217 | S11 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG2
217 | S12 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG3
217 | S13 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG4
217 | S14 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG5
217 | S15 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG6
217 | S16 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG7
217 | S17 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800 | SG8
217 | S18 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG1
217 | S19 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG2
217 | S20 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG3
217 | S21 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG4
217 | S22 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG5
217 | S23 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG6
217 | S24 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG7
217 | S25 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50 | SG8
217 | S26 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG1
217 | S27 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG2
217 | S28 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG3
217 | S29 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG4
217 | S30 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG5
217 | S31 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG6
217 | S32 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG7
217 | S33 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800 | SG8
217 | S34 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
217 | S35 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
217 | S36 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
217 | S37 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
217 | S38 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
217 | S39 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
217 | S40 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
217 | S41 | UCP1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
217 | O1 | UCP1 | IUC> ALARM START | SIGNAL_OUT | RW | 0...4294967295
217 | O2 | UCP1 | IUC> ALARM | SIGNAL_OUT | RW | 0...4294967295
217 | O3 | UCP1 | IUC> START | SIGNAL_OUT | RW | 0...4294967295
217 | O4 | UCP1 | IUC> TRIP | SIGNAL_OUT | RW | 0...4294967295
217 | O5 | UCP1 | IUC> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
217 | V2 | UCP1 | Newest register | UINT32 | R | 0...12
217 | V3 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V4 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V5 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V6 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V7 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V8 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V9 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V10 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V11 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V12 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V13 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V14 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | S42 | UCP1 | EventMaskLo | UINT32 | RW | 0...4294967295
209 | S1 | CRF1 | Cd> (87C) mode | UINT32 | RW | 0=Disabled;1=Activated
209 | V1 | CRF1 | Cd> (87C) condition | UINT32 | R | 0=Normal;1=Trip;2=Blocked
209 | S2 | CRF1 | Select | UINT32 | RW | 0=Primary A;1=Secondary A;2=Per Unit
209 | S3 | CRF1 | Select | UINT32 | RW | 0=REF Curr
209 | I1 | CRF1 | Cd> (87C) Bias current | FLOAT | R | 0...50
209 | I2 | CRF1 | Cd> (87C) Diff current | FLOAT | R | 0...50
209 | I3 | CRF1 | Cd> (87C) Char current | FLOAT | R | 0...50
209 | I4 | CRF1 | Calculated I0 (I0Calc) | FLOAT | R | 0...50
209 | I5 | CRF1 | Measured I0 (3I0) | FLOAT | R | 0...50
209 | S4 | CRF1 | Unbalance compensation | UINT32 | RW | 0=Not used;1=In use
209 | S5 | CRF1 | Comp. natural unbal. | UINT32 | RW | 0=-;1=Comp
209 | I6 | CRF1 | Natural unbalance | FLOAT | R | 0...50
209 | I7 | CRF1 | Natural unbalance ang | FLOAT | R | -360...360
209 | I8 | CRF1 | Compensated magnitude | FLOAT | R | 0...50
209 | I9 | CRF1 | Compensated angle | FLOAT | R | -360...360
209 | S6 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG1
209 | S7 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG2
209 | S8 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG3
209 | S9 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG4
209 | S10 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG5
209 | S11 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG6
209 | S12 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG7
209 | S13 | CRF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG8
209 | S14 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG1
209 | S15 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG2
209 | S16 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG3
209 | S17 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG4
209 | S18 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG5
209 | S19 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG6
209 | S20 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG7
209 | S21 | CRF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG8
209 | S22 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG1
209 | S23 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG2
209 | S24 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG3
209 | S25 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG4
209 | S26 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG5
209 | S27 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG6
209 | S28 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG7
209 | S29 | CRF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc) | SG8
209 | S30 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG1
209 | S31 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG2
209 | S32 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG3
209 | S33 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG4
209 | S34 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG5
209 | S35 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG6
209 | S36 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG7
209 | S37 | CRF1 | Cd> (87C) Pickup | FLOAT | RW | 0.01...50 | SG8
209 | S38 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG1
209 | S39 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG2
209 | S40 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG3
209 | S41 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG4
209 | S42 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG5
209 | S43 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG6
209 | S44 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG7
209 | S45 | CRF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG8
209 | S46 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG1
209 | S47 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG2
209 | S48 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG3
209 | S49 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG4
209 | S50 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG5
209 | S51 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG6
209 | S52 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG7
209 | S53 | CRF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG8
209 | S54 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG1
209 | S55 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG2
209 | S56 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG3
209 | S57 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG4
209 | S58 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG5
209 | S59 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG6
209 | S60 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG7
209 | S61 | CRF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG8
209 | S62 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG1
209 | S63 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG2
209 | S64 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG3
209 | S65 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG4
209 | S66 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG5
209 | S67 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG6
209 | S68 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG7
209 | S69 | CRF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG8
209 | S70 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG1
209 | S71 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG2
209 | S72 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG3
209 | S73 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG4
209 | S74 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG5
209 | S75 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG6
209 | S76 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG7
209 | S77 | CRF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG8
209 | O1 | CRF1 | Cd> (87C) TRIP | SIGNAL_OUT | RW | 0...4294967295
209 | O2 | CRF1 | Cd> (87C) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
209 | I10 | CRF1 | Newest register | UINT32 | R | 0...12
209 | I11 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I12 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I13 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I14 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I15 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I16 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I17 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I18 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I19 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I20 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I21 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I22 | CRF1 | Bias current | FLOAT | R | 0...250
209 | I23 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I24 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I25 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I26 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I27 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I28 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I29 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I30 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I31 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I32 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I33 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I34 | CRF1 | Differential current | FLOAT | R | 0...250
209 | I35 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I36 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I37 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I38 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I39 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I40 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I41 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I42 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I43 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I44 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I45 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | I46 | CRF1 | Characteristics current | FLOAT | R | 0...250
209 | S78 | CRF1 | EventMaskLo | UINT32 | RW | 0...4294967295
209 | S79 | CRF1 | EventMaskHi | UINT32 | RW | 0...4294967295
192 | S1 | NOCS1 | IPW> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
192 | V1 | NOCS1 | IPW> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=StartL1;5=StartL2;6=StartL3;7=TripL1;8=TripL2;9=TripL3;10=StartL1-2;11=StartL2-3;12=StartL3-1;13=TripL1-2;14=TripL2-3;15=TripL31;16=StartL1-2-3;17=TripL1-2-3
192 | I1 | NOCS1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
192 | I2 | NOCS1 | IPW> starts | UINT32 | R | 0...4294967295
192 | I3 | NOCS1 | IPW> trips | UINT32 | R | 0...4294967295
192 | I4 | NOCS1 | IPW> blocks | UINT32 | R | 0...4294967295
192 | S2 | NOCS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
194 | S1 | NOCS2 | IPW>> mode | UINT32 | RW | 0=Disabled;1=Activated
194 | V1 | NOCS2 | IPW>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=StartL1;5=StartL2;6=StartL3;7=TripL1;8=TripL2;9=TripL3;10=StartL1-2;11=StartL2-3;12=StartL3-1;13=TripL1-2;14=TripL2-3;15=TripL31;16=StartL1-2-3;17=TripL1-2-3
194 | I1 | NOCS2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
194 | I2 | NOCS2 | IPW>> starts | UINT32 | R | 0...4294967295
194 | I3 | NOCS2 | IPW>> trips | UINT32 | R | 0...4294967295
194 | I4 | NOCS2 | IPW>> blocks | UINT32 | R | 0...4294967295
194 | S2 | NOCS2 | Clear statistics | UINT32 | W | 0=-;1=Clear
20 | S1 | NOC1 | I> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
20 | V1 | NOC1 | I> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
20 | V2 | NOC1 | I> phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
20 | I1 | NOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
20 | I2 | NOC1 | I> starts | UINT32 | R | 0...4294967295
20 | I3 | NOC1 | I> trips | UINT32 | R | 0...4294967295
20 | I4 | NOC1 | I> blocks | UINT32 | R | 0...4294967295
20 | S2 | NOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
20 | S3 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG1
20 | S4 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG2
20 | S5 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG3
20 | S6 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG4
20 | S7 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG5
20 | S8 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG6
20 | S9 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG7
20 | S10 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG8
20 | S11 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
20 | S12 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
20 | S13 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
20 | S14 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
20 | S15 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
20 | S16 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
20 | S17 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
20 | S18 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
20 | S19 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
20 | S20 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
20 | S21 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
20 | S22 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
20 | S23 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
20 | S24 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
20 | S25 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
20 | S26 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
20 | S27 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
20 | S28 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
20 | S29 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
20 | S30 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
20 | S31 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
20 | S32 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
20 | S33 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
20 | S34 | NOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
20 | O1 | NOC1 | I> START (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O2 | NOC1 | I> START(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O3 | NOC1 | I> START(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O4 | NOC1 | I> START(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O5 | NOC1 | I> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O6 | NOC1 | I> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O7 | NOC1 | I> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O8 | NOC1 | I> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O9 | NOC1 | I> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
20 | V3 | NOC1 | Newest register | UINT32 | R | 0...12
20 | V4 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V5 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V6 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V7 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V8 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V9 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V10 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V11 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V12 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V13 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V14 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V15 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V16 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V17 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V18 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V19 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V20 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V21 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V22 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V23 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V24 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V25 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V26 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V27 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V28 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V29 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V30 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V31 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V32 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V33 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V34 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V35 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V36 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V37 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V38 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V39 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | S35 | NOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
21 | S1 | NOC2 | I>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
21 | S2 | NOC2 | I>> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
21 | V1 | NOC2 | I>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
21 | V2 | NOC2 | I>> phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
21 | I1 | NOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
21 | I2 | NOC2 | I>> starts | UINT32 | R | 0...4294967295
21 | I3 | NOC2 | I>> trips | UINT32 | R | 0...4294967295
21 | I4 | NOC2 | I>> blocks | UINT32 | R | 0...4294967295
21 | S3 | NOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
21 | S4 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG1
21 | S5 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG2
21 | S6 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG3
21 | S7 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG4
21 | S8 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG5
21 | S9 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG6
21 | S10 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG7
21 | S11 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG8
21 | S12 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
21 | S13 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
21 | S14 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
21 | S15 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
21 | S16 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
21 | S17 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
21 | S18 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
21 | S19 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
21 | S20 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
21 | S21 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
21 | S22 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
21 | S23 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
21 | S24 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
21 | S25 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
21 | S26 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
21 | S27 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
21 | S28 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
21 | S29 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
21 | S30 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
21 | S31 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
21 | S32 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
21 | S33 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
21 | S34 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
21 | S35 | NOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
21 | O1 | NOC2 | I>> START (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O2 | NOC2 | I>> START(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O3 | NOC2 | I>> START(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O4 | NOC2 | I>> START(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O5 | NOC2 | I>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O6 | NOC2 | I>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O7 | NOC2 | I>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O8 | NOC2 | I>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O9 | NOC2 | I>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
21 | V3 | NOC2 | Newest register | UINT32 | R | 0...12
21 | V4 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V5 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V6 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V7 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V8 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V9 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V10 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V11 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V12 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V13 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V14 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V15 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V16 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V17 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V18 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V19 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V20 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V21 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V22 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V23 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V24 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V25 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V26 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V27 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V28 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V29 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V30 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V31 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V32 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V33 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V34 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V35 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V36 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V37 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V38 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V39 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | S36 | NOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
22 | S1 | NOC3 | I>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
22 | S2 | NOC3 | I>>> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
22 | V1 | NOC3 | I>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
22 | V2 | NOC3 | I>>> phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
22 | I1 | NOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
22 | I2 | NOC3 | I>>> starts | UINT32 | R | 0...4294967295
22 | I3 | NOC3 | I>>> trips | UINT32 | R | 0...4294967295
22 | I4 | NOC3 | I>>> blocks | UINT32 | R | 0...4294967295
22 | S3 | NOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
22 | S4 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG1
22 | S5 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG2
22 | S6 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG3
22 | S7 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG4
22 | S8 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG5
22 | S9 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG6
22 | S10 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG7
22 | S11 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG8
22 | S12 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
22 | S13 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
22 | S14 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
22 | S15 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
22 | S16 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
22 | S17 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
22 | S18 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
22 | S19 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
22 | S20 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
22 | S21 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
22 | S22 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
22 | S23 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
22 | S24 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
22 | S25 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
22 | S26 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
22 | S27 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
22 | S28 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
22 | S29 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
22 | S30 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
22 | S31 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
22 | S32 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
22 | S33 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
22 | S34 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
22 | S35 | NOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
22 | O1 | NOC3 | I>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O2 | NOC3 | I>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O3 | NOC3 | I>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O4 | NOC3 | I>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O5 | NOC3 | I>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O6 | NOC3 | I>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O7 | NOC3 | I>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O8 | NOC3 | I>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O9 | NOC3 | I>>>BLOCKED | SIGNAL_OUT | RW | 0...4294967295
22 | V3 | NOC3 | Newest register | UINT32 | R | 0...12
22 | V4 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V5 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V6 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V7 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V8 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V9 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V10 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V11 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V12 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V13 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V14 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V15 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V16 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V17 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V18 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V19 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V20 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V21 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V22 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V23 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V24 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V25 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V26 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V27 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V28 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V29 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V30 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V31 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V32 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V33 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V34 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V35 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V36 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V37 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V38 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V39 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | S36 | NOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
23 | S1 | NOC4 | I>>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
23 | S2 | NOC4 | I>>>> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
23 | V1 | NOC4 | I>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
23 | V2 | NOC4 | I>>>> phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
23 | I1 | NOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
23 | I2 | NOC4 | I>>>> starts | UINT32 | R | 0...4294967295
23 | I3 | NOC4 | I>>>> trips | UINT32 | R | 0...4294967295
23 | I4 | NOC4 | I>>>> blocks | UINT32 | R | 0...4294967295
23 | S3 | NOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
23 | S4 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG1
23 | S5 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG2
23 | S6 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG3
23 | S7 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG4
23 | S8 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG5
23 | S9 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG6
23 | S10 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG7
23 | S11 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50 | SG8
23 | S12 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
23 | S13 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
23 | S14 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
23 | S15 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
23 | S16 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
23 | S17 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
23 | S18 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
23 | S19 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
23 | S20 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
23 | S21 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
23 | S22 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
23 | S23 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
23 | S24 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
23 | S25 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
23 | S26 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
23 | S27 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
23 | S28 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
23 | S29 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
23 | S30 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
23 | S31 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
23 | S32 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
23 | S33 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
23 | S34 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
23 | S35 | NOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
23 | O1 | NOC4 | I>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O2 | NOC4 | I>>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O3 | NOC4 | I>>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O4 | NOC4 | I>>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O5 | NOC4 | I>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O6 | NOC4 | I>>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O7 | NOC4 | I>>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O8 | NOC4 | I>>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O9 | NOC4 | I>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
23 | V3 | NOC4 | Newest register | UINT32 | R | 0...12
23 | V4 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V5 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V6 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V7 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V8 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V9 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V10 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V11 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V12 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V13 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V14 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V15 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V16 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V17 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V18 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V19 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V20 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V21 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V22 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V23 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V24 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V25 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V26 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V27 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V28 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V29 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V30 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V31 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V32 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V33 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V34 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V35 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V36 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V37 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V38 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V39 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | S36 | NOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S1 | DOC1 | Idir> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
75 | V1 | DOC1 | Idir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
75 | I1 | DOC1 | Operating angle now | FLOAT | R | -360...360
75 | I2 | DOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
75 | I3 | DOC1 | Idir> starts | UINT32 | R | 0...4294967295
75 | I4 | DOC1 | Idir> trips | UINT32 | R | 0...4294967295
75 | I5 | DOC1 | Idir> blocks | UINT32 | R | 0...4294967295
75 | S2 | DOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
75 | S3 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG1
75 | S4 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG2
75 | S5 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG3
75 | S6 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG4
75 | S7 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG5
75 | S8 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG6
75 | S9 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG7
75 | S10 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG8
75 | S11 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG1
75 | S12 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG2
75 | S13 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG3
75 | S14 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG4
75 | S15 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG5
75 | S16 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG6
75 | S17 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG7
75 | S18 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG8
75 | S19 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG1
75 | S20 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG2
75 | S21 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG3
75 | S22 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG4
75 | S23 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG5
75 | S24 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG6
75 | S25 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG7
75 | S26 | DOC1 | Operating sector center | FLOAT | RW | -180...180 | SG8
75 | S27 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG1
75 | S28 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG2
75 | S29 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG3
75 | S30 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG4
75 | S31 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG5
75 | S32 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG6
75 | S33 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG7
75 | S34 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG8
75 | S35 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
75 | S36 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
75 | S37 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
75 | S38 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
75 | S39 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
75 | S40 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
75 | S41 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
75 | S42 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
75 | S43 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
75 | S44 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
75 | S45 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
75 | S46 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
75 | S47 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
75 | S48 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
75 | S49 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
75 | S50 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
75 | S51 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
75 | S52 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
75 | S53 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
75 | S54 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
75 | S55 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
75 | S56 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
75 | S57 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
75 | S58 | DOC1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
75 | O1 | DOC1 | Idir> START | SIGNAL_OUT | RW | 0...4294967295
75 | O2 | DOC1 | Idir> TRIP | SIGNAL_OUT | RW | 0...4294967295
75 | O3 | DOC1 | Idir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
75 | S59 | DOC1 | Clear registers | UINT32 | W | 0=-;1=Clear
75 | I6 | DOC1 | Newest register | UINT32 | R | 0...12
75 | I7 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I8 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I9 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I10 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I11 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I12 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I13 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I14 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I15 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I16 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I17 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I18 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I19 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I20 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I21 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I22 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I23 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I24 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I25 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I26 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I27 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I28 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I29 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I30 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I31 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I32 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I33 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I34 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I35 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I36 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I37 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I38 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I39 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I40 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I41 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I42 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I43 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I44 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I45 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I46 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I47 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I48 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I49 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I50 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I51 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I52 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I53 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | I54 | DOC1 | Operating angle | FLOAT | R | 0...250
75 | S60 | DOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S61 | DOC1 | EventMaskHi | UINT32 | RW | 0...4294967295
76 | S1 | DOC2 | Idir>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
76 | V1 | DOC2 | Idir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
76 | I1 | DOC2 | Operating angle now | FLOAT | R | -360...360
76 | I2 | DOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
76 | I3 | DOC2 | Idir>> starts | UINT32 | R | 0...4294967295
76 | I4 | DOC2 | Idir>> trips | UINT32 | R | 0...4294967295
76 | I5 | DOC2 | Idir>> blocks | UINT32 | R | 0...4294967295
76 | S2 | DOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
76 | S3 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG1
76 | S4 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG2
76 | S5 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG3
76 | S6 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG4
76 | S7 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG5
76 | S8 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG6
76 | S9 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG7
76 | S10 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG8
76 | S11 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG1
76 | S12 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG2
76 | S13 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG3
76 | S14 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG4
76 | S15 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG5
76 | S16 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG6
76 | S17 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG7
76 | S18 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG8
76 | S19 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG1
76 | S20 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG2
76 | S21 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG3
76 | S22 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG4
76 | S23 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG5
76 | S24 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG6
76 | S25 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG7
76 | S26 | DOC2 | Operating sector center | FLOAT | RW | -180...180 | SG8
76 | S27 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG1
76 | S28 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG2
76 | S29 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG3
76 | S30 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG4
76 | S31 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG5
76 | S32 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG6
76 | S33 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG7
76 | S34 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG8
76 | S35 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
76 | S36 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
76 | S37 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
76 | S38 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
76 | S39 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
76 | S40 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
76 | S41 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
76 | S42 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
76 | S43 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
76 | S44 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
76 | S45 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
76 | S46 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
76 | S47 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
76 | S48 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
76 | S49 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
76 | S50 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
76 | S51 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
76 | S52 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
76 | S53 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
76 | S54 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
76 | S55 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
76 | S56 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
76 | S57 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
76 | S58 | DOC2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
76 | O1 | DOC2 | Idir>> START | SIGNAL_OUT | RW | 0...4294967295
76 | O2 | DOC2 | Idir>> TRIP | SIGNAL_OUT | RW | 0...4294967295
76 | O3 | DOC2 | Idir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
76 | S59 | DOC2 | Clear registers | UINT32 | W | 0=-;1=Clear
76 | I6 | DOC2 | Newest register | UINT32 | R | 0...12
76 | I7 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I8 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I9 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I10 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I11 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I12 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I13 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I14 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I15 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I16 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I17 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I18 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I19 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I20 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I21 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I22 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I23 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I24 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I25 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I26 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I27 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I28 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I29 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I30 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I31 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I32 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I33 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I34 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I35 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I36 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I37 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I38 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I39 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I40 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I41 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I42 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I43 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I44 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I45 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I46 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I47 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I48 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I49 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I50 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I51 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I52 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I53 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | I54 | DOC2 | Operating angle | FLOAT | R | 0...250
76 | S60 | DOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
76 | S61 | DOC2 | EventMaskHi | UINT32 | RW | 0...4294967295
77 | S1 | DOC3 | Idir>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
77 | V1 | DOC3 | Idir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
77 | I1 | DOC3 | Operating angle now | FLOAT | R | -360...360
77 | I2 | DOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
77 | I3 | DOC3 | Idir>>> starts | UINT32 | R | 0...4294967295
77 | I4 | DOC3 | Idir>>> trips | UINT32 | R | 0...4294967295
77 | I5 | DOC3 | Idir>>> blocks | UINT32 | R | 0...4294967295
77 | S2 | DOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
77 | S3 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG1
77 | S4 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG2
77 | S5 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG3
77 | S6 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG4
77 | S7 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG5
77 | S8 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG6
77 | S9 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG7
77 | S10 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG8
77 | S11 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG1
77 | S12 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG2
77 | S13 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG3
77 | S14 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG4
77 | S15 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG5
77 | S16 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG6
77 | S17 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG7
77 | S18 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG8
77 | S19 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG1
77 | S20 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG2
77 | S21 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG3
77 | S22 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG4
77 | S23 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG5
77 | S24 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG6
77 | S25 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG7
77 | S26 | DOC3 | Operating sector center | FLOAT | RW | -180...180 | SG8
77 | S27 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG1
77 | S28 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG2
77 | S29 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG3
77 | S30 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG4
77 | S31 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG5
77 | S32 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG6
77 | S33 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG7
77 | S34 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG8
77 | S35 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
77 | S36 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
77 | S37 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
77 | S38 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
77 | S39 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
77 | S40 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
77 | S41 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
77 | S42 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
77 | S43 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
77 | S44 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
77 | S45 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
77 | S46 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
77 | S47 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
77 | S48 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
77 | S49 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
77 | S50 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
77 | S51 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
77 | S52 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
77 | S53 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
77 | S54 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
77 | S55 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
77 | S56 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
77 | S57 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
77 | S58 | DOC3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
77 | O1 | DOC3 | Idir>>> START | SIGNAL_OUT | RW | 0...4294967295
77 | O2 | DOC3 | Idir>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
77 | O3 | DOC3 | Idir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
77 | S59 | DOC3 | Clear registers | UINT32 | W | 0=-;1=Clear
77 | I6 | DOC3 | Newest register | UINT32 | R | 0...12
77 | I7 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I8 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I9 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I10 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I11 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I12 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I13 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I14 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I15 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I16 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I17 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I18 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I19 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I20 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I21 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I22 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I23 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I24 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I25 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I26 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I27 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I28 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I29 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I30 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I31 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I32 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I33 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I34 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I35 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I36 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I37 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I38 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I39 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I40 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I41 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I42 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I43 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I44 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I45 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I46 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I47 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I48 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I49 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I50 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I51 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I52 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I53 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | I54 | DOC3 | Operating angle | FLOAT | R | 0...250
77 | S60 | DOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
77 | S61 | DOC3 | EventMaskHi | UINT32 | RW | 0...4294967295
78 | S1 | DOC4 | Idir>>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
78 | V1 | DOC4 | Idir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
78 | I1 | DOC4 | Operating angle now | FLOAT | R | -360...360
78 | I2 | DOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
78 | I3 | DOC4 | Idir>>>> starts | UINT32 | R | 0...4294967295
78 | I4 | DOC4 | Idir>>>> trips | UINT32 | R | 0...4294967295
78 | I5 | DOC4 | Idir>>>> blocks | UINT32 | R | 0...4294967295
78 | S2 | DOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
78 | S3 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG1
78 | S4 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG2
78 | S5 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG3
78 | S6 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG4
78 | S7 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG5
78 | S8 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG6
78 | S9 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG7
78 | S10 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir | SG8
78 | S11 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG1
78 | S12 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG2
78 | S13 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG3
78 | S14 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG4
78 | S15 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG5
78 | S16 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG6
78 | S17 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG7
78 | S18 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170 | SG8
78 | S19 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG1
78 | S20 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG2
78 | S21 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG3
78 | S22 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG4
78 | S23 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG5
78 | S24 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG6
78 | S25 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG7
78 | S26 | DOC4 | Operating sector center | FLOAT | RW | -180...180 | SG8
78 | S27 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG1
78 | S28 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG2
78 | S29 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG3
78 | S30 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG4
78 | S31 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG5
78 | S32 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG6
78 | S33 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG7
78 | S34 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG8
78 | S35 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
78 | S36 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
78 | S37 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
78 | S38 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
78 | S39 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
78 | S40 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
78 | S41 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
78 | S42 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
78 | S43 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
78 | S44 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
78 | S45 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
78 | S46 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
78 | S47 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
78 | S48 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
78 | S49 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
78 | S50 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
78 | S51 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
78 | S52 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
78 | S53 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
78 | S54 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
78 | S55 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
78 | S56 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
78 | S57 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
78 | S58 | DOC4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
78 | O1 | DOC4 | Idir>>>> START | SIGNAL_OUT | RW | 0...4294967295
78 | O2 | DOC4 | Idir>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
78 | O3 | DOC4 | Idir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
78 | S59 | DOC4 | Clear registers | UINT32 | W | 0=-;1=Clear
78 | I6 | DOC4 | Newest register | UINT32 | R | 0...12
78 | I7 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I8 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I9 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I10 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I11 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I12 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I13 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I14 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I15 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I16 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I17 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I18 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I19 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I20 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I21 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I22 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I23 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I24 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I25 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I26 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I27 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I28 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I29 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I30 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I31 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I32 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I33 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I34 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I35 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I36 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I37 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I38 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I39 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I40 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I41 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I42 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I43 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I44 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I45 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I46 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I47 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I48 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I49 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I50 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I51 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I52 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I53 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | I54 | DOC4 | Operating angle | FLOAT | R | 0...250
78 | S60 | DOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
78 | S61 | DOC4 | EventMaskHi | UINT32 | RW | 0...4294967295
26 | S1 | NEF1 | I0> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
26 | S2 | NEF1 | I> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
26 | V1 | NEF1 | I0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
26 | I1 | NEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
26 | I2 | NEF1 | I0> starts | UINT32 | R | 0...4294967295
26 | I3 | NEF1 | I0> trips | UINT32 | R | 0...4294967295
26 | I4 | NEF1 | I0> blocks | UINT32 | R | 0...4294967295
26 | S3 | NEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
26 | S4 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG1
26 | S5 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG2
26 | S6 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG3
26 | S7 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG4
26 | S8 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG5
26 | S9 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG6
26 | S10 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG7
26 | S11 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG8
26 | S12 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
26 | S13 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
26 | S14 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
26 | S15 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
26 | S16 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
26 | S17 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
26 | S18 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
26 | S19 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
26 | S20 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
26 | S21 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
26 | S22 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
26 | S23 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
26 | S24 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
26 | S25 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
26 | S26 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
26 | S27 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
26 | S28 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
26 | S29 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
26 | S30 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
26 | S31 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
26 | S32 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
26 | S33 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
26 | S34 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
26 | S35 | NEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
26 | O1 | NEF1 | I0> START | SIGNAL_OUT | RW | 0...4294967295
26 | O2 | NEF1 | I0> TRIP | SIGNAL_OUT | RW | 0...4294967295
26 | O3 | NEF1 | I0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
26 | I5 | NEF1 | Newest register | UINT32 | R | 0...12
26 | I6 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I7 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I8 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I9 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I10 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I11 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I12 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I13 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I14 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I15 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I16 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I17 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | S36 | NEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
27 | S1 | NEF2 | I0>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
27 | S2 | NEF2 | I> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
27 | V1 | NEF2 | I0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
27 | I1 | NEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
27 | I2 | NEF2 | I0>> starts | UINT32 | R | 0...4294967295
27 | I3 | NEF2 | I0>> trips | UINT32 | R | 0...4294967295
27 | I4 | NEF2 | I0>> blocks | UINT32 | R | 0...4294967295
27 | S3 | NEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
27 | S4 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG1
27 | S5 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG2
27 | S6 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG3
27 | S7 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG4
27 | S8 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG5
27 | S9 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG6
27 | S10 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG7
27 | S11 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG8
27 | S12 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
27 | S13 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
27 | S14 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
27 | S15 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
27 | S16 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
27 | S17 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
27 | S18 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
27 | S19 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
27 | S20 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
27 | S21 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
27 | S22 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
27 | S23 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
27 | S24 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
27 | S25 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
27 | S26 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
27 | S27 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
27 | S28 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
27 | S29 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
27 | S30 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
27 | S31 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
27 | S32 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
27 | S33 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
27 | S34 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
27 | S35 | NEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
27 | O1 | NEF2 | I0>> START | SIGNAL_OUT | RW | 0...4294967295
27 | O2 | NEF2 | I0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
27 | O3 | NEF2 | I0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
27 | I5 | NEF2 | Newest register | UINT32 | R | 0...12
27 | I6 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I7 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I8 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I9 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I10 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I11 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I12 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I13 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I14 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I15 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I16 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I17 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | S36 | NEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
28 | S1 | NEF3 | I0>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
28 | S2 | NEF3 | I> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
28 | V1 | NEF3 | I0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
28 | I1 | NEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
28 | I2 | NEF3 | I0>>> starts | UINT32 | R | 0...4294967295
28 | I3 | NEF3 | I0>>> trips | UINT32 | R | 0...4294967295
28 | I4 | NEF3 | I0>>> blocks | UINT32 | R | 0...4294967295
28 | S3 | NEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
28 | S4 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG1
28 | S5 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG2
28 | S6 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG3
28 | S7 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG4
28 | S8 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG5
28 | S9 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG6
28 | S10 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG7
28 | S11 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG8
28 | S12 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
28 | S13 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
28 | S14 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
28 | S15 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
28 | S16 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
28 | S17 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
28 | S18 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
28 | S19 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
28 | S20 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
28 | S21 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
28 | S22 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
28 | S23 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
28 | S24 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
28 | S25 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
28 | S26 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
28 | S27 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
28 | S28 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
28 | S29 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
28 | S30 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
28 | S31 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
28 | S32 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
28 | S33 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
28 | S34 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
28 | S35 | NEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
28 | O1 | NEF3 | I0>>> START | SIGNAL_OUT | RW | 0...4294967295
28 | O2 | NEF3 | I0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
28 | O3 | NEF3 | I0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
28 | I5 | NEF3 | Newest register | UINT32 | R | 0...12
28 | I6 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I7 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I8 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I9 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I10 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I11 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I12 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I13 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I14 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I15 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I16 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I17 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | S36 | NEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
29 | S1 | NEF4 | I0>>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
29 | S2 | NEF4 | I> setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
29 | V1 | NEF4 | I0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
29 | I1 | NEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
29 | I2 | NEF4 | I0>>>> starts | UINT32 | R | 0...4294967295
29 | I3 | NEF4 | I0>>>> trips | UINT32 | R | 0...4294967295
29 | I4 | NEF4 | I0>>>> blocks | UINT32 | R | 0...4294967295
29 | S3 | NEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
29 | S4 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG1
29 | S5 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG2
29 | S6 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG3
29 | S7 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG4
29 | S8 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG5
29 | S9 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG6
29 | S10 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG7
29 | S11 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40 | SG8
29 | S12 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG1
29 | S13 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG2
29 | S14 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG3
29 | S15 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG4
29 | S16 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG5
29 | S17 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG6
29 | S18 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG7
29 | S19 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT | SG8
29 | S20 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
29 | S21 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
29 | S22 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
29 | S23 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
29 | S24 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
29 | S25 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
29 | S26 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
29 | S27 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
29 | S28 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
29 | S29 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
29 | S30 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
29 | S31 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
29 | S32 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
29 | S33 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
29 | S34 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
29 | S35 | NEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
29 | O1 | NEF4 | I0>>>> START | SIGNAL_OUT | RW | 0...4294967295
29 | O2 | NEF4 | I0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
29 | O3 | NEF4 | I0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
29 | I5 | NEF4 | Newest register | UINT32 | R | 0...12
29 | I6 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I7 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I8 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I9 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I10 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I11 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I12 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I13 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I14 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I15 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I16 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I17 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | S36 | NEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
221 | S1 | EFX1 | I0x> [67NX] mode | UINT32 | RW | 0=Disabled;1=Activated
221 | V1 | EFX1 | I0x> condition | UINT32 | R | 0=Normal;1=Start forward;2=Trip forward;3=Blocked;4=Start reverse;5=Trip reverse
221 | I1 | EFX1 | U0 measured | FLOAT | R | 0...500
221 | I2 | EFX1 | 3I0 measured | FLOAT | R | 0...500
221 | I3 | EFX1 | U0 measured 5th harmonic [abs] | FLOAT | R | 0...500
221 | I4 | EFX1 | 3I0 measured 5th harmonic [abs] | FLOAT | R | 0...500
221 | I5 | EFX1 | U0/3I0 5th harmonic angle | FLOAT | R | -360...360
221 | I6 | EFX1 | I0 measured 5th harmonic | FLOAT | R | 0...500
221 | I7 | EFX1 | U0 measured 5th harmonic | FLOAT | R | 0...500
221 | I8 | EFX1 | U0/3I0 5th harmonic angle | FLOAT | R | -360...360
221 | I9 | EFX1 | I0x> starts (forward) | UINT32 | R | 0...4294967295
221 | I10 | EFX1 | I0x> trips (forward) | UINT32 | R | 0...4294967295
221 | I11 | EFX1 | I0x> starts (reverse) | UINT32 | R | 0...4294967295
221 | I12 | EFX1 | I0x> trips (reverse) | UINT32 | R | 0...4294967295
221 | I13 | EFX1 | I0x> blocks | UINT32 | R | 0...4294967295
221 | S2 | EFX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
221 | S3 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG1
221 | S4 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG2
221 | S5 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG3
221 | S6 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG4
221 | S7 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG5
221 | S8 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG6
221 | S9 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG7
221 | S10 | EFX1 | U0 (50Hz) pick-up setting | FLOAT | RW | 1...75 | SG8
221 | S11 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG1
221 | S12 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG2
221 | S13 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG3
221 | S14 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG4
221 | S15 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG5
221 | S16 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG6
221 | S17 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG7
221 | S18 | EFX1 | 3I0 (5th harm.) pick-up setting [abs] | FLOAT | RW | 0.05...1 | SG8
221 | S19 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG1
221 | S20 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG2
221 | S21 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG3
221 | S22 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG4
221 | S23 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG5
221 | S24 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG6
221 | S25 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG7
221 | S26 | EFX1 | 3I0 (5th harm.) angle range +/- setting | FLOAT | RW | 10...45 | SG8
221 | S27 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG1
221 | S28 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG2
221 | S29 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG3
221 | S30 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG4
221 | S31 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG5
221 | S32 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG6
221 | S33 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG7
221 | S34 | EFX1 | 3I0 (5th harm.) angle center setting | FLOAT | RW | -90...90 | SG8
221 | S35 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG1
221 | S36 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG2
221 | S37 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG3
221 | S38 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG4
221 | S39 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG5
221 | S40 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG6
221 | S41 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG7
221 | S42 | EFX1 | Sw (active residual power pickup FWD) | FLOAT | RW | 20...120 | SG8
221 | S43 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG1
221 | S44 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG2
221 | S45 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG3
221 | S46 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG4
221 | S47 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG5
221 | S48 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG6
221 | S49 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG7
221 | S50 | EFX1 | @Sw (active residual power pickup REV) | FLOAT | RW | 20...120 | SG8
221 | S51 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG1
221 | S52 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG2
221 | S53 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG3
221 | S54 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG4
221 | S55 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG5
221 | S56 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG6
221 | S57 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG7
221 | S58 | EFX1 | Sw/@Sw hysteresis | FLOAT | RW | 0.85...0.95 | SG8
221 | S59 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG1
221 | S60 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG2
221 | S61 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG3
221 | S62 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG4
221 | S63 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG5
221 | S64 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG6
221 | S65 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG7
221 | S66 | EFX1 | S/P (angle pickup) | FLOAT | RW | 0...20 | SG8
221 | S67 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG1
221 | S68 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG2
221 | S69 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG3
221 | S70 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG4
221 | S71 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG5
221 | S72 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG6
221 | S73 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG7
221 | S74 | EFX1 | S/P (angle threshold) | FLOAT | RW | 0.85...0.95 | SG8
221 | S75 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG1
221 | S76 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG2
221 | S77 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG3
221 | S78 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG4
221 | S79 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG5
221 | S80 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG6
221 | S81 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG7
221 | S82 | EFX1 | Operating time | FLOAT | RW | 0.02...5 | SG8
221 | S83 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG1
221 | S84 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG2
221 | S85 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG3
221 | S86 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG4
221 | S87 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG5
221 | S88 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG6
221 | S89 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG7
221 | S90 | EFX1 | Release delay | FLOAT | RW | 0...1 | SG8
221 | O1 | EFX1 | I0x> START (forward) | SIGNAL_OUT | RW | 0...4294967295
221 | O2 | EFX1 | I0x> TRIP (forward) | SIGNAL_OUT | RW | 0...4294967295
221 | O3 | EFX1 | I0x> START (reverse) | SIGNAL_OUT | RW | 0...4294967295
221 | O4 | EFX1 | I0x> TRIP (reverse) | SIGNAL_OUT | RW | 0...4294967295
221 | O5 | EFX1 | I0x> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
221 | I14 | EFX1 | Newest register | UINT32 | R | 0...12
221 | I15 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I16 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I17 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I18 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I19 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I20 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I21 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I22 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I23 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I24 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I25 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I26 | EFX1 | I0 before trip (A) | FLOAT | R | 0...250
221 | I27 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I28 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I29 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I30 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I31 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I32 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I33 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I34 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I35 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I36 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I37 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I38 | EFX1 | U0/I0 angle before trip | FLOAT | R | 0...500
221 | I39 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I40 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I41 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I42 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I43 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I44 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I45 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I46 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I47 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I48 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I49 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I50 | EFX1 | U0 trip voltage (%) | FLOAT | R | 0...500
221 | I51 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I52 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I53 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I54 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I55 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I56 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I57 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I58 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I59 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I60 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I61 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I62 | EFX1 | U0 before fault start (%) | FLOAT | R | -360...360
221 | I63 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I64 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I65 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I66 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I67 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I68 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I69 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I70 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I71 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I72 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I73 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I74 | EFX1 | I0 before fault start (A) | FLOAT | R | -360...360
221 | I75 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I76 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I77 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I78 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I79 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I80 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I81 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I82 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I83 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I84 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I85 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I86 | EFX1 | U0/I0 angle before fault start | FLOAT | R | -360...360
221 | I87 | EFX1 | EventMaskLo | UINT32 | RW | 0...4294967295
221 | I88 | EFX1 | EventMaskHi | UINT32 | RW | 0...4294967295
81 | S1 | DEF1 | I0dir> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
81 | V1 | DEF1 | I0dir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
81 | I1 | DEF1 | Detected U0/I0 angle (fi) | FLOAT | R | -360...360
81 | I2 | DEF1 | I0 Magnitude | FLOAT | R | 0...250
81 | I3 | DEF1 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
81 | I4 | DEF1 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
81 | I5 | DEF1 | DEF1 Measured unbalance change | FLOAT | R | 0...250
81 | I6 | DEF1 | DEF1 Measured residual current change | FLOAT | R | 0...250
81 | I7 | DEF1 | DEF1 Measured admittance mag change | FLOAT | R | 0...250
81 | I8 | DEF1 | DEF1 Measured admittance angle change | FLOAT | R | 0...250
81 | I9 | DEF1 | I0 direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
81 | I10 | DEF1 | I0 meas / I0 set now | FLOAT | R | -250...250
81 | I11 | DEF1 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
81 | I12 | DEF1 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
81 | I13 | DEF1 | U0 measurement now | FLOAT | R | 0...500
81 | I14 | DEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
81 | I15 | DEF1 | I0dir> starts | UINT32 | R | 0...4294967295
81 | I16 | DEF1 | I0dir> trips | UINT32 | R | 0...4294967295
81 | I17 | DEF1 | I0dir> blocks | UINT32 | R | 0...4294967295
81 | S2 | DEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
81 | S3 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG1
81 | S4 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG2
81 | S5 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG3
81 | S6 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG4
81 | S7 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG5
81 | S8 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG6
81 | S9 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG7
81 | S10 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG8
81 | S11 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG1
81 | S12 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG2
81 | S13 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG3
81 | S14 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG4
81 | S15 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG5
81 | S16 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG6
81 | S17 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG7
81 | S18 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG8
81 | S19 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG1
81 | S20 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG2
81 | S21 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG3
81 | S22 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG4
81 | S23 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG5
81 | S24 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG6
81 | S25 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG7
81 | S26 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75 | SG8
81 | S27 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG1
81 | S28 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG2
81 | S29 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG3
81 | S30 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG4
81 | S31 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG5
81 | S32 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG6
81 | S33 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG7
81 | S34 | DEF1 | Comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG8
81 | S35 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG1
81 | S36 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG2
81 | S37 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG3
81 | S38 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG4
81 | S39 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG5
81 | S40 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG6
81 | S41 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG7
81 | S42 | DEF1 | Comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG8
81 | S43 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG1
81 | S44 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG2
81 | S45 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG3
81 | S46 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG4
81 | S47 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG5
81 | S48 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG6
81 | S49 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG7
81 | S50 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90 | SG8
81 | S51 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG1
81 | S52 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG2
81 | S53 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG3
81 | S54 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG4
81 | S55 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG5
81 | S56 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG6
81 | S57 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG7
81 | S58 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG8
81 | S59 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG1
81 | S60 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG2
81 | S61 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG3
81 | S62 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG4
81 | S63 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG5
81 | S64 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG6
81 | S65 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG7
81 | S66 | DEF1 | Unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG8
81 | S67 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG1
81 | S68 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG2
81 | S69 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG3
81 | S70 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG4
81 | S71 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG5
81 | S72 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG6
81 | S73 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG7
81 | S74 | DEF1 | Unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG8
81 | S75 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG1
81 | S76 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG2
81 | S77 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG3
81 | S78 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG4
81 | S79 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG5
81 | S80 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG6
81 | S81 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG7
81 | S82 | DEF1 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG8
81 | S83 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG1
81 | S84 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG2
81 | S85 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG3
81 | S86 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG4
81 | S87 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG5
81 | S88 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG6
81 | S89 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG7
81 | S90 | DEF1 | Tripping area center | FLOAT | RW | -360...360 | SG8
81 | S91 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG1
81 | S92 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG2
81 | S93 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG3
81 | S94 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG4
81 | S95 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG5
81 | S96 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG6
81 | S97 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG7
81 | S98 | DEF1 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG8
81 | S99 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG1
81 | S100 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG2
81 | S101 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG3
81 | S102 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG4
81 | S103 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG5
81 | S104 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG6
81 | S105 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG7
81 | S106 | DEF1 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG8
81 | S107 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
81 | S108 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
81 | S109 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
81 | S110 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
81 | S111 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
81 | S112 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
81 | S113 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
81 | S114 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
81 | S115 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
81 | S116 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
81 | S117 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
81 | S118 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
81 | S119 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
81 | S120 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
81 | S121 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
81 | S122 | DEF1 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
81 | O1 | DEF1 | I0dir> START (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O2 | DEF1 | I0dir> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O3 | DEF1 | I0dir> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O4 | DEF1 | I0dir> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O5 | DEF1 | I0dir> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O6 | DEF1 | I0dir> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O7 | DEF1 | I0dir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
81 | I18 | DEF1 | Newest register | UINT32 | R | 0...12
81 | I19 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I20 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I21 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I22 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I23 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I24 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I25 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I26 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I27 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I28 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I29 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I30 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I31 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I32 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I33 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I34 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I35 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I36 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I37 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I38 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I39 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I40 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I41 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I42 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I43 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I44 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I45 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I46 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I47 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I48 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I49 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I50 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I51 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I52 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I53 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I54 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I55 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I56 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I57 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I58 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I59 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I60 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I61 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I62 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I63 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I64 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I65 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I66 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I67 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I68 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I69 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I70 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I71 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I72 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I73 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I74 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I75 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I76 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I77 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I78 | DEF1 | I0(U0) fault angle | FLOAT | R | -360...360
81 | I79 | DEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | I80 | DEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
82 | S1 | DEF2 | I0dir>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
82 | V1 | DEF2 | I0dir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
82 | I1 | DEF2 | Detected U0/I0 angle (fi) | FLOAT | R | -360...360
82 | I2 | DEF2 | I0 Magnitude | FLOAT | R | 0...250
82 | I3 | DEF2 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
82 | I4 | DEF2 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
82 | I5 | DEF2 | DEF2 Measured unbalance change | FLOAT | R | 0...250
82 | I6 | DEF2 | DEF2 Measured residual current change | FLOAT | R | 0...250
82 | I7 | DEF2 | DEF2 Measured admittance mag change | FLOAT | R | 0...250
82 | I8 | DEF2 | DEF2 Measured admittance angle change | FLOAT | R | 0...250
82 | I9 | DEF2 | I0 direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
82 | I10 | DEF2 | I0 meas / I0 set now | FLOAT | R | -250...250
82 | I11 | DEF2 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
82 | I12 | DEF2 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
82 | I13 | DEF2 | U0 measurement now | FLOAT | R | 0...500
82 | I14 | DEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
82 | I15 | DEF2 | I0dir>> starts | UINT32 | R | 0...4294967295
82 | I16 | DEF2 | I0dir>> trips | UINT32 | R | 0...4294967295
82 | I17 | DEF2 | I0dir>> blocks | UINT32 | R | 0...4294967295
82 | S2 | DEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
82 | S3 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG1
82 | S4 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG2
82 | S5 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG3
82 | S6 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG4
82 | S7 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG5
82 | S8 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG6
82 | S9 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG7
82 | S10 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG8
82 | S11 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG1
82 | S12 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG2
82 | S13 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG3
82 | S14 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG4
82 | S15 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG5
82 | S16 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG6
82 | S17 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG7
82 | S18 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40 | SG8
82 | S19 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG1
82 | S20 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG2
82 | S21 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG3
82 | S22 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG4
82 | S23 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG5
82 | S24 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG6
82 | S25 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG7
82 | S26 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75 | SG8
82 | S27 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG1
82 | S28 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG2
82 | S29 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG3
82 | S30 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG4
82 | S31 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG5
82 | S32 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG6
82 | S33 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG7
82 | S34 | DEF2 | Comp. pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40 | SG8
82 | S35 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG1
82 | S36 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG2
82 | S37 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG3
82 | S38 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG4
82 | S39 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG5
82 | S40 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG6
82 | S41 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG7
82 | S42 | DEF2 | Comp. pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75 | SG8
82 | S43 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG1
82 | S44 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG2
82 | S45 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG3
82 | S46 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG4
82 | S47 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG5
82 | S48 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG6
82 | S49 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG7
82 | S50 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG8
82 | S51 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG1
82 | S52 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG2
82 | S53 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG3
82 | S54 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG4
82 | S55 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG5
82 | S56 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG6
82 | S57 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG7
82 | S58 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG8
82 | S59 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG1
82 | S60 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG2
82 | S61 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG3
82 | S62 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG4
82 | S63 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG5
82 | S64 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG6
82 | S65 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG7
82 | S66 | DEF2 | Unearth. pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40 | SG8
82 | S67 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG1
82 | S68 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG2
82 | S69 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG3
82 | S70 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG4
82 | S71 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG5
82 | S72 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG6
82 | S73 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG7
82 | S74 | DEF2 | Unearth. pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75 | SG8
82 | S75 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG1
82 | S76 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG2
82 | S77 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG3
82 | S78 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG4
82 | S79 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG5
82 | S80 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG6
82 | S81 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG7
82 | S82 | DEF2 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG8
82 | S83 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG1
82 | S84 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG2
82 | S85 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG3
82 | S86 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG4
82 | S87 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG5
82 | S88 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG6
82 | S89 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG7
82 | S90 | DEF2 | Tripping area center | FLOAT | RW | -360...360 | SG8
82 | S91 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG1
82 | S92 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG2
82 | S93 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG3
82 | S94 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG4
82 | S95 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG5
82 | S96 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG6
82 | S97 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG7
82 | S98 | DEF2 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG8
82 | S99 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG1
82 | S100 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG2
82 | S101 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG3
82 | S102 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG4
82 | S103 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG5
82 | S104 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG6
82 | S105 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG7
82 | S106 | DEF2 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG8
82 | S107 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
82 | S108 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
82 | S109 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
82 | S110 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
82 | S111 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
82 | S112 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
82 | S113 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
82 | S114 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
82 | S115 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
82 | S116 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
82 | S117 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
82 | S118 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
82 | S119 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
82 | S120 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
82 | S121 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
82 | S122 | DEF2 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
82 | O1 | DEF2 | I0dir>> START (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O2 | DEF2 | I0dir>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O3 | DEF2 | I0dir>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O4 | DEF2 | I0dir>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O5 | DEF2 | I0dir>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O6 | DEF2 | I0dir>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O7 | DEF2 | I0dir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
82 | I18 | DEF2 | Newest register | UINT32 | R | 0...12
82 | I19 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I20 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I21 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I22 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I23 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I24 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I25 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I26 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I27 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I28 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I29 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I30 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I31 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I32 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I33 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I34 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I35 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I36 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I37 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I38 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I39 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I40 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I41 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I42 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I43 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I44 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I45 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I46 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I47 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I48 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I49 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I50 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I51 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I52 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I53 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I54 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I55 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I56 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I57 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I58 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I59 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I60 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I61 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I62 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I63 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I64 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I65 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I66 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I67 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I68 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I69 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I70 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I71 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I72 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I73 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I74 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I75 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I76 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I77 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I78 | DEF2 | I0(U0) fault angle | FLOAT | R | -360...360
82 | I79 | DEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
82 | I80 | DEF2 | EventMaskHi | UINT32 | RW | 0...4294967295
83 | S1 | DEF3 | I0dir>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
83 | V1 | DEF3 | I0dir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
83 | I1 | DEF3 | Detected U0/I0 angle (fi) | FLOAT | R | -360...360
83 | I2 | DEF3 | I0 Magnitude | FLOAT | R | 0...250
83 | I3 | DEF3 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
83 | I4 | DEF3 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
83 | I5 | DEF3 | DEF3 Measured unbalance change | FLOAT | R | 0...250
83 | I6 | DEF3 | DEF3 Measured residual current change | FLOAT | R | 0...250
83 | I7 | DEF3 | DEF3 Measured admittance mag change | FLOAT | R | 0...250
83 | I8 | DEF3 | DEF3 Measured admittance angle change | FLOAT | R | 0...250
83 | I9 | DEF3 | I0 direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
83 | I10 | DEF3 | I0 meas / I0 set now | FLOAT | R | -250...250
83 | I11 | DEF3 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
83 | I12 | DEF3 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
83 | I13 | DEF3 | U0 measurement now | FLOAT | R | 0...500
83 | I14 | DEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
83 | I15 | DEF3 | I0dir>>> starts | UINT32 | R | 0...4294967295
83 | I16 | DEF3 | I0dir>>> trips | UINT32 | R | 0...4294967295
83 | I17 | DEF3 | I0dir>>> blocks | UINT32 | R | 0...4294967295
83 | S2 | DEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
83 | S3 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG1
83 | S4 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG2
83 | S5 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG3
83 | S6 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG4
83 | S7 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG5
83 | S8 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG6
83 | S9 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG7
83 | S10 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG8
83 | S11 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG1
83 | S12 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG2
83 | S13 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG3
83 | S14 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG4
83 | S15 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG5
83 | S16 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG6
83 | S17 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG7
83 | S18 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40 | SG8
83 | S19 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG1
83 | S20 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG2
83 | S21 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG3
83 | S22 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG4
83 | S23 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG5
83 | S24 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG6
83 | S25 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG7
83 | S26 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75 | SG8
83 | S27 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG1
83 | S28 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG2
83 | S29 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG3
83 | S30 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG4
83 | S31 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG5
83 | S32 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG6
83 | S33 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG7
83 | S34 | DEF3 | Comp. pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40 | SG8
83 | S35 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG1
83 | S36 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG2
83 | S37 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG3
83 | S38 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG4
83 | S39 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG5
83 | S40 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG6
83 | S41 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG7
83 | S42 | DEF3 | Comp. pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75 | SG8
83 | S43 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG1
83 | S44 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG2
83 | S45 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG3
83 | S46 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG4
83 | S47 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG5
83 | S48 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG6
83 | S49 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG7
83 | S50 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG8
83 | S51 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG1
83 | S52 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG2
83 | S53 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG3
83 | S54 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG4
83 | S55 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG5
83 | S56 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG6
83 | S57 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG7
83 | S58 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG8
83 | S59 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG1
83 | S60 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG2
83 | S61 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG3
83 | S62 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG4
83 | S63 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG5
83 | S64 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG6
83 | S65 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG7
83 | S66 | DEF3 | Unearth. pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40 | SG8
83 | S67 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG1
83 | S68 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG2
83 | S69 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG3
83 | S70 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG4
83 | S71 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG5
83 | S72 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG6
83 | S73 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG7
83 | S74 | DEF3 | Unearth. pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75 | SG8
83 | S75 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG1
83 | S76 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG2
83 | S77 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG3
83 | S78 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG4
83 | S79 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG5
83 | S80 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG6
83 | S81 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG7
83 | S82 | DEF3 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG8
83 | S83 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG1
83 | S84 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG2
83 | S85 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG3
83 | S86 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG4
83 | S87 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG5
83 | S88 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG6
83 | S89 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG7
83 | S90 | DEF3 | Tripping area center | FLOAT | RW | -360...360 | SG8
83 | S91 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG1
83 | S92 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG2
83 | S93 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG3
83 | S94 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG4
83 | S95 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG5
83 | S96 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG6
83 | S97 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG7
83 | S98 | DEF3 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG8
83 | S99 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG1
83 | S100 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG2
83 | S101 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG3
83 | S102 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG4
83 | S103 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG5
83 | S104 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG6
83 | S105 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG7
83 | S106 | DEF3 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG8
83 | S107 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
83 | S108 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
83 | S109 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
83 | S110 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
83 | S111 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
83 | S112 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
83 | S113 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
83 | S114 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
83 | S115 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
83 | S116 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
83 | S117 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
83 | S118 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
83 | S119 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
83 | S120 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
83 | S121 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
83 | S122 | DEF3 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
83 | O1 | DEF3 | I0dir>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O2 | DEF3 | I0dir>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O3 | DEF3 | I0dir>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O4 | DEF3 | I0dir>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O5 | DEF3 | I0dir>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O6 | DEF3 | I0dir>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O7 | DEF3 | I0dir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
83 | I18 | DEF3 | Newest register | UINT32 | R | 0...12
83 | I19 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I20 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I21 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I22 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I23 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I24 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I25 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I26 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I27 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I28 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I29 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I30 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I31 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I32 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I33 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I34 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I35 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I36 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I37 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I38 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I39 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I40 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I41 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I42 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I43 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I44 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I45 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I46 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I47 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I48 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I49 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I50 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I51 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I52 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I53 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I54 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I55 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I56 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I57 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I58 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I59 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I60 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I61 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I62 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I63 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I64 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I65 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I66 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I67 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I68 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I69 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I70 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I71 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I72 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I73 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I74 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I75 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I76 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I77 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I78 | DEF3 | I0(U0) fault angle | FLOAT | R | -360...360
83 | I79 | DEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
83 | I80 | DEF3 | EventMaskHi | UINT32 | RW | 0...4294967295
84 | S1 | DEF4 | I0dir>>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
84 | V1 | DEF4 | I0dir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
84 | I1 | DEF4 | Detected U0/I0 angle (fi) | FLOAT | R | -360...360
84 | I2 | DEF4 | I0 Magnitude | FLOAT | R | 0...250
84 | I3 | DEF4 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
84 | I4 | DEF4 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
84 | I5 | DEF4 | DEF4 Measured unbalance change | FLOAT | R | 0...250
84 | I6 | DEF4 | DEF4 Measured residual current change | FLOAT | R | 0...250
84 | I7 | DEF4 | DEF4 Measured admittance mag change | FLOAT | R | 0...250
84 | I8 | DEF4 | DEF4 Measured admittance angle change | FLOAT | R | 0...250
84 | I9 | DEF4 | I0 direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
84 | I10 | DEF4 | I0 meas / I0 set now | FLOAT | R | -250...250
84 | I11 | DEF4 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
84 | I12 | DEF4 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
84 | I13 | DEF4 | U0 measurement now | FLOAT | R | 0...500
84 | I14 | DEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
84 | I15 | DEF4 | I0dir>>>> starts | UINT32 | R | 0...4294967295
84 | I16 | DEF4 | I0dir>>>> trips | UINT32 | R | 0...4294967295
84 | I17 | DEF4 | I0dir>>>> blocks | UINT32 | R | 0...4294967295
84 | S2 | DEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
84 | S3 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG1
84 | S4 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG2
84 | S5 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG3
84 | S6 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG4
84 | S7 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG5
84 | S8 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG6
84 | S9 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG7
84 | S10 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt] | SG8
84 | S11 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG1
84 | S12 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG2
84 | S13 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG3
84 | S14 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG4
84 | S15 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG5
84 | S16 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG6
84 | S17 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG7
84 | S18 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40 | SG8
84 | S19 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG1
84 | S20 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG2
84 | S21 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG3
84 | S22 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG4
84 | S23 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG5
84 | S24 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG6
84 | S25 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG7
84 | S26 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75 | SG8
84 | S27 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG1
84 | S28 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG2
84 | S29 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG3
84 | S30 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG4
84 | S31 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG5
84 | S32 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG6
84 | S33 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG7
84 | S34 | DEF4 | Comp. pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40 | SG8
84 | S35 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG1
84 | S36 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG2
84 | S37 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG3
84 | S38 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG4
84 | S39 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG5
84 | S40 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG6
84 | S41 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG7
84 | S42 | DEF4 | Comp. pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75 | SG8
84 | S43 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG1
84 | S44 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG2
84 | S45 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG3
84 | S46 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG4
84 | S47 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG5
84 | S48 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG6
84 | S49 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG7
84 | S50 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90 | SG8
84 | S51 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG1
84 | S52 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG2
84 | S53 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG3
84 | S54 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG4
84 | S55 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG5
84 | S56 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG6
84 | S57 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG7
84 | S58 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG8
84 | S59 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG1
84 | S60 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG2
84 | S61 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG3
84 | S62 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG4
84 | S63 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG5
84 | S64 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG6
84 | S65 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG7
84 | S66 | DEF4 | Unearth. pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40 | SG8
84 | S67 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG1
84 | S68 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG2
84 | S69 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG3
84 | S70 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG4
84 | S71 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG5
84 | S72 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG6
84 | S73 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG7
84 | S74 | DEF4 | Unearth. pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75 | SG8
84 | S75 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG1
84 | S76 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG2
84 | S77 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG3
84 | S78 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG4
84 | S79 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG5
84 | S80 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG6
84 | S81 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG7
84 | S82 | DEF4 | Tripping area size (+/-) | FLOAT | RW | 5...135 | SG8
84 | S83 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG1
84 | S84 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG2
84 | S85 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG3
84 | S86 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG4
84 | S87 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG5
84 | S88 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG6
84 | S89 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG7
84 | S90 | DEF4 | Tripping area center | FLOAT | RW | -360...360 | SG8
84 | S91 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG1
84 | S92 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG2
84 | S93 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG3
84 | S94 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG4
84 | S95 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG5
84 | S96 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG6
84 | S97 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG7
84 | S98 | DEF4 | Definite operating time delay (Compensated) | FLOAT | RW | 0...1800 | SG8
84 | S99 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG1
84 | S100 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG2
84 | S101 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG3
84 | S102 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG4
84 | S103 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG5
84 | S104 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG6
84 | S105 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG7
84 | S106 | DEF4 | Definite operating time delay (Unearthed) | FLOAT | RW | 0...1800 | SG8
84 | S107 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
84 | S108 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
84 | S109 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
84 | S110 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
84 | S111 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
84 | S112 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
84 | S113 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
84 | S114 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
84 | S115 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG1
84 | S116 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG2
84 | S117 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG3
84 | S118 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG4
84 | S119 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG5
84 | S120 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG6
84 | S121 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG7
84 | S122 | DEF4 | 2nd harmonic blocking limit (Iharm / Ifund) | FLOAT | RW | 0.1...50 | SG8
84 | O1 | DEF4 | I0dir>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O2 | DEF4 | I0dir>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O3 | DEF4 | I0dir>>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O4 | DEF4 | I0dir>>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O5 | DEF4 | I0dir>>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O6 | DEF4 | I0dir>>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O7 | DEF4 | I0dir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
84 | I18 | DEF4 | Newest register | UINT32 | R | 0...12
84 | I19 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I20 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I21 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I22 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I23 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I24 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I25 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I26 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I27 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I28 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I29 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I30 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I31 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I32 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I33 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I34 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I35 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I36 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I37 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I38 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I39 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I40 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I41 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I42 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I43 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I44 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I45 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I46 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I47 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I48 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I49 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I50 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I51 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I52 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I53 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I54 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I55 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I56 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I57 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I58 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I59 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I60 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I61 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I62 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I63 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I64 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I65 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I66 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I67 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I68 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I69 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I70 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I71 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I72 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I73 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I74 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I75 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I76 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I77 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I78 | DEF4 | I0(U0) fault angle | FLOAT | R | -360...360
84 | I79 | DEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
84 | I80 | DEF4 | EventMaskHi | UINT32 | RW | 0...4294967295
114 | S1 | IEF1 | I0Int> [67NT] mode | UINT32 | RW | 0=Disabled;1=Activated
114 | V1 | IEF1 | I0Int> condition | UINT32 | R | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
114 | I1 | IEF1 | Spikes remaining to trip > | UINT32 | R | 0...4294967295
114 | I2 | IEF1 | I0Int> starts FWD | UINT32 | R | 0...4294967295
114 | I3 | IEF1 | I0Int> starts REV | UINT32 | R | 0...4294967295
114 | I4 | IEF1 | I0Int> trips | UINT32 | R | 0...4294967295
114 | I5 | IEF1 | I0Int> blocks | UINT32 | R | 0...4294967295
114 | S2 | IEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
114 | S3 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG1
114 | S4 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG2
114 | S5 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG3
114 | S6 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG4
114 | S7 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG5
114 | S8 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG6
114 | S9 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG7
114 | S10 | IEF1 | U0 detect spike > | FLOAT | RW | 1...100 | SG8
114 | S11 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG1
114 | S12 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG2
114 | S13 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG3
114 | S14 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG4
114 | S15 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG5
114 | S16 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG6
114 | S17 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG7
114 | S18 | IEF1 | I0 detect spike > | FLOAT | RW | 0.05...40 | SG8
114 | S19 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG1
114 | S20 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG2
114 | S21 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG3
114 | S22 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG4
114 | S23 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG5
114 | S24 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG6
114 | S25 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG7
114 | S26 | IEF1 | FWD reset time | FLOAT | RW | 0...1800 | SG8
114 | S27 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG1
114 | S28 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG2
114 | S29 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG3
114 | S30 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG4
114 | S31 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG5
114 | S32 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG6
114 | S33 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG7
114 | S34 | IEF1 | REV reset time | FLOAT | RW | 0...1800 | SG8
114 | S35 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
114 | S36 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
114 | S37 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
114 | S38 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
114 | S39 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
114 | S40 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
114 | S41 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
114 | S42 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
114 | S43 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG1
114 | S44 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG2
114 | S45 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG3
114 | S46 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG4
114 | S47 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG5
114 | S48 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG6
114 | S49 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG7
114 | S50 | IEF1 | Spikes to trip > | UINT32 | RW | 2...50 | SG8
114 | O1 | IEF1 | I0Int> IEF DETECTED | SIGNAL_OUT | RW | 0...4294967295
114 | O2 | IEF1 | I0Int> STARTFWD | SIGNAL_OUT | RW | 0...4294967295
114 | O3 | IEF1 | I0Int> STARTREV | SIGNAL_OUT | RW | 0...4294967295
114 | O4 | IEF1 | I0Int> TRIP | SIGNAL_OUT | RW | 0...4294967295
114 | O5 | IEF1 | I0Int> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
114 | I6 | IEF1 | Newest register | UINT32 | R | 0...12
114 | I7 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I8 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I9 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I10 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I11 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I12 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I13 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I14 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I15 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I16 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I17 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I18 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I19 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I20 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I21 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I22 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I23 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I24 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I25 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I26 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I27 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I28 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I29 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I30 | IEF1 | Spikes fwd | UINT32 | R | 0...4294967295
114 | I31 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I32 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I33 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I34 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I35 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I36 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I37 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I38 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I39 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I40 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I41 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I42 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I43 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I44 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I45 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I46 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I47 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I48 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I49 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I50 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I51 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I52 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I53 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I54 | IEF1 | Spikes rev | UINT32 | R | 0...4294967295
114 | I55 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I56 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I57 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I58 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I59 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I60 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I61 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I62 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I63 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I64 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I65 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I66 | IEF1 | Spikes to trip | UINT32 | R | 0...4294967295
114 | I67 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I68 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I69 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I70 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I71 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I72 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I73 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I74 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I75 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I76 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I77 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | I78 | IEF1 | Operating mode | UINT32 | R | 0=Intermittent;1=Transient
114 | S51 | IEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
114 | S52 | IEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
32 | S1 | CUB1 | I2> [46 46R 46L] mode | UINT32 | RW | 0=Disabled;1=Activated
32 | V1 | CUB1 | I2> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
32 | I1 | CUB1 | I2> starts | UINT32 | R | 0...4294967295
32 | I2 | CUB1 | I2> trips | UINT32 | R | 0...4294967295
32 | I3 | CUB1 | I2> blocks | UINT32 | R | 0...4294967295
32 | S2 | CUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
32 | I4 | CUB1 | I2> I2/I1 relation | FLOAT | R | 0...100000
32 | I5 | CUB1 | I2 meas/I2 set | FLOAT | R | 0...100000
32 | S3 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG1
32 | S4 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG2
32 | S5 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG3
32 | S6 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG4
32 | S7 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG5
32 | S8 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG6
32 | S9 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG7
32 | S10 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG8
32 | S11 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG1
32 | S12 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG2
32 | S13 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG3
32 | S14 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG4
32 | S15 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG5
32 | S16 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG6
32 | S17 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG7
32 | S18 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG8
32 | S19 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG1
32 | S20 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG2
32 | S21 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG3
32 | S22 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG4
32 | S23 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG5
32 | S24 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG6
32 | S25 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG7
32 | S26 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2 | SG8
32 | S27 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
32 | S28 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
32 | S29 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
32 | S30 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
32 | S31 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
32 | S32 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
32 | S33 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
32 | S34 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
32 | O1 | CUB1 | I2> START | SIGNAL_OUT | RW | 0...4294967295
32 | O2 | CUB1 | I2> TRIP | SIGNAL_OUT | RW | 0...4294967295
32 | O3 | CUB1 | I2> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
32 | I6 | CUB1 | Newest register | UINT32 | R | 0...12
32 | I7 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I8 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I9 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I10 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I11 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I12 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I13 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I14 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I15 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I16 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I17 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I18 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I19 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I20 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I21 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I22 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I23 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I24 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I25 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I26 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I27 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I28 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I29 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I30 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | S35 | CUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
33 | S1 | CUB2 | I2>> [46 46R 46L] mode | UINT32 | RW | 0=Disabled;1=Activated
33 | V1 | CUB2 | I2>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
33 | I1 | CUB2 | I2>> starts | UINT32 | R | 0...4294967295
33 | I2 | CUB2 | I2>> trips | UINT32 | R | 0...4294967295
33 | I3 | CUB2 | I2>> blocks | UINT32 | R | 0...4294967295
33 | S2 | CUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
33 | I4 | CUB2 | I2>> I2/I1 relation | FLOAT | R | 0...100000
33 | I5 | CUB2 | I2 meas/I2 set | FLOAT | R | 0...100000
33 | S3 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG1
33 | S4 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG2
33 | S5 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG3
33 | S6 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG4
33 | S7 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG5
33 | S8 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG6
33 | S9 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG7
33 | S10 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG8
33 | S11 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG1
33 | S12 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG2
33 | S13 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG3
33 | S14 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG4
33 | S15 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG5
33 | S16 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG6
33 | S17 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG7
33 | S18 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG8
33 | S19 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG1
33 | S20 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG2
33 | S21 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG3
33 | S22 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG4
33 | S23 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG5
33 | S24 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG6
33 | S25 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG7
33 | S26 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2 | SG8
33 | S27 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
33 | S28 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
33 | S29 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
33 | S30 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
33 | S31 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
33 | S32 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
33 | S33 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
33 | S34 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
33 | O1 | CUB2 | I2>> START | SIGNAL_OUT | RW | 0...4294967295
33 | O2 | CUB2 | I2>> TRIP | SIGNAL_OUT | RW | 0...4294967295
33 | O3 | CUB2 | I2>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
33 | I6 | CUB2 | Newest register | UINT32 | R | 0...12
33 | I7 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I8 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I9 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I10 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I11 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I12 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I13 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I14 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I15 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I16 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I17 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I18 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I19 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I20 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I21 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I22 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I23 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I24 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I25 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I26 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I27 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I28 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I29 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I30 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | S35 | CUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
34 | S1 | CUB3 | I2>>> [46 46R 46L] mode | UINT32 | RW | 0=Disabled;1=Activated
34 | V1 | CUB3 | I2>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
34 | I1 | CUB3 | I2>>> starts | UINT32 | R | 0...4294967295
34 | I2 | CUB3 | I2>>> trips | UINT32 | R | 0...4294967295
34 | I3 | CUB3 | I2>>> blocks | UINT32 | R | 0...4294967295
34 | S2 | CUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
34 | I4 | CUB3 | I2>>> I2/I1 relation | FLOAT | R | 0...100000
34 | I5 | CUB3 | I2 meas/I2 set | FLOAT | R | 0...100000
34 | S3 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG1
34 | S4 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG2
34 | S5 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG3
34 | S6 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG4
34 | S7 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG5
34 | S8 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG6
34 | S9 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG7
34 | S10 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG8
34 | S11 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG1
34 | S12 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG2
34 | S13 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG3
34 | S14 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG4
34 | S15 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG5
34 | S16 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG6
34 | S17 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG7
34 | S18 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG8
34 | S19 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG1
34 | S20 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG2
34 | S21 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG3
34 | S22 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG4
34 | S23 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG5
34 | S24 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG6
34 | S25 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG7
34 | S26 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2 | SG8
34 | S27 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
34 | S28 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
34 | S29 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
34 | S30 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
34 | S31 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
34 | S32 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
34 | S33 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
34 | S34 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
34 | O1 | CUB3 | I2>>> START | SIGNAL_OUT | RW | 0...4294967295
34 | O2 | CUB3 | I2>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
34 | O3 | CUB3 | I2>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
34 | I6 | CUB3 | Newest register | UINT32 | R | 0...12
34 | I7 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I8 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I9 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I10 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I11 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I12 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I13 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I14 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I15 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I16 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I17 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I18 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I19 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I20 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I21 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I22 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I23 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I24 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I25 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I26 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I27 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I28 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I29 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I30 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | S35 | CUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
35 | S1 | CUB4 | I2>>>> [46 46R 46L] mode | UINT32 | RW | 0=Disabled;1=Activated
35 | V1 | CUB4 | I2>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
35 | I1 | CUB4 | I2>>>> starts | UINT32 | R | 0...4294967295
35 | I2 | CUB4 | I2>>>> trips | UINT32 | R | 0...4294967295
35 | I3 | CUB4 | I2>>>> blocks | UINT32 | R | 0...4294967295
35 | S2 | CUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
35 | I4 | CUB4 | I2>>>> I2/I1 relation | FLOAT | R | 0...100000
35 | I5 | CUB4 | I2 meas/I2 set | FLOAT | R | 0...100000
35 | S3 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG1
35 | S4 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG2
35 | S5 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG3
35 | S6 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG4
35 | S7 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG5
35 | S8 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG6
35 | S9 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG7
35 | S10 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40 | SG8
35 | S11 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG1
35 | S12 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG2
35 | S13 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG3
35 | S14 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG4
35 | S15 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG5
35 | S16 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG6
35 | S17 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG7
35 | S18 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200 | SG8
35 | S19 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG1
35 | S20 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG2
35 | S21 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG3
35 | S22 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG4
35 | S23 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG5
35 | S24 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG6
35 | S25 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG7
35 | S26 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2 | SG8
35 | S27 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
35 | S28 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
35 | S29 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
35 | S30 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
35 | S31 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
35 | S32 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
35 | S33 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
35 | S34 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
35 | O1 | CUB4 | I2>>>> START | SIGNAL_OUT | RW | 0...4294967295
35 | O2 | CUB4 | I2>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
35 | O3 | CUB4 | I2>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
35 | I6 | CUB4 | Newest register | UINT32 | R | 0...12
35 | I7 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I8 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I9 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I10 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I11 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I12 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I13 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I14 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I15 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I16 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I17 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I18 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I19 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I20 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I21 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I22 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I23 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I24 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I25 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I26 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I27 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I28 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I29 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I30 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | S35 | CUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
37 | S1 | HOC1 | Ih> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
37 | V1 | HOC1 | Ih> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
37 | I1 | HOC1 | Ih> starts | UINT32 | R | 0...4294967295
37 | I2 | HOC1 | Ih> trips | UINT32 | R | 0...4294967295
37 | I3 | HOC1 | Ih> blocks | UINT32 | R | 0...4294967295
37 | S2 | HOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
37 | I4 | HOC1 | Ih meas/ Ih set | FLOAT | R | 0...100000
37 | S3 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG1
37 | S4 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG2
37 | S5 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG3
37 | S6 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG4
37 | S7 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG5
37 | S8 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG6
37 | S9 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG7
37 | S10 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG8
37 | S11 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG1
37 | S12 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG2
37 | S13 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG3
37 | S14 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG4
37 | S15 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG5
37 | S16 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG6
37 | S17 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG7
37 | S18 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG8
37 | S19 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG1
37 | S20 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG2
37 | S21 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG3
37 | S22 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG4
37 | S23 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG5
37 | S24 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG6
37 | S25 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG7
37 | S26 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40 | SG8
37 | S27 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
37 | S28 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
37 | S29 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
37 | S30 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
37 | S31 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
37 | S32 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
37 | S33 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
37 | S34 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
37 | O1 | HOC1 | Ih> START | SIGNAL_OUT | RW | 0...4294967295
37 | O2 | HOC1 | Ih> TRIP | SIGNAL_OUT | RW | 0...4294967295
37 | O3 | HOC1 | Ih> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
37 | I5 | HOC1 | Newest register | UINT32 | R | 0...12
37 | I6 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I7 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I8 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I9 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I10 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I11 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I12 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I13 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I14 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I15 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I16 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I17 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I18 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I19 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I20 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I21 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I22 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I23 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I24 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I25 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I26 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I27 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I28 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I29 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I30 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I31 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I32 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I33 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I34 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I35 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I36 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I37 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I38 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I39 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I40 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I41 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I42 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I43 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I44 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I45 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I46 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I47 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I48 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I49 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I50 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I51 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I52 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I53 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I54 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I55 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I56 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I57 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I58 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I59 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I60 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I61 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I62 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I63 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I64 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I65 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | S35 | HOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
38 | S1 | HOC2 | Ih>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
38 | V1 | HOC2 | Ih>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
38 | I1 | HOC2 | Ih>> starts | UINT32 | R | 0...4294967295
38 | I2 | HOC2 | Ih>> trips | UINT32 | R | 0...4294967295
38 | I3 | HOC2 | Ih>> blocks | UINT32 | R | 0...4294967295
38 | S2 | HOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
38 | I4 | HOC2 | Ih meas/ Ih set | FLOAT | R | 0...100000
38 | S3 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG1
38 | S4 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG2
38 | S5 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG3
38 | S6 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG4
38 | S7 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG5
38 | S8 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG6
38 | S9 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG7
38 | S10 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG8
38 | S11 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG1
38 | S12 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG2
38 | S13 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG3
38 | S14 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG4
38 | S15 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG5
38 | S16 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG6
38 | S17 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG7
38 | S18 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG8
38 | S19 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG1
38 | S20 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG2
38 | S21 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG3
38 | S22 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG4
38 | S23 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG5
38 | S24 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG6
38 | S25 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG7
38 | S26 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40 | SG8
38 | S27 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
38 | S28 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
38 | S29 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
38 | S30 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
38 | S31 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
38 | S32 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
38 | S33 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
38 | S34 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
38 | O1 | HOC2 | Ih>> START | SIGNAL_OUT | RW | 0...4294967295
38 | O2 | HOC2 | Ih>> TRIP | SIGNAL_OUT | RW | 0...4294967295
38 | O3 | HOC2 | Ih>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
38 | I5 | HOC2 | Newest register | UINT32 | R | 0...12
38 | I6 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I7 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I8 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I9 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I10 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I11 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I12 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I13 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I14 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I15 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I16 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I17 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I18 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I19 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I20 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I21 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I22 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I23 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I24 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I25 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I26 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I27 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I28 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I29 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I30 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I31 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I32 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I33 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I34 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I35 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I36 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I37 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I38 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I39 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I40 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I41 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I42 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I43 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I44 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I45 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I46 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I47 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I48 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I49 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I50 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I51 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I52 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I53 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I54 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I55 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I56 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I57 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I58 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I59 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I60 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I61 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I62 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I63 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I64 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I65 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | S35 | HOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
39 | S1 | HOC3 | Ih>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
39 | V1 | HOC3 | Ih>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
39 | I1 | HOC3 | Ih>>> starts | UINT32 | R | 0...4294967295
39 | I2 | HOC3 | Ih>>> trips | UINT32 | R | 0...4294967295
39 | I3 | HOC3 | Ih>>> blocks | UINT32 | R | 0...4294967295
39 | S2 | HOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
39 | I4 | HOC3 | Ih meas/ Ih set | FLOAT | R | 0...100000
39 | S3 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG1
39 | S4 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG2
39 | S5 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG3
39 | S6 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG4
39 | S7 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG5
39 | S8 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG6
39 | S9 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG7
39 | S10 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG8
39 | S11 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG1
39 | S12 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG2
39 | S13 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG3
39 | S14 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG4
39 | S15 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG5
39 | S16 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG6
39 | S17 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG7
39 | S18 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG8
39 | S19 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG1
39 | S20 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG2
39 | S21 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG3
39 | S22 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG4
39 | S23 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG5
39 | S24 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG6
39 | S25 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG7
39 | S26 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40 | SG8
39 | S27 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
39 | S28 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
39 | S29 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
39 | S30 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
39 | S31 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
39 | S32 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
39 | S33 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
39 | S34 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
39 | O1 | HOC3 | Ih>>> START | SIGNAL_OUT | RW | 0...4294967295
39 | O2 | HOC3 | Ih>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
39 | O3 | HOC3 | Ih>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
39 | I5 | HOC3 | Newest register | UINT32 | R | 0...12
39 | I6 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I7 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I8 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I9 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I10 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I11 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I12 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I13 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I14 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I15 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I16 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I17 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I18 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I19 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I20 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I21 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I22 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I23 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I24 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I25 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I26 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I27 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I28 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I29 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I30 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I31 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I32 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I33 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I34 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I35 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I36 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I37 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I38 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I39 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I40 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I41 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I42 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I43 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I44 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I45 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I46 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I47 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I48 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I49 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I50 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I51 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I52 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I53 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I54 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I55 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I56 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I57 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I58 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I59 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I60 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I61 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I62 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I63 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I64 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I65 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | S35 | HOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
40 | S1 | HOC4 | Ih>>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
40 | V1 | HOC4 | Ih>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
40 | I1 | HOC4 | Ih>>>> starts | UINT32 | R | 0...4294967295
40 | I2 | HOC4 | Ih>>>> trips | UINT32 | R | 0...4294967295
40 | I3 | HOC4 | Ih>>>> blocks | UINT32 | R | 0...4294967295
40 | S2 | HOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
40 | I4 | HOC4 | Ih meas/ Ih set | FLOAT | R | 0...100000
40 | S3 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG1
40 | S4 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG2
40 | S5 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG3
40 | S6 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG4
40 | S7 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG5
40 | S8 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG6
40 | S9 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG7
40 | S10 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2 | SG8
40 | S11 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG1
40 | S12 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG2
40 | S13 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG3
40 | S14 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG4
40 | S15 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG5
40 | S16 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG6
40 | S17 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG7
40 | S18 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200 | SG8
40 | S19 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG1
40 | S20 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG2
40 | S21 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG3
40 | S22 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG4
40 | S23 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG5
40 | S24 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG6
40 | S25 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG7
40 | S26 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40 | SG8
40 | S27 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
40 | S28 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
40 | S29 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
40 | S30 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
40 | S31 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
40 | S32 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
40 | S33 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
40 | S34 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
40 | O1 | HOC4 | Ih>>>> START | SIGNAL_OUT | RW | 0...4294967295
40 | O2 | HOC4 | Ih>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
40 | O3 | HOC4 | Ih>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
40 | I5 | HOC4 | Newest register | UINT32 | R | 0...12
40 | I6 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I7 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I8 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I9 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I10 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I11 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I12 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I13 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I14 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I15 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I16 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I17 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I18 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I19 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I20 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I21 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I22 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I23 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I24 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I25 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I26 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I27 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I28 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I29 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I30 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I31 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I32 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I33 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I34 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I35 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I36 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I37 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I38 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I39 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I40 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I41 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I42 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I43 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I44 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I45 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I46 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I47 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I48 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I49 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I50 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I51 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I52 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I53 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I54 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I55 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I56 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I57 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I58 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I59 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I60 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I61 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I62 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I63 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I64 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I65 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | S35 | HOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
42 | S1 | CLP1 | CLP mode | UINT32 | RW | 0=Disabled;1=Activated
42 | V1 | CLP1 | CLP condition | UINT32 | R | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
42 | I1 | CLP1 | CLP starts | UINT32 | R | 0...4294967295
42 | I2 | CLP1 | CLP blocks | UINT32 | R | 0...4294967295
42 | S2 | CLP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
42 | S3 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG1
42 | S4 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG2
42 | S5 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG3
42 | S6 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG4
42 | S7 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG5
42 | S8 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG6
42 | S9 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG7
42 | S10 | CLP1 | I Low | FLOAT | RW | 0.01...40 | SG8
42 | S11 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG1
42 | S12 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG2
42 | S13 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG3
42 | S14 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG4
42 | S15 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG5
42 | S16 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG6
42 | S17 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG7
42 | S18 | CLP1 | I High | FLOAT | RW | 0.01...40 | SG8
42 | S19 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG1
42 | S20 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG2
42 | S21 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG3
42 | S22 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG4
42 | S23 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG5
42 | S24 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG6
42 | S25 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG7
42 | S26 | CLP1 | I Over | FLOAT | RW | 0.01...40 | SG8
42 | S27 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG1
42 | S28 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG2
42 | S29 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG3
42 | S30 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG4
42 | S31 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG5
42 | S32 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG6
42 | S33 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG7
42 | S34 | CLP1 | CLPU tset | FLOAT | RW | 0...1800 | SG8
42 | S35 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG1
42 | S36 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG2
42 | S37 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG3
42 | S38 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG4
42 | S39 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG5
42 | S40 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG6
42 | S41 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG7
42 | S42 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800 | SG8
42 | S43 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG1
42 | S44 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG2
42 | S45 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG3
42 | S46 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG4
42 | S47 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG5
42 | S48 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG6
42 | S49 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG7
42 | S50 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800 | SG8
42 | O1 | CLP1 | CLPU ACT | SIGNAL_OUT | RW | 0...4294967295
42 | O2 | CLP1 | CLPU BLOCKED | SIGNAL_OUT | RW | 0...4294967295
42 | I3 | CLP1 | Newest register | UINT32 | R | 0...12
42 | I4 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I5 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I6 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I7 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I8 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I9 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I10 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I11 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I12 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I13 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I14 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I15 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I16 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I17 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I18 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I19 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I20 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I21 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I22 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I23 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I24 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I25 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I26 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I27 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I28 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I29 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I30 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I31 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I32 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I33 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I34 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I35 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I36 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I37 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I38 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I39 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | S51 | CLP1 | EventMaskLo | UINT32 | RW | 0...4294967295
44 | S1 | CBF1 | CBFP [50BF] mode | UINT32 | RW | 0=Disabled;1=Activated
44 | V1 | CBF1 | CBFP condition | UINT32 | R | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
44 | I1 | CBF1 | Retrips | UINT32 | R | 0...4294967295
44 | I2 | CBF1 | CBFPs | UINT32 | R | 0...4294967295
44 | I3 | CBF1 | CBFP starts | UINT32 | R | 0...4294967295
44 | I4 | CBF1 | CBFP blocks | UINT32 | R | 0...4294967295
44 | S2 | CBF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
44 | S3 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG1
44 | S4 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG2
44 | S5 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG3
44 | S6 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG4
44 | S7 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG5
44 | S8 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG6
44 | S9 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG7
44 | S10 | CBF1 | Operating Mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO | SG8
44 | S11 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG1
44 | S12 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG2
44 | S13 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG3
44 | S14 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG4
44 | S15 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG5
44 | S16 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG6
44 | S17 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG7
44 | S18 | CBF1 | Iset | FLOAT | RW | 0.01...40 | SG8
44 | S19 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG1
44 | S20 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG2
44 | S21 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG3
44 | S22 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG4
44 | S23 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG5
44 | S24 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG6
44 | S25 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG7
44 | S26 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc | SG8
44 | S27 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG1
44 | S28 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG2
44 | S29 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG3
44 | S30 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG4
44 | S31 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG5
44 | S32 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG6
44 | S33 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG7
44 | S34 | CBF1 | I0set | FLOAT | RW | 0.005...40 | SG8
44 | S35 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG1
44 | S36 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG2
44 | S37 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG3
44 | S38 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG4
44 | S39 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG5
44 | S40 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG6
44 | S41 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG7
44 | S42 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=Yes | SG8
44 | S43 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG1
44 | S44 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG2
44 | S45 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG3
44 | S46 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG4
44 | S47 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG5
44 | S48 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG6
44 | S49 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG7
44 | S50 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800 | SG8
44 | S51 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG1
44 | S52 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG2
44 | S53 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG3
44 | S54 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG4
44 | S55 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG5
44 | S56 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG6
44 | S57 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG7
44 | S58 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800 | SG8
44 | O1 | CBF1 | CBFP START | SIGNAL_OUT | RW | 0...4294967295
44 | O2 | CBF1 | CBFP RETRIP | SIGNAL_OUT | RW | 0...4294967295
44 | O3 | CBF1 | CBFP ACT | SIGNAL_OUT | RW | 0...4294967295
44 | O4 | CBF1 | CBFP BLOCKED | SIGNAL_OUT | RW | 0...4294967295
44 | I5 | CBF1 | Newest register | UINT32 | R | 0...12
44 | I6 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I7 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I8 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I9 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I10 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I11 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I12 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I13 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I14 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I15 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I16 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I17 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I18 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I19 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I20 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I21 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I22 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I23 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I24 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I25 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I26 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I27 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I28 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I29 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I30 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I31 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I32 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I33 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I34 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I35 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I36 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I37 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I38 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I39 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I40 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I41 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I42 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I43 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I44 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I45 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I46 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I47 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I48 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I49 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I50 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I51 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I52 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I53 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | S59 | CBF1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S1 | MST1 | MST mode | UINT32 | R | 0=Disabled;1=Activated
62 | V1 | MST1 | Motor is now | UINT32 | R | 0=Stopped;1=Starting;2=Running;3=Stalled
62 | I1 | MST1 | Times motor started | UINT32 | R | 0...4294967295
62 | I2 | MST1 | Times motor starts succeed | UINT32 | R | 0...4294967295
62 | I3 | MST1 | Times motor stopped | UINT32 | R | 0...4294967295
62 | S2 | MST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
62 | I4 | MST1 | Run after last start | UINT32 | R | 0...4294967295
62 | I5 | MST1 | Total motor run time | UINT32 | R | 0...4294967295
62 | I6 | MST1 | Last start duration | UINT32 | R | 0...4294967295
62 | I7 | MST1 | Total starting time | UINT32 | R | 0...4294967295
62 | I8 | MST1 | Last stopped duration | UINT32 | R | 0...4294967295
62 | I9 | MST1 | Total stopped time | UINT32 | R | 0...4294967295
62 | S3 | MST1 | Clear total times | UINT32 | W | 0=-;1=Clear
62 | S4 | MST1 | Per unitize relay currents to Motor In | UINT32 | RW | 0=No, use CT nominal as pu.;1=Yes, scale all to Imot
62 | S5 | MST1 | Motor nominal current | FLOAT | RW | 0.1...10000
62 | S6 | MST1 | Nominal Starting current | FLOAT | RW | 0.1...40
62 | S7 | MST1 | Start detect current | FLOAT | RW | 0.1...40
62 | S8 | MST1 | Min locked rotor current | FLOAT | RW | 0.1...40
62 | S9 | MST1 | Max locked rotor current | FLOAT | RW | 0.1...40
62 | S10 | MST1 | Maximum overload current | FLOAT | RW | 0.1...40
62 | S11 | MST1 | No Load current | FLOAT | RW | 0.1...40
62 | S12 | MST1 | Motor service factor | FLOAT | RW | 0.01...5
62 | S13 | MST1 | Hot condition theta limit | FLOAT | RW | 0...100
62 | S14 | MST1 | Safe stall time cold | FLOAT | RW | 0.1...600
62 | S15 | MST1 | Safe stall time hot | FLOAT | RW | 0.1...600
62 | S16 | MST1 | Allowed Starts when cold | UINT32 | RW | 1...100
62 | S17 | MST1 | Allowed Starts when hot | UINT32 | RW | 1...100
62 | S18 | MST1 | Given Hot/Cold starts in time of: | FLOAT | RW | 0.1...100
62 | S19 | MST1 | Min time betw. starts | FLOAT | RW | 0.1...600
62 | S20 | MST1 | Overall differential protection | UINT32 | RW | 0=Machine diff. (Yy);1=Diff.with trafo(Xx)
62 | O1 | MST1 | Motor stopped | SIGNAL_OUT | RW | 0...4294967295
62 | O2 | MST1 | Motor starting | SIGNAL_OUT | RW | 0...4294967295
62 | O3 | MST1 | Motor running | SIGNAL_OUT | RW | 0...4294967295
62 | O4 | MST1 | Motor stalled | SIGNAL_OUT | RW | 0...4294967295
62 | O5 | MST1 | Missing phase | SIGNAL_OUT | RW | 0...4294967295
62 | O6 | MST1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
62 | O7 | MST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
62 | O8 | MST1 | High overcurrent | SIGNAL_OUT | RW | 0...4294967295
62 | I10 | MST1 | Newest register | UINT32 | R | 0...12
62 | I11 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I12 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I13 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I14 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I15 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I16 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I17 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I18 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I19 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I20 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I21 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I22 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I23 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I24 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I25 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I26 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I27 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I28 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I29 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I30 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I31 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I32 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I33 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I34 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I35 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I36 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I37 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I38 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I39 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I40 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I41 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I42 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I43 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I44 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I45 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I46 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I47 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I48 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I49 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I50 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I51 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I52 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I53 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I54 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I55 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I56 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I57 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I58 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I59 | MST1 | Motor load | FLOAT | R | 0...250
62 | I60 | MST1 | Motor load | FLOAT | R | 0...250
62 | I61 | MST1 | Motor load | FLOAT | R | 0...250
62 | I62 | MST1 | Motor load | FLOAT | R | 0...250
62 | I63 | MST1 | Motor load | FLOAT | R | 0...250
62 | I64 | MST1 | Motor load | FLOAT | R | 0...250
62 | I65 | MST1 | Motor load | FLOAT | R | 0...250
62 | I66 | MST1 | Motor load | FLOAT | R | 0...250
62 | I67 | MST1 | Motor load | FLOAT | R | 0...250
62 | I68 | MST1 | Motor load | FLOAT | R | 0...250
62 | I69 | MST1 | Motor load | FLOAT | R | 0...250
62 | I70 | MST1 | Motor load | FLOAT | R | 0...250
62 | S21 | MST1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S22 | MST1 | EventMaskHi | UINT32 | RW | 0...4294967295
72 | V1 | TRF1 | Transformer is now | UINT32 | R | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
72 | I1 | TRF1 | Times overloaded | UINT32 | R | 0...4294967295
72 | I2 | TRF1 | Times heavily overloaded | UINT32 | R | 0...4294967295
72 | S1 | TRF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
72 | I3 | TRF1 | Normal loading | UINT32 | R | 0...4294967295
72 | I4 | TRF1 | Overloading cumulative | UINT32 | R | 0...4294967295
72 | I5 | TRF1 | Last overload duration | UINT32 | R | 0...4294967295
72 | I6 | TRF1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
72 | I7 | TRF1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
72 | S2 | TRF1 | Clear total times | UINT32 | W | 0=-;1=Clear
72 | S3 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S4 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S5 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S6 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S7 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S8 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S9 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S10 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S11 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S12 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S13 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S14 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S15 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S16 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.001...800
72 | S17 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S18 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S19 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S20 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S21 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S22 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S23 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S24 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...750
72 | S25 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S26 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S27 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S28 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S29 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S30 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S31 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S32 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...750
72 | S33 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S34 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S35 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S36 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S37 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S38 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S39 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S40 | TRF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
72 | S41 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S42 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S43 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S44 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S45 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S46 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S47 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S48 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S49 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S50 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S51 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S52 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S53 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S54 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S55 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | S56 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | V2 | TRF1 | Bias selection | UINT32 | R | 0=Selection Ok;1=Selection different
72 | V3 | TRF1 | Pick-up setting | UINT32 | R | 0=not checked;1=Setting seems ok;2=Sensitive ok;3=Too sensitive;4=False trip likely;5=Coarse ok;6=Insensitive;7=Dangerously high
72 | V4 | TRF1 | Turnpoint 1 setting | UINT32 | R | 0=not checked;1=Ok;2=Seems average;3=Is sensitive;4=Ok;5=Is conservative;6=Is sensitive;7=Ok;8=Is average;9=Is conservative;10=Ok;11=Too conservative;12=Too sensitive
72 | V5 | TRF1 | Slope1 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V6 | TRF1 | Turnpoint2 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V7 | TRF1 | Slope2 setting | UINT32 | R | 0=not checked;1=Ok;2=Wrong;
72 | O1 | TRF1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
72 | O2 | TRF1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O3 | TRF1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O4 | TRF1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
72 | O5 | TRF1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | O6 | TRF1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | I8 | TRF1 | Newest register | UINT32 | R | 0...12
72 | I9 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I10 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I11 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I12 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I13 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I14 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I15 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I16 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I17 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I18 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I19 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I20 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I21 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I22 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I23 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I24 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I25 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I26 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I27 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I28 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I29 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I30 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I31 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I32 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I33 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I34 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I35 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I36 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I37 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I38 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I39 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I40 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I41 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I42 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I43 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I44 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I45 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I46 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I47 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I48 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I49 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I50 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I51 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I52 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I53 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I54 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I55 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I56 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I57 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I58 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I59 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I60 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I61 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I62 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I63 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I64 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I65 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I66 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I67 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I68 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I69 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I70 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I71 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I72 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I73 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I74 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I75 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I76 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I77 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I78 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I79 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I80 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | S57 | TRF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S1 | DIF1 | Idx> [87T/87G/87M/87N] mode | UINT32 | RW | 0=Disabled;1=Activated
71 | V1 | DIF1 | Idx> condition | UINT32 | R | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On
71 | V2 | DIF1 | REFHV> condition | UINT32 | R | 0b=HV REF Blocked;1b=HV REF Trip
71 | V3 | DIF1 | REFLV> condition | UINT32 | R | 0b=LV REF Blocked;1b=LV REF Trip
71 | I1 | DIF1 | Idb> trips | UINT32 | R | 0...4294967295
71 | I2 | DIF1 | Idb> f2h blocks | UINT32 | R | 0...4294967295
71 | I3 | DIF1 | Idb> f5h blocks | UINT32 | R | 0...4294967295
71 | I4 | DIF1 | Idb> Ext blocks | UINT32 | R | 0...4294967295
71 | I5 | DIF1 | Idi> trips | UINT32 | R | 0...4294967295
71 | I6 | DIF1 | Idi> Ext blocks | UINT32 | R | 0...4294967295
71 | I7 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I8 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | I9 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I10 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | S2 | DIF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
71 | I11 | DIF1 | L1 Bias current | FLOAT | R | 0...50
71 | I12 | DIF1 | L1 Differential current | FLOAT | R | 0...4000
71 | I13 | DIF1 | L1 Char (max allowed differential) | FLOAT | R | 0...4000
71 | I14 | DIF1 | L2 Bias current | FLOAT | R | 0...50
71 | I15 | DIF1 | L2 Differential current | FLOAT | R | 0...4000
71 | I16 | DIF1 | L2 Char (max allowed differential) | FLOAT | R | 0...4000
71 | I17 | DIF1 | L3 Bias current | FLOAT | R | 0...50
71 | I18 | DIF1 | L3 Differential current | FLOAT | R | 0...4000
71 | I19 | DIF1 | L3 Char (max allowed differential) | FLOAT | R | 0...4000
71 | I20 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...50
71 | I21 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...4000
71 | I22 | DIF1 | HV I0d> Char (max allowed differential) | FLOAT | R | 0...4000
71 | I23 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...50
71 | I24 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...4000
71 | I25 | DIF1 | LV I0d> Char (max allowed differential) | FLOAT | R | 0...4000
71 | S3 | DIF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
71 | S4 | DIF1 | Transf. Vect. group | UINT32 | R | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
71 | V4 | DIF1 | L1 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V5 | DIF1 | L2 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V6 | DIF1 | L3 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | I26 | DIF1 | L1 Magnitude difference | FLOAT | R | 0...50
71 | I27 | DIF1 | L1 Angle difference | FLOAT | R | -360...360
71 | I28 | DIF1 | L2 Magnitude difference | FLOAT | R | 0...50
71 | I29 | DIF1 | L2 Angle difference | FLOAT | R | -360...360
71 | I30 | DIF1 | L3 Magnitude difference | FLOAT | R | 0...50
71 | I31 | DIF1 | L3 Angle difference | FLOAT | R | -360...360
71 | S5 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S6 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S7 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S8 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S9 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S10 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S11 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S12 | DIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
71 | S13 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S14 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S15 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S16 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S17 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S18 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S19 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S20 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S21 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG1
71 | S22 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG2
71 | S23 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG3
71 | S24 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG4
71 | S25 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG5
71 | S26 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG6
71 | S27 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG7
71 | S28 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG8
71 | S29 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG1
71 | S30 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG2
71 | S31 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG3
71 | S32 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG4
71 | S33 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG5
71 | S34 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG6
71 | S35 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG7
71 | S36 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG8
71 | S37 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG1
71 | S38 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG2
71 | S39 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG3
71 | S40 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG4
71 | S41 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG5
71 | S42 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG6
71 | S43 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG7
71 | S44 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG8
71 | S45 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG1
71 | S46 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG2
71 | S47 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG3
71 | S48 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG4
71 | S49 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG5
71 | S50 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG6
71 | S51 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG7
71 | S52 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG8
71 | S53 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG1
71 | S54 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG2
71 | S55 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG3
71 | S56 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG4
71 | S57 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG5
71 | S58 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG6
71 | S59 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG7
71 | S60 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG8
71 | S61 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S62 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S63 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S64 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S65 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S66 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S67 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S68 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S69 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG1
71 | S70 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG2
71 | S71 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG3
71 | S72 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG4
71 | S73 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG5
71 | S74 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG6
71 | S75 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG7
71 | S76 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG8
71 | S77 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG1
71 | S78 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG2
71 | S79 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG3
71 | S80 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG4
71 | S81 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG5
71 | S82 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG6
71 | S83 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG7
71 | S84 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG8
71 | S85 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG1
71 | S86 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG2
71 | S87 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG3
71 | S88 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG4
71 | S89 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG5
71 | S90 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG6
71 | S91 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG7
71 | S92 | DIF1 | 5th harm maximum uptime | FLOAT | RW | 0...10 | SG8
71 | S93 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S94 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S95 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S96 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S97 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S98 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S99 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S100 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S101 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG1
71 | S102 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG2
71 | S103 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG3
71 | S104 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG4
71 | S105 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG5
71 | S106 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG6
71 | S107 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG7
71 | S108 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG8
71 | S109 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S110 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S111 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S112 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S113 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S114 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S115 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S116 | DIF1 | HV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S117 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S118 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S119 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S120 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S121 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S122 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S123 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S124 | DIF1 | HV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S125 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG1
71 | S126 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG2
71 | S127 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG3
71 | S128 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG4
71 | S129 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG5
71 | S130 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG6
71 | S131 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG7
71 | S132 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100 | SG8
71 | S133 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG1
71 | S134 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG2
71 | S135 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG3
71 | S136 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG4
71 | S137 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG5
71 | S138 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG6
71 | S139 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG7
71 | S140 | DIF1 | HV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG8
71 | S141 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG1
71 | S142 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG2
71 | S143 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG3
71 | S144 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG4
71 | S145 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG5
71 | S146 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG6
71 | S147 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG7
71 | S148 | DIF1 | HV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG8
71 | S149 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG1
71 | S150 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG2
71 | S151 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG3
71 | S152 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG4
71 | S153 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG5
71 | S154 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG6
71 | S155 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG7
71 | S156 | DIF1 | HV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG8
71 | S157 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG1
71 | S158 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG2
71 | S159 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG3
71 | S160 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG4
71 | S161 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG5
71 | S162 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG6
71 | S163 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG7
71 | S164 | DIF1 | HV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG8
71 | S165 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S166 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S167 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S168 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S169 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S170 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S171 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S172 | DIF1 | LV REF diff calculation mode | UINT32 | RW | 0=Add;1=Subtract
71 | S173 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S174 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S175 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S176 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S177 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S178 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S179 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S180 | DIF1 | LV REF bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S181 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG1
71 | S182 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG2
71 | S183 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG3
71 | S184 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG4
71 | S185 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG5
71 | S186 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG6
71 | S187 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG7
71 | S188 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100 | SG8
71 | S189 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG1
71 | S190 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG2
71 | S191 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG3
71 | S192 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG4
71 | S193 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG5
71 | S194 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG6
71 | S195 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG7
71 | S196 | DIF1 | LV I0d> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG8
71 | S197 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG1
71 | S198 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG2
71 | S199 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG3
71 | S200 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG4
71 | S201 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG5
71 | S202 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG6
71 | S203 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG7
71 | S204 | DIF1 | LV I0d> slope 1 | FLOAT | RW | 0.01...250 | SG8
71 | S205 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG1
71 | S206 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG2
71 | S207 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG3
71 | S208 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG4
71 | S209 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG5
71 | S210 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG6
71 | S211 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG7
71 | S212 | DIF1 | LV I0d> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG8
71 | S213 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG1
71 | S214 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG2
71 | S215 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG3
71 | S216 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG4
71 | S217 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG5
71 | S218 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG6
71 | S219 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG7
71 | S220 | DIF1 | LV I0d> slope 2 | FLOAT | RW | 0.01...250 | SG8
71 | O1 | DIF1 | Idb> BIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O2 | DIF1 | Idb> BIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O3 | DIF1 | Idi> NOBIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O4 | DIF1 | Idi> NOBIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O5 | DIF1 | Id> 2nd harmonic block on | SIGNAL_OUT | RW | 0...4294967295
71 | O6 | DIF1 | Id> 5th harmonic block on | SIGNAL_OUT | RW | 0...4294967295
71 | O7 | DIF1 | HV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O8 | DIF1 | HV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O9 | DIF1 | LV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O10 | DIF1 | LV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | I32 | DIF1 | Newest register | UINT32 | R | 0...12
71 | I33 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I34 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I35 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I36 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I37 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I38 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I39 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I40 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I41 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I42 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I43 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I44 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I45 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I46 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I47 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I48 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I49 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I50 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I51 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I52 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I53 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I54 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I55 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I56 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I57 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I58 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I59 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I60 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I61 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I62 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I63 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I64 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I65 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I66 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I67 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I68 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I69 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I70 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I71 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I72 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I73 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I74 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I75 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I76 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I77 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I78 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I79 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I80 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I81 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I82 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I83 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I84 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I85 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I86 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I87 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I88 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I89 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I90 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I91 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I92 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I93 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I94 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I95 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I96 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I97 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I98 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I99 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I100 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I101 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I102 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I103 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I104 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I105 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I106 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I107 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I108 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I109 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I110 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I111 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I112 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I113 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I114 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I115 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I116 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I117 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I118 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I119 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I120 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I121 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I122 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I123 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I124 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I125 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I126 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I127 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I128 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I129 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I130 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I131 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I132 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I133 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I134 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I135 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I136 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I137 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I138 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I139 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I140 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | V7 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V8 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V9 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V10 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V11 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V12 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V13 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V14 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V15 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V16 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V17 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V18 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | I141 | DIF1 | Newest register | UINT32 | R | 0...12
71 | I142 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I143 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I144 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I145 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I146 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I147 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I148 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I149 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I150 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I151 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I152 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I153 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I154 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I155 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I156 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I157 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I158 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I159 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I160 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I161 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I162 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I163 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I164 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I165 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I166 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I167 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I168 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I169 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I170 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I171 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I172 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I173 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I174 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I175 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I176 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I177 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I178 | DIF1 | Newest register | UINT32 | R | 0...12
71 | I179 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I180 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I181 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I182 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I183 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I184 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I185 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I186 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I187 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I188 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I189 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I190 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I191 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I192 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I193 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I194 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I195 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I196 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I197 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I198 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I199 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I200 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I201 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I202 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I203 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I204 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I205 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I206 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I207 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I208 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I209 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I210 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I211 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I212 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I213 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I214 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | S221 | DIF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S222 | DIF1 | EventMaskHi | UINT32 | RW | 0...4294967295
66 | S1 | REF1 | Select | UINT32 | RW | 0=Primary A;1=Secondary A;2=Per Unit
66 | S2 | REF1 | Select | UINT32 | RW | 0=REF Curr
66 | S3 | REF1 | I0d> [87N] mode | UINT32 | RW | 0=Disabled;1=Activated
66 | V1 | REF1 | I0d> condition | UINT32 | R | 0=Normal;1=Trip;2=Blocked
66 | S4 | REF1 | REF or Cable end Diff | UINT32 | RW | 0=REF;1=CED
66 | I1 | REF1 | I0d> Bias current | FLOAT | R | 0...50
66 | I2 | REF1 | I0d> Diff current | FLOAT | R | 0...50
66 | I3 | REF1 | I0d> Char current | FLOAT | R | 0...50
66 | S5 | REF1 | Compensate natural unbalance | UINT32 | RW | 0=-;1=Comp
66 | I4 | REF1 | Natural measured diff R | FLOAT | R | 0...50
66 | I5 | REF1 | Natural measured diff I | FLOAT | R | 0...50
66 | I6 | REF1 | Compensated natural unbalance 3I0 | FLOAT | R | 0...50
66 | I7 | REF1 | Compensated natural unbalance angle 3I0 | FLOAT | R | -360...360
66 | I8 | REF1 | Calculated residual current 3I0 | FLOAT | R | 0...50
66 | I9 | REF1 | Calculated residual current 3I0 angle | FLOAT | R | -360...360
66 | I10 | REF1 | Measured neutral current I0 input | FLOAT | R | 0...50
66 | I11 | REF1 | Measured neutral current I0 angle | FLOAT | R | -360...360
66 | I12 | REF1 | Cable end differential current | FLOAT | R | 0...50
66 | I13 | REF1 | Cable end differential current angle | FLOAT | R | -360...360
66 | S6 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG1
66 | S7 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG2
66 | S8 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG3
66 | S9 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG4
66 | S10 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG5
66 | S11 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG6
66 | S12 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG7
66 | S13 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02 | SG8
66 | S14 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG1
66 | S15 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG2
66 | S16 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG3
66 | S17 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG4
66 | S18 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG5
66 | S19 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG6
66 | S20 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG7
66 | S21 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=Subtract | SG8
66 | S22 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG1
66 | S23 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG2
66 | S24 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG3
66 | S25 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG4
66 | S26 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG5
66 | S27 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG6
66 | S28 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG7
66 | S29 | REF1 | Bias current calculation | UINT32 | RW | 0=(I0In+I0calc)/2;1=max(I0In,I0calc) | SG8
66 | S30 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG1
66 | S31 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG2
66 | S32 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG3
66 | S33 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG4
66 | S34 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG5
66 | S35 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG6
66 | S36 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG7
66 | S37 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50 | SG8
66 | S38 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG1
66 | S39 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG2
66 | S40 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG3
66 | S41 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG4
66 | S42 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG5
66 | S43 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG6
66 | S44 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG7
66 | S45 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50 | SG8
66 | S46 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG1
66 | S47 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG2
66 | S48 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG3
66 | S49 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG4
66 | S50 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG5
66 | S51 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG6
66 | S52 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG7
66 | S53 | REF1 | Slope 1 | FLOAT | RW | 0.01...150 | SG8
66 | S54 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG1
66 | S55 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG2
66 | S56 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG3
66 | S57 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG4
66 | S58 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG5
66 | S59 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG6
66 | S60 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG7
66 | S61 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50 | SG8
66 | S62 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG1
66 | S63 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG2
66 | S64 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG3
66 | S65 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG4
66 | S66 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG5
66 | S67 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG6
66 | S68 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG7
66 | S69 | REF1 | Slope 2 | FLOAT | RW | 0.01...250 | SG8
66 | S70 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG1
66 | S71 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG2
66 | S72 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG3
66 | S73 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG4
66 | S74 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG5
66 | S75 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG6
66 | S76 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG7
66 | S77 | REF1 | REF Trip delay | FLOAT | RW | 0...3600 | SG8
66 | O1 | REF1 | I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
66 | O2 | REF1 | I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
66 | I14 | REF1 | Newest register | UINT32 | R | 0...12
66 | I15 | REF1 | Bias current | FLOAT | R | 0...250
66 | I16 | REF1 | Bias current | FLOAT | R | 0...250
66 | I17 | REF1 | Bias current | FLOAT | R | 0...250
66 | I18 | REF1 | Bias current | FLOAT | R | 0...250
66 | I19 | REF1 | Bias current | FLOAT | R | 0...250
66 | I20 | REF1 | Bias current | FLOAT | R | 0...250
66 | I21 | REF1 | Bias current | FLOAT | R | 0...250
66 | I22 | REF1 | Bias current | FLOAT | R | 0...250
66 | I23 | REF1 | Bias current | FLOAT | R | 0...250
66 | I24 | REF1 | Bias current | FLOAT | R | 0...250
66 | I25 | REF1 | Bias current | FLOAT | R | 0...250
66 | I26 | REF1 | Bias current | FLOAT | R | 0...250
66 | I27 | REF1 | Differential current | FLOAT | R | 0...250
66 | I28 | REF1 | Differential current | FLOAT | R | 0...250
66 | I29 | REF1 | Differential current | FLOAT | R | 0...250
66 | I30 | REF1 | Differential current | FLOAT | R | 0...250
66 | I31 | REF1 | Differential current | FLOAT | R | 0...250
66 | I32 | REF1 | Differential current | FLOAT | R | 0...250
66 | I33 | REF1 | Differential current | FLOAT | R | 0...250
66 | I34 | REF1 | Differential current | FLOAT | R | 0...250
66 | I35 | REF1 | Differential current | FLOAT | R | 0...250
66 | I36 | REF1 | Differential current | FLOAT | R | 0...250
66 | I37 | REF1 | Differential current | FLOAT | R | 0...250
66 | I38 | REF1 | Differential current | FLOAT | R | 0...250
66 | I39 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I40 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I41 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I42 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I43 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I44 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I45 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I46 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I47 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I48 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I49 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I50 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | S78 | REF1 | EventMaskLo | UINT32 | RW | 0...4294967295
66 | S79 | REF1 | EventMaskHi | UINT32 | RW | 0...4294967295
73 | S1 | TOLT1 | TT> [49T] mode | UINT32 | RW | 0=Disabled;1=Activated
73 | V1 | TOLT1 | TT> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
73 | V2 | TOLT1 | TT> inhibit status | UINT32 | R | 0=Normal;1=Inhibit
73 | V3 | TOLT1 | TT> setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault.Override to1.0
73 | V4 | TOLT1 | TT> setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault.Override to1.0
73 | V5 | TOLT1 | TT> setting alarm | UINT32 | R | 0=Nominalcurrent calc ok;1=Nominalcurrent set fault.Overrideto1.0
73 | V6 | TOLT1 | TT> setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
73 | V7 | TOLT1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
73 | I1 | TOLT1 | IN thermal cap current | FLOAT | RW | 0...40
73 | I2 | TOLT1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
73 | S2 | TOLT1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
73 | S3 | TOLT1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
73 | I3 | TOLT1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
73 | I4 | TOLT1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
73 | S4 | TOLT1 | tau1 (t const heating) | FLOAT | RW | 0...500
73 | S5 | TOLT1 | tau2 (t const cooling) | FLOAT | RW | 0...500
73 | S6 | TOLT1 | kSF (service factor) | FLOAT | RW | 0.01...5
73 | S7 | TOLT1 | Cold Reset default theta | FLOAT | RW | 0...150
73 | V8 | TOLT1 | TT> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
73 | I5 | TOLT1 | TT> Time to 100% Theta | UINT32 | R | 0...4294967295
73 | I6 | TOLT1 | TT> Reference T curr. | FLOAT | R | 0...50
73 | I7 | TOLT1 | TT> Active meas curr. | FLOAT | R | 0...50
73 | I8 | TOLT1 | TT> T est.with act. curr. | FLOAT | R | 0...500
73 | I9 | TOLT1 | TT> T at the moment | FLOAT | R | 0...500
73 | I10 | TOLT1 | TT> Max.Temp.Rise All. | FLOAT | R | 0...250
73 | I11 | TOLT1 | TT> Temp.Rise atm. | FLOAT | R | 0...250
73 | I12 | TOLT1 | TT> Hot Spot estimate | FLOAT | R | 0...250
73 | I13 | TOLT1 | TT> Hot Spot Max. All | FLOAT | R | 0...250
73 | I14 | TOLT1 | TT> Used k for amb. temp | FLOAT | R | 0...3
73 | I15 | TOLT1 | TT> Trip delay remaining | UINT32 | R | 0...4294967295
73 | I16 | TOLT1 | TT> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
73 | I17 | TOLT1 | TT> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
73 | I18 | TOLT1 | TT> Inhibit time to rel. | UINT32 | R | 0...4294967295
73 | I19 | TOLT1 | TT> Trip time to rel. | UINT32 | R | 0...4294967295
73 | I20 | TOLT1 | TT> Thermal cap used | FLOAT | R | 0...500
73 | I21 | TOLT1 | Alarm1 inits | UINT32 | R | 0...4294967295
73 | I22 | TOLT1 | Alarm2 inits | UINT32 | R | 0...4294967295
73 | I23 | TOLT1 | Restart Inhibits | UINT32 | R | 0...4294967295
73 | I24 | TOLT1 | Trips | UINT32 | R | 0...4294967295
73 | I25 | TOLT1 | Trips Blocked | UINT32 | R | 0...4294967295
73 | S8 | TOLT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
73 | S9 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S10 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S11 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S12 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S13 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S14 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S15 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S16 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S17 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG1
73 | S18 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG2
73 | S19 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG3
73 | S20 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG4
73 | S21 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG5
73 | S22 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG6
73 | S23 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG7
73 | S24 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150 | SG8
73 | S25 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S26 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S27 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S28 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S29 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S30 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S31 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S32 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S33 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG1
73 | S34 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG2
73 | S35 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG3
73 | S36 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG4
73 | S37 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG5
73 | S38 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG6
73 | S39 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG7
73 | S40 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150 | SG8
73 | S41 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S42 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S43 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S44 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S45 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S46 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S47 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S48 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S49 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG1
73 | S50 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG2
73 | S51 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG3
73 | S52 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG4
73 | S53 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG5
73 | S54 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG6
73 | S55 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG7
73 | S56 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150 | SG8
73 | S57 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG1
73 | S58 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG2
73 | S59 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG3
73 | S60 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG4
73 | S61 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG5
73 | S62 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG6
73 | S63 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG7
73 | S64 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150 | SG8
73 | S65 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG1
73 | S66 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG2
73 | S67 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG3
73 | S68 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG4
73 | S69 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG5
73 | S70 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG6
73 | S71 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG7
73 | S72 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600 | SG8
73 | O1 | TOLT1 | TT> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
73 | O2 | TOLT1 | TT> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
73 | O3 | TOLT1 | TT> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
73 | O4 | TOLT1 | TT> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
73 | O5 | TOLT1 | TT> Trip | SIGNAL_OUT | RW | 0...4294967295
73 | I26 | TOLT1 | Newest register | UINT32 | R | 0...12
73 | I27 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I28 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I29 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I30 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I31 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I32 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I33 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I34 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I35 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I36 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I37 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I38 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I39 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I40 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I41 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I42 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I43 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I44 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I45 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I46 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I47 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I48 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I49 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I50 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I51 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I52 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I53 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I54 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I55 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I56 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I57 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I58 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I59 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I60 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I61 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I62 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | S73 | TOLT1 | EventMaskLo | UINT32 | RW | 0...4294967295
73 | S74 | TOLT1 | EventMaskHi | UINT32 | RW | 0...4294967295
67 | S1 | TOLF1 | TF> [49F] mode | UINT32 | RW | 0=Disabled;1=Activated
67 | V1 | TOLF1 | TF> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
67 | V2 | TOLF1 | TF> inhibit status | UINT32 | R | 0=Normal;1=Inhibit
67 | V3 | TOLF1 | TF> setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault.Override to1.0
67 | V4 | TOLF1 | TF> setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault.Override to1.0
67 | V5 | TOLF1 | TF> setting alarm | UINT32 | R | 0=Nominalcurrent calc ok;1=Nominalcurrent set fault.Overrideto1.0
67 | V6 | TOLF1 | TF> setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
67 | V7 | TOLF1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
67 | I1 | TOLF1 | IN thermal cap current | FLOAT | RW | 0...40
67 | I2 | TOLF1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
67 | I3 | TOLF1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
67 | I4 | TOLF1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
67 | I5 | TOLF1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
67 | I6 | TOLF1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
67 | S2 | TOLF1 | tau (t const) | FLOAT | RW | 0...500
67 | S3 | TOLF1 | Nominal current | FLOAT | RW | 1...9999999
67 | S4 | TOLF1 | kSF (service factor) | FLOAT | RW | 0.01...5
67 | I7 | TOLF1 | TF> Time to 100% Theta | UINT32 | R | 0...4294967295
67 | I8 | TOLF1 | TF> Reference T curr. | FLOAT | R | 0...50
67 | I9 | TOLF1 | TF> Active meas curr. | FLOAT | R | 0...50
67 | I10 | TOLF1 | TF> T est.with act. curr. | FLOAT | R | 0...500
67 | I11 | TOLF1 | TF> T at the moment | FLOAT | R | 0...500
67 | I12 | TOLF1 | TF> Max.Temp.Rise All. | FLOAT | R | 0...250
67 | I13 | TOLF1 | TF> Temp.Rise atm. | FLOAT | R | 0...250
67 | I14 | TOLF1 | TF> Hot Spot estimate | FLOAT | R | 0...250
67 | I15 | TOLF1 | TF> Hot Spot Max. All | FLOAT | R | 0...250
67 | I16 | TOLF1 | TF> Used k for amb. temp | FLOAT | R | 0...3
67 | I17 | TOLF1 | TF> Trip delay remaining | UINT32 | R | 0...4294967295
67 | I18 | TOLF1 | TF> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
67 | I19 | TOLF1 | TF> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
67 | I20 | TOLF1 | TF> Inhibit time to rel. | UINT32 | R | 0...4294967295
67 | I21 | TOLF1 | TF> Trip time to rel. | UINT32 | R | 0...4294967295
67 | I22 | TOLF1 | TF> Thermal cap used | FLOAT | R | 0...500
67 | I23 | TOLF1 | Alarm1 inits | UINT32 | R | 0...4294967295
67 | I24 | TOLF1 | Alarm2 inits | UINT32 | R | 0...4294967295
67 | I25 | TOLF1 | Restart Inhibits | UINT32 | R | 0...4294967295
67 | I26 | TOLF1 | Trips | UINT32 | R | 0...4294967295
67 | I27 | TOLF1 | Trips Blocked | UINT32 | R | 0...4294967295
67 | S5 | TOLF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
67 | S6 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S7 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S8 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S9 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S10 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S11 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S12 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S13 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S14 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG1
67 | S15 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG2
67 | S16 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG3
67 | S17 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG4
67 | S18 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG5
67 | S19 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG6
67 | S20 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG7
67 | S21 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150 | SG8
67 | S22 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S23 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S24 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S25 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S26 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S27 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S28 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S29 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S30 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG1
67 | S31 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG2
67 | S32 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG3
67 | S33 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG4
67 | S34 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG5
67 | S35 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG6
67 | S36 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG7
67 | S37 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150 | SG8
67 | S38 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S39 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S40 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S41 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S42 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S43 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S44 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S45 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S46 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG1
67 | S47 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG2
67 | S48 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG3
67 | S49 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG4
67 | S50 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG5
67 | S51 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG6
67 | S52 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG7
67 | S53 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150 | SG8
67 | S54 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG1
67 | S55 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG2
67 | S56 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG3
67 | S57 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG4
67 | S58 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG5
67 | S59 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG6
67 | S60 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG7
67 | S61 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150 | SG8
67 | S62 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG1
67 | S63 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG2
67 | S64 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG3
67 | S65 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG4
67 | S66 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG5
67 | S67 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG6
67 | S68 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG7
67 | S69 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600 | SG8
67 | O1 | TOLF1 | TF> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
67 | O2 | TOLF1 | TF> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
67 | O3 | TOLF1 | TF> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
67 | O4 | TOLF1 | TF> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
67 | O5 | TOLF1 | TF> Trip | SIGNAL_OUT | RW | 0...4294967295
67 | I28 | TOLF1 | Newest register | UINT32 | R | 0...12
67 | I29 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I30 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I31 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I32 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I33 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I34 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I35 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I36 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I37 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I38 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I39 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I40 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I41 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I42 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I43 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I44 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I45 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I46 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I47 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I48 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I49 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I50 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I51 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I52 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I53 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I54 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I55 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I56 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I57 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I58 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I59 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I60 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I61 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I62 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I63 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I64 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I65 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I66 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I67 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I68 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I69 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I70 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I71 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I72 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I73 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I74 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I75 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I76 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | S70 | TOLF1 | EventMaskLo | UINT32 | RW | 0...4294967295
67 | S71 | TOLF1 | EventMaskHi | UINT32 | RW | 0...4294967295
68 | S1 | TOLM1 | TM> [49M] mode | UINT32 | RW | 0=Disabled;1=Activated
68 | S2 | TOLM1 | TM> Current measurement side | UINT32 | RW | 0=CT1;1=CT2
68 | V1 | TOLM1 | TM> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
68 | V2 | TOLM1 | TM> inhibit status | UINT32 | R | 0=Normal;1=Inhibit
68 | V3 | TOLM1 | TM>Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault.Override to1.0
68 | V4 | TOLM1 | TM>Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault.Override to1.0
68 | V5 | TOLM1 | TM>Setting alarm | UINT32 | R | 0=Nominalcurrent calc ok;1=Nominalcurrent set fault.Overrideto1.0
68 | V6 | TOLM1 | TM>Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
68 | V7 | TOLM1 | Motor status | UINT32 | R | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
68 | S3 | TOLM1 | Pick-up current (x In) | FLOAT | RW | 0...40
68 | S4 | TOLM1 | NPS Biasing in use | UINT32 | RW | 0=No NPS biasing;1=NPS Biasing in use
68 | S5 | TOLM1 | NPS Bias factor | FLOAT | RW | 0.1...10
68 | S6 | TOLM1 | Time constants | UINT32 | RW | 0=Single;1=Multiple
68 | S7 | TOLM1 | Curve AI | UINT32 | RW | 0=Disabled;1=Enabled
68 | S8 | TOLM1 | Long Heat T const (cold) | FLOAT | RW | 0...500
68 | S9 | TOLM1 | Long Heat T const (hot) | FLOAT | RW | 0...500
68 | S10 | TOLM1 | Long Cool T const Run | FLOAT | RW | 0...3000
68 | S11 | TOLM1 | Long Cool T const Stop | FLOAT | RW | 0...3000
68 | S12 | TOLM1 | Short Heat T const (cold) | FLOAT | RW | 0...500
68 | S13 | TOLM1 | Short Heat T const (hot) | FLOAT | RW | 0...500
68 | S14 | TOLM1 | Short Cool T const | FLOAT | RW | 0...3000
68 | S15 | TOLM1 | Wf factor for L/S T const | FLOAT | RW | 0...1
68 | S16 | TOLM1 | T const dyn. balancing | UINT32 | RW | 0=Fixed;1=Dynamic
68 | S17 | TOLM1 | Cold engine time constant | FLOAT | RW | 0...500
68 | S18 | TOLM1 | Hot engine time constant | FLOAT | RW | 0...500
68 | S19 | TOLM1 | Machine low load curve | FLOAT | RW | 1...1000
68 | S20 | TOLM1 | Machine high load curve | FLOAT | RW | 0.1...50
68 | S21 | TOLM1 | Curve weighting factor k | FLOAT | RW | 0.1...30
68 | S22 | TOLM1 | Heating Tau | FLOAT | RW | 0.1...3000
68 | S23 | TOLM1 | Cooling Tau | FLOAT | RW | 0.1...3000
68 | S24 | TOLM1 | Cooling limit | FLOAT | RW | 0.01...1
68 | S25 | TOLM1 | Short Cool T used when stop | FLOAT | RW | 0...3000
68 | S26 | TOLM1 | Cold Reset Theta Default | FLOAT | RW | 0...150
68 | I1 | TOLM1 | Wf in use | FLOAT | R | 0...1
68 | I2 | TOLM1 | Long heat TC in use | FLOAT | R | 0...500
68 | I3 | TOLM1 | Short heat TC in use | FLOAT | R | 0...500
68 | I4 | TOLM1 | Long cool TC in use | FLOAT | R | 0...500
68 | I5 | TOLM1 | Short cool TC in use | FLOAT | R | 0...500
68 | I6 | TOLM1 | Cold stall time | FLOAT | R | 0...500
68 | I7 | TOLM1 | Hot stall time | FLOAT | R | 0...500
68 | S27 | TOLM1 | Dev.Temp (tmax) | UINT32 | RW | 0=A;1=B;2=F;3=H;4=Manual set
68 | S28 | TOLM1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
68 | S29 | TOLM1 | Amb. T Selection | UINT32 | RW | 0=Manual set;1=RTD
68 | S30 | TOLM1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
68 | V8 | TOLM1 | TM> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
68 | I8 | TOLM1 | TM> Time to 100% T | UINT32 | R | 0...4294967295
68 | I9 | TOLM1 | TM> Reference T curr. | FLOAT | R | 0...50
68 | I10 | TOLM1 | TM> Active meas curr. | FLOAT | R | 0...50
68 | I11 | TOLM1 | TM> T est.with act. curr. | FLOAT | R | 0...500
68 | I12 | TOLM1 | TM> T at the moment | FLOAT | R | 0...500
68 | I13 | TOLM1 | TM> Max.Temp.Rise All. | FLOAT | R | 0...250
68 | I14 | TOLM1 | TM> Temp.Rise atm. | FLOAT | R | 0...250
68 | I15 | TOLM1 | TM> Hot Spot estimate | FLOAT | R | 0...250
68 | I16 | TOLM1 | TM> Hot Spot Max. All | FLOAT | R | 0...250
68 | I17 | TOLM1 | TM> Used k for amb. temp | FLOAT | R | 0...5
68 | I18 | TOLM1 | TM> Trip delay remaining | UINT32 | R | 0...4294967295
68 | I19 | TOLM1 | TM> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
68 | I20 | TOLM1 | TM> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
68 | I21 | TOLM1 | TM> Inhibit time to rel. | UINT32 | R | 0...4294967295
68 | I22 | TOLM1 | TM> Trip time to rel. | UINT32 | R | 0...4294967295
68 | I23 | TOLM1 | TM> Thermal cap used | FLOAT | R | 0...500
68 | I24 | TOLM1 | Alarm1 inits | UINT32 | R | 0...4294967295
68 | I25 | TOLM1 | Alarm2 inits | UINT32 | R | 0...4294967295
68 | I26 | TOLM1 | Restart Inhibits | UINT32 | R | 0...4294967295
68 | I27 | TOLM1 | Trips | UINT32 | R | 0...4294967295
68 | I28 | TOLM1 | Trips Blocked | UINT32 | R | 0...4294967295
68 | S31 | TOLM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
68 | S32 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S33 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S34 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S35 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S36 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S37 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S38 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S39 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S40 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG1
68 | S41 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG2
68 | S42 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG3
68 | S43 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG4
68 | S44 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG5
68 | S45 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG6
68 | S46 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG7
68 | S47 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150 | SG8
68 | S48 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S49 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S50 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S51 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S52 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S53 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S54 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S55 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
68 | S56 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG1
68 | S57 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG2
68 | S58 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG3
68 | S59 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG4
68 | S60 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG5
68 | S61 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG6
68 | S62 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG7
68 | S63 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150 | SG8
68 | S64 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S65 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S66 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S67 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S68 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S69 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S70 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S71 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
68 | S72 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG1
68 | S73 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG2
68 | S74 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG3
68 | S75 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG4
68 | S76 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG5
68 | S77 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG6
68 | S78 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG7
68 | S79 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150 | SG8
68 | S80 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG1
68 | S81 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG2
68 | S82 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG3
68 | S83 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG4
68 | S84 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG5
68 | S85 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG6
68 | S86 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG7
68 | S87 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150 | SG8
68 | S88 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG1
68 | S89 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG2
68 | S90 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG3
68 | S91 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG4
68 | S92 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG5
68 | S93 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG6
68 | S94 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG7
68 | S95 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600 | SG8
68 | O1 | TOLM1 | TM> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
68 | O2 | TOLM1 | TM> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
68 | O3 | TOLM1 | TM> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
68 | O4 | TOLM1 | TM> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
68 | O5 | TOLM1 | TM> Trip | SIGNAL_OUT | RW | 0...4294967295
68 | I29 | TOLM1 | Newest register | UINT32 | R | 0...12
68 | I30 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I31 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I32 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I33 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I34 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I35 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I36 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I37 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I38 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I39 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I40 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I41 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I42 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I43 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I44 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I45 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I46 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I47 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I48 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I49 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I50 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I51 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I52 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I53 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I54 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I55 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I56 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I57 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I58 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I59 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I60 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I61 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I62 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I63 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I64 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I65 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I66 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I67 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I68 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I69 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I70 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I71 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I72 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I73 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I74 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I75 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I76 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I77 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I78 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I79 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I80 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I81 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I82 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I83 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I84 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I85 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I86 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I87 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I88 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I89 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I90 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I91 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I92 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I93 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I94 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I95 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I96 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I97 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I98 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I99 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I100 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I101 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I102 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I103 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I104 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I105 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I106 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I107 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I108 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I109 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I110 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I111 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I112 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I113 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I114 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I115 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I116 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I117 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I118 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I119 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I120 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I121 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I122 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I123 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I124 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I125 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I126 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I127 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I128 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I129 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I130 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I131 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I132 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I133 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I134 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I135 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I136 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I137 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | S96 | TOLM1 | EventMaskLo | UINT32 | RW | 0...4294967295
68 | S97 | TOLM1 | EventMaskHi | UINT32 | RW | 0...4294967295
57 | S1 | LCR1 | ISt> [48/14/50LR] mode | UINT32 | RW | 0=Disabled;1=Activated
57 | V1 | LCR1 | ISt> condition | UINT32 | R | 0=Normal;1=Start;2=Set time Trip;3=M cap Trip;4=Blocked
57 | I1 | LCR1 | ISt> starts | UINT32 | R | 0...4294967295
57 | I2 | LCR1 | ISt> set cap used in last start | FLOAT | R | 0...500
57 | I3 | LCR1 | ISt> max cap used in last start | FLOAT | R | 0...500
57 | I4 | LCR1 | ISt> set time trips | UINT32 | R | 0...4294967295
57 | I5 | LCR1 | ISt> max cap trips | UINT32 | R | 0...4294967295
57 | I6 | LCR1 | ISt> blocks | UINT32 | R | 0...4294967295
57 | S2 | LCR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
57 | S3 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG1
57 | S4 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG2
57 | S5 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG3
57 | S6 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG4
57 | S7 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG5
57 | S8 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG6
57 | S9 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG7
57 | S10 | LCR1 | Starting time | FLOAT | RW | 0...1800 | SG8
57 | S11 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG1
57 | S12 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG2
57 | S13 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG3
57 | S14 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG4
57 | S15 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG5
57 | S16 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG6
57 | S17 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG7
57 | S18 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode | SG8
57 | S19 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG1
57 | S20 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG2
57 | S21 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG3
57 | S22 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG4
57 | S23 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG5
57 | S24 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG6
57 | S25 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG7
57 | S26 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes | SG8
57 | S27 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG1
57 | S28 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG2
57 | S29 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG3
57 | S30 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG4
57 | S31 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG5
57 | S32 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG6
57 | S33 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG7
57 | S34 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800 | SG8
57 | S35 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG1
57 | S36 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG2
57 | S37 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG3
57 | S38 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG4
57 | S39 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG5
57 | S40 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG6
57 | S41 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG7
57 | S42 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC | SG8
57 | S43 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG1
57 | S44 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG2
57 | S45 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG3
57 | S46 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG4
57 | S47 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG5
57 | S48 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG6
57 | S49 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG7
57 | S50 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall | SG8
57 | O1 | LCR1 | ISt> START | SIGNAL_OUT | RW | 0...4294967295
57 | O2 | LCR1 | ISt> Set time TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O3 | LCR1 | ISt> Machine cap.TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O4 | LCR1 | ISt> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
57 | I7 | LCR1 | Newest register | UINT32 | R | 0...12
57 | I8 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I9 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I10 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I11 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I12 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I13 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I14 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I15 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I16 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I17 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I18 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I19 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I20 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I21 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I22 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I23 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I24 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I25 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I26 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I27 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I28 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I29 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I30 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I31 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I32 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I33 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I34 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I35 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I36 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I37 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I38 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I39 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I40 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I41 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I42 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I43 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I44 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I45 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I46 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I47 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I48 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I49 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I50 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I51 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I52 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I53 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I54 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I55 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I56 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I57 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I58 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I59 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I60 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I61 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I62 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I63 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I64 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I65 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I66 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I67 | LCR1 | Phase A Current | FLOAT | R | 0...250
57 | I68 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I69 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I70 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I71 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I72 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I73 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I74 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I75 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I76 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I77 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I78 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I79 | LCR1 | Phase B Current | FLOAT | R | 0...250
57 | I80 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I81 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I82 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I83 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I84 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I85 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I86 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I87 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I88 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I89 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I90 | LCR1 | Phase C Current | FLOAT | R | 0...250
57 | I91 | LCR1 | Phase C Current | FLOAT | R | 0...250
56 | S1 | FSP1 | N> [66/86] mode | UINT32 | RW | 0=Disabled;1=Activated
56 | V1 | FSP1 | N> condition | UINT32 | R | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
56 | I1 | FSP1 | N> alarms | UINT32 | R | 0...4294967295
56 | I2 | FSP1 | N> Inhibits | UINT32 | R | 0...4294967295
56 | I3 | FSP1 | N> blocks | UINT32 | R | 0...4294967295
56 | S2 | FSP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
56 | I4 | FSP1 | Start monitoring time left | UINT32 | R | 0...4294967295
56 | I5 | FSP1 | Inhibit time on | UINT32 | R | 0...4294967295
56 | I6 | FSP1 | Alarm time on | UINT32 | R | 0...4294967295
56 | I7 | FSP1 | Time since last start | UINT32 | R | 0...4294967295
56 | I8 | FSP1 | Start count atm. | UINT32 | R | 0...4294967295
56 | I9 | FSP1 | Starts left atm. | UINT32 | R | 0...4294967295
56 | S3 | FSP1 | Give one more start (Warning! Motor may overheat) | UINT32 | W | 0=-;1=One more start
56 | O1 | FSP1 | N> One start remaining (Alarm) | SIGNAL_OUT | RW | 0...4294967295
56 | O2 | FSP1 | N> INHIBIT ON (General) | SIGNAL_OUT | RW | 0...4294967295
56 | O3 | FSP1 | N> INHIBIT ON Mot Running | SIGNAL_OUT | RW | 0...4294967295
56 | O4 | FSP1 | N> INHIBIT ON Mot Stopped | SIGNAL_OUT | RW | 0...4294967295
56 | O5 | FSP1 | N> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
56 | I10 | FSP1 | Newest register | UINT32 | R | 0...12
56 | S4 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S5 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S6 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S7 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S8 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S9 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S10 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S11 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S12 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S13 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S14 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S15 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S16 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S17 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S18 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S19 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S20 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S21 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S22 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S23 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S24 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S25 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S26 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S27 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S28 | FSP1 | Start count | FLOAT | R | 0...250
56 | S29 | FSP1 | Start count | FLOAT | R | 0...250
56 | S30 | FSP1 | Start count | FLOAT | R | 0...250
56 | S31 | FSP1 | Start count | FLOAT | R | 0...250
56 | S32 | FSP1 | Start count | FLOAT | R | 0...250
56 | S33 | FSP1 | Start count | FLOAT | R | 0...250
56 | S34 | FSP1 | Start count | FLOAT | R | 0...250
56 | S35 | FSP1 | Start count | FLOAT | R | 0...250
56 | S36 | FSP1 | Start count | FLOAT | R | 0...250
56 | S37 | FSP1 | Start count | FLOAT | R | 0...250
56 | S38 | FSP1 | Start count | FLOAT | R | 0...250
56 | S39 | FSP1 | Start count | FLOAT | R | 0...250
56 | S40 | FSP1 | EventMaskLo | UINT32 | RW | 0...4294967295
60 | S1 | NUC1 | I< [37] mode | UINT32 | RW | 0=Disabled;1=Activated
60 | V1 | NUC1 | I< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
60 | I1 | NUC1 | I< starts | UINT32 | R | 0...4294967295
60 | I2 | NUC1 | I< trips | UINT32 | R | 0...4294967295
60 | I3 | NUC1 | I< blocks | UINT32 | R | 0...4294967295
60 | S2 | NUC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
60 | S3 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG1
60 | S4 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG2
60 | S5 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG3
60 | S6 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG4
60 | S7 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG5
60 | S8 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG6
60 | S9 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG7
60 | S10 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40 | SG8
60 | S11 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
60 | S12 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
60 | S13 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
60 | S14 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
60 | S15 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
60 | S16 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
60 | S17 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
60 | S18 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
60 | S19 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG1
60 | S20 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG2
60 | S21 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG3
60 | S22 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG4
60 | S23 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG5
60 | S24 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG6
60 | S25 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG7
60 | S26 | NUC1 | Release time delay | FLOAT | RW | 0...150 | SG8
60 | O1 | NUC1 | I< START | SIGNAL_OUT | RW | 0...4294967295
60 | O2 | NUC1 | I< TRIP | SIGNAL_OUT | RW | 0...4294967295
60 | O3 | NUC1 | I< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
60 | I4 | NUC1 | Newest register | UINT32 | R | 0...12
60 | I5 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I6 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I7 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I8 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I9 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I10 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I11 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I12 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I13 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I14 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I15 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I16 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I17 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I18 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I19 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I20 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I21 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I22 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I23 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I24 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I25 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I26 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I27 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I28 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I29 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I30 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I31 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I32 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I33 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I34 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I35 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I36 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I37 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I38 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I39 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I40 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | S27 | NUC1 | EventMaskLo | UINT32 | RW | 0...4294967295
59 | S1 | MJP1 | Im> [50M/51M] mode | UINT32 | RW | 0=Disabled;1=Activated
59 | V1 | MJP1 | Im> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
59 | I1 | MJP1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
59 | I2 | MJP1 | Im> starts | UINT32 | R | 0...4294967295
59 | I3 | MJP1 | Im> trips | UINT32 | R | 0...4294967295
59 | I4 | MJP1 | Im> blocks | UINT32 | R | 0...4294967295
59 | S2 | MJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
59 | S3 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG1
59 | S4 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG2
59 | S5 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG3
59 | S6 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG4
59 | S7 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG5
59 | S8 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG6
59 | S9 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG7
59 | S10 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40 | SG8
59 | S11 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
59 | S12 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
59 | S13 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
59 | S14 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
59 | S15 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
59 | S16 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
59 | S17 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
59 | S18 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
59 | O1 | MJP1 | Im> START | SIGNAL_OUT | RW | 0...4294967295
59 | O2 | MJP1 | Im> TRIP | SIGNAL_OUT | RW | 0...4294967295
59 | O3 | MJP1 | Im> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
59 | I5 | MJP1 | Newest register | UINT32 | R | 0...12
59 | I6 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I7 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I8 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I9 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I10 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I11 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I12 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I13 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I14 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I15 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I16 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I17 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I18 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I19 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I20 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I21 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I22 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I23 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I24 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I25 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I26 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I27 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I28 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I29 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I30 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I31 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I32 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I33 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I34 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I35 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I36 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I37 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I38 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I39 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I40 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I41 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | S19 | MJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
85 | S1 | OV1 | U> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
85 | V1 | OV1 | U> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
85 | I1 | OV1 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
85 | I2 | OV1 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
85 | I3 | OV1 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
85 | I4 | OV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
85 | I5 | OV1 | U> starts | UINT32 | R | 0...4294967295
85 | I6 | OV1 | U> trips | UINT32 | R | 0...4294967295
85 | I7 | OV1 | U> blocks | UINT32 | R | 0...4294967295
85 | S2 | OV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
85 | S3 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
85 | S4 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
85 | S5 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
85 | S6 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
85 | S7 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
85 | S8 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
85 | S9 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
85 | S10 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
85 | S11 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG1
85 | S12 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG2
85 | S13 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG3
85 | S14 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG4
85 | S15 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG5
85 | S16 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG6
85 | S17 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG7
85 | S18 | OV1 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG8
85 | S19 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
85 | S20 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
85 | S21 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
85 | S22 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
85 | S23 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
85 | S24 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
85 | S25 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
85 | S26 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
85 | O1 | OV1 | U> START | SIGNAL_OUT | RW | 0...4294967295
85 | O2 | OV1 | U> TRIP | SIGNAL_OUT | RW | 0...4294967295
85 | O3 | OV1 | U> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
85 | O4 | OV1 | U> START(A) | SIGNAL_OUT | RW | 0...4294967295
85 | O5 | OV1 | U> START(B) | SIGNAL_OUT | RW | 0...4294967295
85 | O6 | OV1 | U> START(C) | SIGNAL_OUT | RW | 0...4294967295
85 | O7 | OV1 | U> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
85 | O8 | OV1 | U> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
85 | O9 | OV1 | U> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
85 | I8 | OV1 | Newest register | UINT32 | R | 0...12
85 | I9 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I10 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I11 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I12 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I13 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I14 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I15 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I16 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I17 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I18 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I19 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I20 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I21 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I22 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I23 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I24 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I25 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I26 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I27 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I28 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I29 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I30 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I31 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I32 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I33 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I34 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I35 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I36 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I37 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I38 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I39 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I40 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I41 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I42 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I43 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I44 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | S27 | OV1 | EventMaskLo | UINT32 | RW | 0...4294967295
86 | S1 | OV2 | U>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
86 | V1 | OV2 | U>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
86 | I1 | OV2 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
86 | I2 | OV2 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
86 | I3 | OV2 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
86 | I4 | OV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
86 | I5 | OV2 | U>> starts | UINT32 | R | 0...4294967295
86 | I6 | OV2 | U>> trips | UINT32 | R | 0...4294967295
86 | I7 | OV2 | U>> blocks | UINT32 | R | 0...4294967295
86 | S2 | OV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
86 | S3 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
86 | S4 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
86 | S5 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
86 | S6 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
86 | S7 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
86 | S8 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
86 | S9 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
86 | S10 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
86 | S11 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG1
86 | S12 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG2
86 | S13 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG3
86 | S14 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG4
86 | S15 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG5
86 | S16 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG6
86 | S17 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG7
86 | S18 | OV2 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG8
86 | S19 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
86 | S20 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
86 | S21 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
86 | S22 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
86 | S23 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
86 | S24 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
86 | S25 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
86 | S26 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
86 | O1 | OV2 | U>> START | SIGNAL_OUT | RW | 0...4294967295
86 | O2 | OV2 | U>> TRIP | SIGNAL_OUT | RW | 0...4294967295
86 | O3 | OV2 | U>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
86 | O4 | OV2 | U>> START(A) | SIGNAL_OUT | RW | 0...4294967295
86 | O5 | OV2 | U>> START(B) | SIGNAL_OUT | RW | 0...4294967295
86 | O6 | OV2 | U>> START(C) | SIGNAL_OUT | RW | 0...4294967295
86 | O7 | OV2 | U>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
86 | O8 | OV2 | U>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
86 | O9 | OV2 | U>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
86 | I8 | OV2 | Newest register | UINT32 | R | 0...12
86 | I9 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I10 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I11 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I12 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I13 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I14 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I15 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I16 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I17 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I18 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I19 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I20 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I21 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I22 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I23 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I24 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I25 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I26 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I27 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I28 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I29 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I30 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I31 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I32 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I33 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I34 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I35 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I36 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I37 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I38 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I39 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I40 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I41 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I42 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I43 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I44 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | S27 | OV2 | EventMaskLo | UINT32 | RW | 0...4294967295
87 | S1 | OV3 | U>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
87 | V1 | OV3 | U>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
87 | I1 | OV3 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
87 | I2 | OV3 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
87 | I3 | OV3 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
87 | I4 | OV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
87 | I5 | OV3 | U>>> starts | UINT32 | R | 0...4294967295
87 | I6 | OV3 | U>>> trips | UINT32 | R | 0...4294967295
87 | I7 | OV3 | U>>> blocks | UINT32 | R | 0...4294967295
87 | S2 | OV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
87 | S3 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
87 | S4 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
87 | S5 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
87 | S6 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
87 | S7 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
87 | S8 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
87 | S9 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
87 | S10 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
87 | S11 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG1
87 | S12 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG2
87 | S13 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG3
87 | S14 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG4
87 | S15 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG5
87 | S16 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG6
87 | S17 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG7
87 | S18 | OV3 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG8
87 | S19 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
87 | S20 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
87 | S21 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
87 | S22 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
87 | S23 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
87 | S24 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
87 | S25 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
87 | S26 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
87 | O1 | OV3 | U>>> START | SIGNAL_OUT | RW | 0...4294967295
87 | O2 | OV3 | U>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
87 | O3 | OV3 | U>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
87 | O4 | OV3 | U>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
87 | O5 | OV3 | U>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
87 | O6 | OV3 | U>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
87 | O7 | OV3 | U>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
87 | O8 | OV3 | U>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
87 | O9 | OV3 | U>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
87 | I8 | OV3 | Newest register | UINT32 | R | 0...12
87 | I9 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I10 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I11 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I12 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I13 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I14 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I15 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I16 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I17 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I18 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I19 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I20 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I21 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I22 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I23 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I24 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I25 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I26 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I27 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I28 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I29 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I30 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I31 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I32 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I33 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I34 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I35 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I36 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I37 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I38 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I39 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I40 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I41 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I42 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I43 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I44 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | S27 | OV3 | EventMaskLo | UINT32 | RW | 0...4294967295
88 | S1 | OV4 | U>>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
88 | V1 | OV4 | U>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
88 | I1 | OV4 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
88 | I2 | OV4 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
88 | I3 | OV4 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
88 | I4 | OV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
88 | I5 | OV4 | U>>>> starts | UINT32 | R | 0...4294967295
88 | I6 | OV4 | U>>>> trips | UINT32 | R | 0...4294967295
88 | I7 | OV4 | U>>>> blocks | UINT32 | R | 0...4294967295
88 | S2 | OV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
88 | S3 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
88 | S4 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
88 | S5 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
88 | S6 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
88 | S7 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
88 | S8 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
88 | S9 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
88 | S10 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
88 | S11 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG1
88 | S12 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG2
88 | S13 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG3
88 | S14 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG4
88 | S15 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG5
88 | S16 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG6
88 | S17 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG7
88 | S18 | OV4 | Pick-up setting Uset | FLOAT | RW | 0.01...250 | SG8
88 | S19 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
88 | S20 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
88 | S21 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
88 | S22 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
88 | S23 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
88 | S24 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
88 | S25 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
88 | S26 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
88 | O1 | OV4 | U>>>> START | SIGNAL_OUT | RW | 0...4294967295
88 | O2 | OV4 | U>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
88 | O3 | OV4 | U>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
88 | O4 | OV4 | U>>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
88 | O5 | OV4 | U>>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
88 | O6 | OV4 | U>>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
88 | O7 | OV4 | U>>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
88 | O8 | OV4 | U>>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
88 | O9 | OV4 | U>>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
88 | I8 | OV4 | Newest register | UINT32 | R | 0...12
88 | I9 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I10 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I11 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I12 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I13 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I14 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I15 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I16 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I17 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I18 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I19 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I20 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I21 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I22 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I23 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I24 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I25 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I26 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I27 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I28 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I29 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I30 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I31 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I32 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I33 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I34 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I35 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I36 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I37 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I38 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I39 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I40 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I41 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I42 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I43 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I44 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | S27 | OV4 | EventMaskLo | UINT32 | RW | 0...4294967295
89 | S1 | UV1 | U< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
89 | V1 | UV1 | U< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
89 | I1 | UV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
89 | I2 | UV1 | U< starts | UINT32 | R | 0...4294967295
89 | I3 | UV1 | U< trips | UINT32 | R | 0...4294967295
89 | I4 | UV1 | U< blocks | UINT32 | R | 0...4294967295
89 | S2 | UV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
89 | S3 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
89 | S4 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
89 | S5 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
89 | S6 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
89 | S7 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
89 | S8 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
89 | S9 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
89 | S10 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
89 | S11 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG1
89 | S12 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG2
89 | S13 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG3
89 | S14 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG4
89 | S15 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG5
89 | S16 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG6
89 | S17 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG7
89 | S18 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120 | SG8
89 | S19 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG1
89 | S20 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG2
89 | S21 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG3
89 | S22 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG4
89 | S23 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG5
89 | S24 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG6
89 | S25 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG7
89 | S26 | UV1 | Block setting Uset< | FLOAT | RW | 0...80 | SG8
89 | S27 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
89 | S28 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
89 | S29 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
89 | S30 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
89 | S31 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
89 | S32 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
89 | S33 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
89 | S34 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
89 | O1 | UV1 | U< START | SIGNAL_OUT | RW | 0...4294967295
89 | O2 | UV1 | U< TRIP | SIGNAL_OUT | RW | 0...4294967295
89 | O3 | UV1 | U< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
89 | O4 | UV1 | U< START(A) | SIGNAL_OUT | RW | 0...4294967295
89 | O5 | UV1 | U< START(B) | SIGNAL_OUT | RW | 0...4294967295
89 | O6 | UV1 | U< START(C) | SIGNAL_OUT | RW | 0...4294967295
89 | O7 | UV1 | U< TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
89 | O8 | UV1 | U< TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
89 | O9 | UV1 | U< TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
89 | I5 | UV1 | Newest register | UINT32 | R | 0...12
89 | I6 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I7 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I8 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I9 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I10 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I11 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I12 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I13 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I14 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I15 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I16 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I17 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I18 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I19 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I20 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I21 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I22 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I23 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I24 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I25 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I26 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I27 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I28 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I29 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I30 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I31 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I32 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I33 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I34 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I35 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I36 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I37 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I38 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I39 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I40 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I41 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | S35 | UV1 | EventMaskLo | UINT32 | RW | 0...4294967295
90 | S1 | UV2 | U<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
90 | V1 | UV2 | U<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
90 | I1 | UV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
90 | I2 | UV2 | U<< starts | UINT32 | R | 0...4294967295
90 | I3 | UV2 | U<< trips | UINT32 | R | 0...4294967295
90 | I4 | UV2 | U<< blocks | UINT32 | R | 0...4294967295
90 | S2 | UV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
90 | S3 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
90 | S4 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
90 | S5 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
90 | S6 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
90 | S7 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
90 | S8 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
90 | S9 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
90 | S10 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
90 | S11 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG1
90 | S12 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG2
90 | S13 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG3
90 | S14 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG4
90 | S15 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG5
90 | S16 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG6
90 | S17 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG7
90 | S18 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120 | SG8
90 | S19 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG1
90 | S20 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG2
90 | S21 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG3
90 | S22 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG4
90 | S23 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG5
90 | S24 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG6
90 | S25 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG7
90 | S26 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80 | SG8
90 | S27 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
90 | S28 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
90 | S29 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
90 | S30 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
90 | S31 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
90 | S32 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
90 | S33 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
90 | S34 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
90 | O1 | UV2 | U<< START | SIGNAL_OUT | RW | 0...4294967295
90 | O2 | UV2 | U<< TRIP | SIGNAL_OUT | RW | 0...4294967295
90 | O3 | UV2 | U<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
90 | O4 | UV2 | U<< START(A) | SIGNAL_OUT | RW | 0...4294967295
90 | O5 | UV2 | U<< START(B) | SIGNAL_OUT | RW | 0...4294967295
90 | O6 | UV2 | U<< START(C) | SIGNAL_OUT | RW | 0...4294967295
90 | O7 | UV2 | U<< TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
90 | O8 | UV2 | U<< TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
90 | O9 | UV2 | U<< TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
90 | I5 | UV2 | Newest register | UINT32 | R | 0...12
90 | I6 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I7 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I8 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I9 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I10 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I11 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I12 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I13 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I14 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I15 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I16 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I17 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I18 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I19 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I20 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I21 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I22 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I23 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I24 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I25 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I26 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I27 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I28 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I29 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I30 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I31 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I32 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I33 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I34 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I35 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I36 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I37 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I38 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I39 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I40 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I41 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | S35 | UV2 | EventMaskLo | UINT32 | RW | 0...4294967295
91 | S1 | UV3 | U<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
91 | V1 | UV3 | U<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
91 | I1 | UV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
91 | I2 | UV3 | U<<< starts | UINT32 | R | 0...4294967295
91 | I3 | UV3 | U<<< trips | UINT32 | R | 0...4294967295
91 | I4 | UV3 | U<<< blocks | UINT32 | R | 0...4294967295
91 | S2 | UV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
91 | S3 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
91 | S4 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
91 | S5 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
91 | S6 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
91 | S7 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
91 | S8 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
91 | S9 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
91 | S10 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
91 | S11 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG1
91 | S12 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG2
91 | S13 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG3
91 | S14 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG4
91 | S15 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG5
91 | S16 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG6
91 | S17 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG7
91 | S18 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120 | SG8
91 | S19 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG1
91 | S20 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG2
91 | S21 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG3
91 | S22 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG4
91 | S23 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG5
91 | S24 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG6
91 | S25 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG7
91 | S26 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80 | SG8
91 | S27 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
91 | S28 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
91 | S29 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
91 | S30 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
91 | S31 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
91 | S32 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
91 | S33 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
91 | S34 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
91 | O1 | UV3 | U<<< START | SIGNAL_OUT | RW | 0...4294967295
91 | O2 | UV3 | U<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
91 | O3 | UV3 | U<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
91 | O4 | UV3 | U<<< START(A) | SIGNAL_OUT | RW | 0...4294967295
91 | O5 | UV3 | U<<< START(B) | SIGNAL_OUT | RW | 0...4294967295
91 | O6 | UV3 | U<<< START(C) | SIGNAL_OUT | RW | 0...4294967295
91 | O7 | UV3 | U<<< TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
91 | O8 | UV3 | U<<< TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
91 | O9 | UV3 | U<<< TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
91 | I5 | UV3 | Newest register | UINT32 | R | 0...12
91 | I6 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I7 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I8 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I9 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I10 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I11 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I12 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I13 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I14 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I15 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I16 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I17 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I18 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I19 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I20 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I21 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I22 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I23 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I24 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I25 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I26 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I27 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I28 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I29 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I30 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I31 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I32 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I33 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I34 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I35 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I36 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I37 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I38 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I39 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I40 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I41 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | S35 | UV3 | EventMaskLo | UINT32 | RW | 0...4294967295
92 | S1 | UV4 | U<<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
92 | V1 | UV4 | U<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
92 | I1 | UV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
92 | I2 | UV4 | U<<<< starts | UINT32 | R | 0...4294967295
92 | I3 | UV4 | U<<<< trips | UINT32 | R | 0...4294967295
92 | I4 | UV4 | U<<<< blocks | UINT32 | R | 0...4294967295
92 | S2 | UV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
92 | S3 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG1
92 | S4 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG2
92 | S5 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG3
92 | S6 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG4
92 | S7 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG5
92 | S8 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG6
92 | S9 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG7
92 | S10 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages | SG8
92 | S11 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG1
92 | S12 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG2
92 | S13 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG3
92 | S14 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG4
92 | S15 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG5
92 | S16 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG6
92 | S17 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG7
92 | S18 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120 | SG8
92 | S19 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG1
92 | S20 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG2
92 | S21 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG3
92 | S22 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG4
92 | S23 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG5
92 | S24 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG6
92 | S25 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG7
92 | S26 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80 | SG8
92 | S27 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
92 | S28 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
92 | S29 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
92 | S30 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
92 | S31 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
92 | S32 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
92 | S33 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
92 | S34 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
92 | O1 | UV4 | U<<<< START | SIGNAL_OUT | RW | 0...4294967295
92 | O2 | UV4 | U<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
92 | O3 | UV4 | U<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
92 | O4 | UV4 | U<<<< START(A) | SIGNAL_OUT | RW | 0...4294967295
92 | O5 | UV4 | U<<<< START(B) | SIGNAL_OUT | RW | 0...4294967295
92 | O6 | UV4 | U<<<< START(C) | SIGNAL_OUT | RW | 0...4294967295
92 | O7 | UV4 | U<<<< TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
92 | O8 | UV4 | U<<<< TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
92 | O9 | UV4 | U<<<< TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
92 | I5 | UV4 | Newest register | UINT32 | R | 0...12
92 | I6 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I7 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I8 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I9 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I10 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I11 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I12 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I13 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I14 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I15 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I16 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I17 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I18 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I19 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I20 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I21 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I22 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I23 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I24 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I25 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I26 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I27 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I28 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I29 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I30 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I31 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I32 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I33 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I34 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I35 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I36 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I37 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I38 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I39 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I40 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I41 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | S35 | UV4 | EventMaskLo | UINT32 | RW | 0...4294967295
238 | S1 | LVRT1 | LVRT [27T] mode | UINT32 | RW | 0=Disabled;1=Activated
238 | V1 | LVRT1 | LVRT condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
238 | I1 | LVRT1 | Measured voltage (U12+U23 avg) | FLOAT | R | 0...1250
238 | I2 | LVRT1 | Umeas/Fault release> | FLOAT | R | 0...1250
238 | I3 | LVRT1 | Umeas/Fault start< | FLOAT | R | 0...1250
238 | I4 | LVRT1 | LVRT starts | UINT32 | R | 0...4294967295
238 | I5 | LVRT1 | LVRT trips | UINT32 | R | 0...4294967295
238 | I6 | LVRT1 | LVRT blocks | UINT32 | R | 0...4294967295
238 | S2 | LVRT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
238 | S3 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG1
238 | S4 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG2
238 | S5 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG3
238 | S6 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG4
238 | S7 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG5
238 | S8 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG6
238 | S9 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG7
238 | S10 | LVRT1 | Fault start< | FLOAT | RW | 50...120 | SG8
238 | S11 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG1
238 | S12 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG2
238 | S13 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG3
238 | S14 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG4
238 | S15 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG5
238 | S16 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG6
238 | S17 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG7
238 | S18 | LVRT1 | Fault release> | FLOAT | RW | 50...120 | SG8
238 | S19 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG1
238 | S20 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG2
238 | S21 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG3
238 | S22 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG4
238 | S23 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG5
238 | S24 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG6
238 | S25 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG7
238 | S26 | LVRT1 | Low voltage block limit | FLOAT | RW | 0...80 | SG8
238 | S27 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG1
238 | S28 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG2
238 | S29 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG3
238 | S30 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG4
238 | S31 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG5
238 | S32 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG6
238 | S33 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG7
238 | S34 | LVRT1 | Amplitude plot[1] | FLOAT | RW | 0...120 | SG8
238 | S35 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG1
238 | S36 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG2
238 | S37 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG3
238 | S38 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG4
238 | S39 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG5
238 | S40 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG6
238 | S41 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG7
238 | S42 | LVRT1 | Time plot[1] | FLOAT | R | 0...1800 | SG8
238 | S43 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG1
238 | S44 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG2
238 | S45 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG3
238 | S46 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG4
238 | S47 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG5
238 | S48 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG6
238 | S49 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG7
238 | S50 | LVRT1 | Amplitude plot[2] | FLOAT | RW | 0...120 | SG8
238 | S51 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG1
238 | S52 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG2
238 | S53 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG3
238 | S54 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG4
238 | S55 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG5
238 | S56 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG6
238 | S57 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG7
238 | S58 | LVRT1 | Time plot[2] | FLOAT | RW | 0.100...1800 | SG8
238 | S59 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG1
238 | S60 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG2
238 | S61 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG3
238 | S62 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG4
238 | S63 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG5
238 | S64 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG6
238 | S65 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG7
238 | S66 | LVRT1 | Amplitude plot[3] | FLOAT | RW | 0...120 | SG8
238 | S67 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG1
238 | S68 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG2
238 | S69 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG3
238 | S70 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG4
238 | S71 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG5
238 | S72 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG6
238 | S73 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG7
238 | S74 | LVRT1 | Time plot[3] | FLOAT | RW | 0.100...1800 | SG8
238 | S75 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG1
238 | S76 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG2
238 | S77 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG3
238 | S78 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG4
238 | S79 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG5
238 | S80 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG6
238 | S81 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG7
238 | S82 | LVRT1 | Amplitude plot[4] | FLOAT | RW | 0...120 | SG8
238 | S83 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG1
238 | S84 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG2
238 | S85 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG3
238 | S86 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG4
238 | S87 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG5
238 | S88 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG6
238 | S89 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG7
238 | S90 | LVRT1 | Time plot[4] | FLOAT | RW | 0.100...1800 | SG8
238 | S91 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG1
238 | S92 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG2
238 | S93 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG3
238 | S94 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG4
238 | S95 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG5
238 | S96 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG6
238 | S97 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG7
238 | S98 | LVRT1 | Amplitude plot[5] | FLOAT | RW | 0...120 | SG8
238 | S99 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG1
238 | S100 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG2
238 | S101 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG3
238 | S102 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG4
238 | S103 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG5
238 | S104 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG6
238 | S105 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG7
238 | S106 | LVRT1 | Time plot[5] | FLOAT | RW | 0.100...1800 | SG8
238 | S107 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG1
238 | S108 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG2
238 | S109 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG3
238 | S110 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG4
238 | S111 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG5
238 | S112 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG6
238 | S113 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG7
238 | S114 | LVRT1 | Amplitude plot[6] | FLOAT | RW | 0...120 | SG8
238 | S115 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG1
238 | S116 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG2
238 | S117 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG3
238 | S118 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG4
238 | S119 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG5
238 | S120 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG6
238 | S121 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG7
238 | S122 | LVRT1 | Time plot[6] | FLOAT | RW | 0.100...1800 | SG8
238 | S123 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG1
238 | S124 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG2
238 | S125 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG3
238 | S126 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG4
238 | S127 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG5
238 | S128 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG6
238 | S129 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG7
238 | S130 | LVRT1 | Amplitude plot[7] | FLOAT | RW | 0...120 | SG8
238 | S131 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG1
238 | S132 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG2
238 | S133 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG3
238 | S134 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG4
238 | S135 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG5
238 | S136 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG6
238 | S137 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG7
238 | S138 | LVRT1 | Time plot[7] | FLOAT | RW | 0.100...1800 | SG8
238 | S139 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG1
238 | S140 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG2
238 | S141 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG3
238 | S142 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG4
238 | S143 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG5
238 | S144 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG6
238 | S145 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG7
238 | S146 | LVRT1 | Amplitude plot[8] | FLOAT | RW | 0...120 | SG8
238 | S147 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG1
238 | S148 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG2
238 | S149 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG3
238 | S150 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG4
238 | S151 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG5
238 | S152 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG6
238 | S153 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG7
238 | S154 | LVRT1 | Time plot[8] | FLOAT | RW | 0.100...1800 | SG8
238 | S155 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG1
238 | S156 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG2
238 | S157 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG3
238 | S158 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG4
238 | S159 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG5
238 | S160 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG6
238 | S161 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG7
238 | S162 | LVRT1 | Amplitude plot[9] | FLOAT | RW | 0...120 | SG8
238 | S163 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG1
238 | S164 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG2
238 | S165 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG3
238 | S166 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG4
238 | S167 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG5
238 | S168 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG6
238 | S169 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG7
238 | S170 | LVRT1 | Time plot[9] | FLOAT | RW | 0.100...1800 | SG8
238 | S171 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG1
238 | S172 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG2
238 | S173 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG3
238 | S174 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG4
238 | S175 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG5
238 | S176 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG6
238 | S177 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG7
238 | S178 | LVRT1 | Amplitude plot[10] | FLOAT | RW | 0...120 | SG8
238 | S179 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG1
238 | S180 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG2
238 | S181 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG3
238 | S182 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG4
238 | S183 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG5
238 | S184 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG6
238 | S185 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG7
238 | S186 | LVRT1 | Time plot[10] | FLOAT | RW | 0.100...1800 | SG8
238 | S187 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG1
238 | S188 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG2
238 | S189 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG3
238 | S190 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG4
238 | S191 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG5
238 | S192 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG6
238 | S193 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG7
238 | S194 | LVRT1 | AR total time to final trip + delay | FLOAT | RW | 0...1800 | SG8
238 | I7 | LVRT1 | AR shot counter | UINT32 | RW | 0...4294967295
238 | O1 | LVRT1 | LVRT START | SIGNAL_OUT | RW | 0...4294967295
238 | O2 | LVRT1 | LVRT TRIP | SIGNAL_OUT | RW | 0...4294967295
238 | O3 | LVRT1 | LVRT BLOCKED | SIGNAL_OUT | RW | 0...4294967295
238 | O4 | LVRT1 | LVRT low voltage BLOCKED | SIGNAL_OUT | RW | 0...4294967295
238 | I8 | LVRT1 | Newest register | UINT32 | R | 0...12
238 | I9 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I10 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I11 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I12 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I13 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I14 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I15 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I16 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I17 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I18 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I19 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | I20 | LVRT1 | Voltage ABC fault | FLOAT | R | 0...250
238 | S195 | LVRT1 | EventMaskLo | UINT32 | RW | 0...4294967295
93 | S1 | NOV1 | U0> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
93 | V1 | NOV1 | U0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
93 | I1 | NOV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
93 | I2 | NOV1 | U0> starts | UINT32 | R | 0...4294967295
93 | I3 | NOV1 | U0> trips | UINT32 | R | 0...4294967295
93 | I4 | NOV1 | U0> blocks | UINT32 | R | 0...4294967295
93 | S2 | NOV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
93 | S3 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG1
93 | S4 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG2
93 | S5 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG3
93 | S6 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG4
93 | S7 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG5
93 | S8 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG6
93 | S9 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG7
93 | S10 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG8
93 | S11 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
93 | S12 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
93 | S13 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
93 | S14 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
93 | S15 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
93 | S16 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
93 | S17 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
93 | S18 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
93 | O1 | NOV1 | U0> START | SIGNAL_OUT | RW | 0...4294967295
93 | O2 | NOV1 | U0> TRIP | SIGNAL_OUT | RW | 0...4294967295
93 | O3 | NOV1 | U0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
93 | I5 | NOV1 | Newest register | UINT32 | R | 0...12
93 | I6 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I7 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I8 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I9 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I10 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I11 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I12 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I13 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I14 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I15 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I16 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I17 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I18 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I19 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I20 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I21 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I22 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I23 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I24 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I25 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I26 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I27 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I28 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I29 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | S19 | NOV1 | EventMaskLo | UINT32 | RW | 0...4294967295
94 | S1 | NOV2 | U0>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
94 | V1 | NOV2 | U0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
94 | I1 | NOV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
94 | I2 | NOV2 | U0>> starts | UINT32 | R | 0...4294967295
94 | I3 | NOV2 | U0>> trips | UINT32 | R | 0...4294967295
94 | I4 | NOV2 | U0>> blocks | UINT32 | R | 0...4294967295
94 | S2 | NOV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
94 | S3 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG1
94 | S4 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG2
94 | S5 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG3
94 | S6 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG4
94 | S7 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG5
94 | S8 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG6
94 | S9 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG7
94 | S10 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG8
94 | S11 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
94 | S12 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
94 | S13 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
94 | S14 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
94 | S15 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
94 | S16 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
94 | S17 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
94 | S18 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
94 | O1 | NOV2 | U0>> START | SIGNAL_OUT | RW | 0...4294967295
94 | O2 | NOV2 | U0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
94 | O3 | NOV2 | U0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
94 | I5 | NOV2 | Newest register | UINT32 | R | 0...12
94 | I6 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I7 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I8 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I9 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I10 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I11 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I12 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I13 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I14 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I15 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I16 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I17 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I18 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I19 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I20 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I21 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I22 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I23 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I24 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I25 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I26 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I27 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I28 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I29 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | S19 | NOV2 | EventMaskLo | UINT32 | RW | 0...4294967295
95 | S1 | NOV3 | U0>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
95 | V1 | NOV3 | U0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
95 | I1 | NOV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
95 | I2 | NOV3 | U0>>> starts | UINT32 | R | 0...4294967295
95 | I3 | NOV3 | U0>>> trips | UINT32 | R | 0...4294967295
95 | I4 | NOV3 | U0>>> blocks | UINT32 | R | 0...4294967295
95 | S2 | NOV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
95 | S3 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG1
95 | S4 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG2
95 | S5 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG3
95 | S6 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG4
95 | S7 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG5
95 | S8 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG6
95 | S9 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG7
95 | S10 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG8
95 | S11 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
95 | S12 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
95 | S13 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
95 | S14 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
95 | S15 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
95 | S16 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
95 | S17 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
95 | S18 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
95 | O1 | NOV3 | U0>>> START | SIGNAL_OUT | RW | 0...4294967295
95 | O2 | NOV3 | U0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
95 | O3 | NOV3 | U0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
95 | I5 | NOV3 | Newest register | UINT32 | R | 0...12
95 | I6 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I7 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I8 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I9 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I10 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I11 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I12 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I13 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I14 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I15 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I16 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I17 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I18 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I19 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I20 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I21 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I22 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I23 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I24 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I25 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I26 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I27 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I28 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I29 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | S19 | NOV3 | EventMaskLo | UINT32 | RW | 0...4294967295
96 | S1 | NOV4 | U0>>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
96 | V1 | NOV4 | U0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
96 | I1 | NOV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
96 | I2 | NOV4 | U0>>>> starts | UINT32 | R | 0...4294967295
96 | I3 | NOV4 | U0>>>> trips | UINT32 | R | 0...4294967295
96 | I4 | NOV4 | U0>>>> blocks | UINT32 | R | 0...4294967295
96 | S2 | NOV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
96 | S3 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG1
96 | S4 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG2
96 | S5 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG3
96 | S6 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG4
96 | S7 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG5
96 | S8 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG6
96 | S9 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG7
96 | S10 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99 | SG8
96 | S11 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
96 | S12 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
96 | S13 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
96 | S14 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
96 | S15 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
96 | S16 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
96 | S17 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
96 | S18 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
96 | O1 | NOV4 | U0>>>> START | SIGNAL_OUT | RW | 0...4294967295
96 | O2 | NOV4 | U0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
96 | O3 | NOV4 | U0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
96 | I5 | NOV4 | Newest register | UINT32 | R | 0...12
96 | I6 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I7 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I8 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I9 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I10 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I11 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I12 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I13 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I14 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I15 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I16 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I17 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I18 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I19 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I20 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I21 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I22 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I23 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I24 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I25 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I26 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I27 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I28 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I29 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | S19 | NOV4 | EventMaskLo | UINT32 | RW | 0...4294967295
130 | S1 | VUB1 | U1/2 >/< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
130 | V1 | VUB1 | U1/2 >/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
130 | V2 | VUB1 | U1/2 >/< Measurement condition | UINT32 | R | 0=Seq Volt available;1=No Seq volts available
130 | I1 | VUB1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
130 | I2 | VUB1 | U1/2 >/< starts | UINT32 | R | 0...4294967295
130 | I3 | VUB1 | U1/2 >/< trips | UINT32 | R | 0...4294967295
130 | I4 | VUB1 | U1/2 >/< blocks | UINT32 | R | 0...4294967295
130 | S2 | VUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
130 | S3 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG1
130 | S4 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG2
130 | S5 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG3
130 | S6 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG4
130 | S7 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG5
130 | S8 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG6
130 | S9 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG7
130 | S10 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG8
130 | S11 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG1
130 | S12 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG2
130 | S13 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG3
130 | S14 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG4
130 | S15 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG5
130 | S16 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG6
130 | S17 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG7
130 | S18 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG8
130 | S19 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG1
130 | S20 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG2
130 | S21 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG3
130 | S22 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG4
130 | S23 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG5
130 | S24 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG6
130 | S25 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG7
130 | S26 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80 | SG8
130 | S27 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
130 | S28 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
130 | S29 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
130 | S30 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
130 | S31 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
130 | S32 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
130 | S33 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
130 | S34 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
130 | O1 | VUB1 | U1/2 >/< START | SIGNAL_OUT | RW | 0...4294967295
130 | O2 | VUB1 | U1/2 >/< TRIP | SIGNAL_OUT | RW | 0...4294967295
130 | O3 | VUB1 | U1/2 >/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
130 | I5 | VUB1 | Newest register | UINT32 | R | 0...12
130 | I6 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I7 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I8 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I9 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I10 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I11 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I12 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I13 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I14 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I15 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I16 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I17 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I18 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I19 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I20 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I21 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I22 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I23 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I24 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I25 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I26 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I27 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I28 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I29 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | S35 | VUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
131 | S1 | VUB2 | U1/2 >>/<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
131 | V1 | VUB2 | U1/2 >>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
131 | V2 | VUB2 | U1/2 >>/<< Measurement condition | UINT32 | R | 0=Seq Volt available;1=No Seq volts available
131 | I1 | VUB2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
131 | I2 | VUB2 | U1/2 >>/<< starts | UINT32 | R | 0...4294967295
131 | I3 | VUB2 | U1/2 >>/<< trips | UINT32 | R | 0...4294967295
131 | I4 | VUB2 | U1/2 >>/<< blocks | UINT32 | R | 0...4294967295
131 | S2 | VUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
131 | S3 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG1
131 | S4 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG2
131 | S5 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG3
131 | S6 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG4
131 | S7 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG5
131 | S8 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG6
131 | S9 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG7
131 | S10 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG8
131 | S11 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG1
131 | S12 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG2
131 | S13 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG3
131 | S14 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG4
131 | S15 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG5
131 | S16 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG6
131 | S17 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG7
131 | S18 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG8
131 | S19 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG1
131 | S20 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG2
131 | S21 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG3
131 | S22 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG4
131 | S23 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG5
131 | S24 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG6
131 | S25 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG7
131 | S26 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80 | SG8
131 | S27 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
131 | S28 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
131 | S29 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
131 | S30 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
131 | S31 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
131 | S32 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
131 | S33 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
131 | S34 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
131 | O1 | VUB2 | U1/2 >>/<< START | SIGNAL_OUT | RW | 0...4294967295
131 | O2 | VUB2 | U1/2 >>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
131 | O3 | VUB2 | U1/2 >>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
131 | I5 | VUB2 | Newest register | UINT32 | R | 0...12
131 | I6 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I7 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I8 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I9 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I10 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I11 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I12 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I13 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I14 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I15 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I16 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I17 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I18 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I19 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I20 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I21 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I22 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I23 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I24 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I25 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I26 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I27 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I28 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I29 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | S35 | VUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
132 | S1 | VUB3 | U1/2 >>>/<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
132 | V1 | VUB3 | U1/2 >>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
132 | V2 | VUB3 | U1/2 >>>/<<< Measurement condition | UINT32 | R | 0=Seq Volt available;1=No Seq volts available
132 | I1 | VUB3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
132 | I2 | VUB3 | U1/2 >>>/<<< starts | UINT32 | R | 0...4294967295
132 | I3 | VUB3 | U1/2 >>>/<<< trips | UINT32 | R | 0...4294967295
132 | I4 | VUB3 | U1/2 >>>/<<< blocks | UINT32 | R | 0...4294967295
132 | S2 | VUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
132 | S3 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG1
132 | S4 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG2
132 | S5 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG3
132 | S6 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG4
132 | S7 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG5
132 | S8 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG6
132 | S9 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG7
132 | S10 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG8
132 | S11 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG1
132 | S12 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG2
132 | S13 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG3
132 | S14 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG4
132 | S15 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG5
132 | S16 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG6
132 | S17 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG7
132 | S18 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG8
132 | S19 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG1
132 | S20 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG2
132 | S21 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG3
132 | S22 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG4
132 | S23 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG5
132 | S24 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG6
132 | S25 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG7
132 | S26 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80 | SG8
132 | S27 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
132 | S28 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
132 | S29 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
132 | S30 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
132 | S31 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
132 | S32 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
132 | S33 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
132 | S34 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
132 | O1 | VUB3 | U1/2 >>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
132 | O2 | VUB3 | U1/2 >>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
132 | O3 | VUB3 | U1/2 >>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
132 | I5 | VUB3 | Newest register | UINT32 | R | 0...12
132 | I6 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I7 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I8 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I9 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I10 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I11 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I12 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I13 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I14 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I15 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I16 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I17 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I18 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I19 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I20 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I21 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I22 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I23 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I24 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I25 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I26 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I27 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I28 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I29 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | S35 | VUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
133 | S1 | VUB4 | U1/2 >>>>/<<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
133 | V1 | VUB4 | U1/2 >>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
133 | V2 | VUB4 | U1/2 >>>>/<<<< Measurement condition | UINT32 | R | 0=Seq Volt available;1=No Seq volts available
133 | I1 | VUB4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
133 | I2 | VUB4 | U1/2 >>>>/<<<< starts | UINT32 | R | 0...4294967295
133 | I3 | VUB4 | U1/2 >>>>/<<<< trips | UINT32 | R | 0...4294967295
133 | I4 | VUB4 | U1/2 >>>>/<<<< blocks | UINT32 | R | 0...4294967295
133 | S2 | VUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
133 | S3 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG1
133 | S4 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG2
133 | S5 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG3
133 | S6 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG4
133 | S7 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG5
133 | S8 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG6
133 | S9 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG7
133 | S10 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under < | SG8
133 | S11 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG1
133 | S12 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG2
133 | S13 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG3
133 | S14 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG4
133 | S15 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG5
133 | S16 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG6
133 | S17 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG7
133 | S18 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150 | SG8
133 | S19 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG1
133 | S20 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG2
133 | S21 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG3
133 | S22 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG4
133 | S23 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG5
133 | S24 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG6
133 | S25 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG7
133 | S26 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80 | SG8
133 | S27 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
133 | S28 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
133 | S29 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
133 | S30 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
133 | S31 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
133 | S32 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
133 | S33 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
133 | S34 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
133 | O1 | VUB4 | U1/2 >>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
133 | O2 | VUB4 | U1/2 >>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
133 | O3 | VUB4 | U1/2 >>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
133 | I5 | VUB4 | Newest register | UINT32 | R | 0...12
133 | I6 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I7 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I8 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I9 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I10 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I11 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I12 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I13 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I14 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I15 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I16 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I17 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I18 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I19 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I20 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I21 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I22 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I23 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I24 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I25 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I26 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I27 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I28 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I29 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | S35 | VUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
99 | S1 | FRQV1 | f</> [81O/81U] mode | UINT32 | RW | 0=Disabled;1=Activated
99 | V1 | FRQV1 | f> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I1 | FRQV1 | f> fmeas / fset | FLOAT | R | 0...20
99 | S2 | FRQV1 | f>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V2 | FRQV1 | f>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I2 | FRQV1 | f>> fmeas / fset | FLOAT | R | 0...20
99 | S3 | FRQV1 | f>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V3 | FRQV1 | f>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I3 | FRQV1 | f>>> fmeas / fset | FLOAT | R | 0...20
99 | S4 | FRQV1 | f>>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V4 | FRQV1 | f>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I4 | FRQV1 | f>>>> fmeas / fset | FLOAT | R | 0...20
99 | S5 | FRQV1 | f< Enable | UINT32 | RW | 0=No;1=Yes
99 | V5 | FRQV1 | f< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I5 | FRQV1 | f< fmeas / fset | FLOAT | R | 0...20
99 | S6 | FRQV1 | f<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V6 | FRQV1 | f<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I6 | FRQV1 | f<< fmeas / fset | FLOAT | R | 0...20
99 | S7 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V7 | FRQV1 | f<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I7 | FRQV1 | f<<< fmeas / fset | FLOAT | R | 0...20
99 | S8 | FRQV1 | f<<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V8 | FRQV1 | f<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
99 | I8 | FRQV1 | f<<<< fmeas / fset | FLOAT | R | 0...20
99 | I9 | FRQV1 | f> starts | UINT32 | R | 0...4294967295
99 | I10 | FRQV1 | f> trips | UINT32 | R | 0...4294967295
99 | I11 | FRQV1 | f> blocks | UINT32 | R | 0...4294967295
99 | I12 | FRQV1 | f>> starts | UINT32 | R | 0...4294967295
99 | I13 | FRQV1 | f>> trips | UINT32 | R | 0...4294967295
99 | I14 | FRQV1 | f>> blocks | UINT32 | R | 0...4294967295
99 | I15 | FRQV1 | f>>> starts | UINT32 | R | 0...4294967295
99 | I16 | FRQV1 | f>>> trips | UINT32 | R | 0...4294967295
99 | I17 | FRQV1 | f>>> blocks | UINT32 | R | 0...4294967295
99 | I18 | FRQV1 | f>>>> starts | UINT32 | R | 0...4294967295
99 | I19 | FRQV1 | f>>>> trips | UINT32 | R | 0...4294967295
99 | I20 | FRQV1 | f>>>> blocks | UINT32 | R | 0...4294967295
99 | I21 | FRQV1 | f< starts | UINT32 | R | 0...4294967295
99 | I22 | FRQV1 | f< trips | UINT32 | R | 0...4294967295
99 | I23 | FRQV1 | f< blocks | UINT32 | R | 0...4294967295
99 | I24 | FRQV1 | f<< starts | UINT32 | R | 0...4294967295
99 | I25 | FRQV1 | f<< trips | UINT32 | R | 0...4294967295
99 | I26 | FRQV1 | f<< blocks | UINT32 | R | 0...4294967295
99 | I27 | FRQV1 | f<<< starts | UINT32 | R | 0...4294967295
99 | I28 | FRQV1 | f<<< trips | UINT32 | R | 0...4294967295
99 | I29 | FRQV1 | f<<< blocks | UINT32 | R | 0...4294967295
99 | I30 | FRQV1 | f<<<< starts | UINT32 | R | 0...4294967295
99 | I31 | FRQV1 | f<<<< trips | UINT32 | R | 0...4294967295
99 | I32 | FRQV1 | f<<<< blocks | UINT32 | R | 0...4294967295
99 | S9 | FRQV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
99 | S10 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S11 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S12 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S13 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S14 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S15 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S16 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S17 | FRQV1 | f> used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S18 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG1
99 | S19 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG2
99 | S20 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG3
99 | S21 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG4
99 | S22 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG5
99 | S23 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG6
99 | S24 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG7
99 | S25 | FRQV1 | f> pick-up | FLOAT | RW | 10...70 | SG8
99 | S26 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG1
99 | S27 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG2
99 | S28 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG3
99 | S29 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG4
99 | S30 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG5
99 | S31 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG6
99 | S32 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG7
99 | S33 | FRQV1 | f> operating time | FLOAT | RW | 0...1800 | SG8
99 | S34 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S35 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S36 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S37 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S38 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S39 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S40 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S41 | FRQV1 | f>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S42 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG1
99 | S43 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG2
99 | S44 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG3
99 | S45 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG4
99 | S46 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG5
99 | S47 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG6
99 | S48 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG7
99 | S49 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70 | SG8
99 | S50 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG1
99 | S51 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG2
99 | S52 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG3
99 | S53 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG4
99 | S54 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG5
99 | S55 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG6
99 | S56 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG7
99 | S57 | FRQV1 | f>> operating time | FLOAT | RW | 0...1800 | SG8
99 | S58 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S59 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S60 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S61 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S62 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S63 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S64 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S65 | FRQV1 | f>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S66 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG1
99 | S67 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG2
99 | S68 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG3
99 | S69 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG4
99 | S70 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG5
99 | S71 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG6
99 | S72 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG7
99 | S73 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70 | SG8
99 | S74 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG1
99 | S75 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG2
99 | S76 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG3
99 | S77 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG4
99 | S78 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG5
99 | S79 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG6
99 | S80 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG7
99 | S81 | FRQV1 | f>>> operating time | FLOAT | RW | 0...1800 | SG8
99 | S82 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S83 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S84 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S85 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S86 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S87 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S88 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S89 | FRQV1 | f>>>> used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S90 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG1
99 | S91 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG2
99 | S92 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG3
99 | S93 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG4
99 | S94 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG5
99 | S95 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG6
99 | S96 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG7
99 | S97 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70 | SG8
99 | S98 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG1
99 | S99 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG2
99 | S100 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG3
99 | S101 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG4
99 | S102 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG5
99 | S103 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG6
99 | S104 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG7
99 | S105 | FRQV1 | f>>>> operating time | FLOAT | RW | 0...1800 | SG8
99 | S106 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S107 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S108 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S109 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S110 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S111 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S112 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S113 | FRQV1 | f< used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S114 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG1
99 | S115 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG2
99 | S116 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG3
99 | S117 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG4
99 | S118 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG5
99 | S119 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG6
99 | S120 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG7
99 | S121 | FRQV1 | f< pick-up | FLOAT | RW | 7...65 | SG8
99 | S122 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG1
99 | S123 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG2
99 | S124 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG3
99 | S125 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG4
99 | S126 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG5
99 | S127 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG6
99 | S128 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG7
99 | S129 | FRQV1 | f< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG8
99 | S130 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG1
99 | S131 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG2
99 | S132 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG3
99 | S133 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG4
99 | S134 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG5
99 | S135 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG6
99 | S136 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG7
99 | S137 | FRQV1 | f< operating time | FLOAT | RW | 0...1800 | SG8
99 | S138 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S139 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S140 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S141 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S142 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S143 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S144 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S145 | FRQV1 | f<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S146 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG1
99 | S147 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG2
99 | S148 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG3
99 | S149 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG4
99 | S150 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG5
99 | S151 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG6
99 | S152 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG7
99 | S153 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65 | SG8
99 | S154 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG1
99 | S155 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG2
99 | S156 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG3
99 | S157 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG4
99 | S158 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG5
99 | S159 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG6
99 | S160 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG7
99 | S161 | FRQV1 | f<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG8
99 | S162 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG1
99 | S163 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG2
99 | S164 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG3
99 | S165 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG4
99 | S166 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG5
99 | S167 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG6
99 | S168 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG7
99 | S169 | FRQV1 | f<< operating time | FLOAT | RW | 0...1800 | SG8
99 | S170 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S171 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S172 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S173 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S174 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S175 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S176 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S177 | FRQV1 | f<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S178 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG1
99 | S179 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG2
99 | S180 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG3
99 | S181 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG4
99 | S182 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG5
99 | S183 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG6
99 | S184 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG7
99 | S185 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65 | SG8
99 | S186 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG1
99 | S187 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG2
99 | S188 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG3
99 | S189 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG4
99 | S190 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG5
99 | S191 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG6
99 | S192 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG7
99 | S193 | FRQV1 | f<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG8
99 | S194 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG1
99 | S195 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG2
99 | S196 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG3
99 | S197 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG4
99 | S198 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG5
99 | S199 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG6
99 | S200 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG7
99 | S201 | FRQV1 | f<<< operating time | FLOAT | RW | 0...1800 | SG8
99 | S202 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
99 | S203 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
99 | S204 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
99 | S205 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
99 | S206 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
99 | S207 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
99 | S208 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
99 | S209 | FRQV1 | f<<<< used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
99 | S210 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG1
99 | S211 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG2
99 | S212 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG3
99 | S213 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG4
99 | S214 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG5
99 | S215 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG6
99 | S216 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG7
99 | S217 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65 | SG8
99 | S218 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG1
99 | S219 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG2
99 | S220 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG3
99 | S221 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG4
99 | S222 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG5
99 | S223 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG6
99 | S224 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG7
99 | S225 | FRQV1 | f<<<< Undervoltage block (0% no blocking) | FLOAT | RW | 0...120 | SG8
99 | S226 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG1
99 | S227 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG2
99 | S228 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG3
99 | S229 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG4
99 | S230 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG5
99 | S231 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG6
99 | S232 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG7
99 | S233 | FRQV1 | f<<<< operating time | FLOAT | RW | 0...1800 | SG8
99 | O1 | FRQV1 | f> START | SIGNAL_OUT | RW | 0...4294967295
99 | O2 | FRQV1 | f> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O3 | FRQV1 | f> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O4 | FRQV1 | f>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O5 | FRQV1 | f>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O6 | FRQV1 | f>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O7 | FRQV1 | f>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O8 | FRQV1 | f>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O9 | FRQV1 | f>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O10 | FRQV1 | f>>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O11 | FRQV1 | f>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O12 | FRQV1 | f>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O13 | FRQV1 | f< START | SIGNAL_OUT | RW | 0...4294967295
99 | O14 | FRQV1 | f< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O15 | FRQV1 | f< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O16 | FRQV1 | f< BLOCKED (Undervoltage) | SIGNAL_OUT | RW | 0...4294967295
99 | O17 | FRQV1 | f<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O18 | FRQV1 | f<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O19 | FRQV1 | f<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O20 | FRQV1 | f<< BLOCKED (Undervoltage) | SIGNAL_OUT | RW | 0...4294967295
99 | O21 | FRQV1 | f<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O22 | FRQV1 | f<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O23 | FRQV1 | f<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O24 | FRQV1 | f<<< BLOCKED (Undervoltage) | SIGNAL_OUT | RW | 0...4294967295
99 | O25 | FRQV1 | f<<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O26 | FRQV1 | f<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O27 | FRQV1 | f<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O28 | FRQV1 | f<<<< BLOCKED (Undervoltage) | SIGNAL_OUT | RW | 0...4294967295
99 | I33 | FRQV1 | Newest register | UINT32 | R | 0...12
99 | I34 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I35 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I36 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I37 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I38 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I39 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I40 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I41 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I42 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I43 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I44 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I45 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | S234 | FRQV1 | EventMaskLo | UINT32 | RW | 0...4294967295
103 | S1 | DFT1 | df/dt >/< [81] mode | UINT32 | RW | 0=Disabled;1=Activated
103 | S2 | DFT1 | Max allowed df/dt rate | FLOAT | RW | 0.1...50
103 | I1 | DFT1 | Measured df/dt | FLOAT | R | 0...20
103 | S3 | DFT1 | df/dt >/< (1) Enable | UINT32 | RW | 0=No;1=Yes
103 | V1 | DFT1 | df/dt >/< (1) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I2 | DFT1 | df/dt >/< (1) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | S4 | DFT1 | df/dt >/< (2) Enable | UINT32 | RW | 0=No;1=Yes
103 | V2 | DFT1 | df/dt >/< (2) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I3 | DFT1 | df/dt >/< (2) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | S5 | DFT1 | df/dt >/< (3) Enable | UINT32 | RW | 0=No;1=Yes
103 | V3 | DFT1 | df/dt >/< (3) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I4 | DFT1 | df/dt >/< (3) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | S6 | DFT1 | df/dt >/< (4) Enable | UINT32 | RW | 0=No;1=Yes
103 | V4 | DFT1 | df/dt >/< (4) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I5 | DFT1 | df/dt >/< (4) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | S7 | DFT1 | df/dt >/< (5) Enable | UINT32 | RW | 0=No;1=Yes
103 | V5 | DFT1 | df/dt >/< (5) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I6 | DFT1 | df/dt >/< (5) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | S8 | DFT1 | df/dt >/< (6) Enable | UINT32 | RW | 0=No;1=Yes
103 | V6 | DFT1 | df/dt >/< (6) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I7 | DFT1 | df/dt >/< (6) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | S9 | DFT1 | df/dt >/< (7) Enable | UINT32 | RW | 0=No;1=Yes
103 | V7 | DFT1 | df/dt >/< (7) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I8 | DFT1 | df/dt >/< (7) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | S10 | DFT1 | df/dt >/< (8) Enable | UINT32 | RW | 0=No;1=Yes
103 | V8 | DFT1 | df/dt >/< (8) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I9 | DFT1 | df/dt >/< (8) df/dt meas / df/dt set | FLOAT | R | 0...20
103 | I10 | DFT1 | df/dt >/< (1) starts | UINT32 | R | 0...4294967295
103 | I11 | DFT1 | df/dt >/< (1) trips | UINT32 | R | 0...4294967295
103 | I12 | DFT1 | df/dt >/< (1) blocks | UINT32 | R | 0...4294967295
103 | I13 | DFT1 | df/dt >/< (2) starts | UINT32 | R | 0...4294967295
103 | I14 | DFT1 | df/dt >/< (2) trips | UINT32 | R | 0...4294967295
103 | I15 | DFT1 | df/dt >/< (2) blocks | UINT32 | R | 0...4294967295
103 | I16 | DFT1 | df/dt >/< (3) starts | UINT32 | R | 0...4294967295
103 | I17 | DFT1 | df/dt >/< (3) trips | UINT32 | R | 0...4294967295
103 | I18 | DFT1 | df/dt >/< (3) blocks | UINT32 | R | 0...4294967295
103 | I19 | DFT1 | df/dt >/< (4) starts | UINT32 | R | 0...4294967295
103 | I20 | DFT1 | df/dt >/< (4) trips | UINT32 | R | 0...4294967295
103 | I21 | DFT1 | df/dt >/< (4) blocks | UINT32 | R | 0...4294967295
103 | I22 | DFT1 | df/dt >/< (5) starts | UINT32 | R | 0...4294967295
103 | I23 | DFT1 | df/dt >/< (5) trips | UINT32 | R | 0...4294967295
103 | I24 | DFT1 | df/dt >/< (5) blocks | UINT32 | R | 0...4294967295
103 | I25 | DFT1 | df/dt >/< (6) starts | UINT32 | R | 0...4294967295
103 | I26 | DFT1 | df/dt >/< (6) trips | UINT32 | R | 0...4294967295
103 | I27 | DFT1 | df/dt >/< (6) blocks | UINT32 | R | 0...4294967295
103 | I28 | DFT1 | df/dt >/< (7) starts | UINT32 | R | 0...4294967295
103 | I29 | DFT1 | df/dt >/< (7) trips | UINT32 | R | 0...4294967295
103 | I30 | DFT1 | df/dt >/< (7) blocks | UINT32 | R | 0...4294967295
103 | I31 | DFT1 | df/dt >/< (8) starts | UINT32 | R | 0...4294967295
103 | I32 | DFT1 | df/dt >/< (8) trips | UINT32 | R | 0...4294967295
103 | I33 | DFT1 | df/dt >/< (8) blocks | UINT32 | R | 0...4294967295
103 | S11 | DFT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
103 | S12 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S13 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S14 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S15 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S16 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S17 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S18 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S19 | DFT1 | df/dt >/< (1) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S20 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S21 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S22 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S23 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S24 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S25 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S26 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S27 | DFT1 | df/dt >/< (1) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S28 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S29 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S30 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S31 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S32 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S33 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S34 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S35 | DFT1 | df/dt >/< (1) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S36 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG1
103 | S37 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG2
103 | S38 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG3
103 | S39 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG4
103 | S40 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG5
103 | S41 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG6
103 | S42 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG7
103 | S43 | DFT1 | df/dt >/< (1) f> limit | FLOAT | RW | 10...70 | SG8
103 | S44 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG1
103 | S45 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG2
103 | S46 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG3
103 | S47 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG4
103 | S48 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG5
103 | S49 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG6
103 | S50 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG7
103 | S51 | DFT1 | df/dt >/< (1) f< limit | FLOAT | RW | 7...65 | SG8
103 | S52 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S53 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S54 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S55 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S56 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S57 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S58 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S59 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S60 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG1
103 | S61 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG2
103 | S62 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG3
103 | S63 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG4
103 | S64 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG5
103 | S65 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG6
103 | S66 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG7
103 | S67 | DFT1 | df/dt >/< (1) operating time | FLOAT | RW | 0...1800 | SG8
103 | S68 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S69 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S70 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S71 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S72 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S73 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S74 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S75 | DFT1 | df/dt >/< (2) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S76 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S77 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S78 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S79 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S80 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S81 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S82 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S83 | DFT1 | df/dt >/< (2) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S84 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S85 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S86 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S87 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S88 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S89 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S90 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S91 | DFT1 | df/dt >/< (2) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S92 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG1
103 | S93 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG2
103 | S94 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG3
103 | S95 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG4
103 | S96 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG5
103 | S97 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG6
103 | S98 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG7
103 | S99 | DFT1 | df/dt >/< (2) f> limit | FLOAT | RW | 10...70 | SG8
103 | S100 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG1
103 | S101 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG2
103 | S102 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG3
103 | S103 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG4
103 | S104 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG5
103 | S105 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG6
103 | S106 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG7
103 | S107 | DFT1 | df/dt >/< (2) f< limit | FLOAT | RW | 7...65 | SG8
103 | S108 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S109 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S110 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S111 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S112 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S113 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S114 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S115 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S116 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG1
103 | S117 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG2
103 | S118 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG3
103 | S119 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG4
103 | S120 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG5
103 | S121 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG6
103 | S122 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG7
103 | S123 | DFT1 | df/dt >/< (2) operating time | FLOAT | RW | 0...1800 | SG8
103 | S124 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S125 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S126 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S127 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S128 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S129 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S130 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S131 | DFT1 | df/dt >/< (3) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S132 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S133 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S134 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S135 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S136 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S137 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S138 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S139 | DFT1 | df/dt >/< (3) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S140 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S141 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S142 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S143 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S144 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S145 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S146 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S147 | DFT1 | df/dt >/< (3) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S148 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG1
103 | S149 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG2
103 | S150 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG3
103 | S151 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG4
103 | S152 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG5
103 | S153 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG6
103 | S154 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG7
103 | S155 | DFT1 | df/dt >/< (3) f> limit | FLOAT | RW | 10...70 | SG8
103 | S156 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG1
103 | S157 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG2
103 | S158 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG3
103 | S159 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG4
103 | S160 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG5
103 | S161 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG6
103 | S162 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG7
103 | S163 | DFT1 | df/dt >/< (3) f< limit | FLOAT | RW | 7...65 | SG8
103 | S164 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S165 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S166 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S167 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S168 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S169 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S170 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S171 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S172 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG1
103 | S173 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG2
103 | S174 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG3
103 | S175 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG4
103 | S176 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG5
103 | S177 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG6
103 | S178 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG7
103 | S179 | DFT1 | df/dt >/< (3) operating time | FLOAT | RW | 0...1800 | SG8
103 | S180 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S181 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S182 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S183 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S184 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S185 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S186 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S187 | DFT1 | df/dt >/< (4) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S188 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S189 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S190 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S191 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S192 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S193 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S194 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S195 | DFT1 | df/dt >/< (4) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S196 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S197 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S198 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S199 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S200 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S201 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S202 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S203 | DFT1 | df/dt >/< (4) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S204 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG1
103 | S205 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG2
103 | S206 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG3
103 | S207 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG4
103 | S208 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG5
103 | S209 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG6
103 | S210 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG7
103 | S211 | DFT1 | df/dt >/< (4) f> limit | FLOAT | RW | 10...70 | SG8
103 | S212 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG1
103 | S213 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG2
103 | S214 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG3
103 | S215 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG4
103 | S216 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG5
103 | S217 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG6
103 | S218 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG7
103 | S219 | DFT1 | df/dt >/< (4) f< limit | FLOAT | RW | 7...65 | SG8
103 | S220 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S221 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S222 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S223 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S224 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S225 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S226 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S227 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S228 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG1
103 | S229 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG2
103 | S230 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG3
103 | S231 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG4
103 | S232 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG5
103 | S233 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG6
103 | S234 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG7
103 | S235 | DFT1 | df/dt >/< (4) operating time | FLOAT | RW | 0...1800 | SG8
103 | S236 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S237 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S238 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S239 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S240 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S241 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S242 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S243 | DFT1 | df/dt >/< (5) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S244 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S245 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S246 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S247 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S248 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S249 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S250 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S251 | DFT1 | df/dt >/< (5) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S252 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S253 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S254 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S255 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S256 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S257 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S258 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S259 | DFT1 | df/dt >/< (5) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S260 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG1
103 | S261 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG2
103 | S262 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG3
103 | S263 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG4
103 | S264 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG5
103 | S265 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG6
103 | S266 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG7
103 | S267 | DFT1 | df/dt >/< (5) f> limit | FLOAT | RW | 10...70 | SG8
103 | S268 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG1
103 | S269 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG2
103 | S270 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG3
103 | S271 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG4
103 | S272 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG5
103 | S273 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG6
103 | S274 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG7
103 | S275 | DFT1 | df/dt >/< (5) f< limit | FLOAT | RW | 7...65 | SG8
103 | S276 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S277 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S278 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S279 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S280 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S281 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S282 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S283 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S284 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG1
103 | S285 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG2
103 | S286 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG3
103 | S287 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG4
103 | S288 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG5
103 | S289 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG6
103 | S290 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG7
103 | S291 | DFT1 | df/dt >/< (5) operating time | FLOAT | RW | 0...1800 | SG8
103 | S292 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S293 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S294 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S295 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S296 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S297 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S298 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S299 | DFT1 | df/dt >/< (6) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S300 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S301 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S302 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S303 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S304 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S305 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S306 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S307 | DFT1 | df/dt >/< (6) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S308 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S309 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S310 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S311 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S312 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S313 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S314 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S315 | DFT1 | df/dt >/< (6) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S316 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG1
103 | S317 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG2
103 | S318 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG3
103 | S319 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG4
103 | S320 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG5
103 | S321 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG6
103 | S322 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG7
103 | S323 | DFT1 | df/dt >/< (6) f> limit | FLOAT | RW | 10...70 | SG8
103 | S324 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG1
103 | S325 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG2
103 | S326 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG3
103 | S327 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG4
103 | S328 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG5
103 | S329 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG6
103 | S330 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG7
103 | S331 | DFT1 | df/dt >/< (6) f< limit | FLOAT | RW | 7...65 | SG8
103 | S332 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S333 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S334 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S335 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S336 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S337 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S338 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S339 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S340 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG1
103 | S341 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG2
103 | S342 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG3
103 | S343 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG4
103 | S344 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG5
103 | S345 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG6
103 | S346 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG7
103 | S347 | DFT1 | df/dt >/< (6) operating time | FLOAT | RW | 0...1800 | SG8
103 | S348 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S349 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S350 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S351 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S352 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S353 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S354 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S355 | DFT1 | df/dt >/< (7) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S356 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S357 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S358 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S359 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S360 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S361 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S362 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S363 | DFT1 | df/dt >/< (7) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S364 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S365 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S366 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S367 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S368 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S369 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S370 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S371 | DFT1 | df/dt >/< (7) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S372 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG1
103 | S373 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG2
103 | S374 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG3
103 | S375 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG4
103 | S376 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG5
103 | S377 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG6
103 | S378 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG7
103 | S379 | DFT1 | df/dt >/< (7) f> limit | FLOAT | RW | 10...70 | SG8
103 | S380 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG1
103 | S381 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG2
103 | S382 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG3
103 | S383 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG4
103 | S384 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG5
103 | S385 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG6
103 | S386 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG7
103 | S387 | DFT1 | df/dt >/< (7) f< limit | FLOAT | RW | 7...65 | SG8
103 | S388 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S389 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S390 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S391 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S392 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S393 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S394 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S395 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S396 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG1
103 | S397 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG2
103 | S398 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG3
103 | S399 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG4
103 | S400 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG5
103 | S401 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG6
103 | S402 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG7
103 | S403 | DFT1 | df/dt >/< (7) operating time | FLOAT | RW | 0...1800 | SG8
103 | S404 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG1
103 | S405 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG2
103 | S406 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG3
103 | S407 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG4
103 | S408 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG5
103 | S409 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG6
103 | S410 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG7
103 | S411 | DFT1 | df/dt >/< (8) used in setting group | UINT32 | RW | 0=No;1=Yes | SG8
103 | S412 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG1
103 | S413 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG2
103 | S414 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG3
103 | S415 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG4
103 | S416 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG5
103 | S417 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG6
103 | S418 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG7
103 | S419 | DFT1 | df/dt >/< (8) operating mode | UINT32 | RW | 0=Rising;1=Falling;2=Both | SG8
103 | S420 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG1
103 | S421 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG2
103 | S422 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG3
103 | S423 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG4
103 | S424 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG5
103 | S425 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG6
103 | S426 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG7
103 | S427 | DFT1 | df/dt >/< (8) frequency limit | UINT32 | R | 0=Not used;1=Use f limit | SG8
103 | S428 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG1
103 | S429 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG2
103 | S430 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG3
103 | S431 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG4
103 | S432 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG5
103 | S433 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG6
103 | S434 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG7
103 | S435 | DFT1 | df/dt >/< (8) f> limit | FLOAT | RW | 10...70 | SG8
103 | S436 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG1
103 | S437 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG2
103 | S438 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG3
103 | S439 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG4
103 | S440 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG5
103 | S441 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG6
103 | S442 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG7
103 | S443 | DFT1 | df/dt >/< (8) f< limit | FLOAT | RW | 7...65 | SG8
103 | S444 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG1
103 | S445 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG2
103 | S446 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG3
103 | S447 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG4
103 | S448 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG5
103 | S449 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG6
103 | S450 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG7
103 | S451 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10 | SG8
103 | S452 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG1
103 | S453 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG2
103 | S454 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG3
103 | S455 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG4
103 | S456 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG5
103 | S457 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG6
103 | S458 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG7
103 | S459 | DFT1 | df/dt >/< (8) operating time | FLOAT | RW | 0...1800 | SG8
103 | O1 | DFT1 | df/dt >/< (1) START | SIGNAL_OUT | RW | 0...4294967295
103 | O2 | DFT1 | df/dt >/< (1) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O3 | DFT1 | df/dt >/< (1) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O4 | DFT1 | df/dt >/< (2) START | SIGNAL_OUT | RW | 0...4294967295
103 | O5 | DFT1 | df/dt >/< (2) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O6 | DFT1 | df/dt >/< (2) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O7 | DFT1 | df/dt >/< (3) START | SIGNAL_OUT | RW | 0...4294967295
103 | O8 | DFT1 | df/dt >/< (3) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O9 | DFT1 | df/dt >/< (3) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O10 | DFT1 | df/dt >/< (4) START | SIGNAL_OUT | RW | 0...4294967295
103 | O11 | DFT1 | df/dt >/< (4) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O12 | DFT1 | df/dt >/< (4) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O13 | DFT1 | df/dt >/< (5) START | SIGNAL_OUT | RW | 0...4294967295
103 | O14 | DFT1 | df/dt >/< (5) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O15 | DFT1 | df/dt >/< (5) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O16 | DFT1 | df/dt >/< (6) START | SIGNAL_OUT | RW | 0...4294967295
103 | O17 | DFT1 | df/dt >/< (6) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O18 | DFT1 | df/dt >/< (6) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O19 | DFT1 | df/dt >/< (7) START | SIGNAL_OUT | RW | 0...4294967295
103 | O20 | DFT1 | df/dt >/< (7) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O21 | DFT1 | df/dt >/< (7) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O22 | DFT1 | df/dt >/< (8) START | SIGNAL_OUT | RW | 0...4294967295
103 | O23 | DFT1 | df/dt >/< (8) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O24 | DFT1 | df/dt >/< (8) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | I34 | DFT1 | Newest register | UINT32 | R | 0...12
103 | I35 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I36 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I37 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I38 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I39 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I40 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I41 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I42 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I43 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I44 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I45 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I46 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I47 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I48 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I49 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I50 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I51 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I52 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I53 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I54 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I55 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I56 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I57 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I58 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | S460 | DFT1 | EventMaskLo | UINT32 | RW | 0...4294967295
183 | V1 | RHC1 | Counter is now | UINT32 | R | 0=Idle;1=Counting
183 | I1 | RHC1 | Running hours | UINT32 | RW | 0...4294967295
183 | I2 | RHC1 | Start count | UINT32 | RW | 0...4294967295
183 | I3 | RHC1 | Clear hours | UINT32 | W | 0=-;1=Clear
183 | S1 | RHC1 | EventMaskLo | UINT32 | RW | 0...4294967295
113 | V1 | GST1 | Generator is now | UINT32 | R | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
113 | I1 | GST1 | Times overloaded | UINT32 | R | 0...4294967295
113 | I2 | GST1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
113 | I3 | GST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
113 | I4 | GST1 | Generating time (Running hours) | UINT32 | R | 0...4294967295
113 | I5 | GST1 | Overloading cumulative | UINT32 | R | 0...4294967295
113 | I6 | GST1 | Last overload duration | UINT32 | R | 0...4294967295
113 | I7 | GST1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
113 | I8 | GST1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
113 | S1 | GST1 | Clear total times | UINT32 | W | 0=-;1=Clear
113 | S2 | GST1 | Generator nominal MVA (S) | FLOAT | RW | 0.001...500
113 | S3 | GST1 | Generator nominal Voltage (Vt) | FLOAT | RW | 0.001...25
113 | S4 | GST1 | Prime mover max power output (Pmax) | FLOAT | RW | 0.001...500
113 | S5 | GST1 | Override CT scaling nominal calculations | UINT32 | RW | 0=No;1=On HV side;2=On LV side;3=On HV and LV sides
113 | S6 | GST1 | Block trafo in protection area | UINT32 | RW | 0=No;1=Yes
113 | S7 | GST1 | Block trafo included in differential zone | UINT32 | RW | 0=No, Only GEN Differential;1=Yes, Overall differential
113 | S8 | GST1 | Generator voltage measurement | UINT32 | RW | 0=LV side VT (no corrections);1=HV side VT(Reduce to LV);2=HV side VT(HV measurements)
113 | S9 | GST1 | Ratio for generator nominal voltage scaling (1 p.u.) | UINT32 | RW | 0=Generator nominal voltage;1=Transformer LV nominal voltage;2=Set Un ratio by hand
113 | I9 | GST1 | Transformer ratio HV -> LV Trafo. | FLOAT | R | 0.01...100
113 | I10 | GST1 | Transformer ratio HV -> LV Gen. | FLOAT | R | 0.01...100
113 | I11 | GST1 | Voltage ratio | FLOAT | RW | 0.001...100
113 | I12 | GST1 | Voltage scaling | FLOAT | R | 0.01...100
113 | S10 | GST1 | Transformer nominal MVA | FLOAT | RW | 0.001...500
113 | S11 | GST1 | HV side nominal voltage | FLOAT | RW | 0.001...500
113 | S12 | GST1 | LV side nominal voltage | FLOAT | RW | 0.001...500
113 | S13 | GST1 | Transformer Zk % | FLOAT | RW | 0.001...25
113 | S14 | GST1 | Transformer nom freq. | FLOAT | RW | 10...75
113 | S15 | GST1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
113 | I13 | GST1 | HV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I14 | GST1 | HV side nominal current(pri) Scaled to Gnom | FLOAT | R | 0.01...50000
113 | I15 | GST1 | HV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I16 | GST1 | HV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I17 | GST1 | LV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I18 | GST1 | LV side nominal current factor between Gnom and Tnom | FLOAT | R | 0.01...50000
113 | I19 | GST1 | LV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I20 | GST1 | LV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I21 | GST1 | Transformer nom impedance | FLOAT | R | 0.01...250
113 | I22 | GST1 | Transformer nom Zk ohm | FLOAT | R | 0.01...250
113 | I23 | GST1 | Transformer nom SC inductance | FLOAT | R | 0.001...100
113 | I24 | GST1 | LV side max 3ph SC curr | FLOAT | R | 0.001...500
113 | I25 | GST1 | LV side 3ph SC to HV side | FLOAT | R | 0.001...500
113 | I26 | GST1 | LV side max 2ph SC curr | FLOAT | R | 0.001...500
113 | I27 | GST1 | LV side 2ph SC to HV side | FLOAT | R | 0.001...500
113 | I28 | GST1 | Trafo HV nominal current | FLOAT | R | 0.01...50000
113 | I29 | GST1 | Trafo LV nominal current | FLOAT | R | 0.01...50000
113 | O1 | GST1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
113 | O2 | GST1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O3 | GST1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O4 | GST1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
113 | O5 | GST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | O6 | GST1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | I30 | GST1 | Newest register | UINT32 | R | 0...12
113 | I31 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I32 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I33 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I34 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I35 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I36 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I37 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I38 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I39 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I40 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I41 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I42 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I43 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I44 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I45 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I46 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I47 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I48 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I49 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I50 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I51 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I52 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I53 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I54 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I55 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I56 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I57 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I58 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I59 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I60 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I61 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I62 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I63 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I64 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I65 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I66 | GST1 | L3 Current | FLOAT | R | 0...250
113 | S16 | GST1 | EventMaskLo | UINT32 | RW | 0...4294967295
164 | S1 | PWR1 | PQS>/< [32] mode | UINT32 | RW | 0=Disabled;1=Activated
164 | V1 | PWR1 | PQS>/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
164 | I1 | PWR1 | Meas/Set at the moment | FLOAT | R | -1250...1250
164 | I2 | PWR1 | Meas/Nom at the moment | FLOAT | R | -1250...1250
164 | I3 | PWR1 | PQS>/< starts | UINT32 | R | 0...4294967295
164 | I4 | PWR1 | PQS>/< trips | UINT32 | R | 0...4294967295
164 | I5 | PWR1 | PQS>/< blocks | UINT32 | R | 0...4294967295
164 | S2 | PWR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
164 | S3 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG1
164 | S4 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG2
164 | S5 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG3
164 | S6 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG4
164 | S7 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG5
164 | S8 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG6
164 | S9 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG7
164 | S10 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500 | SG8
164 | S11 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
164 | S12 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
164 | S13 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
164 | S14 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
164 | S15 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
164 | S16 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
164 | S17 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
164 | S18 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
164 | O1 | PWR1 | PQS>/< START | SIGNAL_OUT | RW | 0...4294967295
164 | O2 | PWR1 | PQS>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
164 | O3 | PWR1 | PQS>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
164 | I6 | PWR1 | Newest register | UINT32 | R | 0...12
164 | I7 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I8 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I9 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I10 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I11 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I12 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I13 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I14 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I15 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I16 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I17 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I18 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | S19 | PWR1 | EventMaskLo | UINT32 | RW | 0...4294967295
165 | S1 | PWR2 | PQS>>/<< [32] mode | UINT32 | RW | 0=Disabled;1=Activated
165 | V1 | PWR2 | PQS>>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
165 | I1 | PWR2 | Meas/Set at the moment | FLOAT | R | -1250...1250
165 | I2 | PWR2 | Meas/Nom at the moment | FLOAT | R | -1250...1250
165 | I3 | PWR2 | PQS>>/<< starts | UINT32 | R | 0...4294967295
165 | I4 | PWR2 | PQS>>/<< trips | UINT32 | R | 0...4294967295
165 | I5 | PWR2 | PQS>>/<< blocks | UINT32 | R | 0...4294967295
165 | S2 | PWR2 | Clear statistics | UINT32 | W | 0=-;1=Clear
165 | S3 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG1
165 | S4 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG2
165 | S5 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG3
165 | S6 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG4
165 | S7 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG5
165 | S8 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG6
165 | S9 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG7
165 | S10 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500 | SG8
165 | S11 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
165 | S12 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
165 | S13 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
165 | S14 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
165 | S15 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
165 | S16 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
165 | S17 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
165 | S18 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
165 | O1 | PWR2 | PQS>>/<< START | SIGNAL_OUT | RW | 0...4294967295
165 | O2 | PWR2 | PQS>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
165 | O3 | PWR2 | PQS>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
165 | I6 | PWR2 | Newest register | UINT32 | R | 0...12
165 | I7 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I8 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I9 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I10 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I11 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I12 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I13 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I14 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I15 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I16 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I17 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I18 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | S19 | PWR2 | EventMaskLo | UINT32 | RW | 0...4294967295
166 | S1 | PWR3 | PQS>>>/<<< [32] mode | UINT32 | RW | 0=Disabled;1=Activated
166 | V1 | PWR3 | PQS>>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
166 | I1 | PWR3 | Meas/Set at the moment | FLOAT | R | -1250...1250
166 | I2 | PWR3 | Meas/Nom at the moment | FLOAT | R | -1250...1250
166 | I3 | PWR3 | PQS>>>/<<< starts | UINT32 | R | 0...4294967295
166 | I4 | PWR3 | PQS>>>/<<< trips | UINT32 | R | 0...4294967295
166 | I5 | PWR3 | PQS>>>/<<< blocks | UINT32 | R | 0...4294967295
166 | S2 | PWR3 | Clear statistics | UINT32 | W | 0=-;1=Clear
166 | S3 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG1
166 | S4 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG2
166 | S5 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG3
166 | S6 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG4
166 | S7 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG5
166 | S8 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG6
166 | S9 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG7
166 | S10 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500 | SG8
166 | S11 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
166 | S12 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
166 | S13 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
166 | S14 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
166 | S15 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
166 | S16 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
166 | S17 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
166 | S18 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
166 | O1 | PWR3 | PQS>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
166 | O2 | PWR3 | PQS>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
166 | O3 | PWR3 | PQS>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
166 | I6 | PWR3 | Newest register | UINT32 | R | 0...12
166 | I7 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I8 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I9 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I10 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I11 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I12 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I13 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I14 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I15 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I16 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I17 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I18 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | S19 | PWR3 | EventMaskLo | UINT32 | RW | 0...4294967295
167 | S1 | PWR4 | PQS>>>>/<<<< [32] mode | UINT32 | RW | 0=Disabled;1=Activated
167 | V1 | PWR4 | PQS>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
167 | I1 | PWR4 | Meas/Set at the moment | FLOAT | R | -1250...1250
167 | I2 | PWR4 | Meas/Nom at the moment | FLOAT | R | -1250...1250
167 | I3 | PWR4 | PQS>>>>/<<<< starts | UINT32 | R | 0...4294967295
167 | I4 | PWR4 | PQS>>>>/<<<< trips | UINT32 | R | 0...4294967295
167 | I5 | PWR4 | PQS>>>>/<<<< blocks | UINT32 | R | 0...4294967295
167 | S2 | PWR4 | Clear statistics | UINT32 | W | 0=-;1=Clear
167 | S3 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG1
167 | S4 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG2
167 | S5 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG3
167 | S6 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG4
167 | S7 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG5
167 | S8 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG6
167 | S9 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG7
167 | S10 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500 | SG8
167 | S11 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
167 | S12 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
167 | S13 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
167 | S14 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
167 | S15 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
167 | S16 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
167 | S17 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
167 | S18 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
167 | O1 | PWR4 | PQS>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
167 | O2 | PWR4 | PQS>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
167 | O3 | PWR4 | PQS>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
167 | I6 | PWR4 | Newest register | UINT32 | R | 0...12
167 | I7 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I8 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I9 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I10 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I11 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I12 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I13 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I14 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I15 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I16 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I17 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I18 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | S19 | PWR4 | EventMaskLo | UINT32 | RW | 0...4294967295
100 | S1 | OPW1 | P> [32] mode (OBSOLETE) | UINT32 | RW | 0=Disabled;1=Activated
100 | V1 | OPW1 | P> condition (OBSOLETE) | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
100 | O1 | OPW1 | P> START (OBSOLETE) | SIGNAL_OUT | RW | 0...4294967295
100 | O2 | OPW1 | P> TRIP (OBSOLETE) | SIGNAL_OUT | RW | 0...4294967295
101 | S1 | UPW1 | P< [37] mode (OBSOLETE) | UINT32 | RW | 0=Disabled;1=Activated
101 | V1 | UPW1 | P< condition (OBSOLETE) | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
101 | O1 | UPW1 | P< START (OBSOLETE) | SIGNAL_OUT | RW | 0...4294967295
101 | O2 | UPW1 | P< TRIP (OBSOLETE) | SIGNAL_OUT | RW | 0...4294967295
102 | S1 | RPW1 | Prev> [32] mode (OBSOLETE) | UINT32 | RW | 0=Disabled;1=Activated
102 | V1 | RPW1 | Prev> condition (OBSOLETE) | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
102 | O1 | RPW1 | Prev> START (OBSOLETE) | SIGNAL_OUT | RW | 0...4294967295
102 | O2 | RPW1 | Prev> TRIP (OBSOLETE) | SIGNAL_OUT | RW | 0...4294967295
110 | S1 | SEF1 | U03rd< [64S] mode | UINT32 | RW | 0=Disabled;1=Activated
110 | V1 | SEF1 | U03rd< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
110 | I1 | SEF1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
110 | I2 | SEF1 | Measured U0 3rd harm (%) | FLOAT | R | 0...1250
110 | I3 | SEF1 | Measured U0 3rd harm (Pri) | FLOAT | R | 0...1250
110 | I4 | SEF1 | U03rd< starts | UINT32 | R | 0...4294967295
110 | I5 | SEF1 | U03rd< trips | UINT32 | R | 0...4294967295
110 | I6 | SEF1 | U03rd< blocks | UINT32 | R | 0...4294967295
110 | S2 | SEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
110 | S3 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG1
110 | S4 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG2
110 | S5 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG3
110 | S6 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG4
110 | S7 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG5
110 | S8 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG6
110 | S9 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG7
110 | S10 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95 | SG8
110 | S11 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG1
110 | S12 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG2
110 | S13 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG3
110 | S14 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG4
110 | S15 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG5
110 | S16 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG6
110 | S17 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG7
110 | S18 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1 | SG8
110 | S19 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
110 | S20 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
110 | S21 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
110 | S22 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
110 | S23 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
110 | S24 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
110 | S25 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
110 | S26 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
110 | O1 | SEF1 | U03rd< START | SIGNAL_OUT | RW | 0...4294967295
110 | O2 | SEF1 | U03rd< TRIP | SIGNAL_OUT | RW | 0...4294967295
110 | O3 | SEF1 | U03rd< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
110 | I7 | SEF1 | Newest register | UINT32 | R | 0...12
110 | I8 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I9 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I10 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I11 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I12 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I13 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I14 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I15 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I16 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I17 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I18 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I19 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I20 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I21 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I22 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I23 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I24 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I25 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I26 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I27 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I28 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I29 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I30 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I31 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | S27 | SEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
109 | S1 | UEX1 | Q< [40] mode | UINT32 | RW | 0=Disabled;1=Activated
109 | V1 | UEX1 | Q< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
109 | I1 | UEX1 | Qmeas/Qset at the moment | FLOAT | R | -1250...1250
109 | I2 | UEX1 | Q< starts | UINT32 | R | 0...4294967295
109 | I3 | UEX1 | Q< trips | UINT32 | R | 0...4294967295
109 | I4 | UEX1 | Q< blocks | UINT32 | R | 0...4294967295
109 | S2 | UEX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
109 | S3 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG1
109 | S4 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG2
109 | S5 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG3
109 | S6 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG4
109 | S7 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG5
109 | S8 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG6
109 | S9 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG7
109 | S10 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent | SG8
109 | S11 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG1
109 | S12 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG2
109 | S13 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG3
109 | S14 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG4
109 | S15 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG5
109 | S16 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG6
109 | S17 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG7
109 | S18 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0 | SG8
109 | S19 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG1
109 | S20 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG2
109 | S21 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG3
109 | S22 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG4
109 | S23 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG5
109 | S24 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG6
109 | S25 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG7
109 | S26 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000 | SG8
109 | S27 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG1
109 | S28 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG2
109 | S29 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG3
109 | S30 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG4
109 | S31 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG5
109 | S32 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG6
109 | S33 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG7
109 | S34 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0 | SG8
109 | S35 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG1
109 | S36 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG2
109 | S37 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG3
109 | S38 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG4
109 | S39 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG5
109 | S40 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG6
109 | S41 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG7
109 | S42 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000 | SG8
109 | S43 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
109 | S44 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
109 | S45 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
109 | S46 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
109 | S47 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
109 | S48 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
109 | S49 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
109 | S50 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
109 | O1 | UEX1 | Q< START | SIGNAL_OUT | RW | 0...4294967295
109 | O2 | UEX1 | Q< TRIP | SIGNAL_OUT | RW | 0...4294967295
109 | O3 | UEX1 | Q< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
109 | I5 | UEX1 | Newest register | UINT32 | R | 0...12
109 | I6 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I7 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I8 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I9 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I10 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I11 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I12 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I13 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I14 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I15 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I16 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I17 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I18 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I19 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I20 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I21 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I22 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I23 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I24 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I25 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I26 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I27 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I28 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I29 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | S51 | UEX1 | EventMaskLo | UINT32 | RW | 0...4294967295
111 | S1 | UIM1 | Z< [21U] mode | UINT32 | RW | 0=Disabled;1=Activated
111 | V1 | UIM1 | Z< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
111 | I1 | UIM1 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
111 | I2 | UIM1 | Z< starts | UINT32 | R | 0...4294967295
111 | I3 | UIM1 | Z< trips | UINT32 | R | 0...4294967295
111 | I4 | UIM1 | Z< blocks | UINT32 | R | 0...4294967295
111 | S2 | UIM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
111 | S3 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG1
111 | S4 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG2
111 | S5 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG3
111 | S6 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG4
111 | S7 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG5
111 | S8 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG6
111 | S9 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG7
111 | S10 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG8
111 | S11 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
111 | S12 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
111 | S13 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
111 | S14 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
111 | S15 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
111 | S16 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
111 | S17 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
111 | S18 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
111 | O1 | UIM1 | Z< START | SIGNAL_OUT | RW | 0...4294967295
111 | O2 | UIM1 | Z< TRIP | SIGNAL_OUT | RW | 0...4294967295
111 | O3 | UIM1 | Z< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
111 | I5 | UIM1 | Newest register | UINT32 | R | 0...12
111 | I6 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I7 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I8 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I9 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I10 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I11 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I12 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I13 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I14 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I15 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I16 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I17 | UIM1 | Z1 fault impedance | FLOAT | R | 0...250
111 | I18 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I19 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I20 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I21 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I22 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I23 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I24 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I25 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I26 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I27 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I28 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I29 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I30 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I31 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I32 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I33 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I34 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I35 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I36 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I37 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I38 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I39 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I40 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I41 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | S19 | UIM1 | EventMaskLo | UINT32 | RW | 0...4294967295
149 | S1 | UIM2 | Z<< [21U] mode | UINT32 | RW | 0=Disabled;1=Activated
149 | V1 | UIM2 | Z<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
149 | I1 | UIM2 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
149 | I2 | UIM2 | Z<< starts | UINT32 | R | 0...4294967295
149 | I3 | UIM2 | Z<< trips | UINT32 | R | 0...4294967295
149 | I4 | UIM2 | Z<< blocks | UINT32 | R | 0...4294967295
149 | S2 | UIM2 | Clear statistics | UINT32 | W | 0=-;1=Clear
149 | S3 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG1
149 | S4 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG2
149 | S5 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG3
149 | S6 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG4
149 | S7 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG5
149 | S8 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG6
149 | S9 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG7
149 | S10 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150 | SG8
149 | S11 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
149 | S12 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
149 | S13 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
149 | S14 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
149 | S15 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
149 | S16 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
149 | S17 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
149 | S18 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
149 | O1 | UIM2 | Z<< START | SIGNAL_OUT | RW | 0...4294967295
149 | O2 | UIM2 | Z<< TRIP | SIGNAL_OUT | RW | 0...4294967295
149 | O3 | UIM2 | Z<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
149 | I5 | UIM2 | Newest register | UINT32 | R | 0...12
149 | I6 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I7 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I8 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I9 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I10 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I11 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I12 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I13 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I14 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I15 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I16 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I17 | UIM2 | Z1 fault impedance | FLOAT | R | 0...250
149 | I18 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I19 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I20 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I21 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I22 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I23 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I24 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I25 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I26 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I27 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I28 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I29 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I30 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I31 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I32 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I33 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I34 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I35 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I36 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I37 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I38 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I39 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I40 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I41 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | S19 | UIM2 | EventMaskLo | UINT32 | RW | 0...4294967295
196 | S1 | URX1 | X< [40] mode | UINT32 | RW | 0=Disabled;1=Activated
196 | V1 | URX1 | X< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
196 | I1 | URX1 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
196 | I2 | URX1 | X< starts | UINT32 | R | 0...4294967295
196 | I3 | URX1 | X< trips | UINT32 | R | 0...4294967295
196 | I4 | URX1 | X< blocks | UINT32 | R | 0...4294967295
196 | S2 | URX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
196 | S3 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG1
196 | S4 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG2
196 | S5 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG3
196 | S6 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG4
196 | S7 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG5
196 | S8 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG6
196 | S9 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG7
196 | S10 | URX1 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG8
196 | S11 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG1
196 | S12 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG2
196 | S13 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG3
196 | S14 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG4
196 | S15 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG5
196 | S16 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG6
196 | S17 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG7
196 | S18 | URX1 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG8
196 | S19 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
196 | S20 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
196 | S21 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
196 | S22 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
196 | S23 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
196 | S24 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
196 | S25 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
196 | S26 | URX1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
196 | O1 | URX1 | X< START | SIGNAL_OUT | RW | 0...4294967295
196 | O2 | URX1 | X< TRIP | SIGNAL_OUT | RW | 0...4294967295
196 | O3 | URX1 | X< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
196 | I5 | URX1 | Newest register | UINT32 | R | 0...12
196 | I6 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I7 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I8 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I9 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I10 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I11 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I12 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I13 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I14 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I15 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I16 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I17 | URX1 | Z1 fault impedance | FLOAT | R | 0...250
196 | I18 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I19 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I20 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I21 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I22 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I23 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I24 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I25 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I26 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I27 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I28 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I29 | URX1 | Z2 fault impedance | FLOAT | R | 0...250
196 | I30 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I31 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I32 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I33 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I34 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I35 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I36 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I37 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I38 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I39 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I40 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | I41 | URX1 | Z3 fault impedance | FLOAT | R | 0...250
196 | S27 | URX1 | EventMaskLo | UINT32 | RW | 0...4294967295
197 | S1 | URX2 | X<< [40] mode | UINT32 | RW | 0=Disabled;1=Activated
197 | V1 | URX2 | X<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
197 | I1 | URX2 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
197 | I2 | URX2 | X<< starts | UINT32 | R | 0...4294967295
197 | I3 | URX2 | X<< trips | UINT32 | R | 0...4294967295
197 | I4 | URX2 | X<< blocks | UINT32 | R | 0...4294967295
197 | S2 | URX2 | Clear statistics | UINT32 | W | 0=-;1=Clear
197 | S3 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG1
197 | S4 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG2
197 | S5 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG3
197 | S6 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG4
197 | S7 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG5
197 | S8 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG6
197 | S9 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG7
197 | S10 | URX2 | X circle offset (pri) | FLOAT | RW | -50000...50000 | SG8
197 | S11 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG1
197 | S12 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG2
197 | S13 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG3
197 | S14 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG4
197 | S15 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG5
197 | S16 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG6
197 | S17 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG7
197 | S18 | URX2 | RX circle radius (pri) | FLOAT | RW | 0.01...50000 | SG8
197 | S19 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG1
197 | S20 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG2
197 | S21 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG3
197 | S22 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG4
197 | S23 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG5
197 | S24 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG6
197 | S25 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG7
197 | S26 | URX2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800 | SG8
197 | O1 | URX2 | X<< START | SIGNAL_OUT | RW | 0...4294967295
197 | O2 | URX2 | X<< TRIP | SIGNAL_OUT | RW | 0...4294967295
197 | O3 | URX2 | X<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
197 | I5 | URX2 | Newest register | UINT32 | R | 0...12
197 | I6 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I7 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I8 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I9 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I10 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I11 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I12 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I13 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I14 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I15 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I16 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I17 | URX2 | Z1 fault impedance | FLOAT | R | 0...250
197 | I18 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I19 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I20 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I21 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I22 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I23 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I24 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I25 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I26 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I27 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I28 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I29 | URX2 | Z2 fault impedance | FLOAT | R | 0...250
197 | I30 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I31 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I32 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I33 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I34 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I35 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I36 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I37 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I38 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I39 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I40 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | I41 | URX2 | Z3 fault impedance | FLOAT | R | 0...250
197 | S27 | URX2 | EventMaskLo | UINT32 | RW | 0...4294967295
112 | S1 | VOC1 | Iv> [51V] mode | UINT32 | RW | 0=Disabled;1=Activated
112 | V1 | VOC1 | Iv> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
112 | I1 | VOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
112 | I2 | VOC1 | Iv> starts | UINT32 | R | 0...4294967295
112 | I3 | VOC1 | Iv> trips | UINT32 | R | 0...4294967295
112 | I4 | VOC1 | Iv> blocks | UINT32 | R | 0...4294967295
112 | S2 | VOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
112 | S3 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG1
112 | S4 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG2
112 | S5 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG3
112 | S6 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG4
112 | S7 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG5
112 | S8 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG6
112 | S9 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG7
112 | S10 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40 | SG8
112 | S11 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG1
112 | S12 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG2
112 | S13 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG3
112 | S14 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG4
112 | S15 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG5
112 | S16 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG6
112 | S17 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG7
112 | S18 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40 | SG8
112 | S19 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG1
112 | S20 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG2
112 | S21 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG3
112 | S22 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG4
112 | S23 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG5
112 | S24 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG6
112 | S25 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG7
112 | S26 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150 | SG8
112 | S27 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG1
112 | S28 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG2
112 | S29 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG3
112 | S30 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG4
112 | S31 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG5
112 | S32 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG6
112 | S33 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG7
112 | S34 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150 | SG8
112 | S35 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
112 | S36 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
112 | S37 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
112 | S38 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
112 | S39 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
112 | S40 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
112 | S41 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
112 | S42 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
112 | O1 | VOC1 | Iv> START | SIGNAL_OUT | RW | 0...4294967295
112 | O2 | VOC1 | Iv> TRIP | SIGNAL_OUT | RW | 0...4294967295
112 | O3 | VOC1 | Iv> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
112 | I5 | VOC1 | Newest register | UINT32 | R | 0...12
112 | I6 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I7 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I8 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I9 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I10 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I11 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I12 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I13 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I14 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I15 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I16 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I17 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I18 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I19 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I20 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I21 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I22 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I23 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I24 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I25 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I26 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I27 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I28 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I29 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I30 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I31 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I32 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I33 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I34 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I35 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I36 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I37 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I38 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I39 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I40 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I41 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I42 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I43 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I44 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I45 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I46 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I47 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I48 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I49 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I50 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I51 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I52 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I53 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I54 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I55 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I56 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I57 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I58 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I59 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I60 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I61 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I62 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I63 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I64 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I65 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | S43 | VOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
161 | S1 | IAE1 | I>U< I.A.E. [50/27] mode | UINT32 | RW | 0=Disabled;1=Activated
161 | V1 | IAE1 | I>U< I.A.E. condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
161 | I1 | IAE1 | I>U< I.A.E. starts | UINT32 | R | 0...4294967295
161 | I2 | IAE1 | I>U< I.A.E. trips | UINT32 | R | 0...4294967295
161 | I3 | IAE1 | I>U< I.A.E. blocks | UINT32 | R | 0...4294967295
161 | S2 | IAE1 | Clear statistics | UINT32 | W | 0=-;1=Clear
161 | S3 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG1
161 | S4 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG2
161 | S5 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG3
161 | S6 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG4
161 | S7 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG5
161 | S8 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG6
161 | S9 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG7
161 | S10 | IAE1 | Voltage limit U< | FLOAT | RW | 0...99 | SG8
161 | S11 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG1
161 | S12 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG2
161 | S13 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG3
161 | S14 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG4
161 | S15 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG5
161 | S16 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG6
161 | S17 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG7
161 | S18 | IAE1 | Time delay for U< activation | FLOAT | RW | 0...1800 | SG8
161 | S19 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG1
161 | S20 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG2
161 | S21 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG3
161 | S22 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG4
161 | S23 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG5
161 | S24 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG6
161 | S25 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG7
161 | S26 | IAE1 | Current limit I>/< | FLOAT | RW | 0.05...3 | SG8
161 | S27 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG1
161 | S28 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG2
161 | S29 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG3
161 | S30 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG4
161 | S31 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG5
161 | S32 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG6
161 | S33 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG7
161 | S34 | IAE1 | Time delay for releasing start condition | FLOAT | RW | 0...1800 | SG8
161 | O1 | IAE1 | I>U< I.A.E. START | SIGNAL_OUT | RW | 0...4294967295
161 | O2 | IAE1 | I>U< I.A.E. TRIP | SIGNAL_OUT | RW | 0...4294967295
161 | O3 | IAE1 | I>U< I.A.E. BLOCKED | SIGNAL_OUT | RW | 0...4294967295
161 | I4 | IAE1 | Newest register | UINT32 | R | 0...12
161 | I5 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I6 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I7 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I8 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I9 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I10 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I11 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I12 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I13 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I14 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I15 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I16 | IAE1 | Phase AB voltage | FLOAT | R | 0...250
161 | I17 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I18 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I19 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I20 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I21 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I22 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I23 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I24 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I25 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I26 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I27 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I28 | IAE1 | Phase BC voltage | FLOAT | R | 0...250
161 | I29 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I30 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I31 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I32 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I33 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I34 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I35 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I36 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I37 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I38 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I39 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | I40 | IAE1 | Phase CA voltage | FLOAT | R | 0...250
161 | S35 | IAE1 | EventMaskLo | UINT32 | RW | 0...4294967295
128 | S1 | VHZ1 | V/Hz > [24] mode | UINT32 | RW | 0=Disabled;1=Activated
128 | S2 | VHZ1 | V/Hz(1) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V1 | VHZ1 | V/Hz(1) > condition | UINT32 | R | 0=Normal;1=Start;;2=Alarm;3=Trip;4=Blocked
128 | I1 | VHZ1 | V/Hz(1) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | S3 | VHZ1 | V/Hz(2) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V2 | VHZ1 | V/Hz(2) > condition | UINT32 | R | 0=Normal;1=Start;;2=Alarm;3=Trip;4=Blocked
128 | I2 | VHZ1 | V/Hz(2) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | I3 | VHZ1 | U/f at the moment | FLOAT | R | -100...100
128 | I4 | VHZ1 | U/f atm to nominal U/f ratio | FLOAT | R | -100...100
128 | I5 | VHZ1 | V/Hz(1) > Starts | UINT32 | R | 0...4294967295
128 | I6 | VHZ1 | V/Hz(1) > Alarms | UINT32 | R | 0...4294967295
128 | I7 | VHZ1 | V/Hz(1) > Trips | UINT32 | R | 0...4294967295
128 | I8 | VHZ1 | V/Hz(1) > Blocks | UINT32 | R | 0...4294967295
128 | I9 | VHZ1 | V/Hz(2) > Starts | UINT32 | R | 0...4294967295
128 | I10 | VHZ1 | V/Hz(2) > Alarms | UINT32 | R | 0...4294967295
128 | I11 | VHZ1 | V/Hz(2) > Trips | UINT32 | R | 0...4294967295
128 | I12 | VHZ1 | V/Hz(2) > Blocks | UINT32 | R | 0...4294967295
128 | S4 | VHZ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
128 | S5 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG1
128 | S6 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG2
128 | S7 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG3
128 | S8 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG4
128 | S9 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG5
128 | S10 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG6
128 | S11 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG7
128 | S12 | VHZ1 | V/Hz(1) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG8
128 | S13 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG1
128 | S14 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG2
128 | S15 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG3
128 | S16 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG4
128 | S17 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG5
128 | S18 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG6
128 | S19 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG7
128 | S20 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG8
128 | S21 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG1
128 | S22 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG2
128 | S23 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG3
128 | S24 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG4
128 | S25 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG5
128 | S26 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG6
128 | S27 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG7
128 | S28 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800 | SG8
128 | S29 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG1
128 | S30 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG2
128 | S31 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG3
128 | S32 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG4
128 | S33 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG5
128 | S34 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG6
128 | S35 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG7
128 | S36 | VHZ1 | V/Hz(2) > pick-up (% of nominal) | FLOAT | RW | 0.01...75 | SG8
128 | S37 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG1
128 | S38 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG2
128 | S39 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG3
128 | S40 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG4
128 | S41 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG5
128 | S42 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG6
128 | S43 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG7
128 | S44 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800 | SG8
128 | S45 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG1
128 | S46 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG2
128 | S47 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG3
128 | S48 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG4
128 | S49 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG5
128 | S50 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG6
128 | S51 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG7
128 | S52 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800 | SG8
128 | O1 | VHZ1 | V/Hz(1) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O2 | VHZ1 | V/Hz(1) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O3 | VHZ1 | V/Hz(1) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O4 | VHZ1 | V/Hz(1) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | O5 | VHZ1 | V/Hz(2) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O6 | VHZ1 | V/Hz(2) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O7 | VHZ1 | V/Hz(2) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O8 | VHZ1 | V/Hz(2) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | I13 | VHZ1 | Newest register | UINT32 | R | 0...12
128 | I14 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I15 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I16 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I17 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I18 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I19 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I20 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I21 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I22 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I23 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I24 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I25 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I26 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I27 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I28 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I29 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I30 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I31 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I32 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I33 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I34 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I35 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I36 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I37 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I38 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I39 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I40 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I41 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I42 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I43 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I44 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I45 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I46 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I47 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I48 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I49 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I50 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I51 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I52 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I53 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I54 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I55 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I56 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I57 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I58 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I59 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I60 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I61 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I62 | VHZ1 | Newest register | UINT32 | R | 0...12
128 | I63 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I64 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I65 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I66 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I67 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I68 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I69 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I70 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I71 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I72 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I73 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I74 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I75 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I76 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I77 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I78 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I79 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I80 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I81 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I82 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I83 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I84 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I85 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I86 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I87 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I88 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I89 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I90 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I91 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I92 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I93 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I94 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I95 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I96 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I97 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I98 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I99 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I100 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I101 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I102 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I103 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I104 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I105 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I106 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I107 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I108 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I109 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I110 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | S53 | VHZ1 | EventMaskLo | UINT32 | RW | 0...4294967295
129 | S1 | UPF1 | PF< [55] mode | UINT32 | RW | 0=Disabled;1=Activated
129 | V1 | UPF1 | PF< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
129 | S2 | UPF1 | Available modes | UINT32 | RW | 0=Trip;1=Trip and Alarm
129 | I1 | UPF1 | PFmeas/PFalarm at the moment | FLOAT | R | 0...1250
129 | I2 | UPF1 | PFmeas/PFtrip at the moment | FLOAT | R | 0...1250
129 | I3 | UPF1 | PF< Alarm Starts | UINT32 | R | 0...4294967295
129 | I4 | UPF1 | PF< Alarms | UINT32 | R | 0...4294967295
129 | I5 | UPF1 | PF< Starts | UINT32 | R | 0...4294967295
129 | I6 | UPF1 | PF< Trips | UINT32 | R | 0...4294967295
129 | I7 | UPF1 | PF< Blocks | UINT32 | R | 0...4294967295
129 | S3 | UPF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
129 | S4 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG1
129 | S5 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG2
129 | S6 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG3
129 | S7 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG4
129 | S8 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG5
129 | S9 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG6
129 | S10 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG7
129 | S11 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99 | SG8
129 | S12 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG1
129 | S13 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG2
129 | S14 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG3
129 | S15 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG4
129 | S16 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG5
129 | S17 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG6
129 | S18 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG7
129 | S19 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800 | SG8
129 | S20 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG1
129 | S21 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG2
129 | S22 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG3
129 | S23 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG4
129 | S24 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG5
129 | S25 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG6
129 | S26 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG7
129 | S27 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99 | SG8
129 | S28 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG1
129 | S29 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG2
129 | S30 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG3
129 | S31 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG4
129 | S32 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG5
129 | S33 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG6
129 | S34 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG7
129 | S35 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800 | SG8
129 | O1 | UPF1 | PF< START | SIGNAL_OUT | RW | 0...4294967295
129 | O2 | UPF1 | PF< TRIP | SIGNAL_OUT | RW | 0...4294967295
129 | O3 | UPF1 | PF< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
129 | I8 | UPF1 | Newest register | UINT32 | R | 0...12
129 | I9 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I10 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I11 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I12 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I13 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I14 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I15 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I16 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I17 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I18 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I19 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I20 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | S36 | UPF1 | EventMaskLo | UINT32 | RW | 0...4294967295
189 | S1 | LDIF1 | IdL> mode | UINT32 | RW | 0=Disabled;1=Activated
189 | V1 | LDIF1 | IdL> condition | UINT32 | R | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On
189 | I1 | LDIF1 | Idb> trips | UINT32 | R | 0...4294967295
189 | I2 | LDIF1 | Idb> f2h blocks | UINT32 | R | 0...4294967295
189 | I3 | LDIF1 | Idb> f5h blocks | UINT32 | R | 0...4294967295
189 | I4 | LDIF1 | Idb> Ext blocks | UINT32 | R | 0...4294967295
189 | I5 | LDIF1 | Idi> trips | UINT32 | R | 0...4294967295
189 | I6 | LDIF1 | Idi> Ext blocks | UINT32 | R | 0...4294967295
189 | S2 | LDIF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
189 | I7 | LDIF1 | L1 Bias current | FLOAT | R | 0...50
189 | I8 | LDIF1 | L1 Diff current | FLOAT | R | 0...4000
189 | I9 | LDIF1 | L1 Char current | FLOAT | R | 0...4000
189 | I10 | LDIF1 | L2 Bias current | FLOAT | R | 0...50
189 | I11 | LDIF1 | L2 Diff current | FLOAT | R | 0...4000
189 | I12 | LDIF1 | L2 Char current | FLOAT | R | 0...4000
189 | I13 | LDIF1 | L3 Bias current | FLOAT | R | 0...50
189 | I14 | LDIF1 | L3 Diff current | FLOAT | R | 0...4000
189 | I15 | LDIF1 | L3 Char current | FLOAT | R | 0...4000
189 | S3 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S4 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S5 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S6 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S7 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S8 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S9 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S10 | LDIF1 | Differential calculation mode | UINT32 | RW | 0=Subtract;1=Add
189 | S11 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S12 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S13 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S14 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S15 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S16 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S17 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S18 | LDIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
189 | S19 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG1
189 | S20 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG2
189 | S21 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG3
189 | S22 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG4
189 | S23 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG5
189 | S24 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG6
189 | S25 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG7
189 | S26 | LDIF1 | Idb> Pickup | FLOAT | RW | 0.01...100 | SG8
189 | S27 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG1
189 | S28 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG2
189 | S29 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG3
189 | S30 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG4
189 | S31 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG5
189 | S32 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG6
189 | S33 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG7
189 | S34 | LDIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50 | SG8
189 | S35 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG1
189 | S36 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG2
189 | S37 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG3
189 | S38 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG4
189 | S39 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG5
189 | S40 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG6
189 | S41 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG7
189 | S42 | LDIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250 | SG8
189 | S43 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG1
189 | S44 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG2
189 | S45 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG3
189 | S46 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG4
189 | S47 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG5
189 | S48 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG6
189 | S49 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG7
189 | S50 | LDIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50 | SG8
189 | S51 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG1
189 | S52 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG2
189 | S53 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG3
189 | S54 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG4
189 | S55 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG5
189 | S56 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG6
189 | S57 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG7
189 | S58 | LDIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250 | SG8
189 | S59 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S60 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S61 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S62 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S63 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S64 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S65 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S66 | LDIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
189 | S67 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG1
189 | S68 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG2
189 | S69 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG3
189 | S70 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG4
189 | S71 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG5
189 | S72 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG6
189 | S73 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG7
189 | S74 | LDIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50 | SG8
189 | S75 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG1
189 | S76 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG2
189 | S77 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG3
189 | S78 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG4
189 | S79 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG5
189 | S80 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG6
189 | S81 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG7
189 | S82 | LDIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50 | SG8
189 | S83 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S84 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S85 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S86 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S87 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S88 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S89 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S90 | LDIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
189 | S91 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG1
189 | S92 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG2
189 | S93 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG3
189 | S94 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG4
189 | S95 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG5
189 | S96 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG6
189 | S97 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG7
189 | S98 | LDIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500 | SG8
189 | O1 | LDIF1 | IdLb> BIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
189 | O2 | LDIF1 | IdLb> BIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
189 | O3 | LDIF1 | IdLi> NOBIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
189 | O4 | LDIF1 | IdLi> NOBIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
189 | O5 | LDIF1 | IdL> 2nd harm. block on | SIGNAL_OUT | RW | 0...4294967295
189 | O6 | LDIF1 | IdL> 5th harm. block on | SIGNAL_OUT | RW | 0...4294967295
189 | I16 | LDIF1 | Newest register | UINT32 | R | 0...12
189 | I17 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I18 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I19 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I20 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I21 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I22 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I23 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I24 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I25 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I26 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I27 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I28 | LDIF1 | L1 Bias current | FLOAT | R | 0...250
189 | I29 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I30 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I31 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I32 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I33 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I34 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I35 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I36 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I37 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I38 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I39 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I40 | LDIF1 | L1 Differential current | FLOAT | R | 0...250
189 | I41 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I42 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I43 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I44 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I45 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I46 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I47 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I48 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I49 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I50 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I51 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I52 | LDIF1 | L1 Characteristics current | FLOAT | R | 0...250
189 | I53 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I54 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I55 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I56 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I57 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I58 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I59 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I60 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I61 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I62 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I63 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I64 | LDIF1 | L2 Bias current | FLOAT | R | 0...250
189 | I65 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I66 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I67 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I68 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I69 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I70 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I71 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I72 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I73 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I74 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I75 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I76 | LDIF1 | L2 Differential current | FLOAT | R | 0...250
189 | I77 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I78 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I79 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I80 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I81 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I82 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I83 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I84 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I85 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I86 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I87 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I88 | LDIF1 | L2 Characteristics current | FLOAT | R | 0...250
189 | I89 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I90 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I91 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I92 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I93 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I94 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I95 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I96 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I97 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I98 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I99 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I100 | LDIF1 | L3 Bias current | FLOAT | R | 0...250
189 | I101 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I102 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I103 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I104 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I105 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I106 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I107 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I108 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I109 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I110 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I111 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I112 | LDIF1 | L3 Differential current | FLOAT | R | 0...250
189 | I113 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I114 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I115 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I116 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I117 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I118 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I119 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I120 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I121 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I122 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I123 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | I124 | LDIF1 | L3 Characteristics current | FLOAT | R | 0...250
189 | V2 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V3 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V4 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V5 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V6 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V7 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V8 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V9 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V10 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V11 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V12 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | V13 | LDIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
189 | S99 | LDIF1 | EventMaskLo | UINT32 | RW | 0...4294967295
189 | S100 | LDIF1 | EventMaskHi | UINT32 | RW | 0...4294967295
239 | O1 | PVPS | PVPS Line comm ok | SIGNAL_OUT | RW | 0...4294967295
239 | O2 | PVPS | PVPS Line comm failure | SIGNAL_OUT | RW | 0...4294967295
239 | O3 | PVPS | PVPS Any line protection failure | SIGNAL_OUT | RW | 0...4294967295
239 | O4 | PVPS | PVPS Units synchronization Ok | SIGNAL_OUT | RW | 0...4294967295
239 | O5 | PVPS | PVPS Synchronization lost | SIGNAL_OUT | RW | 0...4294967295
141 | I1 | RTDIN | S1 Measurement(Raw) | FLOAT | R | -200...2000
141 | I2 | RTDIN | S1 Resistance | FLOAT | R | 0...4000
141 | I3 | RTDIN | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I4 | RTDIN | S1 Filtered measurement | FLOAT | R | -200...2000
141 | I5 | RTDIN | S2 Measurement(Raw) | FLOAT | R | -200...2000
141 | I6 | RTDIN | S2 Resistance | FLOAT | R | 0...4000
141 | I7 | RTDIN | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I8 | RTDIN | S2 Filtered measurement | FLOAT | R | -200...2000
141 | I9 | RTDIN | S3 Measurement(Raw) | FLOAT | R | -200...2000
141 | I10 | RTDIN | S3 Resistance | FLOAT | R | 0...4000
141 | I11 | RTDIN | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I12 | RTDIN | S3 Filtered measurement | FLOAT | R | -200...2000
141 | I13 | RTDIN | S4 Measurement(Raw) | FLOAT | R | -200...2000
141 | I14 | RTDIN | S4 Resistance | FLOAT | R | 0...4000
141 | I15 | RTDIN | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I16 | RTDIN | S4 Filtered measurement | FLOAT | R | -200...2000
141 | I17 | RTDIN | S5 Measurement(Raw) | FLOAT | R | -200...2000
141 | I18 | RTDIN | S5 Resistance | FLOAT | R | 0...4000
141 | I19 | RTDIN | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I20 | RTDIN | S5 Filtered measurement | FLOAT | R | -200...2000
141 | I21 | RTDIN | S6 Measurement(Raw) | FLOAT | R | -200...2000
141 | I22 | RTDIN | S6 Resistance | FLOAT | R | 0...4000
141 | I23 | RTDIN | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I24 | RTDIN | S6 Filtered measurement | FLOAT | R | -200...2000
141 | I25 | RTDIN | S7 Measurement(Raw) | FLOAT | R | -200...2000
141 | I26 | RTDIN | S7 Resistance | FLOAT | R | 0...4000
141 | I27 | RTDIN | S7 Measurement mA | FLOAT | R | 0...20
141 | I28 | RTDIN | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I29 | RTDIN | S7 Filtered measurement | FLOAT | R | -200...2000
141 | I30 | RTDIN | S8 Measurement(Raw) | FLOAT | R | -200...2000
141 | I31 | RTDIN | S8 Resistance | FLOAT | R | 0...4000
141 | I32 | RTDIN | S8 Measurement mA | FLOAT | R | 0...20
141 | I33 | RTDIN | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I34 | RTDIN | S8 Filtered measurement | FLOAT | R | -200...2000
141 | I35 | RTDIN | S9 Measurement(Raw) | FLOAT | R | -200...2000
141 | I36 | RTDIN | S9 Resistance | FLOAT | R | 0...4000
141 | I37 | RTDIN | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I38 | RTDIN | S9 Filtered measurement | FLOAT | R | -200...2000
141 | I39 | RTDIN | S10 Measurement(Raw) | FLOAT | R | -200...2000
141 | I40 | RTDIN | S10 Resistance | FLOAT | R | 0...4000
141 | I41 | RTDIN | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I42 | RTDIN | S10 Filtered measurement | FLOAT | R | -200...2000
141 | I43 | RTDIN | S11 Measurement(Raw) | FLOAT | R | -200...2000
141 | I44 | RTDIN | S11 Resistance | FLOAT | R | 0...4000
141 | I45 | RTDIN | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I46 | RTDIN | S11 Filtered measurement | FLOAT | R | -200...2000
141 | I47 | RTDIN | S12 Measurement(Raw) | FLOAT | R | -200...2000
141 | I48 | RTDIN | S12 Resistance | FLOAT | R | 0...4000
141 | I49 | RTDIN | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I50 | RTDIN | S12 Filtered measurement | FLOAT | R | -200...2000
141 | I51 | RTDIN | S13 Measurement(Raw) | FLOAT | R | -200...2000
141 | I52 | RTDIN | S13 Resistance | FLOAT | R | 0...4000
141 | I53 | RTDIN | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I54 | RTDIN | S13 Filtered measurement | FLOAT | R | -200...2000
141 | I55 | RTDIN | S14 Measurement(Raw) | FLOAT | R | -200...2000
141 | I56 | RTDIN | S14 Resistance | FLOAT | R | 0...4000
141 | I57 | RTDIN | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I58 | RTDIN | S14 Filtered measurement | FLOAT | R | -200...2000
141 | I59 | RTDIN | S15 Measurement(Raw) | FLOAT | R | -200...2000
141 | I60 | RTDIN | S15 Resistance | FLOAT | R | 0...4000
141 | I61 | RTDIN | S15 Measurement mA | FLOAT | R | 0...20
141 | I62 | RTDIN | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I63 | RTDIN | S15 Filtered measurement | FLOAT | R | -200...2000
141 | I64 | RTDIN | S16 Measurement(Raw) | FLOAT | R | -200...2000
141 | I65 | RTDIN | S16 Resistance | FLOAT | R | 0...4000
141 | I66 | RTDIN | S16 Measurement mA | FLOAT | R | 0...20
141 | I67 | RTDIN | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I68 | RTDIN | S16 Filtered measurement | FLOAT | R | -200...2000
69 | S1 | RTD1 | RTD mode | UINT32 | RW | 0=Disabled;1=Activated
69 | S2 | RTD1 | S1 enable | UINT32 | RW | 0=No;1=Yes
69 | I1 | RTD1 | S1 Measurement (Protection) | FLOAT | R | -200...2000
69 | V1 | RTD1 | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S3 | RTD1 | S1 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I2 | RTD1 | S1 Alarm1 act | UINT32 | R | 0...4294967295
69 | S4 | RTD1 | S1 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S5 | RTD1 | S1 Alarm1 | FLOAT | RW | -200...2000
69 | S6 | RTD1 | S1 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I3 | RTD1 | S1 Alarm2 act | UINT32 | R | 0...4294967295
69 | S7 | RTD1 | S1 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S8 | RTD1 | S1 Alarm2 | FLOAT | RW | -200...2000
69 | I4 | RTD1 | S2 Measurement (Protection) | FLOAT | R | -200...2000
69 | V2 | RTD1 | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S9 | RTD1 | S2 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I5 | RTD1 | S2 Alarm1 act | UINT32 | R | 0...4294967295
69 | S10 | RTD1 | S2 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S11 | RTD1 | S2 Alarm1 | FLOAT | RW | -200...2000
69 | S12 | RTD1 | S2 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I6 | RTD1 | S2 Alarm2 act | UINT32 | R | 0...4294967295
69 | S13 | RTD1 | S2 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S14 | RTD1 | S2 Alarm2 | FLOAT | RW | -200...2000
69 | I7 | RTD1 | S3 Measurement (Protection) | FLOAT | R | -200...2000
69 | V3 | RTD1 | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S15 | RTD1 | S3 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I8 | RTD1 | S3 Alarm1 act | UINT32 | R | 0...4294967295
69 | S16 | RTD1 | S3 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S17 | RTD1 | S3 Alarm1 | FLOAT | RW | -200...2000
69 | S18 | RTD1 | S3 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I9 | RTD1 | S3 Alarm2 act | UINT32 | R | 0...4294967295
69 | S19 | RTD1 | S3 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S20 | RTD1 | S3 Alarm2 | FLOAT | RW | -200...2000
69 | I10 | RTD1 | S4 Measurement (Protection) | FLOAT | R | -200...2000
69 | V4 | RTD1 | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S21 | RTD1 | S4 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I11 | RTD1 | S4 Alarm1 act | UINT32 | R | 0...4294967295
69 | S22 | RTD1 | S4 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S23 | RTD1 | S4 Alarm1 | FLOAT | RW | -200...2000
69 | S24 | RTD1 | S4 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I12 | RTD1 | S4 Alarm2 act | UINT32 | R | 0...4294967295
69 | S25 | RTD1 | S4 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S26 | RTD1 | S4 Alarm2 | FLOAT | RW | -200...2000
69 | I13 | RTD1 | S5 Measurement (Protection) | FLOAT | R | -200...2000
69 | V5 | RTD1 | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S27 | RTD1 | S5 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I14 | RTD1 | S5 Alarm1 act | UINT32 | R | 0...4294967295
69 | S28 | RTD1 | S5 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S29 | RTD1 | S5 Alarm1 | FLOAT | RW | -200...2000
69 | S30 | RTD1 | S5 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I15 | RTD1 | S5 Alarm2 act | UINT32 | R | 0...4294967295
69 | S31 | RTD1 | S5 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S32 | RTD1 | S5 Alarm2 | FLOAT | RW | -200...2000
69 | I16 | RTD1 | S6 Measurement (Protection) | FLOAT | R | -200...2000
69 | V6 | RTD1 | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S33 | RTD1 | S6 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I17 | RTD1 | S6 Alarm1 act | UINT32 | R | 0...4294967295
69 | S34 | RTD1 | S6 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S35 | RTD1 | S6 Alarm1 | FLOAT | RW | -200...2000
69 | S36 | RTD1 | S6 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I18 | RTD1 | S6 Alarm2 act | UINT32 | R | 0...4294967295
69 | S37 | RTD1 | S6 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S38 | RTD1 | S6 Alarm2 | FLOAT | RW | -200...2000
69 | I19 | RTD1 | S7 Measurement (Protection) | FLOAT | R | -200...2000
69 | V7 | RTD1 | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S39 | RTD1 | S7 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I20 | RTD1 | S7 Alarm1 act | UINT32 | R | 0...4294967295
69 | S40 | RTD1 | S7 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S41 | RTD1 | S7 Alarm1 | FLOAT | RW | -200...2000
69 | S42 | RTD1 | S7 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I21 | RTD1 | S7 Alarm2 act | UINT32 | R | 0...4294967295
69 | S43 | RTD1 | S7 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S44 | RTD1 | S7 Alarm2 | FLOAT | RW | -200...2000
69 | I22 | RTD1 | S8 Measurement (Protection) | FLOAT | R | -200...2000
69 | V8 | RTD1 | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S45 | RTD1 | S8 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I23 | RTD1 | S8 Alarm1 act | UINT32 | R | 0...4294967295
69 | S46 | RTD1 | S8 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S47 | RTD1 | S8 Alarm1 | FLOAT | RW | -200...2000
69 | S48 | RTD1 | S8 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I24 | RTD1 | S8 Alarm2 act | UINT32 | R | 0...4294967295
69 | S49 | RTD1 | S8 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S50 | RTD1 | S8 Alarm2 | FLOAT | RW | -200...2000
69 | I25 | RTD1 | S9 Measurement (Protection) | FLOAT | R | -200...2000
69 | V9 | RTD1 | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S51 | RTD1 | S9 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I26 | RTD1 | S9 Alarm1 act | UINT32 | R | 0...4294967295
69 | S52 | RTD1 | S9 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S53 | RTD1 | S9 Alarm1 | FLOAT | RW | -200...2000
69 | S54 | RTD1 | S9 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I27 | RTD1 | S9 Alarm2 act | UINT32 | R | 0...4294967295
69 | S55 | RTD1 | S9 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S56 | RTD1 | S9 Alarm2 | FLOAT | RW | -200...2000
69 | I28 | RTD1 | S10 Measurement (Protection) | FLOAT | R | -200...2000
69 | V10 | RTD1 | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S57 | RTD1 | S10 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I29 | RTD1 | S10 Alarm1 act | UINT32 | R | 0...4294967295
69 | S58 | RTD1 | S10 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S59 | RTD1 | S10 Alarm1 | FLOAT | RW | -200...2000
69 | S60 | RTD1 | S10 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I30 | RTD1 | S10 Alarm2 act | UINT32 | R | 0...4294967295
69 | S61 | RTD1 | S10 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S62 | RTD1 | S10 Alarm2 | FLOAT | RW | -200...2000
69 | I31 | RTD1 | S11 Measurement (Protection) | FLOAT | R | -200...2000
69 | V11 | RTD1 | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S63 | RTD1 | S11 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I32 | RTD1 | S11 Alarm1 act | UINT32 | R | 0...4294967295
69 | S64 | RTD1 | S11 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S65 | RTD1 | S11 Alarm1 | FLOAT | RW | -200...2000
69 | S66 | RTD1 | S11 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I33 | RTD1 | S11 Alarm2 act | UINT32 | R | 0...4294967295
69 | S67 | RTD1 | S11 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S68 | RTD1 | S11 Alarm2 | FLOAT | RW | -200...2000
69 | I34 | RTD1 | S12 Measurement (Protection) | FLOAT | R | -200...2000
69 | V12 | RTD1 | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S69 | RTD1 | S12 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I35 | RTD1 | S12 Alarm1 act | UINT32 | R | 0...4294967295
69 | S70 | RTD1 | S12 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S71 | RTD1 | S12 Alarm1 | FLOAT | RW | -200...2000
69 | S72 | RTD1 | S12 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I36 | RTD1 | S12 Alarm2 act | UINT32 | R | 0...4294967295
69 | S73 | RTD1 | S12 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S74 | RTD1 | S12 Alarm2 | FLOAT | RW | -200...2000
69 | I37 | RTD1 | S13 Measurement (Protection) | FLOAT | R | -200...2000
69 | V13 | RTD1 | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S75 | RTD1 | S13 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I38 | RTD1 | S13 Alarm1 act | UINT32 | R | 0...4294967295
69 | S76 | RTD1 | S13 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S77 | RTD1 | S13 Alarm1 | FLOAT | RW | -200...2000
69 | S78 | RTD1 | S13 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I39 | RTD1 | S13 Alarm2 act | UINT32 | R | 0...4294967295
69 | S79 | RTD1 | S13 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S80 | RTD1 | S13 Alarm2 | FLOAT | RW | -200...2000
69 | I40 | RTD1 | S14 Measurement (Protection) | FLOAT | R | -200...2000
69 | V14 | RTD1 | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S81 | RTD1 | S14 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I41 | RTD1 | S14 Alarm1 act | UINT32 | R | 0...4294967295
69 | S82 | RTD1 | S14 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S83 | RTD1 | S14 Alarm1 | FLOAT | RW | -200...2000
69 | S84 | RTD1 | S14 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I42 | RTD1 | S14 Alarm2 act | UINT32 | R | 0...4294967295
69 | S85 | RTD1 | S14 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S86 | RTD1 | S14 Alarm2 | FLOAT | RW | -200...2000
69 | I43 | RTD1 | S15 Measurement (Protection) | FLOAT | R | -200...2000
69 | V15 | RTD1 | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S87 | RTD1 | S15 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I44 | RTD1 | S15 Alarm1 act | UINT32 | R | 0...4294967295
69 | S88 | RTD1 | S15 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S89 | RTD1 | S15 Alarm1 | FLOAT | RW | -200...2000
69 | S90 | RTD1 | S15 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I45 | RTD1 | S15 Alarm2 act | UINT32 | R | 0...4294967295
69 | S91 | RTD1 | S15 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S92 | RTD1 | S15 Alarm2 | FLOAT | RW | -200...2000
69 | I46 | RTD1 | S16 Measurement (Protection) | FLOAT | R | -200...2000
69 | V16 | RTD1 | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S93 | RTD1 | S16 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I47 | RTD1 | S16 Alarm1 act | UINT32 | R | 0...4294967295
69 | S94 | RTD1 | S16 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S95 | RTD1 | S16 Alarm1 | FLOAT | RW | -200...2000
69 | S96 | RTD1 | S16 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I48 | RTD1 | S16 Alarm2 act | UINT32 | R | 0...4294967295
69 | S97 | RTD1 | S16 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S98 | RTD1 | S16 Alarm2 | FLOAT | RW | -200...2000
69 | O1 | RTD1 | S1 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O2 | RTD1 | S1 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O3 | RTD1 | S1 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O4 | RTD1 | S2 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O5 | RTD1 | S2 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O6 | RTD1 | S2 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O7 | RTD1 | S3 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O8 | RTD1 | S3 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O9 | RTD1 | S3 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O10 | RTD1 | S4 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O11 | RTD1 | S4 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O12 | RTD1 | S4 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O13 | RTD1 | S5 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O14 | RTD1 | S5 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O15 | RTD1 | S5 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O16 | RTD1 | S6 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O17 | RTD1 | S6 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O18 | RTD1 | S6 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O19 | RTD1 | S7 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O20 | RTD1 | S7 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O21 | RTD1 | S7 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O22 | RTD1 | S8 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O23 | RTD1 | S8 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O24 | RTD1 | S8 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O25 | RTD1 | S9 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O26 | RTD1 | S9 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O27 | RTD1 | S9 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O28 | RTD1 | S10 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O29 | RTD1 | S10 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O30 | RTD1 | S10 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O31 | RTD1 | S11 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O32 | RTD1 | S11 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O33 | RTD1 | S11 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O34 | RTD1 | S12 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O35 | RTD1 | S12 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O36 | RTD1 | S12 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O37 | RTD1 | S13 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O38 | RTD1 | S13 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O39 | RTD1 | S13 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O40 | RTD1 | S14 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O41 | RTD1 | S14 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O42 | RTD1 | S14 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O43 | RTD1 | S15 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O44 | RTD1 | S15 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O45 | RTD1 | S15 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | O46 | RTD1 | S16 Alarm1 On | SIGNAL_OUT | RW | 0...4294967295
69 | O47 | RTD1 | S16 Alarm2 On | SIGNAL_OUT | RW | 0...4294967295
69 | O48 | RTD1 | S16 Meas Invalid | SIGNAL_OUT | RW | 0...4294967295
69 | S99 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
69 | S100 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
70 | S1 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
70 | S2 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
210 | S1 | OOS1 | Pole slip [78] mode | UINT32 | RW | 0=Disabled;1=Activated
210 | V1 | OOS1 | Pole slip condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
210 | V2 | OOS1 | Configuration status | UINT32 | R | 0=Ok;1=Incorrect VT set;2=Incorrect char. Set
210 | I1 | OOS1 | Pole slip starts | UINT32 | R | 0...4294967295
210 | I2 | OOS1 | Pole slip trips | UINT32 | R | 0...4294967295
210 | I3 | OOS1 | Pole slip blocks | UINT32 | R | 0...4294967295
210 | S2 | OOS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
210 | S3 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG1
210 | S4 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG2
210 | S5 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG3
210 | S6 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG4
210 | S7 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG5
210 | S8 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG6
210 | S9 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG7
210 | S10 | OOS1 | X Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG8
210 | S11 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG1
210 | S12 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG2
210 | S13 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG3
210 | S14 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG4
210 | S15 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG5
210 | S16 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG6
210 | S17 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG7
210 | S18 | OOS1 | R Detection circle offset from origo (pri) | FLOAT | RW | -50000...50000 | SG8
210 | S19 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG1
210 | S20 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG2
210 | S21 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG3
210 | S22 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG4
210 | S23 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG5
210 | S24 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG6
210 | S25 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG7
210 | S26 | OOS1 | Detection circle r (pri) | FLOAT | RW | 0.01...50000 | SG8
210 | S27 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG1
210 | S28 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG2
210 | S29 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG3
210 | S30 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG4
210 | S31 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG5
210 | S32 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG6
210 | S33 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG7
210 | S34 | OOS1 | R+ side blinder location (pri) | FLOAT | RW | 0...50000 | SG8
210 | S35 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG1
210 | S36 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG2
210 | S37 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG3
210 | S38 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG4
210 | S39 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG5
210 | S40 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG6
210 | S41 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG7
210 | S42 | OOS1 | R- side blinder location (pri) | FLOAT | RW | -50000...0 | SG8
210 | S43 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG1
210 | S44 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG2
210 | S45 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG3
210 | S46 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG4
210 | S47 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG5
210 | S48 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG6
210 | S49 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG7
210 | S50 | OOS1 | Minimum locus traverse time between blinders | FLOAT | RW | 0...1800 | SG8
210 | S51 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG1
210 | S52 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG2
210 | S53 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG3
210 | S54 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG4
210 | S55 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG5
210 | S56 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG6
210 | S57 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG7
210 | S58 | OOS1 | Pole slip detection limit to trip | UINT32 | RW | 1...5 | SG8
210 | S59 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG1
210 | S60 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG2
210 | S61 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG3
210 | S62 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG4
210 | S63 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG5
210 | S64 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG6
210 | S65 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG7
210 | S66 | OOS1 | Reset slip detection after last detected slip | FLOAT | RW | 0...1800 | SG8
210 | O1 | OOS1 | PoleSlip detection START | SIGNAL_OUT | RW | 0...4294967295
210 | O2 | OOS1 | PoleSlip TRIP | SIGNAL_OUT | RW | 0...4294967295
210 | O3 | OOS1 | PoleSlip detection BLOCKED | SIGNAL_OUT | RW | 0...4294967295
210 | I4 | OOS1 | Newest register | UINT32 | R | 0...12
210 | S67 | OOS1 | EventMaskLo | UINT32 | RW | 0...4294967295
74 | S1 | ARC1 | I/I0 Arc> [50ARC/50NARC] mode | UINT32 | RW | 0=Disabled;1=Activated
74 | V1 | ARC1 | I/I0 Arc> condition | UINT32 | R | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
74 | V2 | ARC1 | Sensor status | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | S2 | ARC1 | I/I0 Arc> Self supervision test pulse on option card 1 | UINT32 | RW | 0=Disabled;1=On
74 | S3 | ARC1 | I/I0 Arc> Self supervision test pulse on option card 2 | UINT32 | RW | 0=Disabled;1=On
74 | S4 | ARC1 | I/I0 Arc> Self supervision test pulse on option card 3 | UINT32 | RW | 0=Disabled;1=On
74 | S5 | ARC1 | I/I0 Arc> Self supervision test pulse on option card 4 | UINT32 | RW | 0=Disabled;1=On
74 | S6 | ARC1 | I/I0 Arc> Self supervision test pulse on option card 5 | UINT32 | RW | 0=Disabled;1=On
74 | S7 | ARC1 | I/I0 Arc> Self supervision test pulse on option card 6 | UINT32 | RW | 0=Disabled;1=On
74 | I1 | ARC1 | I/I0 Arc> Zone1 Trips | UINT32 | R | 0...4294967295
74 | I2 | ARC1 | I/I0 Arc> Zone1 Blocks | UINT32 | R | 0...4294967295
74 | I3 | ARC1 | I/I0 Arc> Zone2 Trips | UINT32 | R | 0...4294967295
74 | I4 | ARC1 | I/I0 Arc> Zone2 Blocks | UINT32 | R | 0...4294967295
74 | I5 | ARC1 | I/I0 Arc> Zone3 Trips | UINT32 | R | 0...4294967295
74 | I6 | ARC1 | I/I0 Arc> Zone3 Blocks | UINT32 | R | 0...4294967295
74 | I7 | ARC1 | I/I0 Arc> Zone4 Trips | UINT32 | R | 0...4294967295
74 | I8 | ARC1 | I/I0 Arc> Zone4 Blocks | UINT32 | R | 0...4294967295
74 | S8 | ARC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
74 | I9 | ARC1 | Channel 1 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I10 | ARC1 | Channel 1 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I11 | ARC1 | Channel 2 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I12 | ARC1 | Channel 2 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I13 | ARC1 | Channel 3 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I14 | ARC1 | Channel 3 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I15 | ARC1 | Channel 4 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I16 | ARC1 | Channel 4 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I17 | ARC1 | Channel 5 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I18 | ARC1 | Channel 5 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I19 | ARC1 | Channel 6 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I20 | ARC1 | Channel 6 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I21 | ARC1 | Channel 7 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I22 | ARC1 | Channel 7 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I23 | ARC1 | Channel 8 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I24 | ARC1 | Channel 8 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I25 | ARC1 | Channel 9 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I26 | ARC1 | Channel 9 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I27 | ARC1 | Channel 10 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I28 | ARC1 | Channel 10 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I29 | ARC1 | Channel 11 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I30 | ARC1 | Channel 11 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I31 | ARC1 | Channel 12 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I32 | ARC1 | Channel 12 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I33 | ARC1 | Channel 13 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I34 | ARC1 | Channel 13 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I35 | ARC1 | Channel 14 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I36 | ARC1 | Channel 14 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I37 | ARC1 | Channel 15 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I38 | ARC1 | Channel 15 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I39 | ARC1 | Channel 16 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I40 | ARC1 | Channel 16 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I41 | ARC1 | Channel 17 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I42 | ARC1 | Channel 17 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I43 | ARC1 | Channel 18 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I44 | ARC1 | Channel 18 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I45 | ARC1 | Channel 19 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I46 | ARC1 | Channel 19 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I47 | ARC1 | Channel 20 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I48 | ARC1 | Channel 20 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I49 | ARC1 | Channel 21 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I50 | ARC1 | Channel 21 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I51 | ARC1 | Channel 22 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I52 | ARC1 | Channel 22 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I53 | ARC1 | Channel 23 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I54 | ARC1 | Channel 23 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I55 | ARC1 | Channel 24 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I56 | ARC1 | Channel 24 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I57 | ARC1 | Fiber sensor 1 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I58 | ARC1 | Fiber sensor 1 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I59 | ARC1 | Fiber sensor 2 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I60 | ARC1 | Fiber sensor 2 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I61 | ARC1 | Fiber sensor 3 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I62 | ARC1 | Fiber sensor 3 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I63 | ARC1 | Fiber sensor 4 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I64 | ARC1 | Fiber sensor 4 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I65 | ARC1 | Fiber sensor 5 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I66 | ARC1 | Fiber sensor 5 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I67 | ARC1 | Fiber sensor 6 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I68 | ARC1 | Fiber sensor 6 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I69 | ARC1 | Fiber sensor 7 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I70 | ARC1 | Fiber sensor 7 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I71 | ARC1 | Fiber sensor 8 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I72 | ARC1 | Fiber sensor 8 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I73 | ARC1 | Fiber sensor 9 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I74 | ARC1 | Fiber sensor 9 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I75 | ARC1 | Fiber sensor 10 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I76 | ARC1 | Fiber sensor 10 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I77 | ARC1 | Fiber sensor 11 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I78 | ARC1 | Fiber sensor 11 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I79 | ARC1 | Fiber sensor 12 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I80 | ARC1 | Fiber sensor 12 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I81 | ARC1 | Fiber sensor 13 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I82 | ARC1 | Fiber sensor 13 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I83 | ARC1 | Fiber sensor 14 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I84 | ARC1 | Fiber sensor 14 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I85 | ARC1 | Fiber sensor 15 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I86 | ARC1 | Fiber sensor 15 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I87 | ARC1 | Fiber sensor 16 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I88 | ARC1 | Fiber sensor 16 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I89 | ARC1 | Fiber sensor 17 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I90 | ARC1 | Fiber sensor 17 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I91 | ARC1 | Fiber sensor 18 enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I92 | ARC1 | Fiber sensor 18 status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I93 | ARC1 | Fiber card 1 QD enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I94 | ARC1 | Fiber card 2 QD enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I95 | ARC1 | Fiber card 3 QD enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I96 | ARC1 | Fiber card 4 QD enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I97 | ARC1 | Fiber card 5 QD enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | I98 | ARC1 | Fiber card 6 QD enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S9 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG1
74 | S10 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG2
74 | S11 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG3
74 | S12 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG4
74 | S13 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG5
74 | S14 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG6
74 | S15 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG7
74 | S16 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40 | SG8
74 | S17 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG1
74 | S18 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG2
74 | S19 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG3
74 | S20 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG4
74 | S21 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG5
74 | S22 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG6
74 | S23 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG7
74 | S24 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02 | SG8
74 | S25 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG1
74 | S26 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG2
74 | S27 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG3
74 | S28 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG4
74 | S29 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG5
74 | S30 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG6
74 | S31 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG7
74 | S32 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40 | SG8
74 | S33 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S34 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S35 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S36 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S37 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S38 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S39 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S40 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S41 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S42 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S43 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S44 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S45 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S46 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S47 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S48 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S49 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S50 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S51 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S52 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S53 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S54 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S55 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S56 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S57 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S58 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S59 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S60 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S61 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S62 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S63 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S64 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S65 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S66 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S67 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S68 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S69 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S70 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S71 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S72 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S73 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S74 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S75 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S76 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S77 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S78 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S79 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S80 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S81 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S82 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S83 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S84 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S85 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S86 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S87 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S88 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S89 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG1
74 | S90 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG2
74 | S91 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG3
74 | S92 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG4
74 | S93 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG5
74 | S94 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG6
74 | S95 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG7
74 | S96 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG8
74 | S97 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S98 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S99 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S100 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S101 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S102 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S103 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S104 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S105 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S106 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S107 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S108 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S109 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S110 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S111 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S112 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S113 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S114 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S115 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S116 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S117 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S118 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S119 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S120 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S121 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S122 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S123 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S124 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S125 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S126 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S127 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S128 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S129 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S130 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S131 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S132 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S133 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S134 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S135 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S136 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S137 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S138 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S139 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S140 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S141 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S142 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S143 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S144 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S145 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S146 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S147 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S148 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S149 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S150 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S151 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S152 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S153 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG1
74 | S154 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG2
74 | S155 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG3
74 | S156 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG4
74 | S157 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG5
74 | S158 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG6
74 | S159 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG7
74 | S160 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG8
74 | S161 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S162 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S163 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S164 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S165 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S166 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S167 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S168 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S169 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S170 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S171 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S172 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S173 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S174 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S175 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S176 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S177 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S178 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S179 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S180 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S181 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S182 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S183 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S184 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S185 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S186 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S187 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S188 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S189 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S190 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S191 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S192 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S193 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S194 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S195 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S196 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S197 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S198 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S199 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S200 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S201 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S202 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S203 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S204 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S205 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S206 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S207 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S208 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S209 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S210 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S211 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S212 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S213 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S214 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S215 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S216 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S217 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG1
74 | S218 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG2
74 | S219 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG3
74 | S220 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG4
74 | S221 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG5
74 | S222 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG6
74 | S223 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG7
74 | S224 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG8
74 | S225 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S226 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S227 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S228 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S229 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S230 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S231 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S232 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S233 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S234 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S235 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S236 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S237 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S238 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S239 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S240 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S241 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S242 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S243 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S244 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S245 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S246 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S247 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S248 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S249 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S250 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S251 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S252 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S253 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S254 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S255 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S256 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S257 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S258 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S259 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S260 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S261 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S262 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S263 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S264 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S265 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S266 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S267 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S268 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S269 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S270 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S271 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S272 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S273 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG1
74 | S274 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG2
74 | S275 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG3
74 | S276 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG4
74 | S277 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG5
74 | S278 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG6
74 | S279 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG7
74 | S280 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled | SG8
74 | S281 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG1
74 | S282 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG2
74 | S283 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG3
74 | S284 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG4
74 | S285 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG5
74 | S286 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG6
74 | S287 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG7
74 | S288 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In | SG8
74 | O1 | ARC1 | I/I0 Arc> Ph.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O2 | ARC1 | I/I0 Arc> Res.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O3 | ARC1 | I/I0 Arc> Zone1.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O4 | ARC1 | I/I0 Arc> Zone2.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O5 | ARC1 | I/I0 Arc> Zone3.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O6 | ARC1 | I/I0 Arc> Zone4.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O7 | ARC1 | I/I0 Arc> Ph.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O8 | ARC1 | I/I0 Arc> Res.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O9 | ARC1 | I/I0 Arc> Ph.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O10 | ARC1 | I/I0 Arc> Res.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O11 | ARC1 | I/I0 Arc> Zone1 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O12 | ARC1 | I/I0 Arc> Zone1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O13 | ARC1 | I/I0 Arc> Zone2 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O14 | ARC1 | I/I0 Arc> Zone2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O15 | ARC1 | I/I0 Arc> Zone3 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O16 | ARC1 | I/I0 Arc> Zone3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O17 | ARC1 | I/I0 Arc> Zone4 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O18 | ARC1 | I/I0 Arc> Zone4 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O19 | ARC1 | I/I0 Arc> S1 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O20 | ARC1 | I/I0 Arc> S2 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O21 | ARC1 | I/I0 Arc> S3 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O22 | ARC1 | I/I0 Arc> S4 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O23 | ARC1 | I/I0 Arc> S5 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O24 | ARC1 | I/I0 Arc> S6 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O25 | ARC1 | I/I0 Arc> S7 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O26 | ARC1 | I/I0 Arc> S8 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O27 | ARC1 | I/I0 Arc> S9 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O28 | ARC1 | I/I0 Arc> S10 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O29 | ARC1 | I/I0 Arc> S11 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O30 | ARC1 | I/I0 Arc> S12 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O31 | ARC1 | I/I0 Arc> S13 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O32 | ARC1 | I/I0 Arc> S14 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O33 | ARC1 | I/I0 Arc> S15 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O34 | ARC1 | I/I0 Arc> S16 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O35 | ARC1 | I/I0 Arc> S17 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O36 | ARC1 | I/I0 Arc> S18 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O37 | ARC1 | I/I0 Arc> S19 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O38 | ARC1 | I/I0 Arc> S20 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O39 | ARC1 | I/I0 Arc> S21 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O40 | ARC1 | I/I0 Arc> S22 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O41 | ARC1 | I/I0 Arc> S23 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O42 | ARC1 | I/I0 Arc> S24 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O43 | ARC1 | I/I0 Arc> Fiber 1 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O44 | ARC1 | I/I0 Arc> Fiber 2 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O45 | ARC1 | I/I0 Arc> Fiber 3 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O46 | ARC1 | I/I0 Arc> Fiber 4 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O47 | ARC1 | I/I0 Arc> Fiber 5 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O48 | ARC1 | I/I0 Arc> Fiber 6 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O49 | ARC1 | I/I0 Arc> Fiber 7 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O50 | ARC1 | I/I0 Arc> Fiber 8 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O51 | ARC1 | I/I0 Arc> Fiber 9 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O52 | ARC1 | I/I0 Arc> Fiber 10 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O53 | ARC1 | I/I0 Arc> Fiber 11 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O54 | ARC1 | I/I0 Arc> Fiber 12 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O55 | ARC1 | I/I0 Arc> Fiber 13 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O56 | ARC1 | I/I0 Arc> Fiber 14 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O57 | ARC1 | I/I0 Arc> Fiber 15 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O58 | ARC1 | I/I0 Arc> Fiber 16 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O59 | ARC1 | I/I0 Arc> Fiber 17 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O60 | ARC1 | I/I0 Arc> Fiber 18 fault | SIGNAL_OUT | RW | 0...4294967295
74 | O61 | ARC1 | I/I0 Arc> IO unit fault | SIGNAL_OUT | RW | 0...4294967295
74 | I99 | ARC1 | Newest register | UINT32 | R | 0...12
74 | I100 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I101 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I102 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I103 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I104 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I105 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I106 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I107 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I108 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I109 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I110 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I111 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I112 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I113 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I114 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I115 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I116 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I117 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I118 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I119 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I120 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I121 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I122 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I123 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I124 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I125 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I126 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I127 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I128 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I129 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I130 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I131 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I132 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I133 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I134 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I135 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I136 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I137 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I138 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I139 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I140 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I141 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I142 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I143 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I144 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I145 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I146 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I147 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I148 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I149 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I150 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I151 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I152 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I153 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I154 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I155 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I156 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I157 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I158 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I159 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | S289 | ARC1 | EventMaskLo | UINT32 | RW | 0...4294967295
74 | S290 | ARC1 | EventMaskHi | UINT32 | RW | 0...4294967295
229 | S1 | ARCOE1 | EventMaskOutputsLo | UINT32 | RW | 0...4294967295
229 | S2 | ARCOE1 | EventMaskOutputsHi | UINT32 | RW | 0...4294967295
230 | S1 | ARCOE2 | EventMaskOutputsFiberLo | UINT32 | RW | 0...4294967295
230 | S2 | ARCOE2 | EventMaskOutputsFiberHi | UINT32 | RW | 0...4294967295
225 | S1 | ARCS1 | EventMaskSenorsLo | UINT32 | RW | 0...4294967295
225 | S2 | ARCS1 | EventMaskSensorsHi | UINT32 | RW | 0...4294967295
226 | S1 | ARCS2 | EventMaskFibersLo | UINT32 | RW | 0...4294967295
226 | S2 | ARCS2 | EventMaskFibersHi | UINT32 | RW | 0...4294967295
227 | S1 | ARCSE1 | EventMaskSensorsErrorLo | UINT32 | RW | 0...4294967295
227 | S2 | ARCSE1 | EventMaskSensorsErrorHi | UINT32 | RW | 0...4294967295
228 | S1 | ARCSE2 | EventMaskFibersErrorLo | UINT32 | RW | 0...4294967295
228 | S2 | ARCSE2 | EventMaskFibersErrorHi | UINT32 | RW | 0...4294967295
52 | S1 | CTS1 | CTS1 mode | UINT32 | RW | 0=Disabled;1=Activated
52 | V1 | CTS1 | CTS1 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
52 | I1 | CTS1 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
52 | I2 | CTS1 | Natural unbalance ang | FLOAT | R | -360...360
52 | I3 | CTS1 | Measured current difference Isum, I0 | FLOAT | R | 0...50
52 | I4 | CTS1 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
52 | I5 | CTS1 | CTS1 alarms | UINT32 | R | 0...4294967295
52 | I6 | CTS1 | CTS1 blocks | UINT32 | R | 0...4294967295
52 | S2 | CTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
52 | S3 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG1
52 | S4 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG2
52 | S5 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG3
52 | S6 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG4
52 | S7 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG5
52 | S8 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG6
52 | S9 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG7
52 | S10 | CTS1 | Iset High limit | FLOAT | RW | 0.01...40 | SG8
52 | S11 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG1
52 | S12 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG2
52 | S13 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG3
52 | S14 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG4
52 | S15 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG5
52 | S16 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG6
52 | S17 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG7
52 | S18 | CTS1 | Iset Low limit | FLOAT | RW | 0.01...40 | SG8
52 | S19 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG1
52 | S20 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG2
52 | S21 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG3
52 | S22 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG4
52 | S23 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG5
52 | S24 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG6
52 | S25 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG7
52 | S26 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100 | SG8
52 | S27 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG1
52 | S28 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG2
52 | S29 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG3
52 | S30 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG4
52 | S31 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG5
52 | S32 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG6
52 | S33 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG7
52 | S34 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG8
52 | S35 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG1
52 | S36 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG2
52 | S37 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG3
52 | S38 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG4
52 | S39 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG5
52 | S40 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG6
52 | S41 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG7
52 | S42 | CTS1 | Isum difference | FLOAT | RW | 0.01...40 | SG8
52 | S43 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG1
52 | S44 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG2
52 | S45 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG3
52 | S46 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG4
52 | S47 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG5
52 | S48 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG6
52 | S49 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG7
52 | S50 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800 | SG8
52 | O1 | CTS1 | CTS1 ALARM | SIGNAL_OUT | RW | 0...4294967295
52 | O2 | CTS1 | CTS1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
52 | I7 | CTS1 | Newest register | UINT32 | R | 0...12
52 | I8 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I9 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I10 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I11 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I12 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I13 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I14 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I15 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I16 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I17 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I18 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I19 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I20 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I21 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I22 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I23 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I24 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I25 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I26 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I27 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I28 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I29 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I30 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I31 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I32 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I33 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I34 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I35 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I36 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I37 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I38 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I39 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I40 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I41 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I42 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I43 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I44 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I45 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I46 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I47 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I48 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I49 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I50 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I51 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I52 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I53 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I54 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I55 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I56 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I57 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I58 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I59 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I60 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I61 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I62 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I63 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I64 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I65 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I66 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I67 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I68 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I69 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I70 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I71 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I72 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I73 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I74 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I75 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I76 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I77 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I78 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I79 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | S51 | CTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
52 | S52 | CTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
54 | S1 | CTS2 | CTS2 mode | UINT32 | RW | 0=Disabled;1=Activated
54 | V1 | CTS2 | CTS2 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
54 | I1 | CTS2 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
54 | I2 | CTS2 | Natural unbalance ang | FLOAT | R | -360...360
54 | I3 | CTS2 | Measured current difference Isum, I0 | FLOAT | R | 0...50
54 | I4 | CTS2 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
54 | I5 | CTS2 | CTS2 alarms | UINT32 | R | 0...4294967295
54 | I6 | CTS2 | CTS2 blocks | UINT32 | R | 0...4294967295
54 | S2 | CTS2 | Clear statistics | UINT32 | W | 0=-;1=Clear
54 | S3 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG1
54 | S4 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG2
54 | S5 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG3
54 | S6 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG4
54 | S7 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG5
54 | S8 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG6
54 | S9 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG7
54 | S10 | CTS2 | Iset High limit | FLOAT | RW | 0.01...40 | SG8
54 | S11 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG1
54 | S12 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG2
54 | S13 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG3
54 | S14 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG4
54 | S15 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG5
54 | S16 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG6
54 | S17 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG7
54 | S18 | CTS2 | Iset Low limit | FLOAT | RW | 0.01...40 | SG8
54 | S19 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG1
54 | S20 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG2
54 | S21 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG3
54 | S22 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG4
54 | S23 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG5
54 | S24 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG6
54 | S25 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG7
54 | S26 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100 | SG8
54 | S27 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG1
54 | S28 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG2
54 | S29 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG3
54 | S30 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG4
54 | S31 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG5
54 | S32 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG6
54 | S33 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG7
54 | S34 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100 | SG8
54 | S35 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG1
54 | S36 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG2
54 | S37 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG3
54 | S38 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG4
54 | S39 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG5
54 | S40 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG6
54 | S41 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG7
54 | S42 | CTS2 | Isum difference | FLOAT | RW | 0.01...40 | SG8
54 | S43 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG1
54 | S44 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG2
54 | S45 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG3
54 | S46 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG4
54 | S47 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG5
54 | S48 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG6
54 | S49 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG7
54 | S50 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800 | SG8
54 | O1 | CTS2 | CTS2 ALARM | SIGNAL_OUT | RW | 0...4294967295
54 | O2 | CTS2 | CTS2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
54 | I7 | CTS2 | Newest register | UINT32 | R | 0...12
54 | I8 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I9 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I10 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I11 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I12 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I13 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I14 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I15 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I16 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I17 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I18 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I19 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I20 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I21 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I22 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I23 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I24 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I25 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I26 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I27 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I28 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I29 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I30 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I31 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I32 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I33 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I34 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I35 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I36 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I37 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I38 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I39 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I40 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I41 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I42 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I43 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I44 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I45 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I46 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I47 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I48 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I49 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I50 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I51 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I52 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I53 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I54 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I55 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I56 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I57 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I58 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I59 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I60 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I61 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I62 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I63 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I64 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I65 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I66 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I67 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I68 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I69 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I70 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I71 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I72 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I73 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I74 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I75 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I76 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I77 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I78 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I79 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | S51 | CTS2 | EventMaskLo | UINT32 | RW | 0...4294967295
54 | S52 | CTS2 | EventMaskHi | UINT32 | RW | 0...4294967295
53 | S1 | VTS1 | VTS [60] mode | UINT32 | RW | 0=Disabled;1=Activated
53 | V1 | VTS1 | VTS condition | UINT32 | R | 0=Normal;1=Start;2=VTLinefail;3=VTBusfail;4=Blocked
53 | V2 | VTS1 | Bus voltages | UINT32 | R | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
53 | I1 | VTS1 | VTS Starts | UINT32 | R | 0...4294967295
53 | I2 | VTS1 | Line fuse fails | UINT32 | R | 0...4294967295
53 | I3 | VTS1 | Bus fuse fails | UINT32 | R | 0...4294967295
53 | I4 | VTS1 | VTS Blocks | UINT32 | R | 0...4294967295
53 | S2 | VTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
53 | S3 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG1
53 | S4 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG2
53 | S5 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG3
53 | S6 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG4
53 | S7 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG5
53 | S8 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG6
53 | S9 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG7
53 | S10 | VTS1 | Voltage low pick-up | FLOAT | RW | 0.05...0.5 | SG8
53 | S11 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG1
53 | S12 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG2
53 | S13 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG3
53 | S14 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG4
53 | S15 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG5
53 | S16 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG6
53 | S17 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG7
53 | S18 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1 | SG8
53 | S19 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG1
53 | S20 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG2
53 | S21 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG3
53 | S22 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG4
53 | S23 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG5
53 | S24 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG6
53 | S25 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG7
53 | S26 | VTS1 | Angle shift limit | FLOAT | RW | 2...90 | SG8
53 | S27 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG1
53 | S28 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG2
53 | S29 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG3
53 | S30 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG4
53 | S31 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG5
53 | S32 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG6
53 | S33 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG7
53 | S34 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG8
53 | S35 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG1
53 | S36 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG2
53 | S37 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG3
53 | S38 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG4
53 | S39 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG5
53 | S40 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG6
53 | S41 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG7
53 | S42 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes | SG8
53 | S43 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG1
53 | S44 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG2
53 | S45 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG3
53 | S46 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG4
53 | S47 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG5
53 | S48 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG6
53 | S49 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG7
53 | S50 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800 | SG8
53 | O1 | VTS1 | VTS Start | SIGNAL_OUT | RW | 0...4294967295
53 | O2 | VTS1 | VTS Fail Alarm Line | SIGNAL_OUT | RW | 0...4294967295
53 | O3 | VTS1 | VTS Fail Alarm Bus | SIGNAL_OUT | RW | 0...4294967295
53 | O4 | VTS1 | VTS Blocked(time delay) | SIGNAL_OUT | RW | 0...4294967295
53 | I5 | VTS1 | Newest register | UINT32 | R | 0...12
53 | I6 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I7 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I8 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I9 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I10 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I11 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I12 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I13 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I14 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I15 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I16 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I17 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I18 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I19 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I20 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I21 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I22 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I23 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I24 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I25 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I26 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I27 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I28 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I29 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I30 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I31 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I32 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I33 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I34 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I35 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I36 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I37 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I38 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I39 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I40 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I41 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I42 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I43 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I44 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I45 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I46 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I47 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I48 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I49 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I50 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I51 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I52 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I53 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I54 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I55 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I56 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I57 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I58 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I59 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I60 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I61 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I62 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I63 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I64 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I65 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | S51 | VTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
53 | S52 | VTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
43 | S1 | FLX1 | Fault locator [21FL] mode | UINT32 | RW | 0=Disabled;1=Activated
43 | V1 | FLX1 | Fault locator condition | UINT32 | R | 0=Idle;1=Triggered;2=Calc ready
43 | I1 | FLX1 | Times fault locator triggered | UINT32 | R | 0...4294967295
43 | I2 | FLX1 | Latest fault reactance | FLOAT | R | 0...1800
43 | I3 | FLX1 | Latest fault distance | FLOAT | R | 0...1800
43 | I4 | FLX1 | Latest fault IL1 | FLOAT | R | 0...1800
43 | I5 | FLX1 | Latest fault IL2 | FLOAT | R | 0...1800
43 | I6 | FLX1 | Latest fault IL3 | FLOAT | R | 0...1800
43 | I7 | FLX1 | Latest fault IL1 | FLOAT | R | 0...1800
43 | I8 | FLX1 | Latest fault IL2 | FLOAT | R | 0...1800
43 | I9 | FLX1 | Latest fault IL3 | FLOAT | R | 0...1800
43 | V2 | FLX1 | Latest fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | V3 | FLX1 | Latest fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | S2 | FLX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
43 | S3 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG1
43 | S4 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG2
43 | S5 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG3
43 | S6 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG4
43 | S7 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG5
43 | S8 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG6
43 | S9 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG7
43 | S10 | FLX1 | Trigger current > | FLOAT | RW | 0...40 | SG8
43 | S11 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG1
43 | S12 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG2
43 | S13 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG3
43 | S14 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG4
43 | S15 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG5
43 | S16 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG6
43 | S17 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG7
43 | S18 | FLX1 | Reactance per km | FLOAT | RW | 0...5 | SG8
43 | I10 | FLX1 | Newest register | UINT32 | R | 0...12
43 | I11 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I12 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I13 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I14 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I15 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I16 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I17 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I18 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I19 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I20 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I21 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I22 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I23 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I24 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I25 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I26 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I27 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I28 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I29 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I30 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I31 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I32 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I33 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I34 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I35 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I36 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I37 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I38 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I39 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I40 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I41 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I42 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I43 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I44 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I45 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I46 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I47 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I48 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I49 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I50 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I51 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I52 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I53 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I54 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I55 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I56 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I57 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I58 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I59 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I60 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I61 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I62 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I63 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I64 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I65 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I66 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I67 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I68 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I69 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I70 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I71 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I72 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I73 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I74 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I75 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I76 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I77 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I78 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I79 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I80 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I81 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I82 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I83 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I84 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I85 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I86 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I87 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I88 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I89 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I90 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I91 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I92 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I93 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I94 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I95 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I96 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I97 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I98 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I99 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I100 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I101 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I102 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I103 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I104 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I105 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I106 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I107 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I108 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I109 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I110 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I111 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I112 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I113 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I114 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I115 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I116 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I117 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I118 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I119 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I120 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I121 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I122 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I123 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I124 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I125 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I126 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I127 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I128 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I129 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I130 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | S19 | FLX1 | EventMaskLo | UINT32 | RW | 0...4294967295
55 | S1 | THD1 | THD mode | UINT32 | RW | 0=Disabled;1=Activated
55 | V1 | THD1 | THD condition | UINT32 | R | 0=Normal;1=Start;2=Alarm;3=Blocked
55 | S2 | THD1 | Measurement magnitude | UINT32 | RW | 0=Amplitude;1=Power
55 | I1 | THD1 | THD starts | UINT32 | R | 0...4294967295
55 | I2 | THD1 | THD alarms | UINT32 | R | 0...4294967295
55 | I3 | THD1 | THD blocks | UINT32 | R | 0...4294967295
55 | S3 | THD1 | Clear statistics | UINT32 | W | 0=-;1=Clear
55 | S4 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S5 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S6 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S7 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S8 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S9 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S10 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S11 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S12 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S13 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S14 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S15 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S16 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S17 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S18 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S19 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S20 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S21 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S22 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S23 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S24 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S25 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S26 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S27 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S28 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG1
55 | S29 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG2
55 | S30 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG3
55 | S31 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG4
55 | S32 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG5
55 | S33 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG6
55 | S34 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG7
55 | S35 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100 | SG8
55 | S36 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG1
55 | S37 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG2
55 | S38 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG3
55 | S39 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG4
55 | S40 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG5
55 | S41 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG6
55 | S42 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG7
55 | S43 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100 | SG8
55 | S44 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG1
55 | S45 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG2
55 | S46 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG3
55 | S47 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG4
55 | S48 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG5
55 | S49 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG6
55 | S50 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG7
55 | S51 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100 | SG8
55 | S52 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG1
55 | S53 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG2
55 | S54 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG3
55 | S55 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG4
55 | S56 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG5
55 | S57 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG6
55 | S58 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG7
55 | S59 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800 | SG8
55 | S60 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG1
55 | S61 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG2
55 | S62 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG3
55 | S63 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG4
55 | S64 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG5
55 | S65 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG6
55 | S66 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG7
55 | S67 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800 | SG8
55 | S68 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG1
55 | S69 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG2
55 | S70 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG3
55 | S71 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG4
55 | S72 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG5
55 | S73 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG6
55 | S74 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG7
55 | S75 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800 | SG8
55 | O1 | THD1 | THDPH> START | SIGNAL_OUT | RW | 0...4294967295
55 | O2 | THD1 | THDPH> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O3 | THD1 | THDI01> START | SIGNAL_OUT | RW | 0...4294967295
55 | O4 | THD1 | THDI01> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O5 | THD1 | THDI02> START | SIGNAL_OUT | RW | 0...4294967295
55 | O6 | THD1 | THDI02> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O7 | THD1 | THD> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
55 | I4 | THD1 | Newest register | UINT32 | R | 0...12
55 | I5 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I6 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I7 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I8 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I9 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I10 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I11 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I12 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I13 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I14 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I15 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I16 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I17 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I18 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I19 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I20 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I21 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I22 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I23 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I24 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I25 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I26 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I27 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I28 | THD1 | I02 THD | FLOAT | R | 0...250
55 | S76 | THD1 | EventMaskLo | UINT32 | RW | 0...4294967295
211 | S1 | THDV1 | THDV mode | UINT32 | RW | 0=Disabled;1=Activated
211 | V1 | THDV1 | THDV condition | UINT32 | R | 0=Normal;1=Start;2=Alarm;3=Blocked
211 | S2 | THDV1 | Measurement magnitude | UINT32 | RW | 0=Amplitude;1=Power
211 | I1 | THDV1 | THDV starts | UINT32 | R | 0...4294967295
211 | I2 | THDV1 | THDV alarms | UINT32 | R | 0...4294967295
211 | I3 | THDV1 | THDV blocks | UINT32 | R | 0...4294967295
211 | S3 | THDV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
211 | S4 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S5 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S6 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S7 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S8 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S9 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S10 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S11 | THDV1 | Enable THDV Alarm | UINT32 | RW | 0=Disabled;1=Enabled
211 | S12 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG1
211 | S13 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG2
211 | S14 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG3
211 | S15 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG4
211 | S16 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG5
211 | S17 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG6
211 | S18 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG7
211 | S19 | THDV1 | THDV pick up | FLOAT | RW | 0.1...100 | SG8
211 | S20 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG1
211 | S21 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG2
211 | S22 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG3
211 | S23 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG4
211 | S24 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG5
211 | S25 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG6
211 | S26 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG7
211 | S27 | THDV1 | THDV alarm delay | FLOAT | RW | 0...1800 | SG8
211 | O1 | THDV1 | THDV> START | SIGNAL_OUT | RW | 0...4294967295
211 | O2 | THDV1 | THDV> ALARM | SIGNAL_OUT | RW | 0...4294967295
211 | O3 | THDV1 | THDV> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
211 | I4 | THDV1 | Newest register | UINT32 | R | 0...12
211 | S28 | THDV1 | EventMaskLo | UINT32 | RW | 0...4294967295
58 | S1 | CBW1 | CBW mode | UINT32 | RW | 0=Disabled;1=Activated
58 | V1 | CBW1 | CBW condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On
58 | I1 | CBW1 | Breaker operations | UINT32 | R | 0...4294967295
58 | I2 | CBW1 | Alarm 1 counter | UINT32 | R | 0...4294967295
58 | I3 | CBW1 | Alarm 2 counter | UINT32 | R | 0...4294967295
58 | I4 | CBW1 | L1 Operations left | FLOAT | R | 0...4294967295
58 | I5 | CBW1 | L2 Operations left | FLOAT | R | 0...4294967295
58 | I6 | CBW1 | L3 Operations left | FLOAT | R | 0...4294967295
58 | S2 | CBW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
58 | S3 | CBW1 | Alarm 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S4 | CBW1 | Alarm 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S5 | CBW1 | Alarm 1 Set | UINT32 | RW | 0...200000
58 | S6 | CBW1 | Alarm 2 Set | UINT32 | RW | 0...200000
58 | S7 | CBW1 | Operations 1 | FLOAT | RW | 0...200000
58 | S8 | CBW1 | Operations 2 | FLOAT | RW | 0...200000
58 | S9 | CBW1 | Current 1 | FLOAT | RW | 0...100
58 | S10 | CBW1 | Current 2 | FLOAT | RW | 0...100
58 | O1 | CBW1 | CBW Alarm 1 act | SIGNAL_OUT | RW | 0...4294967295
58 | I7 | CBW1 | Newest register | UINT32 | R | 0...12
58 | I8 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I9 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I10 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I11 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I12 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I13 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I14 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I15 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I16 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I17 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I18 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I19 | CBW1 | L1 Operations left | FLOAT | R | 0...600000
58 | I20 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I21 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I22 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I23 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I24 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I25 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I26 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I27 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I28 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I29 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I30 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I31 | CBW1 | L2 Operations left | FLOAT | R | 0...600000
58 | I32 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I33 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I34 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I35 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I36 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I37 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I38 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I39 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I40 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I41 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I42 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | I43 | CBW1 | L3 Operations left | FLOAT | R | 0...600000
58 | S11 | CBW1 | EventMaskLo | UINT32 | RW | 0...4294967295
97 | S1 | NJK1 | U0> RECL [79] mode | UINT32 | RW | 0=Disabled;1=Activated
97 | V1 | NJK1 | U0> RECL condition | UINT32 | R | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
97 | I1 | NJK1 | Requests | UINT32 | R | 0...4294967295
97 | I2 | NJK1 | Blocks | UINT32 | R | 0...4294967295
97 | I3 | NJK1 | Starts | UINT32 | R | 0...4294967295
97 | I4 | NJK1 | Breaker closes | UINT32 | R | 0...4294967295
97 | S2 | NJK1 | Clear statistics | UINT32 | W | 0=-;1=Clear
97 | S3 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG1
97 | S4 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG2
97 | S5 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG3
97 | S6 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG4
97 | S7 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG5
97 | S8 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG6
97 | S9 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG7
97 | S10 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800 | SG8
97 | O1 | NJK1 | U0> RECL Blocked | SIGNAL_OUT | RW | 0...4294967295
97 | O2 | NJK1 | U0> RECL Active | SIGNAL_OUT | RW | 0...4294967295
97 | O3 | NJK1 | U0> RECL CLOSE | SIGNAL_OUT | RW | 0...4294967295
97 | O4 | NJK1 | U0> RECL BLKU0 | SIGNAL_OUT | RW | 0...4294967295
97 | I5 | NJK1 | Newest register | UINT32 | R | 0...12
97 | I6 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I7 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I8 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I9 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I10 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I11 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I12 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I13 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I14 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I15 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I16 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I17 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I18 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I19 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I20 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I21 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I22 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I23 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I24 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I25 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I26 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I27 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I28 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I29 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | S11 | NJK1 | EventMaskLo | UINT32 | RW | 0...4294967295
61 | S1 | SOF1 | SOTF mode | UINT32 | RW | 0=Disabled;1=Activated
61 | V1 | SOF1 | SOTF condition | UINT32 | R | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
61 | I1 | SOF1 | Inits | UINT32 | R | 0...4294967295
61 | I2 | SOF1 | Starts | UINT32 | R | 0...4294967295
61 | I3 | SOF1 | Trips | UINT32 | R | 0...4294967295
61 | I4 | SOF1 | Blocks | UINT32 | R | 0...4294967295
61 | S2 | SOF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
61 | S3 | SOF1 | Setting group in use | UINT32 | RW | 0...255
61 | S4 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG1
61 | S5 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG2
61 | S6 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG3
61 | S7 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG4
61 | S8 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG5
61 | S9 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG6
61 | S10 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG7
61 | S11 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800 | SG8
61 | O1 | SOF1 | SOTF Blocked | SIGNAL_OUT | RW | 0...4294967295
61 | O2 | SOF1 | SOTF Active | SIGNAL_OUT | RW | 0...4294967295
61 | O3 | SOF1 | SOTF Trip | SIGNAL_OUT | RW | 0...4294967295
61 | I5 | SOF1 | Newest register | UINT32 | R | 0...12
61 | I6 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I7 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I8 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I9 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I10 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I11 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I12 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I13 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I14 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I15 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I16 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I17 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I18 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I19 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I20 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I21 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I22 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I23 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I24 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I25 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I26 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I27 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I28 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I29 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | S12 | SOF1 | EventMaskLo | UINT32 | RW | 0...4294967295
142 | S1 | DOS1 | Energy dose counter mode | UINT32 | RW | 0=Disabled;1=Activated
142 | S2 | DOS1 | Clear pulse counters | UINT32 | W | 0=-;1=Clear
142 | S3 | DOS1 | DC 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S4 | DOS1 | DC 1 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I1 | DOS1 | DC 1 Input signal | FLOAT | R | -1000000...1000000
142 | S5 | DOS1 | DC 1 Pulse magnitude | FLOAT | RW | 0...1800
142 | S6 | DOS1 | DC 1 Pulse length | FLOAT | RW | 0...1800
142 | I2 | DOS1 | DC 1 Pulses sent | UINT32 | R | 0...4294967295
142 | S7 | DOS1 | DC 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S8 | DOS1 | DC 2 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I3 | DOS1 | DC 2 Input signal | FLOAT | R | -1000000...1000000
142 | S9 | DOS1 | DC 2 Pulse magnitude | FLOAT | RW | 0...1800
142 | S10 | DOS1 | DC 2 Pulse length | FLOAT | RW | 0...1800
142 | I4 | DOS1 | DC 2 Pulses sent | UINT32 | R | 0...4294967295
142 | S11 | DOS1 | DC 3 Enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S12 | DOS1 | DC 3 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I5 | DOS1 | DC 3 Input signal | FLOAT | R | -1000000...1000000
142 | S13 | DOS1 | DC 3 Pulse magnitude | FLOAT | RW | 0...1800
142 | S14 | DOS1 | DC 3 Pulse length | FLOAT | RW | 0...1800
142 | I6 | DOS1 | DC 3 Pulses sent | UINT32 | R | 0...4294967295
142 | S15 | DOS1 | DC 4 Enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S16 | DOS1 | DC 4 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I7 | DOS1 | DC 4 Input signal | FLOAT | R | -1000000...1000000
142 | S17 | DOS1 | DC 4 Pulse magnitude | FLOAT | RW | 0...1800
142 | S18 | DOS1 | DC 4 Pulse length | FLOAT | RW | 0...1800
142 | I8 | DOS1 | DC 4 Pulses sent | UINT32 | R | 0...4294967295
142 | O1 | DOS1 | DC 1 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O2 | DOS1 | DC 2 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O3 | DOS1 | DC 3 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O4 | DOS1 | DC 4 Pulse out | SIGNAL_OUT | RW | 0...4294967295
186 | S1 | DOS2 | Energy dose counter mode | UINT32 | RW | 0=Disabled;1=Activated
186 | S2 | DOS2 | Clear pulse counters | UINT32 | W | 0=-;1=Clear
186 | S3 | DOS2 | DC2 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
186 | S4 | DOS2 | DC2 1 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
186 | I1 | DOS2 | DC2 1 Input signal | FLOAT | R | -1000000...1000000
186 | S5 | DOS2 | DC2 1 Pulse magnitude | FLOAT | RW | 0...1800
186 | S6 | DOS2 | DC2 1 Pulse length | FLOAT | RW | 0...1800
186 | I2 | DOS2 | DC2 1 Pulses sent | UINT32 | R | 0...4294967295
186 | S7 | DOS2 | DC2 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
186 | S8 | DOS2 | DC2 2 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
186 | I3 | DOS2 | DC2 2 Input signal | FLOAT | R | -1000000...1000000
186 | S9 | DOS2 | DC2 2 Pulse magnitude | FLOAT | RW | 0...1800
186 | S10 | DOS2 | DC2 2 Pulse length | FLOAT | RW | 0...1800
186 | I4 | DOS2 | DC2 2 Pulses sent | UINT32 | R | 0...4294967295
186 | S11 | DOS2 | DC2 3 Enable | UINT32 | RW | 0=Disabled;1=Enabled
186 | S12 | DOS2 | DC2 3 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
186 | I5 | DOS2 | DC2 3 Input signal | FLOAT | R | -1000000...1000000
186 | S13 | DOS2 | DC2 3 Pulse magnitude | FLOAT | RW | 0...1800
186 | S14 | DOS2 | DC2 3 Pulse length | FLOAT | RW | 0...1800
186 | I6 | DOS2 | DC2 3 Pulses sent | UINT32 | R | 0...4294967295
186 | S15 | DOS2 | DC2 4 Enable | UINT32 | RW | 0=Disabled;1=Enabled
186 | S16 | DOS2 | DC2 4 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
186 | I7 | DOS2 | DC2 4 Input signal | FLOAT | R | -1000000...1000000
186 | S17 | DOS2 | DC2 4 Pulse magnitude | FLOAT | RW | 0...1800
186 | S18 | DOS2 | DC2 4 Pulse length | FLOAT | RW | 0...1800
186 | I8 | DOS2 | DC2 4 Pulses sent | UINT32 | R | 0...4294967295
186 | O1 | DOS2 | DC2 1 Pulse out | SIGNAL_OUT | RW | 0...4294967295
186 | O2 | DOS2 | DC2 2 Pulse out | SIGNAL_OUT | RW | 0...4294967295
186 | O3 | DOS2 | DC2 3 Pulse out | SIGNAL_OUT | RW | 0...4294967295
186 | O4 | DOS2 | DC2 4 Pulse out | SIGNAL_OUT | RW | 0...4294967295
144 | V1 | PCS1 | PCS1 Switch Status | SIGNAL_OUT | RW | 0...4294967295
145 | V1 | PCS2 | PCS2 Switch Status | SIGNAL_OUT | RW | 0...4294967295
146 | V1 | PCS3 | PCS3 Switch Status | SIGNAL_OUT | RW | 0...4294967295
147 | V1 | PCS4 | PCS4 Switch Status | SIGNAL_OUT | RW | 0...4294967295
148 | V1 | PCS5 | PCS5 Switch Status | SIGNAL_OUT | RW | 0...4294967295
45 | S1 | SYN1 | SYN(1,2,3) [25] mode | UINT32 | RW | 0=Disabled;1=Activated
45 | V1 | SYN1 | SYN1 Condition | UINT32 | R | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok;7b=SYN1 block input active
45 | V2 | SYN1 | SYN2 Condition | UINT32 | R | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok;7b=SYN2 block input active
45 | V3 | SYN1 | SYN3 Condition | UINT32 | R | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok;7b=SYN3 block input active
45 | I1 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I2 | SYN1 | SYN1 Mag diff | FLOAT | R | -120...120
45 | I3 | SYN1 | SYN1 Ang diff | FLOAT | R | -360...360
45 | I4 | SYN1 | SYN1 freq diff | FLOAT | R | -75...75
45 | I5 | SYN1 | SYN1 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S2 | SYN1 | SYN1 Estimated BRK Closing time | FLOAT | R | 0...360
45 | S3 | SYN1 | SYN1 Networks rotating time | FLOAT | R | 0...360
45 | S4 | SYN1 | SYN1 Networks placement atm | FLOAT | R | -360...360
45 | I6 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I7 | SYN1 | SYN2 Mag diff | FLOAT | R | -120...120
45 | I8 | SYN1 | SYN2 Ang diff | FLOAT | R | -360...360
45 | I9 | SYN1 | SYN2 freq diff | FLOAT | R | -75...75
45 | I10 | SYN1 | SYN2 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S5 | SYN1 | SYN2 Estimated BRK Closing time | FLOAT | R | 0...360
45 | S6 | SYN1 | SYN2 Networks rotating time | FLOAT | R | 0...360
45 | S7 | SYN1 | SYN2 Networks placement atm | FLOAT | R | -360...360
45 | I11 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I12 | SYN1 | SYN3 Mag diff | FLOAT | R | -120...120
45 | I13 | SYN1 | SYN3 Ang diff | FLOAT | R | -360...360
45 | I14 | SYN1 | SYN3 freq diff | FLOAT | R | -75...75
45 | I15 | SYN1 | SYN3 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S8 | SYN1 | SYN3 Estimated BRK Closing time | FLOAT | R | 0...360
45 | S9 | SYN1 | SYN3 Networks rotating time | FLOAT | R | 0...360
45 | S10 | SYN1 | SYN3 Networks placement atm | FLOAT | R | -360...360
45 | S11 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG1
45 | S12 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG2
45 | S13 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG3
45 | S14 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG4
45 | S15 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG5
45 | S16 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG6
45 | S17 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG7
45 | S18 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG8
45 | S19 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG1
45 | S20 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG2
45 | S21 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG3
45 | S22 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG4
45 | S23 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG5
45 | S24 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG6
45 | S25 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG7
45 | S26 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105 | SG8
45 | S27 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG1
45 | S28 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG2
45 | S29 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG3
45 | S30 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG4
45 | S31 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG5
45 | S32 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG6
45 | S33 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG7
45 | S34 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50 | SG8
45 | S35 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG1
45 | S36 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG2
45 | S37 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG3
45 | S38 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG4
45 | S39 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG5
45 | S40 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG6
45 | S41 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG7
45 | S42 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50 | SG8
45 | S43 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG1
45 | S44 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG2
45 | S45 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG3
45 | S46 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG4
45 | S47 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG5
45 | S48 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG6
45 | S49 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG7
45 | S50 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102 | SG8
45 | S51 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG1
45 | S52 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG2
45 | S53 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG3
45 | S54 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG4
45 | S55 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG5
45 | S56 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG6
45 | S57 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG7
45 | S58 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800 | SG8
45 | S59 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG1
45 | S60 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG2
45 | S61 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG3
45 | S62 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG4
45 | S63 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG5
45 | S64 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG6
45 | S65 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG7
45 | S66 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100 | SG8
45 | S67 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG1
45 | S68 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG2
45 | S69 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG3
45 | S70 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG4
45 | S71 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG5
45 | S72 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG6
45 | S73 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG7
45 | S74 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100 | SG8
45 | S75 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG1
45 | S76 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG2
45 | S77 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG3
45 | S78 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG4
45 | S79 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG5
45 | S80 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG6
45 | S81 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG7
45 | S82 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50 | SG8
45 | S83 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG1
45 | S84 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG2
45 | S85 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG3
45 | S86 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG4
45 | S87 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG5
45 | S88 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG6
45 | S89 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG7
45 | S90 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90 | SG8
45 | S91 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG1
45 | S92 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG2
45 | S93 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG3
45 | S94 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG4
45 | S95 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG5
45 | S96 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG6
45 | S97 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG7
45 | S98 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5 | SG8
45 | S99 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG1
45 | S100 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG2
45 | S101 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG3
45 | S102 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG4
45 | S103 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG5
45 | S104 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG6
45 | S105 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG7
45 | S106 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG8
45 | S107 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG1
45 | S108 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG2
45 | S109 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG3
45 | S110 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG4
45 | S111 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG5
45 | S112 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG6
45 | S113 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG7
45 | S114 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105 | SG8
45 | S115 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG1
45 | S116 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG2
45 | S117 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG3
45 | S118 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG4
45 | S119 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG5
45 | S120 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG6
45 | S121 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG7
45 | S122 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50 | SG8
45 | S123 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG1
45 | S124 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG2
45 | S125 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG3
45 | S126 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG4
45 | S127 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG5
45 | S128 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG6
45 | S129 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG7
45 | S130 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50 | SG8
45 | S131 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG1
45 | S132 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG2
45 | S133 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG3
45 | S134 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG4
45 | S135 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG5
45 | S136 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG6
45 | S137 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG7
45 | S138 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102 | SG8
45 | S139 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG1
45 | S140 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG2
45 | S141 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG3
45 | S142 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG4
45 | S143 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG5
45 | S144 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG6
45 | S145 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG7
45 | S146 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800 | SG8
45 | S147 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG1
45 | S148 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG2
45 | S149 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG3
45 | S150 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG4
45 | S151 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG5
45 | S152 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG6
45 | S153 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG7
45 | S154 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100 | SG8
45 | S155 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG1
45 | S156 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG2
45 | S157 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG3
45 | S158 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG4
45 | S159 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG5
45 | S160 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG6
45 | S161 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG7
45 | S162 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100 | SG8
45 | S163 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG1
45 | S164 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG2
45 | S165 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG3
45 | S166 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG4
45 | S167 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG5
45 | S168 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG6
45 | S169 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG7
45 | S170 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50 | SG8
45 | S171 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG1
45 | S172 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG2
45 | S173 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG3
45 | S174 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG4
45 | S175 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG5
45 | S176 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG6
45 | S177 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG7
45 | S178 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90 | SG8
45 | S179 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG1
45 | S180 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG2
45 | S181 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG3
45 | S182 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG4
45 | S183 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG5
45 | S184 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG6
45 | S185 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG7
45 | S186 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5 | SG8
45 | S187 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG1
45 | S188 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG2
45 | S189 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG3
45 | S190 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG4
45 | S191 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG5
45 | S192 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG6
45 | S193 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG7
45 | S194 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD | SG8
45 | S195 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG1
45 | S196 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG2
45 | S197 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG3
45 | S198 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG4
45 | S199 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG5
45 | S200 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG6
45 | S201 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG7
45 | S202 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105 | SG8
45 | S203 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG1
45 | S204 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG2
45 | S205 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG3
45 | S206 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG4
45 | S207 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG5
45 | S208 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG6
45 | S209 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG7
45 | S210 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50 | SG8
45 | S211 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG1
45 | S212 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG2
45 | S213 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG3
45 | S214 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG4
45 | S215 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG5
45 | S216 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG6
45 | S217 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG7
45 | S218 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50 | SG8
45 | S219 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG1
45 | S220 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG2
45 | S221 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG3
45 | S222 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG4
45 | S223 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG5
45 | S224 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG6
45 | S225 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG7
45 | S226 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102 | SG8
45 | S227 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG1
45 | S228 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG2
45 | S229 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG3
45 | S230 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG4
45 | S231 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG5
45 | S232 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG6
45 | S233 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG7
45 | S234 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800 | SG8
45 | S235 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG1
45 | S236 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG2
45 | S237 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG3
45 | S238 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG4
45 | S239 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG5
45 | S240 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG6
45 | S241 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG7
45 | S242 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100 | SG8
45 | S243 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG1
45 | S244 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG2
45 | S245 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG3
45 | S246 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG4
45 | S247 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG5
45 | S248 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG6
45 | S249 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG7
45 | S250 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100 | SG8
45 | S251 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG1
45 | S252 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG2
45 | S253 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG3
45 | S254 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG4
45 | S255 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG5
45 | S256 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG6
45 | S257 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG7
45 | S258 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50 | SG8
45 | S259 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG1
45 | S260 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG2
45 | S261 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG3
45 | S262 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG4
45 | S263 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG5
45 | S264 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG6
45 | S265 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG7
45 | S266 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90 | SG8
45 | S267 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG1
45 | S268 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG2
45 | S269 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG3
45 | S270 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG4
45 | S271 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG5
45 | S272 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG6
45 | S273 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG7
45 | S274 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5 | SG8
45 | O1 | SYN1 | SYN1 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O2 | SYN1 | SYN1 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O3 | SYN1 | SYN1 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O4 | SYN1 | SYN1 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O5 | SYN1 | SYN1 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O6 | SYN1 | SYN1 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O7 | SYN1 | SYN1 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O8 | SYN1 | SYN1 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O9 | SYN1 | SYN1 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O10 | SYN1 | SYN1 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O11 | SYN1 | SYN1 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O12 | SYN1 | SYN1 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O13 | SYN1 | SYN1 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O14 | SYN1 | SYN1 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O15 | SYN1 | SYN1 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O16 | SYN1 | SYN1 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O17 | SYN1 | SYN1 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O18 | SYN1 | SYN1 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O19 | SYN1 | SYN1 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O20 | SYN1 | SYN1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O21 | SYN1 | SYN1 In progress | SIGNAL_OUT | RW | 0...4294967295
45 | O22 | SYN1 | SYN2 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O23 | SYN1 | SYN2 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O24 | SYN1 | SYN2 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O25 | SYN1 | SYN2 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O26 | SYN1 | SYN2 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O27 | SYN1 | SYN2 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O28 | SYN1 | SYN2 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O29 | SYN1 | SYN2 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O30 | SYN1 | SYN2 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O31 | SYN1 | SYN2 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O32 | SYN1 | SYN2 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O33 | SYN1 | SYN2 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O34 | SYN1 | SYN2 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O35 | SYN1 | SYN2 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O36 | SYN1 | SYN2 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O37 | SYN1 | SYN2 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O38 | SYN1 | SYN2 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O39 | SYN1 | SYN2 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O40 | SYN1 | SYN2 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O41 | SYN1 | SYN2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O42 | SYN1 | SYN2 In progress | SIGNAL_OUT | RW | 0...4294967295
45 | O43 | SYN1 | SYN3 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O44 | SYN1 | SYN3 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O45 | SYN1 | SYN3 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O46 | SYN1 | SYN3 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O47 | SYN1 | SYN3 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O48 | SYN1 | SYN3 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O49 | SYN1 | SYN3 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O50 | SYN1 | SYN3 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O51 | SYN1 | SYN3 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O52 | SYN1 | SYN3 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O53 | SYN1 | SYN3 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O54 | SYN1 | SYN3 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O55 | SYN1 | SYN3 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O56 | SYN1 | SYN3 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O57 | SYN1 | SYN3 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O58 | SYN1 | SYN3 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O59 | SYN1 | SYN3 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O60 | SYN1 | SYN3 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O61 | SYN1 | SYN3 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O62 | SYN1 | SYN3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O63 | SYN1 | SYN3 In progress | SIGNAL_OUT | RW | 0...4294967295
45 | I16 | SYN1 | Newest register | UINT32 | R | 0...12
45 | I17 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I18 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I19 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I20 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I21 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I22 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I23 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I24 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I25 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I26 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I27 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I28 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I29 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I30 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I31 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I32 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I33 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I34 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I35 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I36 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I37 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I38 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I39 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I40 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I41 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I42 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I43 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I44 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I45 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I46 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I47 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I48 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I49 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I50 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I51 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I52 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I53 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I54 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I55 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I56 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I57 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I58 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I59 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I60 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I61 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I62 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I63 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I64 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I65 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I66 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I67 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I68 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I69 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I70 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I71 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I72 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I73 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I74 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I75 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I76 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I77 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I78 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I79 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I80 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I81 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I82 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I83 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I84 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I85 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I86 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I87 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I88 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I89 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I90 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I91 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I92 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I93 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I94 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I95 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I96 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I97 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I98 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I99 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I100 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I101 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I102 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I103 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I104 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I105 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I106 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I107 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I108 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I109 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I110 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I111 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I112 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I113 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I114 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I115 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I116 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I117 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I118 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I119 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I120 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I121 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I122 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I123 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I124 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I125 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I126 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I127 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I128 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I129 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I130 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I131 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I132 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I133 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I134 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I135 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I136 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I137 | SYN1 | Newest register | UINT32 | R | 0...12
45 | I138 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I139 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I140 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I141 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I142 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I143 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I144 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I145 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I146 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I147 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I148 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I149 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I150 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I151 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I152 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I153 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I154 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I155 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I156 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I157 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I158 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I159 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I160 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I161 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I162 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I163 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I164 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I165 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I166 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I167 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I168 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I169 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I170 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I171 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I172 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I173 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I174 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I175 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I176 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I177 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I178 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I179 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I180 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I181 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I182 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I183 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I184 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I185 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I186 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I187 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I188 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I189 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I190 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I191 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I192 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I193 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I194 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I195 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I196 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I197 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I198 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I199 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I200 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I201 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I202 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I203 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I204 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I205 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I206 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I207 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I208 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I209 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I210 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I211 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I212 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I213 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I214 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I215 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I216 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I217 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I218 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I219 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I220 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I221 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I222 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I223 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I224 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I225 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I226 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I227 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I228 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I229 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I230 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I231 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I232 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I233 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I234 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I235 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I236 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I237 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I238 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I239 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I240 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I241 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I242 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I243 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I244 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I245 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I246 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I247 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I248 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I249 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I250 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I251 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I252 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I253 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I254 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I255 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I256 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I257 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I258 | SYN1 | Newest register | UINT32 | R | 0...12
45 | I259 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I260 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I261 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I262 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I263 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I264 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I265 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I266 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I267 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I268 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I269 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I270 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I271 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I272 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I273 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I274 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I275 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I276 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I277 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I278 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I279 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I280 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I281 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I282 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I283 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I284 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I285 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I286 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I287 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I288 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I289 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I290 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I291 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I292 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I293 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I294 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I295 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I296 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I297 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I298 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I299 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I300 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I301 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I302 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I303 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I304 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I305 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I306 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I307 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I308 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I309 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I310 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I311 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I312 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I313 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I314 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I315 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I316 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I317 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I318 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I319 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I320 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I321 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I322 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I323 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I324 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I325 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I326 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I327 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I328 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I329 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I330 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I331 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I332 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I333 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I334 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I335 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I336 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I337 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I338 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I339 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I340 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I341 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I342 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I343 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I344 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I345 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I346 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I347 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I348 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I349 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I350 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I351 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I352 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I353 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I354 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I355 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I356 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I357 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I358 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I359 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I360 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I361 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I362 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I363 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I364 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I365 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I366 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I367 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I368 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I369 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I370 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I371 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I372 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I373 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I374 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I375 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I376 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I377 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I378 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | S275 | SYN1 | EventMaskLo | UINT32 | RW | 0...4294967295
45 | S276 | SYN1 | EventMaskHi | UINT32 | RW | 0...4294967295
232 | S1 | SYNX1 | SYN1 Extra EventMaskLo | UINT32 | RW | 0...4294967295
232 | S2 | SYNX1 | SYN1 Extra EventMaskHi | UINT32 | RW | 0...4294967295
233 | S1 | SYNX2 | SYN2 Extra EventMaskLo | UINT32 | RW | 0...4294967295
233 | S2 | SYNX2 | SYN2 Extra EventMaskHi | UINT32 | RW | 0...4294967295
234 | S1 | SYNX3 | SYN3 Extra EventMaskLo | UINT32 | RW | 0...4294967295
234 | S2 | SYNX3 | SYN3 Extra EventMaskHi | UINT32 | RW | 0...4294967295
155 | S1 | VJP1 | Vector jump <DELTA><alpha> > [78] mode | UINT32 | RW | 0=Disabled;1=Activated
155 | V1 | VJP1 | Vector jump <DELTA><alpha> > condition | UINT32 | R | 0=Normal;1=Blocked;2=Trip;3=Alarm
155 | S2 | VJP1 | Available stages | UINT32 | RW | 0=Trip;1=Trip and Alarm
155 | S3 | VJP1 | Monitored voltages | UINT32 | RW | 0=System all P-P Voltages;1=System any P-P Voltage;2=System L12 Voltage;3=System L23 Voltage;4=System L31 Voltage;5=System all P-E voltages;6=System any P-E voltage;7=System L1 Voltage;8=System L2 Voltage;9=System L3 Voltage;10=U4 Voltage
155 | V2 | VJP1 | Selected voltage measurement | UINT32 | R | 0=Selection Ok;1=Selection not available
155 | I1 | VJP1 | <DELTA><alpha> > U1 angle difference | FLOAT | R | -360...360
155 | I2 | VJP1 | <DELTA><alpha> U1 meas/set | FLOAT | R | -360...360
155 | I3 | VJP1 | <DELTA><alpha> U2 angle difference | FLOAT | R | -360...360
155 | I4 | VJP1 | <DELTA><alpha> U2 meas/set | FLOAT | R | -360...360
155 | I5 | VJP1 | <DELTA><alpha> U3 angle difference | FLOAT | R | -360...360
155 | I6 | VJP1 | <DELTA><alpha> U3 meas/set | FLOAT | R | -360...360
155 | I7 | VJP1 | <DELTA><alpha> > Alarms | UINT32 | R | 0...4294967295
155 | I8 | VJP1 | <DELTA><alpha> > Trips | UINT32 | R | 0...4294967295
155 | I9 | VJP1 | <DELTA><alpha> > Blocks | UINT32 | R | 0...4294967295
155 | S4 | VJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
155 | S5 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG1
155 | S6 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG2
155 | S7 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG3
155 | S8 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG4
155 | S9 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG5
155 | S10 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG6
155 | S11 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG7
155 | S12 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30 | SG8
155 | S13 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG1
155 | S14 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG2
155 | S15 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG3
155 | S16 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG4
155 | S17 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG5
155 | S18 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG6
155 | S19 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG7
155 | S20 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30 | SG8
155 | S21 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG1
155 | S22 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG2
155 | S23 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG3
155 | S24 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG4
155 | S25 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG5
155 | S26 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG6
155 | S27 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG7
155 | S28 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100 | SG8
155 | O1 | VJP1 | <DELTA><alpha> > TRIP | SIGNAL_OUT | RW | 0...4294967295
155 | O2 | VJP1 | <DELTA><alpha> > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
155 | I10 | VJP1 | Newest register | UINT32 | R | 0...12
155 | I11 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I12 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I13 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I14 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I15 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I16 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I17 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I18 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I19 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I20 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I21 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I22 | VJP1 | L2(3) ang difference fault | FLOAT | R | -360...360
155 | I23 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I24 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I25 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I26 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I27 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I28 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I29 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I30 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I31 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I32 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I33 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I34 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I35 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I36 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I37 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I38 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I39 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I40 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I41 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I42 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I43 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I44 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I45 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I46 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | S29 | VJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S1 | OBJ1 | Object1 mode | UINT32 | RW | 0=Disabled;1=Activated
46 | I1 | OBJ1 | Object1 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I2 | OBJ1 | Object1 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
46 | I3 | OBJ1 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | S2 | OBJ1 | Breaker traverse time | FLOAT | RW | 0.02...500
46 | S3 | OBJ1 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
46 | S4 | OBJ1 | Sync wait timeout | FLOAT | RW | 0.02...500
46 | S5 | OBJ1 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
46 | S6 | OBJ1 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
46 | S7 | OBJ1 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
46 | S8 | OBJ1 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
46 | S9 | OBJ1 | Control Termination Timeout | FLOAT | RW | 0.02...500
46 | S10 | OBJ1 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
46 | O1 | OBJ1 | Object1 Status Open | SIGNAL_OUT | RW | 0...4294967295
46 | O2 | OBJ1 | Object1 Status Closed | SIGNAL_OUT | RW | 0...4294967295
46 | O3 | OBJ1 | Object1 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
46 | O4 | OBJ1 | Object1 Status Bad | SIGNAL_OUT | RW | 0...4294967295
46 | O5 | OBJ1 | Object1 Open Command | SIGNAL_OUT | RW | 0...4294967295
46 | O6 | OBJ1 | Object1 Close Command | SIGNAL_OUT | RW | 0...4294967295
46 | O7 | OBJ1 | Object1 Open Request | SIGNAL_OUT | RW | 0...4294967295
46 | O8 | OBJ1 | Object1 Close Request | SIGNAL_OUT | RW | 0...4294967295
46 | O9 | OBJ1 | Object1 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
46 | O10 | OBJ1 | Object1 No sync wait | SIGNAL_OUT | RW | 0...4294967295
46 | O11 | OBJ1 | Object1 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
46 | O12 | OBJ1 | Object1 No sync fail | SIGNAL_OUT | RW | 0...4294967295
46 | O13 | OBJ1 | Object1 Open timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O14 | OBJ1 | Object1 Close timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O15 | OBJ1 | Object1 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O16 | OBJ1 | Object1 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O17 | OBJ1 | Object1 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
46 | O18 | OBJ1 | Object1 Final Trip | SIGNAL_OUT | RW | 0...4294967295
46 | O19 | OBJ1 | Object1 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
46 | O20 | OBJ1 | Object1 condition warning act | SIGNAL_OUT | RW | 0...4294967295
46 | O21 | OBJ1 | Object1 contact abrasion alarm | SIGNAL_OUT | RW | 0...4294967295
46 | O22 | OBJ1 | Object1 contact abrasion warning | SIGNAL_OUT | RW | 0...4294967295
46 | O23 | OBJ1 | Object1 Operating time exceeded | SIGNAL_OUT | RW | 0...4294967295
46 | O24 | OBJ1 | Object1 Open Blocked | SIGNAL_OUT | RW | 0...4294967295
46 | O25 | OBJ1 | Object1 Close Blocked | SIGNAL_OUT | RW | 0...4294967295
46 | O26 | OBJ1 | Object1 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
46 | S11 | OBJ1 | Object1 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
46 | S12 | OBJ1 | Object1 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
46 | S13 | OBJ1 | Object1 abrasion sum threshold warning | FLOAT | RW | 0...1000000
46 | I4 | OBJ1 | Newest register | UINT32 | R | 0...12
46 | I5 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I6 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I7 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I8 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I9 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I10 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I11 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I12 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I13 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I14 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I15 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I16 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I17 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I18 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I19 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I20 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I21 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I22 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I23 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I24 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I25 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I26 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I27 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I28 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I29 | OBJ1 | Open requests | UINT32 | R | 0...4294967295
46 | I30 | OBJ1 | Close requests | UINT32 | R | 0...4294967295
46 | I31 | OBJ1 | Open requests failed | UINT32 | R | 0...4294967295
46 | I32 | OBJ1 | Close requests failed | UINT32 | R | 0...4294967295
46 | S14 | OBJ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
46 | S15 | OBJ1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S16 | OBJ1 | EventMaskHi | UINT32 | RW | 0...4294967295
47 | S1 | OBJ2 | Object2 mode | UINT32 | RW | 0=Disabled;1=Activated
47 | I1 | OBJ2 | Object2 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I2 | OBJ2 | Object2 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
47 | I3 | OBJ2 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | S2 | OBJ2 | Breaker traverse time | FLOAT | RW | 0.02...500
47 | S3 | OBJ2 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
47 | S4 | OBJ2 | Sync wait timeout | FLOAT | RW | 0.02...500
47 | S5 | OBJ2 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
47 | S6 | OBJ2 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
47 | S7 | OBJ2 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
47 | S8 | OBJ2 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
47 | S9 | OBJ2 | Control Termination Timeout | FLOAT | RW | 0.02...500
47 | S10 | OBJ2 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
47 | O1 | OBJ2 | Object2 Status Open | SIGNAL_OUT | RW | 0...4294967295
47 | O2 | OBJ2 | Object2 Status Closed | SIGNAL_OUT | RW | 0...4294967295
47 | O3 | OBJ2 | Object2 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
47 | O4 | OBJ2 | Object2 Status Bad | SIGNAL_OUT | RW | 0...4294967295
47 | O5 | OBJ2 | Object2 Open Command | SIGNAL_OUT | RW | 0...4294967295
47 | O6 | OBJ2 | Object2 Close Command | SIGNAL_OUT | RW | 0...4294967295
47 | O7 | OBJ2 | Object2 Open Request | SIGNAL_OUT | RW | 0...4294967295
47 | O8 | OBJ2 | Object2 Close Request | SIGNAL_OUT | RW | 0...4294967295
47 | O9 | OBJ2 | Object2 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
47 | O10 | OBJ2 | Object2 No sync wait | SIGNAL_OUT | RW | 0...4294967295
47 | O11 | OBJ2 | Object2 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
47 | O12 | OBJ2 | Object2 No sync fail | SIGNAL_OUT | RW | 0...4294967295
47 | O13 | OBJ2 | Object2 Open timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O14 | OBJ2 | Object2 Close timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O15 | OBJ2 | Object2 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O16 | OBJ2 | Object2 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O17 | OBJ2 | Object2 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
47 | O18 | OBJ2 | Object2 Final Trip | SIGNAL_OUT | RW | 0...4294967295
47 | O19 | OBJ2 | Object2 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
47 | O20 | OBJ2 | Object2 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
47 | S11 | OBJ2 | Object2 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
47 | S12 | OBJ2 | Object2 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
47 | S13 | OBJ2 | Object2 abrasion sum threshold warning | FLOAT | RW | 0...1000000
47 | I4 | OBJ2 | Newest register | UINT32 | R | 0...12
47 | I5 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I6 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I7 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I8 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I9 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I10 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I11 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I12 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I13 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I14 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I15 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I16 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I17 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I18 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I19 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I20 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I21 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I22 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I23 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I24 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I25 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I26 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I27 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I28 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I29 | OBJ2 | Open requests | UINT32 | R | 0...4294967295
47 | I30 | OBJ2 | Close requests | UINT32 | R | 0...4294967295
47 | I31 | OBJ2 | Open requests failed | UINT32 | R | 0...4294967295
47 | I32 | OBJ2 | Close requests failed | UINT32 | R | 0...4294967295
47 | S14 | OBJ2 | Clear statistics | UINT32 | W | 0=-;1=Clear
47 | S15 | OBJ2 | EventMaskLo | UINT32 | RW | 0...4294967295
47 | S16 | OBJ2 | EventMaskHi | UINT32 | RW | 0...4294967295
48 | S1 | OBJ3 | Object3 mode | UINT32 | RW | 0=Disabled;1=Activated
48 | I1 | OBJ3 | Object3 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I2 | OBJ3 | Object3 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
48 | I3 | OBJ3 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | S2 | OBJ3 | Breaker traverse time | FLOAT | RW | 0.02...500
48 | S3 | OBJ3 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
48 | S4 | OBJ3 | Sync wait timeout | FLOAT | RW | 0.02...500
48 | S5 | OBJ3 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
48 | S6 | OBJ3 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
48 | S7 | OBJ3 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
48 | S8 | OBJ3 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
48 | S9 | OBJ3 | Control Termination Timeout | FLOAT | RW | 0.02...500
48 | S10 | OBJ3 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
48 | O1 | OBJ3 | Object3 Status Open | SIGNAL_OUT | RW | 0...4294967295
48 | O2 | OBJ3 | Object3 Status Closed | SIGNAL_OUT | RW | 0...4294967295
48 | O3 | OBJ3 | Object3 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
48 | O4 | OBJ3 | Object3 Status Bad | SIGNAL_OUT | RW | 0...4294967295
48 | O5 | OBJ3 | Object3 Open Command | SIGNAL_OUT | RW | 0...4294967295
48 | O6 | OBJ3 | Object3 Close Command | SIGNAL_OUT | RW | 0...4294967295
48 | O7 | OBJ3 | Object3 Open Request | SIGNAL_OUT | RW | 0...4294967295
48 | O8 | OBJ3 | Object3 Close Request | SIGNAL_OUT | RW | 0...4294967295
48 | O9 | OBJ3 | Object3 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
48 | O10 | OBJ3 | Object3 No sync wait | SIGNAL_OUT | RW | 0...4294967295
48 | O11 | OBJ3 | Object3 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
48 | O12 | OBJ3 | Object3 No sync fail | SIGNAL_OUT | RW | 0...4294967295
48 | O13 | OBJ3 | Object3 Open timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O14 | OBJ3 | Object3 Close timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O15 | OBJ3 | Object3 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O16 | OBJ3 | Object3 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O17 | OBJ3 | Object3 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
48 | O18 | OBJ3 | Object3 Final Trip | SIGNAL_OUT | RW | 0...4294967295
48 | O19 | OBJ3 | Object3 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
48 | O20 | OBJ3 | Object3 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
48 | S11 | OBJ3 | Object3 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
48 | S12 | OBJ3 | Object3 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
48 | S13 | OBJ3 | Object3 abrasion sum threshold warning | FLOAT | RW | 0...1000000
48 | I4 | OBJ3 | Newest register | UINT32 | R | 0...12
48 | I5 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I6 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I7 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I8 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I9 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I10 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I11 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I12 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I13 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I14 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I15 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I16 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I17 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I18 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I19 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I20 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I21 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I22 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I23 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I24 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I25 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I26 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I27 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I28 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I29 | OBJ3 | Open requests | UINT32 | R | 0...4294967295
48 | I30 | OBJ3 | Close requests | UINT32 | R | 0...4294967295
48 | I31 | OBJ3 | Open requests failed | UINT32 | R | 0...4294967295
48 | I32 | OBJ3 | Close requests failed | UINT32 | R | 0...4294967295
48 | S14 | OBJ3 | Clear statistics | UINT32 | W | 0=-;1=Clear
48 | S15 | OBJ3 | EventMaskLo | UINT32 | RW | 0...4294967295
48 | S16 | OBJ3 | EventMaskHi | UINT32 | RW | 0...4294967295
49 | S1 | OBJ4 | Object4 mode | UINT32 | RW | 0=Disabled;1=Activated
49 | I1 | OBJ4 | Object4 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I2 | OBJ4 | Object4 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
49 | I3 | OBJ4 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | S2 | OBJ4 | Breaker traverse time | FLOAT | RW | 0.02...500
49 | S3 | OBJ4 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
49 | S4 | OBJ4 | Sync wait timeout | FLOAT | RW | 0.02...500
49 | S5 | OBJ4 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
49 | S6 | OBJ4 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
49 | S7 | OBJ4 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
49 | S8 | OBJ4 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
49 | S9 | OBJ4 | Control Termination Timeout | FLOAT | RW | 0.02...500
49 | S10 | OBJ4 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
49 | O1 | OBJ4 | Object4 Status Open | SIGNAL_OUT | RW | 0...4294967295
49 | O2 | OBJ4 | Object4 Status Closed | SIGNAL_OUT | RW | 0...4294967295
49 | O3 | OBJ4 | Object4 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
49 | O4 | OBJ4 | Object4 Status Bad | SIGNAL_OUT | RW | 0...4294967295
49 | O5 | OBJ4 | Object4 Open Command | SIGNAL_OUT | RW | 0...4294967295
49 | O6 | OBJ4 | Object4 Close Command | SIGNAL_OUT | RW | 0...4294967295
49 | O7 | OBJ4 | Object4 Open Request | SIGNAL_OUT | RW | 0...4294967295
49 | O8 | OBJ4 | Object4 Close Request | SIGNAL_OUT | RW | 0...4294967295
49 | O9 | OBJ4 | Object4 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
49 | O10 | OBJ4 | Object4 No sync wait | SIGNAL_OUT | RW | 0...4294967295
49 | O11 | OBJ4 | Object4 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
49 | O12 | OBJ4 | Object4 No sync fail | SIGNAL_OUT | RW | 0...4294967295
49 | O13 | OBJ4 | Object4 Open timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O14 | OBJ4 | Object4 Close timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O15 | OBJ4 | Object4 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O16 | OBJ4 | Object4 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O17 | OBJ4 | Object4 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
49 | O18 | OBJ4 | Object4 Final Trip | SIGNAL_OUT | RW | 0...4294967295
49 | O19 | OBJ4 | Object4 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
49 | O20 | OBJ4 | Object4 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
49 | S11 | OBJ4 | Object4 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
49 | S12 | OBJ4 | Object4 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
49 | S13 | OBJ4 | Object4 abrasion sum threshold warning | FLOAT | RW | 0...1000000
49 | I4 | OBJ4 | Newest register | UINT32 | R | 0...12
49 | I5 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I6 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I7 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I8 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I9 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I10 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I11 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I12 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I13 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I14 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I15 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I16 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I17 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I18 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I19 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I20 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I21 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I22 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I23 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I24 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I25 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I26 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I27 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I28 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I29 | OBJ4 | Open requests | UINT32 | R | 0...4294967295
49 | I30 | OBJ4 | Close requests | UINT32 | R | 0...4294967295
49 | I31 | OBJ4 | Open requests failed | UINT32 | R | 0...4294967295
49 | I32 | OBJ4 | Close requests failed | UINT32 | R | 0...4294967295
49 | S14 | OBJ4 | Clear statistics | UINT32 | W | 0=-;1=Clear
49 | S15 | OBJ4 | EventMaskLo | UINT32 | RW | 0...4294967295
49 | S16 | OBJ4 | EventMaskHi | UINT32 | RW | 0...4294967295
50 | S1 | OBJ5 | Object5 mode | UINT32 | RW | 0=Disabled;1=Activated
50 | I1 | OBJ5 | Object5 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I2 | OBJ5 | Object5 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
50 | I3 | OBJ5 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | S2 | OBJ5 | Breaker traverse time | FLOAT | RW | 0.02...500
50 | S3 | OBJ5 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
50 | S4 | OBJ5 | Sync wait timeout | FLOAT | RW | 0.02...500
50 | S5 | OBJ5 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
50 | S6 | OBJ5 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
50 | S7 | OBJ5 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
50 | S8 | OBJ5 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
50 | S9 | OBJ5 | Control Termination Timeout | FLOAT | RW | 0.02...500
50 | S10 | OBJ5 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
50 | O1 | OBJ5 | Object5 Status Open | SIGNAL_OUT | RW | 0...4294967295
50 | O2 | OBJ5 | Object5 Status Closed | SIGNAL_OUT | RW | 0...4294967295
50 | O3 | OBJ5 | Object5 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
50 | O4 | OBJ5 | Object5 Status Bad | SIGNAL_OUT | RW | 0...4294967295
50 | O5 | OBJ5 | Object5 Open Command | SIGNAL_OUT | RW | 0...4294967295
50 | O6 | OBJ5 | Object5 Close Command | SIGNAL_OUT | RW | 0...4294967295
50 | O7 | OBJ5 | Object5 Open Request | SIGNAL_OUT | RW | 0...4294967295
50 | O8 | OBJ5 | Object5 Close Request | SIGNAL_OUT | RW | 0...4294967295
50 | O9 | OBJ5 | Object5 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
50 | O10 | OBJ5 | Object5 No sync wait | SIGNAL_OUT | RW | 0...4294967295
50 | O11 | OBJ5 | Object5 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
50 | O12 | OBJ5 | Object5 No sync fail | SIGNAL_OUT | RW | 0...4294967295
50 | O13 | OBJ5 | Object5 Open timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O14 | OBJ5 | Object5 Close timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O15 | OBJ5 | Object5 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O16 | OBJ5 | Object5 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O17 | OBJ5 | Object5 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
50 | O18 | OBJ5 | Object5 Final Trip | SIGNAL_OUT | RW | 0...4294967295
50 | O19 | OBJ5 | Object5 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
50 | O20 | OBJ5 | Object5 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
50 | S11 | OBJ5 | Object5 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
50 | S12 | OBJ5 | Object5 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
50 | S13 | OBJ5 | Object5 abrasion sum threshold warning | FLOAT | RW | 0...1000000
50 | I4 | OBJ5 | Newest register | UINT32 | R | 0...12
50 | I5 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I6 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I7 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I8 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I9 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I10 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I11 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I12 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I13 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I14 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I15 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I16 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I17 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I18 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I19 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I20 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I21 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I22 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I23 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I24 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I25 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I26 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I27 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I28 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I29 | OBJ5 | Open requests | UINT32 | R | 0...4294967295
50 | I30 | OBJ5 | Close requests | UINT32 | R | 0...4294967295
50 | I31 | OBJ5 | Open requests failed | UINT32 | R | 0...4294967295
50 | I32 | OBJ5 | Close requests failed | UINT32 | R | 0...4294967295
50 | S14 | OBJ5 | Clear statistics | UINT32 | W | 0=-;1=Clear
50 | S15 | OBJ5 | EventMaskLo | UINT32 | RW | 0...4294967295
50 | S16 | OBJ5 | EventMaskHi | UINT32 | RW | 0...4294967295
150 | S1 | OBJ6 | Object6 mode | UINT32 | RW | 0=Disabled;1=Activated
150 | I1 | OBJ6 | Object6 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I2 | OBJ6 | Object6 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
150 | I3 | OBJ6 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | S2 | OBJ6 | Breaker traverse time | FLOAT | RW | 0.02...500
150 | S3 | OBJ6 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
150 | S4 | OBJ6 | Sync wait timeout | FLOAT | RW | 0.02...500
150 | S5 | OBJ6 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
150 | S6 | OBJ6 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
150 | S7 | OBJ6 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
150 | S8 | OBJ6 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
150 | S9 | OBJ6 | Control Termination Timeout | FLOAT | RW | 0.02...500
150 | S10 | OBJ6 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
150 | O1 | OBJ6 | Object6 Status Open | SIGNAL_OUT | RW | 0...4294967295
150 | O2 | OBJ6 | Object6 Status Closed | SIGNAL_OUT | RW | 0...4294967295
150 | O3 | OBJ6 | Object6 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
150 | O4 | OBJ6 | Object6 Status Bad | SIGNAL_OUT | RW | 0...4294967295
150 | O5 | OBJ6 | Object6 Open Command | SIGNAL_OUT | RW | 0...4294967295
150 | O6 | OBJ6 | Object6 Close Command | SIGNAL_OUT | RW | 0...4294967295
150 | O7 | OBJ6 | Object6 Open Request | SIGNAL_OUT | RW | 0...4294967295
150 | O8 | OBJ6 | Object6 Close Request | SIGNAL_OUT | RW | 0...4294967295
150 | O9 | OBJ6 | Object6 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
150 | O10 | OBJ6 | Object6 No sync wait | SIGNAL_OUT | RW | 0...4294967295
150 | O11 | OBJ6 | Object6 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
150 | O12 | OBJ6 | Object6 No sync fail | SIGNAL_OUT | RW | 0...4294967295
150 | O13 | OBJ6 | Object6 Open timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O14 | OBJ6 | Object6 Close timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O15 | OBJ6 | Object6 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O16 | OBJ6 | Object6 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O17 | OBJ6 | Object6 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
150 | O18 | OBJ6 | Object6 Final Trip | SIGNAL_OUT | RW | 0...4294967295
150 | O19 | OBJ6 | Object6 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
150 | O20 | OBJ6 | Object6 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
150 | S11 | OBJ6 | Object6 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
150 | S12 | OBJ6 | Object6 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
150 | S13 | OBJ6 | Object6 abrasion sum threshold warning | FLOAT | RW | 0...1000000
150 | I4 | OBJ6 | Newest register | UINT32 | R | 0...12
150 | I5 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I6 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I7 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I8 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I9 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I10 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I11 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I12 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I13 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I14 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I15 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I16 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I17 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I18 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I19 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I20 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I21 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I22 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I23 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I24 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I25 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I26 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I27 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I28 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I29 | OBJ6 | Open requests | UINT32 | R | 0...4294967295
150 | I30 | OBJ6 | Close requests | UINT32 | R | 0...4294967295
150 | I31 | OBJ6 | Open requests failed | UINT32 | R | 0...4294967295
150 | I32 | OBJ6 | Close requests failed | UINT32 | R | 0...4294967295
150 | S14 | OBJ6 | Clear statistics | UINT32 | W | 0=-;1=Clear
150 | S15 | OBJ6 | EventMaskLo | UINT32 | RW | 0...4294967295
150 | S16 | OBJ6 | EventMaskHi | UINT32 | RW | 0...4294967295
151 | S1 | OBJ7 | Object7 mode | UINT32 | RW | 0=Disabled;1=Activated
151 | I1 | OBJ7 | Object7 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I2 | OBJ7 | Object7 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
151 | I3 | OBJ7 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | S2 | OBJ7 | Breaker traverse time | FLOAT | RW | 0.02...500
151 | S3 | OBJ7 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
151 | S4 | OBJ7 | Sync wait timeout | FLOAT | RW | 0.02...500
151 | S5 | OBJ7 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
151 | S6 | OBJ7 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
151 | S7 | OBJ7 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
151 | S8 | OBJ7 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
151 | S9 | OBJ7 | Control Termination Timeout | FLOAT | RW | 0.02...500
151 | S10 | OBJ7 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
151 | O1 | OBJ7 | Object7 Status Open | SIGNAL_OUT | RW | 0...4294967295
151 | O2 | OBJ7 | Object7 Status Closed | SIGNAL_OUT | RW | 0...4294967295
151 | O3 | OBJ7 | Object7 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
151 | O4 | OBJ7 | Object7 Status Bad | SIGNAL_OUT | RW | 0...4294967295
151 | O5 | OBJ7 | Object7 Open Command | SIGNAL_OUT | RW | 0...4294967295
151 | O6 | OBJ7 | Object7 Close Command | SIGNAL_OUT | RW | 0...4294967295
151 | O7 | OBJ7 | Object7 Open Request | SIGNAL_OUT | RW | 0...4294967295
151 | O8 | OBJ7 | Object7 Close Request | SIGNAL_OUT | RW | 0...4294967295
151 | O9 | OBJ7 | Object7 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
151 | O10 | OBJ7 | Object7 No sync wait | SIGNAL_OUT | RW | 0...4294967295
151 | O11 | OBJ7 | Object7 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
151 | O12 | OBJ7 | Object7 No sync fail | SIGNAL_OUT | RW | 0...4294967295
151 | O13 | OBJ7 | Object7 Open timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O14 | OBJ7 | Object7 Close timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O15 | OBJ7 | Object7 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O16 | OBJ7 | Object7 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O17 | OBJ7 | Object7 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
151 | O18 | OBJ7 | Object7 Final Trip | SIGNAL_OUT | RW | 0...4294967295
151 | O19 | OBJ7 | Object7 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
151 | O20 | OBJ7 | Object7 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
151 | S11 | OBJ7 | Object7 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
151 | S12 | OBJ7 | Object7 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
151 | S13 | OBJ7 | Object7 abrasion sum threshold warning | FLOAT | RW | 0...1000000
151 | I4 | OBJ7 | Newest register | UINT32 | R | 0...12
151 | I5 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I6 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I7 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I8 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I9 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I10 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I11 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I12 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I13 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I14 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I15 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I16 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I17 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I18 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I19 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I20 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I21 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I22 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I23 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I24 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I25 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I26 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I27 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I28 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I29 | OBJ7 | Open requests | UINT32 | R | 0...4294967295
151 | I30 | OBJ7 | Close requests | UINT32 | R | 0...4294967295
151 | I31 | OBJ7 | Open requests failed | UINT32 | R | 0...4294967295
151 | I32 | OBJ7 | Close requests failed | UINT32 | R | 0...4294967295
151 | S14 | OBJ7 | Clear statistics | UINT32 | W | 0=-;1=Clear
151 | S15 | OBJ7 | EventMaskLo | UINT32 | RW | 0...4294967295
151 | S16 | OBJ7 | EventMaskHi | UINT32 | RW | 0...4294967295
152 | S1 | OBJ8 | Object8 mode | UINT32 | RW | 0=Disabled;1=Activated
152 | I1 | OBJ8 | Object8 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I2 | OBJ8 | Object8 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
152 | I3 | OBJ8 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | S2 | OBJ8 | Breaker traverse time | FLOAT | RW | 0.02...500
152 | S3 | OBJ8 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
152 | S4 | OBJ8 | Sync wait timeout | FLOAT | RW | 0.02...500
152 | S5 | OBJ8 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
152 | S6 | OBJ8 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
152 | S7 | OBJ8 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
152 | S8 | OBJ8 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
152 | S9 | OBJ8 | Control Termination Timeout | FLOAT | RW | 0.02...500
152 | S10 | OBJ8 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
152 | O1 | OBJ8 | Object8 Status Open | SIGNAL_OUT | RW | 0...4294967295
152 | O2 | OBJ8 | Object8 Status Closed | SIGNAL_OUT | RW | 0...4294967295
152 | O3 | OBJ8 | Object8 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
152 | O4 | OBJ8 | Object8 Status Bad | SIGNAL_OUT | RW | 0...4294967295
152 | O5 | OBJ8 | Object8 Open Command | SIGNAL_OUT | RW | 0...4294967295
152 | O6 | OBJ8 | Object8 Close Command | SIGNAL_OUT | RW | 0...4294967295
152 | O7 | OBJ8 | Object8 Open Request | SIGNAL_OUT | RW | 0...4294967295
152 | O8 | OBJ8 | Object8 Close Request | SIGNAL_OUT | RW | 0...4294967295
152 | O9 | OBJ8 | Object8 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
152 | O10 | OBJ8 | Object8 No sync wait | SIGNAL_OUT | RW | 0...4294967295
152 | O11 | OBJ8 | Object8 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
152 | O12 | OBJ8 | Object8 No sync fail | SIGNAL_OUT | RW | 0...4294967295
152 | O13 | OBJ8 | Object8 Open timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O14 | OBJ8 | Object8 Close timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O15 | OBJ8 | Object8 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O16 | OBJ8 | Object8 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O17 | OBJ8 | Object8 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
152 | O18 | OBJ8 | Object8 Final Trip | SIGNAL_OUT | RW | 0...4294967295
152 | O19 | OBJ8 | Object8 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
152 | O20 | OBJ8 | Object8 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
152 | S11 | OBJ8 | Object8 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
152 | S12 | OBJ8 | Object8 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
152 | S13 | OBJ8 | Object8 abrasion sum threshold warning | FLOAT | RW | 0...1000000
152 | I4 | OBJ8 | Newest register | UINT32 | R | 0...12
152 | I5 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I6 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I7 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I8 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I9 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I10 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I11 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I12 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I13 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I14 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I15 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I16 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I17 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I18 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I19 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I20 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I21 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I22 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I23 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I24 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I25 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I26 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I27 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I28 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I29 | OBJ8 | Open requests | UINT32 | R | 0...4294967295
152 | I30 | OBJ8 | Close requests | UINT32 | R | 0...4294967295
152 | I31 | OBJ8 | Open requests failed | UINT32 | R | 0...4294967295
152 | I32 | OBJ8 | Close requests failed | UINT32 | R | 0...4294967295
152 | S14 | OBJ8 | Clear statistics | UINT32 | W | 0=-;1=Clear
152 | S15 | OBJ8 | EventMaskLo | UINT32 | RW | 0...4294967295
152 | S16 | OBJ8 | EventMaskHi | UINT32 | RW | 0...4294967295
153 | S1 | OBJ9 | Object9 mode | UINT32 | RW | 0=Disabled;1=Activated
153 | I1 | OBJ9 | Object9 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I2 | OBJ9 | Object9 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
153 | I3 | OBJ9 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | S2 | OBJ9 | Breaker traverse time | FLOAT | RW | 0.02...500
153 | S3 | OBJ9 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
153 | S4 | OBJ9 | Sync wait timeout | FLOAT | RW | 0.02...500
153 | S5 | OBJ9 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
153 | S6 | OBJ9 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
153 | S7 | OBJ9 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
153 | S8 | OBJ9 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
153 | S9 | OBJ9 | Control Termination Timeout | FLOAT | RW | 0.02...500
153 | S10 | OBJ9 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
153 | O1 | OBJ9 | Object9 Status Open | SIGNAL_OUT | RW | 0...4294967295
153 | O2 | OBJ9 | Object9 Status Closed | SIGNAL_OUT | RW | 0...4294967295
153 | O3 | OBJ9 | Object9 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
153 | O4 | OBJ9 | Object9 Status Bad | SIGNAL_OUT | RW | 0...4294967295
153 | O5 | OBJ9 | Object9 Open Command | SIGNAL_OUT | RW | 0...4294967295
153 | O6 | OBJ9 | Object9 Close Command | SIGNAL_OUT | RW | 0...4294967295
153 | O7 | OBJ9 | Object9 Open Request | SIGNAL_OUT | RW | 0...4294967295
153 | O8 | OBJ9 | Object9 Close Request | SIGNAL_OUT | RW | 0...4294967295
153 | O9 | OBJ9 | Object9 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
153 | O10 | OBJ9 | Object9 No sync wait | SIGNAL_OUT | RW | 0...4294967295
153 | O11 | OBJ9 | Object9 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
153 | O12 | OBJ9 | Object9 No sync fail | SIGNAL_OUT | RW | 0...4294967295
153 | O13 | OBJ9 | Object9 Open timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O14 | OBJ9 | Object9 Close timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O15 | OBJ9 | Object9 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O16 | OBJ9 | Object9 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O17 | OBJ9 | Object9 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
153 | O18 | OBJ9 | Object9 Final Trip | SIGNAL_OUT | RW | 0...4294967295
153 | O19 | OBJ9 | Object9 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
153 | O20 | OBJ9 | Object9 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
153 | S11 | OBJ9 | Object9 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
153 | S12 | OBJ9 | Object9 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
153 | S13 | OBJ9 | Object9 abrasion sum threshold warning | FLOAT | RW | 0...1000000
153 | I4 | OBJ9 | Newest register | UINT32 | R | 0...12
153 | I5 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I6 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I7 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I8 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I9 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I10 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I11 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I12 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I13 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I14 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I15 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I16 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I17 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I18 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I19 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I20 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I21 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I22 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I23 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I24 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I25 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I26 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I27 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I28 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I29 | OBJ9 | Open requests | UINT32 | R | 0...4294967295
153 | I30 | OBJ9 | Close requests | UINT32 | R | 0...4294967295
153 | I31 | OBJ9 | Open requests failed | UINT32 | R | 0...4294967295
153 | I32 | OBJ9 | Close requests failed | UINT32 | R | 0...4294967295
153 | S14 | OBJ9 | Clear statistics | UINT32 | W | 0=-;1=Clear
153 | S15 | OBJ9 | EventMaskLo | UINT32 | RW | 0...4294967295
153 | S16 | OBJ9 | EventMaskHi | UINT32 | RW | 0...4294967295
154 | S1 | OBJ10 | Object10 mode | UINT32 | RW | 0=Disabled;1=Activated
154 | I1 | OBJ10 | Object10 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I2 | OBJ10 | Object10 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
154 | I3 | OBJ10 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | S2 | OBJ10 | Breaker traverse time | FLOAT | RW | 0.02...500
154 | S3 | OBJ10 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
154 | S4 | OBJ10 | Sync wait timeout | FLOAT | RW | 0.02...500
154 | S5 | OBJ10 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
154 | S6 | OBJ10 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
154 | S7 | OBJ10 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
154 | S8 | OBJ10 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
154 | S9 | OBJ10 | Control Termination Timeout | FLOAT | RW | 0.02...500
154 | S10 | OBJ10 | Final Trip pulse length (0 continuous signal) | FLOAT | RW | 0...500
154 | O1 | OBJ10 | Object10 Status Open | SIGNAL_OUT | RW | 0...4294967295
154 | O2 | OBJ10 | Object10 Status Closed | SIGNAL_OUT | RW | 0...4294967295
154 | O3 | OBJ10 | Object10 Status Intermediate | SIGNAL_OUT | RW | 0...4294967295
154 | O4 | OBJ10 | Object10 Status Bad | SIGNAL_OUT | RW | 0...4294967295
154 | O5 | OBJ10 | Object10 Open Command | SIGNAL_OUT | RW | 0...4294967295
154 | O6 | OBJ10 | Object10 Close Command | SIGNAL_OUT | RW | 0...4294967295
154 | O7 | OBJ10 | Object10 Open Request | SIGNAL_OUT | RW | 0...4294967295
154 | O8 | OBJ10 | Object10 Close Request | SIGNAL_OUT | RW | 0...4294967295
154 | O9 | OBJ10 | Object10 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
154 | O10 | OBJ10 | Object10 No sync wait | SIGNAL_OUT | RW | 0...4294967295
154 | O11 | OBJ10 | Object10 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
154 | O12 | OBJ10 | Object10 No sync fail | SIGNAL_OUT | RW | 0...4294967295
154 | O13 | OBJ10 | Object10 Open timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O14 | OBJ10 | Object10 Close timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O15 | OBJ10 | Object10 Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O16 | OBJ10 | Object10 Close Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O17 | OBJ10 | Object10 Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
154 | O18 | OBJ10 | Object10 Final Trip | SIGNAL_OUT | RW | 0...4294967295
154 | O19 | OBJ10 | Object10 condition alarm act | SIGNAL_OUT | RW | 0...4294967295
154 | O20 | OBJ10 | Object10 TCS Alarm | SIGNAL_OUT | RW | 0...4294967295
154 | S11 | OBJ10 | Object10 abrasion alarm/warning enable | UINT32 | RW | 0=Disabled;1=Enabled
154 | S12 | OBJ10 | Object10 abrasion sum threshold alarm | FLOAT | RW | 0...1000000
154 | S13 | OBJ10 | Object10 abrasion sum threshold warning | FLOAT | RW | 0...1000000
154 | I4 | OBJ10 | Newest register | UINT32 | R | 0...12
154 | I5 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I6 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I7 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I8 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I9 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I10 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I11 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I12 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I13 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I14 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I15 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I16 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I17 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I18 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I19 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I20 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I21 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I22 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I23 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I24 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I25 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I26 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I27 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I28 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I29 | OBJ10 | Open requests | UINT32 | R | 0...4294967295
154 | I30 | OBJ10 | Close requests | UINT32 | R | 0...4294967295
154 | I31 | OBJ10 | Open requests failed | UINT32 | R | 0...4294967295
154 | I32 | OBJ10 | Close requests failed | UINT32 | R | 0...4294967295
154 | S14 | OBJ10 | Clear statistics | UINT32 | W | 0=-;1=Clear
154 | S15 | OBJ10 | EventMaskLo | UINT32 | RW | 0...4294967295
154 | S16 | OBJ10 | EventMaskHi | UINT32 | RW | 0...4294967295
104 | S1 | CIN1 | Indicator 1 mode | UINT32 | RW | 0=Disabled;1=Activated
104 | I1 | CIN1 | Ind.1 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
105 | S1 | CIN2 | Indicator 2 mode | UINT32 | RW | 0=Disabled;1=Activated
105 | I1 | CIN2 | Ind.2 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
106 | S1 | CIN3 | Indicator 3 mode | UINT32 | RW | 0=Disabled;1=Activated
106 | I1 | CIN3 | Ind.3 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
107 | S1 | CIN4 | Indicator 4 mode | UINT32 | RW | 0=Disabled;1=Activated
107 | I1 | CIN4 | Ind.4 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
108 | S1 | CIN5 | Indicator 5 mode | UINT32 | RW | 0=Disabled;1=Activated
108 | I1 | CIN5 | Ind.5 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
168 | S1 | CIN6 | Indicator 6 mode | UINT32 | RW | 0=Disabled;1=Activated
168 | I1 | CIN6 | Ind.6 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
169 | S1 | CIN7 | Indicator 7 mode | UINT32 | RW | 0=Disabled;1=Activated
169 | I1 | CIN7 | Ind.7 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
170 | S1 | CIN8 | Indicator 8 mode | UINT32 | RW | 0=Disabled;1=Activated
170 | I1 | CIN8 | Ind.8 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
171 | S1 | CIN9 | Indicator 9 mode | UINT32 | RW | 0=Disabled;1=Activated
171 | I1 | CIN9 | Ind.9 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
172 | S1 | CIN10 | Indicator 10 mode | UINT32 | RW | 0=Disabled;1=Activated
172 | I1 | CIN10 | Ind.10 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
173 | S1 | CIN11 | Indicator 11 mode | UINT32 | RW | 0=Disabled;1=Activated
173 | I1 | CIN11 | Ind.11 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
174 | S1 | CIN12 | Indicator 12 mode | UINT32 | RW | 0=Disabled;1=Activated
174 | I1 | CIN12 | Ind.12 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
175 | S1 | CIN13 | Indicator 13 mode | UINT32 | RW | 0=Disabled;1=Activated
175 | I1 | CIN13 | Ind.13 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
176 | S1 | CIN14 | Indicator 14 mode | UINT32 | RW | 0=Disabled;1=Activated
176 | I1 | CIN14 | Ind.14 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
177 | S1 | CIN15 | Indicator 15 mode | UINT32 | RW | 0=Disabled;1=Activated
177 | I1 | CIN15 | Ind.15 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
178 | S1 | CIN16 | Indicator 16 mode | UINT32 | RW | 0=Disabled;1=Activated
178 | I1 | CIN16 | Ind.16 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
179 | S1 | CIN17 | Indicator 17 mode | UINT32 | RW | 0=Disabled;1=Activated
179 | I1 | CIN17 | Ind.17 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
180 | S1 | CIN18 | Indicator 18 mode | UINT32 | RW | 0=Disabled;1=Activated
180 | I1 | CIN18 | Ind.18 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
181 | S1 | CIN19 | Indicator 19 mode | UINT32 | RW | 0=Disabled;1=Activated
181 | I1 | CIN19 | Ind.19 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
182 | S1 | CIN20 | Indicator 20 mode | UINT32 | RW | 0=Disabled;1=Activated
182 | I1 | CIN20 | Ind.20 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
63 | S1 | AR1 | Auto-recloser [79] mode | UINT32 | RW | 0=Disabled;1=Activated
63 | V1 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear
63 | V2 | AR1 | Timer active | UINT32 | R | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
63 | I1 | AR1 | AR Timer value | FLOAT | R | 0...1800
63 | I2 | AR1 | AR Started | UINT32 | R | 0...4294967295
63 | I3 | AR1 | Shot 1 Started | UINT32 | R | 0...4294967295
63 | I4 | AR1 | Shot 2 Started | UINT32 | R | 0...4294967295
63 | I5 | AR1 | Shot 3 Started | UINT32 | R | 0...4294967295
63 | I6 | AR1 | Shot 4 Started | UINT32 | R | 0...4294967295
63 | I7 | AR1 | Shot 5 Started | UINT32 | R | 0...4294967295
63 | I8 | AR1 | Shot 1 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I9 | AR1 | Shot 2 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I10 | AR1 | Shot 3 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I11 | AR1 | Shot 4 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I12 | AR1 | Shot 5 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I13 | AR1 | Shot 1 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I14 | AR1 | Shot 2 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I15 | AR1 | Shot 3 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I16 | AR1 | Shot 4 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I17 | AR1 | Shot 5 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I18 | AR1 | Shot 1 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I19 | AR1 | Shot 2 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I20 | AR1 | Shot 3 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I21 | AR1 | Shot 4 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I22 | AR1 | Shot 5 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I23 | AR1 | Shot 1 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I24 | AR1 | Shot 2 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I25 | AR1 | Shot 3 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I26 | AR1 | Shot 4 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I27 | AR1 | Shot 5 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I28 | AR1 | Shot 1 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I29 | AR1 | Shot 2 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I30 | AR1 | Shot 3 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I31 | AR1 | Shot 4 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I32 | AR1 | Shot 5 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I33 | AR1 | Shots failed | UINT32 | R | 0...4294967295
63 | I34 | AR1 | Shots cleared | UINT32 | R | 0...4294967295
63 | I35 | AR1 | Final trips | UINT32 | R | 0...4294967295
63 | S2 | AR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
63 | S3 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG1
63 | S4 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG2
63 | S5 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG3
63 | S6 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG4
63 | S7 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG5
63 | S8 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG6
63 | S9 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG7
63 | S10 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5;5=Single Pole object | SG8
63 | S11 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S12 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S13 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S14 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S15 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S16 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S17 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S18 | AR1 | AR enabled in setting group | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S19 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG1
63 | S20 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG2
63 | S21 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG3
63 | S22 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG4
63 | S23 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG5
63 | S24 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG6
63 | S25 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG7
63 | S26 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets | SG8
63 | S27 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG1
63 | S28 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG2
63 | S29 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG3
63 | S30 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG4
63 | S31 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG5
63 | S32 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG6
63 | S33 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG7
63 | S34 | AR1 | Successfull reclose start general reclaim | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim | SG8
63 | S35 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG1
63 | S36 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG2
63 | S37 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG3
63 | S38 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG4
63 | S39 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG5
63 | S40 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG6
63 | S41 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG7
63 | S42 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800 | SG8
63 | S43 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S44 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S45 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S46 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S47 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S48 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S49 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S50 | AR1 | Object close reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S51 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S52 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S53 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S54 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S55 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S56 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S57 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S58 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S59 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S60 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S61 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S62 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S63 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S64 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S65 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S66 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S67 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S68 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S69 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S70 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S71 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S72 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S73 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S74 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S75 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S76 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S77 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S78 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S79 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S80 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S81 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S82 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S83 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S84 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S85 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S86 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S87 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S88 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S89 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S90 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S91 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S92 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S93 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S94 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S95 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S96 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S97 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S98 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S99 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S100 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S101 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S102 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S103 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S104 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S105 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S106 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S107 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S108 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S109 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S110 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S111 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S112 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S113 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S114 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S115 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S116 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S117 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S118 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S119 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S120 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S121 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S122 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S123 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S124 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S125 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S126 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S127 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S128 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S129 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S130 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S131 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S132 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S133 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S134 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S135 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S136 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S137 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S138 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S139 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S140 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S141 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S142 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S143 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S144 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S145 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S146 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S147 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S148 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S149 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S150 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S151 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S152 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S153 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S154 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S155 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S156 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S157 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S158 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S159 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S160 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S161 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S162 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S163 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S164 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S165 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S166 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S167 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S168 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S169 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S170 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S171 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S172 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S173 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S174 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S175 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S176 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S177 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S178 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S179 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S180 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S181 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S182 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S183 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S184 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S185 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S186 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S187 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S188 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S189 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S190 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S191 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S192 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S193 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S194 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S195 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S196 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S197 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S198 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S199 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S200 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S201 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S202 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S203 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S204 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S205 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S206 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S207 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S208 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S209 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S210 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S211 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S212 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S213 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S214 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S215 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S216 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S217 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S218 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S219 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S220 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S221 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S222 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S223 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S224 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S225 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S226 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S227 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S228 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S229 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S230 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S231 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S232 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S233 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S234 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S235 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S236 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S237 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S238 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S239 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S240 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S241 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S242 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S243 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG1
63 | S244 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG2
63 | S245 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG3
63 | S246 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG4
63 | S247 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG5
63 | S248 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG6
63 | S249 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG7
63 | S250 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled | SG8
63 | S251 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S252 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S253 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S254 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S255 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S256 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S257 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S258 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S259 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S260 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S261 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S262 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S263 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S264 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S265 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S266 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S267 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S268 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S269 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S270 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S271 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S272 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S273 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S274 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S275 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S276 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S277 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S278 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S279 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S280 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S281 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S282 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S283 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S284 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S285 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S286 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S287 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S288 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S289 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S290 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S291 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S292 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S293 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S294 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S295 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S296 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S297 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S298 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S299 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S300 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S301 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S302 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S303 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S304 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S305 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S306 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S307 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S308 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S309 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S310 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S311 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S312 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S313 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S314 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S315 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S316 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S317 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S318 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S319 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S320 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S321 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S322 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S323 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S324 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S325 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S326 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S327 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S328 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S329 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S330 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S331 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S332 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S333 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S334 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S335 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S336 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S337 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S338 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S339 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S340 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S341 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S342 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S343 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S344 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S345 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S346 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S347 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S348 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S349 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S350 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S351 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S352 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S353 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S354 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S355 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S356 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S357 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S358 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S359 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S360 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S361 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S362 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S363 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S364 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S365 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S366 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S367 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S368 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S369 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S370 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S371 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S372 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S373 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S374 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S375 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S376 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S377 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S378 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S379 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S380 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S381 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S382 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S383 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S384 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S385 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S386 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S387 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S388 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S389 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S390 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S391 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S392 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S393 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S394 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S395 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S396 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S397 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S398 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S399 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S400 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S401 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S402 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S403 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S404 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S405 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S406 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S407 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S408 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S409 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S410 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S411 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S412 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S413 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S414 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S415 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S416 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S417 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S418 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S419 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S420 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S421 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S422 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S423 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S424 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S425 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S426 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S427 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S428 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S429 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S430 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S431 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S432 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S433 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S434 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S435 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S436 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S437 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S438 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S439 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S440 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S441 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S442 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S443 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG1
63 | S444 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG2
63 | S445 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG3
63 | S446 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG4
63 | S447 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG5
63 | S448 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG6
63 | S449 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG7
63 | S450 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800 | SG8
63 | S451 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S452 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S453 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S454 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S455 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S456 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S457 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S458 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S459 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S460 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S461 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S462 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S463 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S464 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S465 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S466 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S467 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S468 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S469 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S470 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S471 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S472 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S473 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S474 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S475 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S476 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S477 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S478 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S479 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S480 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S481 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S482 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S483 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S484 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S485 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S486 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S487 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S488 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S489 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S490 | AR1 | AR1 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S491 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S492 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S493 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S494 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S495 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S496 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S497 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S498 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S499 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S500 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S501 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S502 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S503 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S504 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S505 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S506 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S507 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S508 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S509 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S510 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S511 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S512 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S513 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S514 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S515 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S516 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S517 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S518 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S519 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S520 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S521 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S522 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S523 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S524 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S525 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S526 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S527 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S528 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S529 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S530 | AR1 | AR2 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S531 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S532 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S533 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S534 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S535 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S536 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S537 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S538 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S539 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S540 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S541 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S542 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S543 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S544 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S545 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S546 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S547 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S548 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S549 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S550 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S551 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S552 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S553 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S554 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S555 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S556 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S557 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S558 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S559 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S560 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S561 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S562 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S563 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S564 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S565 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S566 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S567 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S568 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S569 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S570 | AR1 | AR3 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S571 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S572 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S573 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S574 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S575 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S576 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S577 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S578 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S579 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S580 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S581 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S582 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S583 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S584 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S585 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S586 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S587 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S588 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S589 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S590 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S591 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S592 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S593 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S594 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S595 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S596 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S597 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S598 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S599 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S600 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S601 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S602 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S603 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S604 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S605 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S606 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S607 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S608 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S609 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S610 | AR1 | AR4 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S611 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S612 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S613 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S614 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S615 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S616 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S617 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S618 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S619 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S620 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S621 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S622 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S623 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S624 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S625 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S626 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S627 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S628 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S629 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S630 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S631 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S632 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S633 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S634 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S635 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S636 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S637 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S638 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S639 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S640 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S641 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S642 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S643 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG1
63 | S644 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG2
63 | S645 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG3
63 | S646 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG4
63 | S647 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG5
63 | S648 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG6
63 | S649 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG7
63 | S650 | AR1 | AR5 Shot Dead time delay | FLOAT | RW | 0...1800 | SG8
63 | S651 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S652 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S653 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S654 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S655 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S656 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S657 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S658 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S659 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S660 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S661 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S662 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S663 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S664 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S665 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S666 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S667 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S668 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S669 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S670 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S671 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S672 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S673 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S674 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S675 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S676 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S677 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S678 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S679 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S680 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S681 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S682 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S683 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S684 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S685 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S686 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S687 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S688 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S689 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S690 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S691 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S692 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S693 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S694 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S695 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S696 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S697 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S698 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S699 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S700 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S701 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S702 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S703 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S704 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S705 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S706 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S707 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S708 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S709 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S710 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S711 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S712 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S713 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S714 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S715 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S716 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S717 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S718 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S719 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S720 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S721 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S722 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S723 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S724 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S725 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S726 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S727 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S728 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S729 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S730 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S731 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S732 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S733 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S734 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S735 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S736 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S737 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S738 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S739 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S740 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S741 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S742 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S743 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S744 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S745 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S746 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S747 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S748 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S749 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S750 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S751 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S752 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S753 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S754 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S755 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S756 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S757 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S758 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S759 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S760 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S761 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S762 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S763 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S764 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S765 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S766 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S767 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S768 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S769 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S770 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S771 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S772 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S773 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S774 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S775 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S776 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S777 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S778 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S779 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S780 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S781 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S782 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S783 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S784 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S785 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S786 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S787 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S788 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S789 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S790 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S791 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S792 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S793 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S794 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S795 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S796 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S797 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S798 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S799 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S800 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S801 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S802 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S803 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S804 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S805 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S806 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S807 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S808 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S809 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S810 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S811 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S812 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S813 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S814 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S815 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S816 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S817 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S818 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S819 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S820 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S821 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S822 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S823 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S824 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S825 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S826 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S827 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S828 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S829 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S830 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S831 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S832 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S833 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S834 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S835 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S836 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S837 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S838 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S839 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S840 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S841 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S842 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S843 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG1
63 | S844 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG2
63 | S845 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG3
63 | S846 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG4
63 | S847 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG5
63 | S848 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG6
63 | S849 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG7
63 | S850 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination | SG8
63 | S851 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S852 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S853 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S854 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S855 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S856 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S857 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S858 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S859 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S860 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S861 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S862 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S863 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S864 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S865 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S866 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S867 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S868 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S869 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S870 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S871 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S872 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S873 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S874 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S875 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S876 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S877 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S878 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S879 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S880 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S881 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S882 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S883 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S884 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S885 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S886 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S887 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S888 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S889 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S890 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S891 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S892 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S893 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S894 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S895 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S896 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S897 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S898 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S899 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S900 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S901 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S902 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S903 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S904 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S905 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S906 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S907 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S908 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S909 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S910 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S911 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S912 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S913 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S914 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S915 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S916 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S917 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S918 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S919 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S920 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S921 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S922 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S923 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S924 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S925 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S926 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S927 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S928 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S929 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S930 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S931 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S932 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S933 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S934 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S935 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S936 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S937 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S938 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S939 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S940 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S941 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S942 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S943 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S944 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S945 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S946 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S947 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S948 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S949 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S950 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S951 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S952 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S953 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S954 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S955 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S956 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S957 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S958 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S959 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S960 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S961 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S962 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S963 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S964 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S965 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S966 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S967 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S968 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S969 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S970 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S971 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S972 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S973 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S974 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S975 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S976 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S977 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S978 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S979 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S980 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S981 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S982 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S983 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S984 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S985 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S986 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S987 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S988 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S989 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S990 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S991 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S992 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S993 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S994 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S995 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S996 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S997 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S998 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S999 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S1000 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S1001 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S1002 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S1003 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S1004 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S1005 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S1006 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S1007 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S1008 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S1009 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S1010 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S1011 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S1012 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S1013 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S1014 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S1015 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S1016 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S1017 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S1018 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S1019 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S1020 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S1021 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S1022 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S1023 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S1024 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S1025 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S1026 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S1027 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S1028 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S1029 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S1030 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S1031 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S1032 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S1033 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S1034 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S1035 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S1036 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S1037 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S1038 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S1039 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S1040 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S1041 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S1042 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S1043 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG1
63 | S1044 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG2
63 | S1045 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG3
63 | S1046 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG4
63 | S1047 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG5
63 | S1048 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG6
63 | S1049 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG7
63 | S1050 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800 | SG8
63 | S1051 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1052 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1053 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1054 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1055 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1056 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1057 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1058 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1059 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1060 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1061 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1062 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1063 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1064 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1065 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1066 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1067 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1068 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1069 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1070 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1071 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1072 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1073 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1074 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1075 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1076 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1077 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1078 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1079 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1080 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1081 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1082 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1083 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1084 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1085 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1086 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1087 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1088 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1089 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1090 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1091 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1092 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1093 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1094 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1095 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1096 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1097 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1098 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1099 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1100 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1101 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1102 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1103 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1104 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1105 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1106 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1107 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1108 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1109 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1110 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1111 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1112 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1113 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1114 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1115 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1116 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1117 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1118 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1119 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1120 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1121 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1122 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1123 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1124 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1125 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1126 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1127 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1128 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1129 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1130 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1131 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1132 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1133 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1134 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1135 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1136 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1137 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1138 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1139 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1140 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1141 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1142 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1143 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1144 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1145 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1146 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1147 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1148 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1149 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1150 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1151 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1152 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1153 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1154 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1155 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1156 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1157 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1158 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1159 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1160 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1161 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1162 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1163 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1164 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1165 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1166 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1167 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1168 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1169 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1170 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1171 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1172 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1173 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1174 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1175 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1176 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1177 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1178 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1179 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1180 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1181 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1182 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1183 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1184 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1185 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1186 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1187 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1188 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1189 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1190 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1191 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1192 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1193 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1194 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1195 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1196 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1197 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1198 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1199 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1200 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1201 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1202 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1203 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1204 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1205 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1206 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1207 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1208 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1209 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1210 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1211 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1212 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1213 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1214 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1215 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1216 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1217 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1218 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1219 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1220 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1221 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1222 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1223 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1224 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1225 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1226 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1227 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1228 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1229 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1230 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1231 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1232 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1233 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1234 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1235 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1236 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1237 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1238 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1239 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1240 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1241 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1242 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | S1243 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG1
63 | S1244 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG2
63 | S1245 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG3
63 | S1246 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG4
63 | S1247 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG5
63 | S1248 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG6
63 | S1249 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG7
63 | S1250 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800 | SG8
63 | O1 | AR1 | AR On | SIGNAL_OUT | RW | 0...4294967295
63 | O2 | AR1 | AR Off | SIGNAL_OUT | RW | 0...4294967295
63 | O3 | AR1 | AR In Progress | SIGNAL_OUT | RW | 0...4294967295
63 | O4 | AR1 | AR1 Request On | SIGNAL_OUT | RW | 0...4294967295
63 | O5 | AR1 | AR2 Request On | SIGNAL_OUT | RW | 0...4294967295
63 | O6 | AR1 | AR3 Request On | SIGNAL_OUT | RW | 0...4294967295
63 | O7 | AR1 | AR4 Request On | SIGNAL_OUT | RW | 0...4294967295
63 | O8 | AR1 | AR5 Request On | SIGNAL_OUT | RW | 0...4294967295
63 | O9 | AR1 | AR Running | SIGNAL_OUT | RW | 0...4294967295
63 | O10 | AR1 | AR Shot 1 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O11 | AR1 | AR Shot 2 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O12 | AR1 | AR Shot 3 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O13 | AR1 | AR Shot 4 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O14 | AR1 | AR Shot 5 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O15 | AR1 | AR Sequence finished | SIGNAL_OUT | RW | 0...4294967295
63 | O16 | AR1 | AR Final Trip | SIGNAL_OUT | RW | 0...4294967295
63 | O17 | AR1 | Dead time on | SIGNAL_OUT | RW | 0...4294967295
63 | O18 | AR1 | ARC time on | SIGNAL_OUT | RW | 0...4294967295
63 | O19 | AR1 | Reclaim time on | SIGNAL_OUT | RW | 0...4294967295
63 | O20 | AR1 | AR Ready | SIGNAL_OUT | RW | 0...4294967295
63 | O21 | AR1 | AR Lockout after successfull sequence | SIGNAL_OUT | RW | 0...4294967295
63 | O22 | AR1 | AR Operation Inhibit | SIGNAL_OUT | RW | 0...4294967295
63 | O23 | AR1 | AR Locked | SIGNAL_OUT | RW | 0...4294967295
63 | I36 | AR1 | Newest register | UINT32 | R | 0...12
63 | I37 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I38 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I39 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I40 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I41 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I42 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I43 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I44 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I45 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I46 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I47 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I48 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I49 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I50 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I51 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I52 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I53 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I54 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I55 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I56 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I57 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I58 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I59 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I60 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I61 | AR1 | Active time | FLOAT | R | 0...1800
63 | I62 | AR1 | Active time | FLOAT | R | 0...1800
63 | I63 | AR1 | Active time | FLOAT | R | 0...1800
63 | I64 | AR1 | Active time | FLOAT | R | 0...1800
63 | I65 | AR1 | Active time | FLOAT | R | 0...1800
63 | I66 | AR1 | Active time | FLOAT | R | 0...1800
63 | I67 | AR1 | Active time | FLOAT | R | 0...1800
63 | I68 | AR1 | Active time | FLOAT | R | 0...1800
63 | I69 | AR1 | Active time | FLOAT | R | 0...1800
63 | I70 | AR1 | Active time | FLOAT | R | 0...1800
63 | I71 | AR1 | Active time | FLOAT | R | 0...1800
63 | I72 | AR1 | Active time | FLOAT | R | 0...1800
63 | S1251 | AR1 | EventMaskLo | UINT32 | RW | 0...4294967295
63 | S1252 | AR1 | EventMaskHi | UINT32 | RW | 0...4294967295
135 | S1 | EMON1 | Monitor mode | UINT32 | RW | 0=Disabled;1=Activated
135 | S2 | EMON1 | I> (50) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V1 | EMON1 | I> (50) Monitor condition | UINT32 | R | 0=Normal;1=FLTdetected
135 | S3 | EMON1 | I0> (50N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S4 | EMON1 | I0> (50N) I0 input | UINT32 | RW | 0=I01;1=I02;2=I0Calc
135 | V2 | EMON1 | I0> (50N) Monitor condition | UINT32 | R | 0=Normal;1=FLTdetected
135 | S5 | EMON1 | Idir> (67) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V3 | EMON1 | Idir> (67) Monitor condition | UINT32 | R | 0=Normal;1=FLTdetected
135 | S6 | EMON1 | I0dir> (67N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S7 | EMON1 | I0dir> (67N) I0 input | UINT32 | RW | 0=I01;1=I02
135 | S8 | EMON1 | I0dir> (67N) U0 measurement input selection | UINT32 | RW | 0=U3 Input;1=U4 Input;2=Select
135 | S9 | EMON1 | I0dir> (67N) U0 measurement input selection | UINT32 | RW | 0=U0Calc;1=U4Input;2=Select
135 | V4 | EMON1 | I0dir> (67N) Monitor condition | UINT32 | R | 0=Normal;1=FLTdetected
135 | S10 | EMON1 | I0Int> (67NT) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S11 | EMON1 | I0Int> (67NT) I0 input | UINT32 | RW | 0=I01;1=I02
135 | V5 | EMON1 | I0Int> (67NT) Monitor condition | UINT32 | R | 0=Normal;1=FLTFW;2=FLTREV
135 | S12 | EMON1 | U< (27) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S13 | EMON1 | U< (27) Measured magnitude | UINT32 | RW | 0=P-PVoltages;1=P-EVoltages
135 | S14 | EMON1 | U< (27) pick-up terms | UINT32 | RW | 0=1voltage;1=2voltages;2=3voltages
135 | V6 | EMON1 | U< (27) Monitor condition | UINT32 | R | 0=Normal;1=Undervoltage;2=Novoltage
135 | S15 | EMON1 | U0> (59N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S16 | EMON1 | U0> (59N) measurement input selection | UINT32 | RW | 0=U3 Input;1=U4 Input;2=Select
135 | S17 | EMON1 | U0> (59N) measurement input selection | UINT32 | RW | 0=U0Calc;1=U4Input;2=Select
135 | V7 | EMON1 | U0> (59N) Monitor condition | UINT32 | R | 0=Normal;1=FLTdetected
135 | S18 | EMON1 | FL (21FL) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V8 | EMON1 | FL (21FL) Monitor condition | UINT32 | R | 0=Normal;1=FLTdetected
135 | I1 | EMON1 | I> (50) Alarms | UINT32 | R | 0...4294967295
135 | I2 | EMON1 | I0> (50N) Alarms | UINT32 | R | 0...4294967295
135 | I3 | EMON1 | Idir> (67) Alarms | UINT32 | R | 0...4294967295
135 | I4 | EMON1 | I0dir> (67N) Alarms | UINT32 | R | 0...4294967295
135 | I5 | EMON1 | I0Int> (67) Alarms FWD | UINT32 | R | 0...4294967295
135 | I6 | EMON1 | I0Int> (67) Alarms REV | UINT32 | R | 0...4294967295
135 | I7 | EMON1 | U< (27) Undervoltage Alarms | UINT32 | R | 0...4294967295
135 | I8 | EMON1 | U< (27) No voltage Alarms | UINT32 | R | 0...4294967295
135 | I9 | EMON1 | U0> (59N) Alarms | UINT32 | R | 0...4294967295
135 | I10 | EMON1 | FL (21FL) Triggered | UINT32 | R | 0...4294967295
135 | S19 | EMON1 | Clear statistics | UINT32 | W | 0=-;1=Clear
135 | S20 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG1
135 | S21 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG2
135 | S22 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG3
135 | S23 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG4
135 | S24 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG5
135 | S25 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG6
135 | S26 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG7
135 | S27 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40 | SG8
135 | S28 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG1
135 | S29 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG2
135 | S30 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG3
135 | S31 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG4
135 | S32 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG5
135 | S33 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG6
135 | S34 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG7
135 | S35 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40 | SG8
135 | S36 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG1
135 | S37 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG2
135 | S38 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG3
135 | S39 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG4
135 | S40 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG5
135 | S41 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG6
135 | S42 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG7
135 | S43 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir | SG8
135 | S44 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG1
135 | S45 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG2
135 | S46 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG3
135 | S47 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG4
135 | S48 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG5
135 | S49 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG6
135 | S50 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG7
135 | S51 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170 | SG8
135 | S52 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG1
135 | S53 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG2
135 | S54 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG3
135 | S55 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG4
135 | S56 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG5
135 | S57 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG6
135 | S58 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG7
135 | S59 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180 | SG8
135 | S60 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG1
135 | S61 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG2
135 | S62 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG3
135 | S63 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG4
135 | S64 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG5
135 | S65 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG6
135 | S66 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG7
135 | S67 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40 | SG8
135 | S68 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG1
135 | S69 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG2
135 | S70 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG3
135 | S71 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG4
135 | S72 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG5
135 | S73 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG6
135 | S74 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG7
135 | S75 | EMON1 | I0dir> (67N) grounding type | UINT32 | RW | 0=Unearthed;1=PetersencoilGND;2=Grounded;3=I0Cos&I0SinBroadrangewithMCD | SG8
135 | S76 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG1
135 | S77 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG2
135 | S78 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG3
135 | S79 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG4
135 | S80 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG5
135 | S81 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG6
135 | S82 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG7
135 | S83 | EMON1 | I0dir> (67N) pick-up setting I0set> | FLOAT | RW | 0.005...40 | SG8
135 | S84 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG1
135 | S85 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG2
135 | S86 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG3
135 | S87 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG4
135 | S88 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG5
135 | S89 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG6
135 | S90 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG7
135 | S91 | EMON1 | I0dir> (67N) pick-up setting U0set> | FLOAT | RW | 1...75 | SG8
135 | S92 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG1
135 | S93 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG2
135 | S94 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG3
135 | S95 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG4
135 | S96 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG5
135 | S97 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG6
135 | S98 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG7
135 | S99 | EMON1 | I0dir> (67N) comp. pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40 | SG8
135 | S100 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG1
135 | S101 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG2
135 | S102 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG3
135 | S103 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG4
135 | S104 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG5
135 | S105 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG6
135 | S106 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG7
135 | S107 | EMON1 | I0dir> (67N) comp. pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75 | SG8
135 | S108 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG1
135 | S109 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG2
135 | S110 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG3
135 | S111 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG4
135 | S112 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG5
135 | S113 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG6
135 | S114 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG7
135 | S115 | EMON1 | I0dir> (67N) resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0 | SG8
135 | S116 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG1
135 | S117 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG2
135 | S118 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG3
135 | S119 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG4
135 | S120 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG5
135 | S121 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG6
135 | S122 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG7
135 | S123 | EMON1 | I0dir> (67N) unearth. pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40 | SG8
135 | S124 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG1
135 | S125 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG2
135 | S126 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG3
135 | S127 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG4
135 | S128 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG5
135 | S129 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG6
135 | S130 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG7
135 | S131 | EMON1 | I0dir> (67N) unearth. pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75 | SG8
135 | S132 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG1
135 | S133 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG2
135 | S134 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG3
135 | S135 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG4
135 | S136 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG5
135 | S137 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG6
135 | S138 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG7
135 | S139 | EMON1 | I0dir> (67N) fault area size (+/-) | FLOAT | RW | 45...135 | SG8
135 | S140 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG1
135 | S141 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG2
135 | S142 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG3
135 | S143 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG4
135 | S144 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG5
135 | S145 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG6
135 | S146 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG7
135 | S147 | EMON1 | I0dir> (67N) fault area center | FLOAT | RW | -360...360 | SG8
135 | S148 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG1
135 | S149 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG2
135 | S150 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG3
135 | S151 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG4
135 | S152 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG5
135 | S153 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG6
135 | S154 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG7
135 | S155 | EMON1 | I0Int> (67NT) U0 detect spike > | FLOAT | RW | 1...100 | SG8
135 | S156 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG1
135 | S157 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG2
135 | S158 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG3
135 | S159 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG4
135 | S160 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG5
135 | S161 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG6
135 | S162 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG7
135 | S163 | EMON1 | I0Int> (67NT) I0 detect spike > | FLOAT | RW | 0.05...40 | SG8
135 | S164 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG1
135 | S165 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG2
135 | S166 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG3
135 | S167 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG4
135 | S168 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG5
135 | S169 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG6
135 | S170 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG7
135 | S171 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800 | SG8
135 | S172 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG1
135 | S173 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG2
135 | S174 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG3
135 | S175 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG4
135 | S176 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG5
135 | S177 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG6
135 | S178 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG7
135 | S179 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800 | SG8
135 | S180 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG1
135 | S181 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG2
135 | S182 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG3
135 | S183 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG4
135 | S184 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG5
135 | S185 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG6
135 | S186 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG7
135 | S187 | EMON1 | I0Int> (67NT) spikes to Indicate > | UINT32 | RW | 1...50 | SG8
135 | S188 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG1
135 | S189 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG2
135 | S190 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG3
135 | S191 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG4
135 | S192 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG5
135 | S193 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG6
135 | S194 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG7
135 | S195 | EMON1 | U< (27) undervoltage set< | FLOAT | RW | 0...120 | SG8
135 | S196 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG1
135 | S197 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG2
135 | S198 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG3
135 | S199 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG4
135 | S200 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG5
135 | S201 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG6
135 | S202 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG7
135 | S203 | EMON1 | U< (27) no voltage set< | FLOAT | RW | 0...80 | SG8
135 | S204 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG1
135 | S205 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG2
135 | S206 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG3
135 | S207 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG4
135 | S208 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG5
135 | S209 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG6
135 | S210 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG7
135 | S211 | EMON1 | U0V> (59N) overvoltage set > | FLOAT | RW | 1...99 | SG8
135 | S212 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG1
135 | S213 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG2
135 | S214 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG3
135 | S215 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG4
135 | S216 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG5
135 | S217 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG6
135 | S218 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG7
135 | S219 | EMON1 | FL (21FL) trigger current > | FLOAT | RW | 0...40 | SG8
135 | S220 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG1
135 | S221 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG2
135 | S222 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG3
135 | S223 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG4
135 | S224 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG5
135 | S225 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG6
135 | S226 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG7
135 | S227 | EMON1 | FL (21FL) reactance per km | FLOAT | RW | 0.001...5 | SG8
135 | O1 | EMON1 | I> (50) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O2 | EMON1 | I0> (50N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O3 | EMON1 | Idir> (67) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O4 | EMON1 | I0dir> (67N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O5 | EMON1 | I0int> (67NT) Alarm FWD | SIGNAL_OUT | RW | 0...4294967295
135 | O6 | EMON1 | I0int> (67NT) Alarm REV | SIGNAL_OUT | RW | 0...4294967295
135 | O7 | EMON1 | U< (27) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O8 | EMON1 | U< (27) No voltage | SIGNAL_OUT | RW | 0...4294967295
135 | O9 | EMON1 | U0> (59N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O10 | EMON1 | FL (21FL) Triggered | SIGNAL_OUT | RW | 0...4294967295
135 | I11 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I12 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I13 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I14 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I15 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I16 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I17 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I18 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I19 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I20 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I21 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I22 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I23 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I24 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I25 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I26 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I27 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I28 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I29 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I30 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I31 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I32 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I33 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I34 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I35 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I36 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I37 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I38 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I39 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I40 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I41 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I42 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I43 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I44 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I45 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I46 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I47 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I48 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I49 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I50 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I51 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I52 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I53 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I54 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I55 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I56 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I57 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I58 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I59 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I60 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I61 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I62 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I63 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I64 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I65 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I66 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I67 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I68 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I69 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I70 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I71 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I72 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I73 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I74 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I75 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I76 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I77 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I78 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I79 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I80 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I81 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I82 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I83 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I84 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I85 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I86 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I87 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I88 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I89 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I90 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I91 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I92 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I93 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I94 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I95 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I96 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I97 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I98 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I99 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I100 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I101 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I102 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I103 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I104 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I105 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I106 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I107 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I108 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I109 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I110 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I111 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I112 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I113 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I114 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I115 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I116 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I117 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I118 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I119 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I120 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I121 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I122 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I123 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I124 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I125 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I126 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I127 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I128 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I129 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I130 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I131 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I132 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I133 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I134 | EMON1 | I0 fault angle | FLOAT | R | -360...360
135 | I135 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I136 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I137 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I138 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I139 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I140 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I141 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I142 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I143 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I144 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I145 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I146 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I147 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I148 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I149 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I150 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I151 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I152 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I153 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I154 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I155 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I156 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I157 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I158 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I159 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I160 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I161 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I162 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I163 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I164 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I165 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I166 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I167 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I168 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I169 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I170 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I171 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I172 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I173 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I174 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I175 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I176 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I177 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I178 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I179 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I180 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I181 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I182 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I183 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I184 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I185 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I186 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I187 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I188 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I189 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I190 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I191 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I192 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I193 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I194 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I195 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I196 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I197 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I198 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I199 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I200 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I201 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I202 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I203 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I204 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I205 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I206 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I207 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I208 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I209 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I210 | EMON1 | Newest register | UINT32 | R | 0...12
135 | I211 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I212 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I213 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I214 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I215 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I216 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I217 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I218 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I219 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I220 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I221 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I222 | EMON1 | Fault direction | UINT32 | R | 0=Notdetected;1=Forward;2=Reverse
135 | I223 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I224 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I225 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I226 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I227 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I228 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I229 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I230 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I231 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I232 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I233 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I234 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I235 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I236 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I237 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I238 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I239 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I240 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I241 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I242 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I243 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I244 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I245 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I246 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I247 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I248 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I249 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I250 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I251 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I252 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I253 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I254 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I255 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I256 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I257 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I258 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | S228 | EMON1 | EventMaskLo | UINT32 | RW | 0...4294967295
135 | S229 | EMON1 | EventMaskHi | UINT32 | RW | 0...4294967295
143 | O1 | ALARM | ALARM 1 | SIGNAL_IN | RW | 0...4294967295
143 | O2 | ALARM | ALARM 2 | SIGNAL_IN | RW | 0...4294967295
143 | O3 | ALARM | ALARM 3 | SIGNAL_IN | RW | 0...4294967295
143 | O4 | ALARM | ALARM 4 | SIGNAL_IN | RW | 0...4294967295
143 | O5 | ALARM | ALARM 5 | SIGNAL_IN | RW | 0...4294967295
143 | O6 | ALARM | ALARM 6 | SIGNAL_IN | RW | 0...4294967295
143 | O7 | ALARM | ALARM 7 | SIGNAL_IN | RW | 0...4294967295
143 | O8 | ALARM | ALARM 8 | SIGNAL_IN | RW | 0...4294967295
143 | O9 | ALARM | ALARM 9 | SIGNAL_IN | RW | 0...4294967295
143 | O10 | ALARM | ALARM 10 | SIGNAL_IN | RW | 0...4294967295
143 | O11 | ALARM | ALARM 11 | SIGNAL_IN | RW | 0...4294967295
143 | O12 | ALARM | ALARM 12 | SIGNAL_IN | RW | 0...4294967295
143 | O13 | ALARM | ALARM 13 | SIGNAL_IN | RW | 0...4294967295
143 | O14 | ALARM | ALARM 14 | SIGNAL_IN | RW | 0...4294967295
143 | O15 | ALARM | ALARM 15 | SIGNAL_IN | RW | 0...4294967295
143 | O16 | ALARM | ALARM 16 | SIGNAL_IN | RW | 0...4294967295
143 | O17 | ALARM | ALARM 17 | SIGNAL_IN | RW | 0...4294967295
143 | O18 | ALARM | ALARM 18 | SIGNAL_IN | RW | 0...4294967295
143 | O19 | ALARM | ALARM 19 | SIGNAL_IN | RW | 0...4294967295
143 | O20 | ALARM | ALARM 20 | SIGNAL_IN | RW | 0...4294967295
143 | O21 | ALARM | ALARM 21 | SIGNAL_IN | RW | 0...4294967295
143 | O22 | ALARM | ALARM 22 | SIGNAL_IN | RW | 0...4294967295
143 | O23 | ALARM | ALARM 23 | SIGNAL_IN | RW | 0...4294967295
143 | O24 | ALARM | ALARM 24 | SIGNAL_IN | RW | 0...4294967295
143 | O25 | ALARM | ALARM 25 | SIGNAL_IN | RW | 0...4294967295
143 | O26 | ALARM | ALARM 26 | SIGNAL_IN | RW | 0...4294967295
143 | O27 | ALARM | ALARM 27 | SIGNAL_IN | RW | 0...4294967295
143 | O28 | ALARM | ALARM 28 | SIGNAL_IN | RW | 0...4294967295
143 | O29 | ALARM | ALARM 29 | SIGNAL_IN | RW | 0...4294967295
143 | O30 | ALARM | ALARM 30 | SIGNAL_IN | RW | 0...4294967295
143 | O31 | ALARM | ALARM 31 | SIGNAL_IN | RW | 0...4294967295
143 | O32 | ALARM | ALARM 32 | SIGNAL_IN | RW | 0...4294967295
143 | O33 | ALARM | ALARM 33 | SIGNAL_IN | RW | 0...4294967295
143 | O34 | ALARM | ALARM 34 | SIGNAL_IN | RW | 0...4294967295
143 | O35 | ALARM | ALARM 35 | SIGNAL_IN | RW | 0...4294967295
143 | O36 | ALARM | ALARM 36 | SIGNAL_IN | RW | 0...4294967295
143 | O37 | ALARM | ALARM 37 | SIGNAL_IN | RW | 0...4294967295
143 | O38 | ALARM | ALARM 38 | SIGNAL_IN | RW | 0...4294967295
143 | O39 | ALARM | ALARM 39 | SIGNAL_IN | RW | 0...4294967295
143 | O40 | ALARM | ALARM 40 | SIGNAL_IN | RW | 0...4294967295
143 | O41 | ALARM | ALARM 41 | SIGNAL_IN | RW | 0...4294967295
143 | O42 | ALARM | ALARM 42 | SIGNAL_IN | RW | 0...4294967295
143 | O43 | ALARM | ALARM 43 | SIGNAL_IN | RW | 0...4294967295
143 | O44 | ALARM | ALARM 44 | SIGNAL_IN | RW | 0...4294967295
143 | O45 | ALARM | ALARM 45 | SIGNAL_IN | RW | 0...4294967295
143 | O46 | ALARM | ALARM 46 | SIGNAL_IN | RW | 0...4294967295
143 | O47 | ALARM | ALARM 47 | SIGNAL_IN | RW | 0...4294967295
143 | O48 | ALARM | ALARM 48 | SIGNAL_IN | RW | 0...4294967295
143 | O49 | ALARM | ALARM 49 | SIGNAL_IN | RW | 0...4294967295
143 | O50 | ALARM | ALARM 50 | SIGNAL_IN | RW | 0...4294967295
143 | O51 | ALARM | ALARM 51 | SIGNAL_IN | RW | 0...4294967295
143 | O52 | ALARM | ALARM 52 | SIGNAL_IN | RW | 0...4294967295
143 | O53 | ALARM | ALARM 53 | SIGNAL_IN | RW | 0...4294967295
143 | O54 | ALARM | ALARM 54 | SIGNAL_IN | RW | 0...4294967295
143 | O55 | ALARM | ALARM 55 | SIGNAL_IN | RW | 0...4294967295
143 | O56 | ALARM | ALARM 56 | SIGNAL_IN | RW | 0...4294967295
143 | O57 | ALARM | ALARM 57 | SIGNAL_IN | RW | 0...4294967295
143 | O58 | ALARM | ALARM 58 | SIGNAL_IN | RW | 0...4294967295
143 | O59 | ALARM | ALARM 59 | SIGNAL_IN | RW | 0...4294967295
143 | O60 | ALARM | ALARM 60 | SIGNAL_IN | RW | 0...4294967295
143 | O61 | ALARM | ALARM 61 | SIGNAL_IN | RW | 0...4294967295
143 | O62 | ALARM | ALARM 62 | SIGNAL_IN | RW | 0...4294967295
143 | O63 | ALARM | ALARM 63 | SIGNAL_IN | RW | 0...4294967295
143 | O64 | ALARM | ALARM 64 | SIGNAL_IN | RW | 0...4294967295
143 | O65 | ALARM | ALARM 65 | SIGNAL_IN | RW | 0...4294967295
143 | O66 | ALARM | ALARM 66 | SIGNAL_IN | RW | 0...4294967295
143 | O67 | ALARM | ALARM 67 | SIGNAL_IN | RW | 0...4294967295
143 | O68 | ALARM | ALARM 68 | SIGNAL_IN | RW | 0...4294967295
143 | O69 | ALARM | ALARM 69 | SIGNAL_IN | RW | 0...4294967295
143 | O70 | ALARM | ALARM 70 | SIGNAL_IN | RW | 0...4294967295
143 | O71 | ALARM | ALARM 71 | SIGNAL_IN | RW | 0...4294967295
143 | O72 | ALARM | ALARM 72 | SIGNAL_IN | RW | 0...4294967295
143 | O73 | ALARM | ALARM 73 | SIGNAL_IN | RW | 0...4294967295
143 | O74 | ALARM | ALARM 74 | SIGNAL_IN | RW | 0...4294967295
143 | O75 | ALARM | ALARM 75 | SIGNAL_IN | RW | 0...4294967295
143 | O76 | ALARM | ALARM 76 | SIGNAL_IN | RW | 0...4294967295
143 | O77 | ALARM | ALARM 77 | SIGNAL_IN | RW | 0...4294967295
143 | O78 | ALARM | ALARM 78 | SIGNAL_IN | RW | 0...4294967295
143 | O79 | ALARM | ALARM 79 | SIGNAL_IN | RW | 0...4294967295
143 | O80 | ALARM | ALARM 80 | SIGNAL_IN | RW | 0...4294967295
143 | O81 | ALARM | ALARM 81 | SIGNAL_IN | RW | 0...4294967295
143 | O82 | ALARM | ALARM 82 | SIGNAL_IN | RW | 0...4294967295
143 | O83 | ALARM | ALARM 83 | SIGNAL_IN | RW | 0...4294967295
143 | O84 | ALARM | ALARM 84 | SIGNAL_IN | RW | 0...4294967295
143 | O85 | ALARM | ALARM 85 | SIGNAL_IN | RW | 0...4294967295
143 | O86 | ALARM | ALARM 86 | SIGNAL_IN | RW | 0...4294967295
143 | O87 | ALARM | ALARM 87 | SIGNAL_IN | RW | 0...4294967295
143 | O88 | ALARM | ALARM 88 | SIGNAL_IN | RW | 0...4294967295
143 | O89 | ALARM | ALARM 89 | SIGNAL_IN | RW | 0...4294967295
143 | O90 | ALARM | ALARM 90 | SIGNAL_IN | RW | 0...4294967295
143 | O91 | ALARM | ALARM 91 | SIGNAL_IN | RW | 0...4294967295
143 | O92 | ALARM | ALARM 92 | SIGNAL_IN | RW | 0...4294967295
143 | O93 | ALARM | ALARM 93 | SIGNAL_IN | RW | 0...4294967295
143 | O94 | ALARM | ALARM 94 | SIGNAL_IN | RW | 0...4294967295
143 | O95 | ALARM | ALARM 95 | SIGNAL_IN | RW | 0...4294967295
143 | O96 | ALARM | ALARM 96 | SIGNAL_IN | RW | 0...4294967295
143 | O97 | ALARM | ALARM 97 | SIGNAL_IN | RW | 0...4294967295
143 | O98 | ALARM | ALARM 98 | SIGNAL_IN | RW | 0...4294967295
143 | O99 | ALARM | ALARM 99 | SIGNAL_IN | RW | 0...4294967295
143 | O100 | ALARM | ALARM 100 | SIGNAL_IN | RW | 0...4294967295
143 | O101 | ALARM | ALARM 101 | SIGNAL_IN | RW | 0...4294967295
143 | O102 | ALARM | ALARM 102 | SIGNAL_IN | RW | 0...4294967295
143 | O103 | ALARM | ALARM 103 | SIGNAL_IN | RW | 0...4294967295
143 | O104 | ALARM | ALARM 104 | SIGNAL_IN | RW | 0...4294967295
143 | O105 | ALARM | ALARM 105 | SIGNAL_IN | RW | 0...4294967295
143 | O106 | ALARM | ALARM 106 | SIGNAL_IN | RW | 0...4294967295
143 | O107 | ALARM | ALARM 107 | SIGNAL_IN | RW | 0...4294967295
143 | O108 | ALARM | ALARM 108 | SIGNAL_IN | RW | 0...4294967295
143 | O109 | ALARM | ALARM 109 | SIGNAL_IN | RW | 0...4294967295
143 | O110 | ALARM | ALARM 110 | SIGNAL_IN | RW | 0...4294967295
143 | O111 | ALARM | ALARM 111 | SIGNAL_IN | RW | 0...4294967295
143 | O112 | ALARM | ALARM 112 | SIGNAL_IN | RW | 0...4294967295
143 | O113 | ALARM | ALARM 113 | SIGNAL_IN | RW | 0...4294967295
143 | O114 | ALARM | ALARM 114 | SIGNAL_IN | RW | 0...4294967295
143 | O115 | ALARM | ALARM 115 | SIGNAL_IN | RW | 0...4294967295
143 | O116 | ALARM | ALARM 116 | SIGNAL_IN | RW | 0...4294967295
143 | O117 | ALARM | ALARM 117 | SIGNAL_IN | RW | 0...4294967295
143 | O118 | ALARM | ALARM 118 | SIGNAL_IN | RW | 0...4294967295
143 | O119 | ALARM | ALARM 119 | SIGNAL_IN | RW | 0...4294967295
143 | O120 | ALARM | ALARM 120 | SIGNAL_IN | RW | 0...4294967295
143 | O121 | ALARM | ALARM 121 | SIGNAL_IN | RW | 0...4294967295
143 | O122 | ALARM | ALARM 122 | SIGNAL_IN | RW | 0...4294967295
143 | O123 | ALARM | ALARM 123 | SIGNAL_IN | RW | 0...4294967295
143 | O124 | ALARM | ALARM 124 | SIGNAL_IN | RW | 0...4294967295
143 | O125 | ALARM | ALARM 125 | SIGNAL_IN | RW | 0...4294967295
143 | O126 | ALARM | ALARM 126 | SIGNAL_IN | RW | 0...4294967295
143 | O127 | ALARM | ALARM 127 | SIGNAL_IN | RW | 0...4294967295
143 | O128 | ALARM | ALARM 128 | SIGNAL_IN | RW | 0...4294967295
159 | S1 | ALARM1 | EventMaskLo | UINT32 | RW | 0...4294967295
159 | S2 | ALARM1 | EventMaskHi | UINT32 | RW | 0...4294967295
160 | S1 | ALARM2 | EventMaskLo | UINT32 | RW | 0...4294967295
160 | S2 | ALARM2 | EventMaskHi | UINT32 | RW | 0...4294967295
184 | S1 | ALARM3 | EventMaskLo | UINT32 | RW | 0...4294967295
184 | S2 | ALARM3 | EventMaskHi | UINT32 | RW | 0...4294967295
185 | S1 | ALARM4 | EventMaskLo | UINT32 | RW | 0...4294967295
185 | S2 | ALARM4 | EventMaskHi | UINT32 | RW | 0...4294967295
156 | S1 | GMAG | Excitation control mode | UINT32 | RW | 0=Disabled;1=Activated
156 | S2 | GMAG | Excitation current measurement from | UINT32 | RW | 0=CT1(3ph HV);1=CT2 (3ph LV)
156 | S3 | GMAG | Excitation power measurement from | UINT32 | RW | 0=POW1;1=POW2
156 | S4 | GMAG | Force control signals on | UINT32 | RW | 0=None;1=FCL On limit;2=UEL in operation;3=SCL Overexc.;4=SCL Underexc.;5=High I P alarm;6=Instant FCL on;7=Low supply voltage;8=FCR Mode on;9=AVR Mode On;10=Low meas. Voltage on.;11=IGBT shorted on;12=PWM enabled;13=Rectifier trip;14=Bridge 1 temp high;15=Bridge 2 temp high;16=Excitation On;17=Excitation Off;18=Diode fault on;19=Overcurrent on
156 | S5 | GMAG | Force Indicator signals on | UINT32 | RW | 0=None;1=Synchronized;2=Islandmode;3=Field breaker is open;4=Field breaker is closed;5=Field flashing on;6=Long field flashing on;7=Test mode is on;8=Phase retard on;9=Reset on;10=Command AVR on;11=Command FCR On;12=Command MVAR On;13=Command PF on;14=Excitation run order;15=Increase On;16=Decrease On;17=AVR Bus on;18=FCR Bus on;19=MVAR Bus On;20=PF Bus On;21=Overriding control on;22=AVR Ref on Low limit;23=AVR Ref on High limit;24=FCR ref on Low limit;25=FCR ref on High limit;
156 | S6 | GMAG | Force Indicator signals on | UINT32 | RW | 0=None;1=VHZ limit active;2=Process panel activated;3=Parameters activated;4=Bus activated;5=Reset and excitation off;6=Field breaker does not open;7=NewRef start;8=Generator breaker is closed;9=Fieldbreaker off Gen breaker on;10=Disturbed mode;11=Disturbed mode pulse;12=Following line voltage;13=Test square enabled;14=Order open Field breaker;15=Order close Field breaker;16=Q unloaded;17=MVAR ref on high limit;18=MVAR ref on low limit;19=PF ref on high limit:20=PF ref on low limit;21=AVR start reference;22=FCR start reference;23=Unload MVAR;24=MVAR mode on;25=PF mode on
156 | I1 | GMAG | Testmode On | SIGNAL_IN | RW | 0...4294967295
156 | I2 | GMAG | Command AVR | SIGNAL_IN | RW | 0...4294967295
156 | I3 | GMAG | Command FCR | SIGNAL_IN | RW | 0...4294967295
156 | I4 | GMAG | Command MVar | SIGNAL_IN | RW | 0...4294967295
156 | I5 | GMAG | Command PF | SIGNAL_IN | RW | 0...4294967295
156 | I6 | GMAG | Reset | SIGNAL_IN | RW | 0...4294967295
156 | I7 | GMAG | Increase | SIGNAL_IN | RW | 0...4294967295
156 | I8 | GMAG | Decrease | SIGNAL_IN | RW | 0...4294967295
156 | I9 | GMAG | Field breaker Off | SIGNAL_IN | RW | 0...4294967295
156 | I10 | GMAG | Field breaker On | SIGNAL_IN | RW | 0...4294967295
156 | I11 | GMAG | Unload Mvar | SIGNAL_IN | RW | 0...4294967295
156 | S7 | GMAG | Command Excitation to Remote control | UINT32 | RW | 0=Off;1=On
156 | S8 | GMAG | Command AVR (remote) | UINT32 | RW | 0=Off;1=On
156 | S9 | GMAG | Command FCR (remote) | UINT32 | RW | 0=Off;1=On
156 | S10 | GMAG | Command MVAR (remote) | UINT32 | RW | 0=Off;1=On
156 | S11 | GMAG | Command PF (remote) | UINT32 | RW | 0=Off;1=On
156 | S12 | GMAG | Unload Q (remote) | UINT32 | RW | 0=Off;1=On
156 | S13 | GMAG | Reset (remote) | UINT32 | RW | 0=Off;1=On
156 | S14 | GMAG | AVR Ref execute (remote) | UINT32 | RW | 0=Off;1=On
156 | S15 | GMAG | AVR Ref value (remote) | FLOAT | RW | 0...450000
156 | S16 | GMAG | FCR Ref execute (remote) | UINT32 | RW | 0=Off;1=On
156 | S17 | GMAG | FCR Ref value (remote) | FLOAT | RW | 0...100
156 | S18 | GMAG | MVar Ref execute (remote) | UINT32 | RW | 0=Off;1=On
156 | S19 | GMAG | Read MVar Ref from | UINT32 | RW | 0=Value from comm Bus;1=Value from AI
156 | S20 | GMAG | MVar Ref selection | UINT32 | RW | 0=Scaled input 1;1=Scaled input 2;2=Scaled input 3;3=Scaled input 4
156 | S21 | GMAG | Update MVar Ref automatically when threshold exceeds | UINT32 | RW | 0=No;1=Yes
156 | S22 | GMAG | MVar Ref change threshold (AI) | FLOAT | RW | 0...50
156 | S23 | GMAG | MVar Ref value (kVar) (remote) | FLOAT | RW | -1000...1000
156 | S24 | GMAG | MVar Ref value (MVar) (remote) | FLOAT | RW | -1000...1000
156 | S25 | GMAG | PF Ref execute (remote) | UINT32 | RW | 0=Off;1=On
156 | S26 | GMAG | PF Ref value (remote) | FLOAT | RW | -1...1
156 | S27 | GMAG | Open FB command (remote) | UINT32 | RW | 0=Off;1=On
156 | S28 | GMAG | Close FB command (remote) | UINT32 | RW | 0=Off;1=On
156 | S29 | GMAG | AVR speed 90 (remote) | UINT32 | RW | 0=Off;1=On
156 | S30 | GMAG | Ind GB closed (remote) | UINT32 | RW | 0=Off;1=On
156 | S31 | GMAG | Island mode (remote) | UINT32 | RW | 0=Off;1=On
156 | S32 | GMAG | Command voltage matching (remote) | UINT32 | RW | 0=Off;1=On
156 | S33 | GMAG | Grid voltage (remote) | FLOAT | RW | 0...500
156 | S34 | GMAG | AVR Ref start (remote) | UINT32 | RW | 0=Off;1=On
156 | S35 | GMAG | Command Excitation to Remote control Received | UINT32 | R | 0=No;1=Yes
156 | S36 | GMAG | Command AVR (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S37 | GMAG | Command FCR (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S38 | GMAG | Command MVAR (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S39 | GMAG | Command PF (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S40 | GMAG | Unload Q (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S41 | GMAG | Reset (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S42 | GMAG | AVR Ref execute (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S43 | GMAG | AVR Ref value (remote) Received | FLOAT | R | 0...450000
156 | S44 | GMAG | FCR Ref execute (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S45 | GMAG | FCR Ref value (remote) Received | FLOAT | R | 0...100
156 | S46 | GMAG | MVar Ref execute (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S47 | GMAG | MVar Ref value (remote) Received | FLOAT | R | -1000...1000
156 | S48 | GMAG | PF Ref execute (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S49 | GMAG | PF Ref value (remote) Received | FLOAT | R | -1...1
156 | S50 | GMAG | Open FB command (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S51 | GMAG | Close FB command (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S52 | GMAG | AVR speed 90 (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S53 | GMAG | Ind GB closed (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S54 | GMAG | Island mode (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S55 | GMAG | Command voltage matching (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S56 | GMAG | Grid voltage (remote) Received | FLOAT | R | 0...500
156 | S57 | GMAG | AVR Ref start (remote) Received | UINT32 | R | 0=No;1=Yes
156 | S58 | GMAG | Reset remote Received indications | UINT32 | RW | 0=-;1=Reset
156 | S59 | GMAG | Field current (remote) | FLOAT | R | -500...500
156 | S60 | GMAG | AVR Ref actual (remote) | FLOAT | R | -500...500
156 | S61 | GMAG | FCR Ref actual (remote) | FLOAT | R | -500...500
156 | S62 | GMAG | MVAR Ref actual (remote) | FLOAT | R | -500...500
156 | S63 | GMAG | PF Ref actual (remote) | FLOAT | R | -500...500
156 | S64 | GMAG | Mode FCR (remote) | UINT32 | R | 0=Off;1=On
156 | S65 | GMAG | Mode AVR (remote) | UINT32 | R | 0=Off;1=On
156 | S66 | GMAG | Mode MVAR (remote) | UINT32 | R | 0=Off;1=On
156 | S67 | GMAG | Mode PF (remote) | UINT32 | R | 0=Off;1=On
156 | I12 | GMAG | Increase | SIGNAL_IN | RW | 0...4294967295
156 | I13 | GMAG | Decrease | SIGNAL_IN | RW | 0...4294967295
156 | I14 | GMAG | TestMode Increase | SIGNAL_IN | RW | 0...4294967295
156 | I15 | GMAG | TestMode Decrease | SIGNAL_IN | RW | 0...4294967295
156 | I16 | GMAG | Command AVR | SIGNAL_IN | RW | 0...4294967295
156 | I17 | GMAG | Command FCR | SIGNAL_IN | RW | 0...4294967295
156 | I18 | GMAG | Command MVar | SIGNAL_IN | RW | 0...4294967295
156 | I19 | GMAG | Command PF | SIGNAL_IN | RW | 0...4294967295
156 | I20 | GMAG | Command Remote Bus | SIGNAL_IN | RW | 0...4294967295
156 | I21 | GMAG | Force IO / params control only | SIGNAL_IN | RW | 0...4294967295
156 | I22 | GMAG | Unload Q | SIGNAL_IN | RW | 0...4294967295
156 | I23 | GMAG | Reset | SIGNAL_IN | RW | 0...4294967295
156 | I24 | GMAG | Field Breaker Status Closed In | SIGNAL_IN | RW | 0...4294967295
156 | I25 | GMAG | Excitation Off Command | SIGNAL_IN | RW | 0...4294967295
156 | I26 | GMAG | Excitation On Command | SIGNAL_IN | RW | 0...4294967295
156 | I27 | GMAG | Open FB Command | SIGNAL_IN | RW | 0...4294967295
156 | I28 | GMAG | Close FB Command | SIGNAL_IN | RW | 0...4294967295
156 | I29 | GMAG | Incoming trip signal | SIGNAL_IN | RW | 0...4294967295
156 | I30 | GMAG | Field overcurrent | SIGNAL_IN | RW | 0...4294967295
156 | I31 | GMAG | Speed >90% input | SIGNAL_IN | RW | 0...4294967295
156 | I32 | GMAG | Generator breaker Status Closed In | SIGNAL_IN | RW | 0...4294967295
156 | I33 | GMAG | Line breaker Status Closed In | SIGNAL_IN | RW | 0...4294967295
156 | I34 | GMAG | VT Supervision Fail status | SIGNAL_IN | RW | 0...4294967295
156 | I35 | GMAG | Activate electrical braking | SIGNAL_IN | RW | 0...4294967295
156 | I36 | GMAG | External islanding detection | SIGNAL_IN | RW | 0...4294967295
156 | I37 | GMAG | Common TRIP | SIGNAL_IN | RW | 0...4294967295
156 | I38 | GMAG | Voltage matching input | SIGNAL_IN | RW | 0...4294967295
156 | I39 | GMAG | Backup supply On | SIGNAL_IN | RW | 0...4294967295
156 | I40 | GMAG | Block Under excitation limiter | SIGNAL_IN | RW | 0...4294967295
156 | I41 | GMAG | Block Field current limiter (time delayed) | SIGNAL_IN | RW | 0...4294967295
156 | I42 | GMAG | Block Field current limiter (Instant) | SIGNAL_IN | RW | 0...4294967295
156 | I43 | GMAG | Block Stator current limiter | SIGNAL_IN | RW | 0...4294967295
156 | I44 | GMAG | Motor mode Starting (bypass FCR starting ramp) | SIGNAL_IN | RW | 0...4294967295
156 | I45 | GMAG | Block Process Panel and Remote control | SIGNAL_IN | RW | 0...4294967295
156 | I46 | GMAG | Select channel (0=A 1=B) | SIGNAL_IN | RW | 0...4294967295
156 | I47 | GMAG | Disable commands to bridge | SIGNAL_IN | RW | 0...4294967295
156 | I48 | GMAG | Local Channel status (1=Ok) | SIGNAL_IN | RW | 0...4294967295
156 | I49 | GMAG | Remote Channel status (1=Ok) | SIGNAL_IN | RW | 0...4294967295
156 | I50 | GMAG | PSS External Enable (1=Enabled) | SIGNAL_IN | RW | 0...4294967295
156 | I51 | GMAG | PSS External Block (1=Blocked) | SIGNAL_IN | RW | 0...4294967295
156 | O1 | GMAG | GMAG Field current limiter active | SIGNAL_OUT | RW | 0...4294967295
156 | O2 | GMAG | GMAG Under excitation limiter active | SIGNAL_OUT | RW | 0...4294967295
156 | O3 | GMAG | GMAG Stator current limiter overexcited active | SIGNAL_OUT | RW | 0...4294967295
156 | O4 | GMAG | GMAG Stator current limiter underexcited active | SIGNAL_OUT | RW | 0...4294967295
156 | O5 | GMAG | GMAG High active current | SIGNAL_OUT | RW | 0...4294967295
156 | O6 | GMAG | GMAG Instantaneous field current limiter | SIGNAL_OUT | RW | 0...4294967295
156 | O7 | GMAG | GMAG Low supply voltage | SIGNAL_OUT | RW | 0...4294967295
156 | O8 | GMAG | GMAG FCR Mode | SIGNAL_OUT | RW | 0...4294967295
156 | O9 | GMAG | GMAG AVR Mode | SIGNAL_OUT | RW | 0...4294967295
156 | O10 | GMAG | GMAG MVAR Mode | SIGNAL_OUT | RW | 0...4294967295
156 | O11 | GMAG | GMAG PF Mode | SIGNAL_OUT | RW | 0...4294967295
156 | O12 | GMAG | GMAG Low measured voltage | SIGNAL_OUT | RW | 0...4294967295
156 | O13 | GMAG | GMAG IGBT shorted | SIGNAL_OUT | RW | 0...4294967295
156 | O14 | GMAG | GMAG PWM Enabled | SIGNAL_OUT | RW | 0...4294967295
156 | O15 | GMAG | GMAG PWM AC1 On | SIGNAL_OUT | RW | 0...4294967295
156 | O16 | GMAG | GMAG PWM DC1 On | SIGNAL_OUT | RW | 0...4294967295
156 | O17 | GMAG | GMAG PWM AC2 On | SIGNAL_OUT | RW | 0...4294967295
156 | O18 | GMAG | GMAG PWM DC2 On | SIGNAL_OUT | RW | 0...4294967295
156 | O19 | GMAG | GMAG Rectifier trip | SIGNAL_OUT | RW | 0...4294967295
156 | O20 | GMAG | GMAG Bridge1 temperature high | SIGNAL_OUT | RW | 0...4294967295
156 | O21 | GMAG | GMAG Bridge2 temperature high | SIGNAL_OUT | RW | 0...4294967295
156 | O22 | GMAG | GMAG Excitation On | SIGNAL_OUT | RW | 0...4294967295
156 | O23 | GMAG | GMAG Excitation Off | SIGNAL_OUT | RW | 0...4294967295
156 | O24 | GMAG | GMAG Diode fault | SIGNAL_OUT | RW | 0...4294967295
156 | O25 | GMAG | GMAG Overcurrent | SIGNAL_OUT | RW | 0...4294967295
156 | O26 | GMAG | GMAG Bridge 1 DI1 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O27 | GMAG | GMAG Bridge 1 DI2 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O28 | GMAG | GMAG Bridge 1 DI3 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O29 | GMAG | GMAG Bridge 1 DI4 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O30 | GMAG | GMAG Bridge 1 DI5 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O31 | GMAG | GMAG Bridge 1 DI6 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O32 | GMAG | GMAG Bridge 1 DI7 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O33 | GMAG | GMAG Bridge 1 DI8 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O34 | GMAG | GMAG Bridge 2 DI1 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O35 | GMAG | GMAG Bridge 2 DI2 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O36 | GMAG | GMAG Bridge 2 DI3 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O37 | GMAG | GMAG Bridge 2 DI4 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O38 | GMAG | GMAG Bridge 2 DI5 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O39 | GMAG | GMAG Bridge 2 DI6 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O40 | GMAG | GMAG Bridge 2 DI7 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O41 | GMAG | GMAG Bridge 2 DI8 Signal | SIGNAL_OUT | RW | 0...4294967295
156 | O42 | GMAG | GMAG Synchronised | SIGNAL_OUT | RW | 0...4294967295
156 | O43 | GMAG | GMAG Islandmode | SIGNAL_OUT | RW | 0...4294967295
156 | O44 | GMAG | GMAG Field Breaker is open | SIGNAL_OUT | RW | 0...4294967295
156 | O45 | GMAG | GMAG Field Breaker is closed | SIGNAL_OUT | RW | 0...4294967295
156 | O46 | GMAG | GMAG Field flashing | SIGNAL_OUT | RW | 0...4294967295
156 | O47 | GMAG | GMAG Long field flashing | SIGNAL_OUT | RW | 0...4294967295
156 | O48 | GMAG | GMAG Test mode on | SIGNAL_OUT | RW | 0...4294967295
156 | O49 | GMAG | GMAG Phase retard | SIGNAL_OUT | RW | 0...4294967295
156 | O50 | GMAG | GMAG Reset On | SIGNAL_OUT | RW | 0...4294967295
156 | O51 | GMAG | GMAG Command AVR | SIGNAL_OUT | RW | 0...4294967295
156 | O52 | GMAG | GMAG Command FCR | SIGNAL_OUT | RW | 0...4294967295
156 | O53 | GMAG | GMAG Command MVar | SIGNAL_OUT | RW | 0...4294967295
156 | O54 | GMAG | GMAG Command PF | SIGNAL_OUT | RW | 0...4294967295
156 | O55 | GMAG | GMAG Excitation run order | SIGNAL_OUT | RW | 0...4294967295
156 | O56 | GMAG | GMAG Increase | SIGNAL_OUT | RW | 0...4294967295
156 | O57 | GMAG | GMAG Decrease | SIGNAL_OUT | RW | 0...4294967295
156 | O58 | GMAG | GMAG AVR Bus | SIGNAL_OUT | RW | 0...4294967295
156 | O59 | GMAG | GMAG FCR Bus | SIGNAL_OUT | RW | 0...4294967295
156 | O60 | GMAG | GMAG MVAR Bus | SIGNAL_OUT | RW | 0...4294967295
156 | O61 | GMAG | GMAG PF Bus | SIGNAL_OUT | RW | 0...4294967295
156 | O62 | GMAG | GMAG Overriding control | SIGNAL_OUT | RW | 0...4294967295
156 | O63 | GMAG | GMAG Increase MVar PF | SIGNAL_OUT | RW | 0...4294967295
156 | O64 | GMAG | GMAG Decrease MVar PF | SIGNAL_OUT | RW | 0...4294967295
156 | O65 | GMAG | GMAG Low Q Error | SIGNAL_OUT | RW | 0...4294967295
156 | O66 | GMAG | GMAG AVR ref on low limit | SIGNAL_OUT | RW | 0...4294967295
156 | O67 | GMAG | GMAG AVR ref on high limit | SIGNAL_OUT | RW | 0...4294967295
156 | O68 | GMAG | GMAG FCR ref on low limit | SIGNAL_OUT | RW | 0...4294967295
156 | O69 | GMAG | GMAG FCR ref on high limit | SIGNAL_OUT | RW | 0...4294967295
156 | O70 | GMAG | GMAG VHZ limit active | SIGNAL_OUT | RW | 0...4294967295
156 | O71 | GMAG | GMAG ProcessPanel activated | SIGNAL_OUT | RW | 0...4294967295
156 | O72 | GMAG | GMAG Parameters activated | SIGNAL_OUT | RW | 0...4294967295
156 | O73 | GMAG | GMAG Bus activated | SIGNAL_OUT | RW | 0...4294967295
156 | O74 | GMAG | GMAG Reset and excitation off | SIGNAL_OUT | RW | 0...4294967295
156 | O75 | GMAG | GMAG Field breaker does not open | SIGNAL_OUT | RW | 0...4294967295
156 | O76 | GMAG | GMAG New reference start | SIGNAL_OUT | RW | 0...4294967295
156 | O77 | GMAG | GMAG GB is closed | SIGNAL_OUT | RW | 0...4294967295
156 | O78 | GMAG | GMAG Field breaker is open Gen breaker is Closed | SIGNAL_OUT | RW | 0...4294967295
156 | O79 | GMAG | GMAG Disturbed mode | SIGNAL_OUT | RW | 0...4294967295
156 | O80 | GMAG | GMAG Disturbed mode pulse | SIGNAL_OUT | RW | 0...4294967295
156 | O81 | GMAG | GMAG Following line volt | SIGNAL_OUT | RW | 0...4294967295
156 | O82 | GMAG | GMAG Test square enabled | SIGNAL_OUT | RW | 0...4294967295
156 | O83 | GMAG | GMAG Order open FB | SIGNAL_OUT | RW | 0...4294967295
156 | O84 | GMAG | GMAG Order close FB | SIGNAL_OUT | RW | 0...4294967295
156 | O85 | GMAG | GMAG Reactive power unloaded | SIGNAL_OUT | RW | 0...4294967295
156 | O86 | GMAG | GMAG Mvar ref on highlimit | SIGNAL_OUT | RW | 0...4294967295
156 | O87 | GMAG | GMAG Mvar ref on lowlimit | SIGNAL_OUT | RW | 0...4294967295
156 | O88 | GMAG | GMAG PF ref on highlimit | SIGNAL_OUT | RW | 0...4294967295
156 | O89 | GMAG | GMAG PF ref on lowlimit | SIGNAL_OUT | RW | 0...4294967295
156 | O90 | GMAG | GMAG AVR Start Ref | SIGNAL_OUT | RW | 0...4294967295
156 | O91 | GMAG | GMAG FCR Start Ref | SIGNAL_OUT | RW | 0...4294967295
156 | O92 | GMAG | GMAG PSS is Active | SIGNAL_OUT | RW | 0...4294967295
156 | O93 | GMAG | GMAG PSS is Blocked | SIGNAL_OUT | RW | 0...4294967295
156 | O94 | GMAG | GMAG Contr.mode (0=online, 1=standby) | SIGNAL_OUT | RW | 0...4294967295
156 | S68 | GMAG | Control EventMaskLo | UINT32 | RW | 0...4294967295
156 | S69 | GMAG | Control EventMaskHi | UINT32 | RW | 0...4294967295
157 | S1 | GMAG1 | Normal EventMaskLo | UINT32 | RW | 0...4294967295
157 | S2 | GMAG1 | Normal EventMaskMid | UINT32 | RW | 0...4294967295
158 | S1 | GMAG2 | Normal EventMaskMid2 | UINT32 | RW | 0...4294967295
158 | S2 | GMAG2 | Normal EventMaskHi | UINT32 | RW | 0...4294967295
162 | S1 | GSYN | Synchronizer mode | UINT32 | RW | 0=Disabled;1=Activated
162 | S2 | GSYN | Synchronizing by | UINT32 | RW | 0=System voltages to U3/U4 Input
162 | S3 | GSYN | Synchronizer reference voltage input | UINT32 | RW | 0=U4 Input;1=U3 Input
162 | S4 | GSYN | Voltage difference calculation mode | UINT32 | RW | 0=System is reference;1=U3/U4 Input is reference
162 | S5 | GSYN | Synchronizer voltage reference | UINT32 | RW | 0=UL12;1=UL23;2=UL31;3=UL1;4=UL2;5=UL3
162 | S6 | GSYN | Synchronizer measurement settings | UINT32 | R | 0=Meas.Conf.Incorrect;1=PP and PE voltages;2=PP Voltages;
162 | S7 | GSYN | Synchronizer status | UINT32 | R | 0=Conf.Error;1=Idle Ready;2=Synchronizing;3=Blocked
162 | S8 | GSYN | Force control signals on | UINT32 | RW | 0=None;1=Blocked On;2=Running On;3=Increase U On;4=Decrease U On;5=Increase F On;6=Decrease F On;7=CB Close On;8=LongSyncTime On
162 | S9 | GSYN | Enable on-screen synchronizer view | UINT32 | RW | 0=Disabled;1=Activated
162 | S10 | GSYN | Synchronizing by | UINT32 | RW | 0=Autosynchronizer;1=Manual commands
162 | S11 | GSYN | Manual switching mode | UINT32 | RW | 0=Assisted synchroswitch;1=I know what I am doing
162 | S12 | GSYN | Synchroswitch status | UINT32 | R | 0=Standstill;1=Departing;2=Enclosing
162 | S13 | GSYN | Magnitude side A | FLOAT | R | 0...200
162 | S14 | GSYN | Magnitude side B | FLOAT | R | 0...200
162 | S15 | GSYN | Frequency side A | FLOAT | R | 0...75
162 | S16 | GSYN | Frequency side B | FLOAT | R | 0...75
162 | S17 | GSYN | Magnitude difference | FLOAT | R | -200...200
162 | S18 | GSYN | Frequency difference | FLOAT | R | -100...100
162 | S19 | GSYN | Angle difference | FLOAT | R | -360...360
162 | S20 | GSYN | Magnitude difference on closing BRK | FLOAT | R | -200...200
162 | S21 | GSYN | Frequency difference on closing BRK | FLOAT | R | -100...100
162 | S22 | GSYN | Angle difference on closing BRK | FLOAT | R | -360...360
162 | S23 | GSYN | Estimated BRK Closing time | FLOAT | R | 0...360
162 | S24 | GSYN | Networks rotating time | FLOAT | R | 0...360
162 | S25 | GSYN | Networks placement atm | FLOAT | R | -360...360
162 | S26 | GSYN | Synchronizing time left | FLOAT | R | 0...1800
162 | S27 | GSYN | Get measurement errors for fine tuning | UINT32 | RW | 0=-;1=Get errors
162 | S28 | GSYN | Magnitude difference fine tune | FLOAT | RW | -200...200
162 | S29 | GSYN | Frequency difference fine tune | FLOAT | RW | -100...100
162 | S30 | GSYN | Angle difference fine tune | FLOAT | RW | -360...360
162 | S31 | GSYN | Generator voltage> | FLOAT | RW | 0...105
162 | S32 | GSYN | Generator voltage< | FLOAT | RW | 0...105
162 | S33 | GSYN | Bus voltage< | FLOAT | RW | 0...105
162 | S34 | GSYN | Generator frequency fGn> | FLOAT | RW | 0...102
162 | S35 | GSYN | Synchronizing start delay | FLOAT | RW | 0...1800
162 | S36 | GSYN | Minimum voltage allowed for synchronizing | FLOAT | RW | 0...105
162 | S37 | GSYN | Maximum voltage allowed for synchronizing | FLOAT | RW | 0...200
162 | S38 | GSYN | Maximum zero voltage allowed for synchronizing (100% disabled) | FLOAT | RW | 0...100
162 | S39 | GSYN | Maximum allowed voltage difference | FLOAT | RW | 0.1...100
162 | S40 | GSYN | Maximum allowed overfrequency difference to allow synchronizing | FLOAT | RW | 0...60
162 | S41 | GSYN | Maximum allowed underfrequency difference to allow synchronizing | FLOAT | RW | 0...60
162 | S42 | GSYN | Max.Time for synchronizing | FLOAT | RW | 0...1800
162 | S43 | GSYN | Maximum allowed angular disposition to allow synchronizing | FLOAT | RW | -25...25
162 | S44 | GSYN | Adjustment for measurement inaccuracy or set of desired volt. offset | FLOAT | RW | -95...95
162 | S45 | GSYN | Adjustment for measurement inaccuracy or set of desired angular offset | FLOAT | RW | -60...60
162 | S46 | GSYN | Adjustment for measurement inaccuracy or set of desired freq. offset | FLOAT | RW | -0.5...2
162 | S47 | GSYN | Voltage adjustment slope | FLOAT | RW | 0...25
162 | S48 | GSYN | Volt. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S49 | GSYN | Volt. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S50 | GSYN | Volt. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S51 | GSYN | Freq. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S52 | GSYN | Freq. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S53 | GSYN | Freq. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S54 | GSYN | Maximum allowed voltage difference to start synchronizing | FLOAT | RW | 0...50
162 | S55 | GSYN | Block voltage up commands over | FLOAT | RW | 0...50
162 | S56 | GSYN | Block voltage down commands under | FLOAT | RW | -50...50
162 | S57 | GSYN | Integrator sum when voltage adjustment pulse is generated | FLOAT | RW | 0...50
162 | S58 | GSYN | Voltage adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S59 | GSYN | Frequency adjustment slope when increasing | FLOAT | RW | 0...10
162 | S60 | GSYN | Frequency adjustment slope when decreasing | FLOAT | RW | -10...0
162 | S61 | GSYN | Maximum allowed frequency difference to start synchronizing | FLOAT | RW | 0...25
162 | S62 | GSYN | Integrator sum when frequency adjustment pulse is generated | FLOAT | RW | 0...50
162 | S63 | GSYN | Frequency adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S64 | GSYN | Filter time for angle derivative | FLOAT | RW | 0...1800
162 | S65 | GSYN | Circuit breaker pre-closing adjustment constant | FLOAT | RW | 0...10
162 | S66 | GSYN | Circuit breaker pre-closing time incl auxiliary relays | FLOAT | RW | 0...1800
162 | S67 | GSYN | Lenght of circuit breaker closing pulse | FLOAT | RW | 0...1800
162 | I1 | GSYN | Start Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I2 | GSYN | Stop Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I3 | GSYN | Block and Interrupt Synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I4 | GSYN | Breaker Closed | SIGNAL_IN | RW | 0...4294967295
162 | I5 | GSYN | Open synchronizer HMI | SIGNAL_IN | RW | 0...4294967295
162 | I6 | GSYN | Manual increase voltage | SIGNAL_IN | RW | 0...4294967295
162 | I7 | GSYN | Manual decrease voltage | SIGNAL_IN | RW | 0...4294967295
162 | I8 | GSYN | Manual increase frequency | SIGNAL_IN | RW | 0...4294967295
162 | I9 | GSYN | Manual decrease frequency | SIGNAL_IN | RW | 0...4294967295
162 | I10 | GSYN | Manual Close Breaker | SIGNAL_IN | RW | 0...4294967295
162 | I11 | GSYN | DeadBus synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I12 | GSYN | BlackStart synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | O1 | GSYN | GSYN Voltage Mag.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O2 | GSYN | GSYN Voltage Freq.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O3 | GSYN | GSYN Voltage Ang.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O4 | GSYN | GSYN Blocked | SIGNAL_OUT | RW | 0...4294967295
162 | O5 | GSYN | GSYN Running | SIGNAL_OUT | RW | 0...4294967295
162 | O6 | GSYN | GSYN Increase Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O7 | GSYN | GSYN Decrease Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O8 | GSYN | GSYN Increase Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O9 | GSYN | GSYN Decrease Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O10 | GSYN | GSYN Breaker Close Pulse | SIGNAL_OUT | RW | 0...4294967295
162 | O11 | GSYN | GSYN Long Sync Time | SIGNAL_OUT | RW | 0...4294967295
162 | O12 | GSYN | GSYN Nets Standstill | SIGNAL_OUT | RW | 0...4294967295
162 | O13 | GSYN | GSYN Nets Departing | SIGNAL_OUT | RW | 0...4294967295
162 | O14 | GSYN | GSYN Nets Enclosing | SIGNAL_OUT | RW | 0...4294967295
162 | S68 | GSYN | Control EventMaskLo | UINT32 | RW | 0...4294967295
162 | S69 | GSYN | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | S1 | VREC | Fault register mode | UINT32 | RW | 0=Disabled;1=Activated
163 | S2 | VREC | Scale current values to primary | UINT32 | RW | 0=No;1=Yes
163 | S3 | VREC | Record fault types (Overcurrrent & Voltage Over/Under) faults | UINT32 | RW | 0=No;1=Yes
163 | I1 | VREC | Fault register trigger | SIGNAL_IN | RW | 0...4294967295
163 | I2 | VREC | Reset last fault values from memory | SIGNAL_IN | RW | 0...4294967295
163 | I3 | VREC | Tripped stage | UINT32 | R | 0=-;1=I> Trip;2=I>> Trip;3=I>>> Trip;4=I>>>> Trip;5=IDir> Trip;6=IDir>> Trip;7=IDir>>> Trip;8=IDir>>>> Trip;9=U> Trip;10=U>> Trip;11=U>>> Trip;12=U>>>> Trip;13=U< Trip;14=U<< Trip;15=U<<< Trip;16=U<<<< Trip;17=I0> TRIP;18=I0>> Trip;19=I0>>> Trip;20=I0>>>> Trip;21=I0Dir> Trip;22=I0Dir>> Trip;23=I0Dir>>> Trip;24=I0Dir>>>> Trip;25=f> Trip;26=f>> Trip;27=f>>> Trip;28=f>>>> Trip;29=f< Trip;30=f<< Trip;31=f<<< Trip;32=f<<<< Trip
163 | I4 | VREC | Overcurrent fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency
163 | I5 | VREC | Voltage fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
163 | I6 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I7 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I8 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I9 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I10 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I11 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I12 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I13 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I14 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I15 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I16 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | I17 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermaloverload;15=Unbalance;16=Harmonicovercurrent
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295
231 | V1 | PFC1 | PFC condition | UINT32 | R | 0=Normal;1=Discharging;2=Blocked;3=Switching interval;4=Starting
231 | S1 | PFC1 | More kvar | UINT32 | W | 0=-;1=Increase kVAr
231 | S2 | PFC1 | Less kvar | UINT32 | W | 0=-;1=Decrease kVAr
231 | S3 | PFC1 | More kvar | UINT32 | W | 0=-;1=Increase kVAr
231 | S4 | PFC1 | Less kvar | UINT32 | W | 0=-;1=Decrease kVAr
231 | I1 | PFC1 | Bank 1 close counter | UINT32 | RW | 0...4294967295
231 | I2 | PFC1 | Bank 1 close counter (mimic) | UINT32 | RW | 0...4294967295
231 | I3 | PFC1 | Bank 2 close counter | UINT32 | RW | 0...4294967295
231 | I4 | PFC1 | Bank 2 close counter (mimic) | UINT32 | RW | 0...4294967295
231 | I5 | PFC1 | Bank 3 close counter | UINT32 | RW | 0...4294967295
231 | I6 | PFC1 | Bank 3 close counter (mimic) | UINT32 | RW | 0...4294967295
231 | I7 | PFC1 | Bank 4 close counter | UINT32 | RW | 0...4294967295
231 | I8 | PFC1 | Bank 4 close counter (mimic) | UINT32 | RW | 0...4294967295
231 | I9 | PFC1 | Bank 5 close counter | UINT32 | RW | 0...4294967295
231 | I10 | PFC1 | Bank 5 close counter (mimic) | UINT32 | RW | 0...4294967295
231 | I11 | PFC1 | Bank control failure calculator | UINT32 | R | 0...4294967295
115 | S1 | VRG1 | Vreg [AVR/90] mode | UINT32 | RW | 0=Disabled;1=Activated
115 | V1 | VRG1 | Vreg settings condition | UINT32 | R | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok
115 | V2 | VRG1 | AVR tap control status | UINT32 | R | 0=OK;1=Tap control failure
115 | V3 | VRG1 | Vreg condition | UINT32 | R | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on
115 | V4 | VRG1 | Vreg timer active | UINT32 | R | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
115 | I1 | VRG1 | Circulating current (A) | FLOAT | R | -50000...50000
115 | I2 | VRG1 | Circulating current deviation (%Un) | FLOAT | R | -50000...50000
115 | I3 | VRG1 | Voltage deviation | FLOAT | R | -50000...50000
115 | I4 | VRG1 | Total deviation | FLOAT | R | -50000...50000
115 | I5 | VRG1 | Tap voltage (kV) | FLOAT | R | -50000...50000
115 | I6 | VRG1 | Voltage difference (kV) | FLOAT | R | -50000...50000
115 | I7 | VRG1 | Time left to operation | FLOAT | R | 0...1800
115 | I8 | VRG1 | Voltage now | FLOAT | R | 0...140
115 | I9 | VRG1 | Voltage difference to set target | FLOAT | R | -100...140
115 | I10 | VRG1 | Voltage set now to | FLOAT | R | -50000...50000
115 | I11 | VRG1 | Tap location now (- 0 +) | FLOAT | R | -30...30
115 | I12 | VRG1 | Absolute tap location | FLOAT | R | 0...50
115 | I13 | VRG1 | Absolute tap location (parallel engine) | FLOAT | R | 0...50
115 | I14 | VRG1 | AVR T1 tap location now (- 0 +) | FLOAT | R | -30...30
115 | I15 | VRG1 | AVR T2 tap location now (- 0 +) | FLOAT | R | -30...30
115 | I16 | VRG1 | AVR T3 tap location now (- 0 +) | FLOAT | R | -30...30
115 | I17 | VRG1 | AVR T4 tap location now (- 0 +) | FLOAT | R | -30...30
115 | I18 | VRG1 | AVR T1 voltage deviation | FLOAT | R | -100...140
115 | I19 | VRG1 | AVR T2 voltage deviation | FLOAT | R | -100...140
115 | I20 | VRG1 | AVR T3 voltage deviation | FLOAT | R | -100...140
115 | I21 | VRG1 | AVR T4 voltage deviation | FLOAT | R | -100...140
115 | I22 | VRG1 | AVR T1 circulating current deviation | FLOAT | R | -50000...50000
115 | I23 | VRG1 | AVR T2 circulating current deviation | FLOAT | R | -50000...50000
115 | I24 | VRG1 | AVR T3 circulating current deviation | FLOAT | R | -50000...50000
115 | I25 | VRG1 | AVR T4 circulating current deviation | FLOAT | R | -50000...50000
115 | I26 | VRG1 | AVR T1 total deviation | FLOAT | R | -50000...50000
115 | I27 | VRG1 | AVR T2 total deviation | FLOAT | R | -50000...50000
115 | I28 | VRG1 | AVR T3 total deviation | FLOAT | R | -50000...50000
115 | I29 | VRG1 | AVR T4 total deviation | FLOAT | R | -50000...50000
115 | I30 | VRG1 | AVR T1 Auto/Manual | UINT32 | R | 0=Automatic;1=Manual
115 | I31 | VRG1 | AVR T2 Auto/Manual | UINT32 | R | 0=Automatic;1=Manual
115 | I32 | VRG1 | AVR 3 Auto/Manual | UINT32 | R | 0=Automatic;1=Manual
115 | I33 | VRG1 | AVR T4 Auto/Manual | UINT32 | R | 0=Automatic;1=Manual
115 | I34 | VRG1 | AVR T1 Independent/Parallel | UINT32 | R | 0=Single;1=Parallel
115 | I35 | VRG1 | AVR T2 Independent/Parallel | UINT32 | R | 0=Single;1=Parallel
115 | I36 | VRG1 | AVR T3 Independent/Parallel | UINT32 | R | 0=Single;1=Parallel
115 | I37 | VRG1 | AVR T4 Independent/Parallel | UINT32 | R | 0=Single;1=Parallel
115 | V5 | VRG1 | Tap changer on high border | UINT32 | R | 0=No;1=Yes
115 | V6 | VRG1 | Tap changer on low border | UINT32 | R | 0=No;1=Yes
115 | I38 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual (loc&rem)
115 | V7 | VRG1 | Remote tap control input | UINT32 | RW | 0=Stop;1=Lower;2=Higher
115 | S2 | VRG1 | Max control pulse length | FLOAT | RW | 0...1800
115 | S3 | VRG1 | Min control pulse length | FLOAT | RW | 0...1800
115 | S4 | VRG1 | Min time between pulses | FLOAT | RW | 0...1800
115 | S5 | VRG1 | Tap failure wait time | FLOAT | RW | 0...1800
115 | V8 | VRG1 | AVR Parallel/Independent status to mimic | UINT32 | R | 0=Parallel;1=Independent
115 | V9 | VRG1 | AVR Follower&Master status to mimic | UINT32 | R | 0=Follower;1=Master
115 | V10 | VRG1 | AVR/block: Parallel communication failure | UINT32 | R | 0=Communication OK;1=Communication failure
115 | V11 | VRG1 | AVR/block: Tap differential failure | UINT32 | R | 0=Tap OK;1=Tap difference failure
115 | V12 | VRG1 | Hierarchy status to mimic | UINT32 | R | 0=Master & follower;1=Circulating reactive current
115 | V13 | VRG1 | Auto/Manual status to mimic | UINT32 | R | 0=Auto;1=Manual
115 | V14 | VRG1 | AVR running status to mimic | UINT32 | R | 0=AVR not running;1=AVR running
115 | V15 | VRG1 | Tap position ind. setting | UINT32 | R | 0=Notselected;1=SetOk;2=Wrongsetting;3=Meas.QualityFault.
115 | I39 | VRG1 | AVR raised voltage | UINT32 | R | 0...4294967295
115 | I40 | VRG1 | AVR reduced voltage | UINT32 | R | 0...4294967295
115 | I41 | VRG1 | AVR control blocked | UINT32 | R | 0...4294967295
115 | I42 | VRG1 | AVR undervoltage blocked | UINT32 | R | 0...4294967295
115 | I43 | VRG1 | AVR overcurrent blocked | UINT32 | R | 0...4294967295
115 | S6 | VRG1 | Clear statistics | UINT32 | W | 0=-;1=Clear
115 | S7 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG1
115 | S8 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG2
115 | S9 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG3
115 | S10 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG4
115 | S11 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG5
115 | S12 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG6
115 | S13 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG7
115 | S14 | VRG1 | Target voltage (UTGT) | FLOAT | RW | 70...140 | SG8
115 | S15 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG1
115 | S16 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG2
115 | S17 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG3
115 | S18 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG4
115 | S19 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG5
115 | S20 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG6
115 | S21 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG7
115 | S22 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use | SG8
115 | S23 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG1
115 | S24 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG2
115 | S25 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG3
115 | S26 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG4
115 | S27 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG5
115 | S28 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG6
115 | S29 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG7
115 | S30 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use | SG8
115 | S31 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG1
115 | S32 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG2
115 | S33 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG3
115 | S34 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG4
115 | S35 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG5
115 | S36 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG6
115 | S37 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG7
115 | S38 | VRG1 | U>/< fast tap recontrol delay T2 in use | UINT32 | RW | 0=Not in use;1=In use | SG8
115 | S39 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG1
115 | S40 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG2
115 | S41 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG3
115 | S42 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG4
115 | S43 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG5
115 | S44 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG6
115 | S45 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG7
115 | S46 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG8
115 | S47 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG1
115 | S48 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG2
115 | S49 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG3
115 | S50 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG4
115 | S51 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG5
115 | S52 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG6
115 | S53 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG7
115 | S54 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG8
115 | S55 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG1
115 | S56 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG2
115 | S57 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG3
115 | S58 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG4
115 | S59 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG5
115 | S60 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG6
115 | S61 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG7
115 | S62 | VRG1 | U>/< T1 time delay (DT) | FLOAT | RW | 0...1800 | SG8
115 | S63 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG1
115 | S64 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG2
115 | S65 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG3
115 | S66 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG4
115 | S67 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG5
115 | S68 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG6
115 | S69 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG7
115 | S70 | VRG1 | U>/< T2 fast recontrol delay (DT) | FLOAT | RW | 0...1800 | SG8
115 | S71 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG1
115 | S72 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG2
115 | S73 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG3
115 | S74 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG4
115 | S75 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG5
115 | S76 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG6
115 | S77 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG7
115 | S78 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use | SG8
115 | S79 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG1
115 | S80 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG2
115 | S81 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG3
115 | S82 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG4
115 | S83 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG5
115 | S84 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG6
115 | S85 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG7
115 | S86 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG8
115 | S87 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG1
115 | S88 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG2
115 | S89 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG3
115 | S90 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG4
115 | S91 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG5
115 | S92 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG6
115 | S93 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG7
115 | S94 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30 | SG8
115 | S95 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG1
115 | S96 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG2
115 | S97 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG3
115 | S98 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG4
115 | S99 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG5
115 | S100 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG6
115 | S101 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG7
115 | S102 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral | SG8
115 | S103 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG1
115 | S104 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG2
115 | S105 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG3
115 | S106 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG4
115 | S107 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG5
115 | S108 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG6
115 | S109 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG7
115 | S110 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800 | SG8
115 | S111 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG1
115 | S112 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG2
115 | S113 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG3
115 | S114 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG4
115 | S115 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG5
115 | S116 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG6
115 | S117 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG7
115 | S118 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use | SG8
115 | S119 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG1
115 | S120 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG2
115 | S121 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG3
115 | S122 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG4
115 | S123 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG5
115 | S124 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG6
115 | S125 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG7
115 | S126 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30 | SG8
115 | S127 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG1
115 | S128 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG2
115 | S129 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG3
115 | S130 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG4
115 | S131 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG5
115 | S132 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG6
115 | S133 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG7
115 | S134 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80 | SG8
115 | S135 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG1
115 | S136 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG2
115 | S137 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG3
115 | S138 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG4
115 | S139 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG5
115 | S140 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG6
115 | S141 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG7
115 | S142 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use | SG8
115 | S143 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG1
115 | S144 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG2
115 | S145 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG3
115 | S146 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG4
115 | S147 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG5
115 | S148 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG6
115 | S149 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG7
115 | S150 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40 | SG8
115 | O1 | VRG1 | AVR Raise Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O2 | VRG1 | AVR Lower Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O3 | VRG1 | AVR In manual control | SIGNAL_OUT | RW | 0...4294967295
115 | O4 | VRG1 | AVR U>/< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O5 | VRG1 | AVR U>>/<< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O6 | VRG1 | AVR Outputs blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O7 | VRG1 | AVR Operation blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O8 | VRG1 | AVR Control wait on | SIGNAL_OUT | RW | 0...4294967295
115 | O9 | VRG1 | AVR U< block active | SIGNAL_OUT | RW | 0...4294967295
115 | O10 | VRG1 | AVR I> block active | SIGNAL_OUT | RW | 0...4294967295
115 | O11 | VRG1 | AVR Tap in highlimit | SIGNAL_OUT | RW | 0...4294967295
115 | O12 | VRG1 | AVR Tap in lowlimit | SIGNAL_OUT | RW | 0...4294967295
115 | O13 | VRG1 | AVR automatic mode | SIGNAL_OUT | RW | 0...4294967295
115 | O14 | VRG1 | AVR manual mode | SIGNAL_OUT | RW | 0...4294967295
115 | O15 | VRG1 | AVR operates as follower | SIGNAL_OUT | RW | 0...4294967295
115 | O16 | VRG1 | AVR operates as master | SIGNAL_OUT | RW | 0...4294967295
115 | O17 | VRG1 | AVR parallel use | SIGNAL_OUT | RW | 0...4294967295
115 | O18 | VRG1 | AVR independent use | SIGNAL_OUT | RW | 0...4294967295
115 | I44 | VRG1 | Newest register | UINT32 | R | 0...12
115 | I45 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I46 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I47 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I48 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I49 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I50 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I51 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I52 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I53 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I54 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I55 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I56 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I57 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I58 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I59 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I60 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I61 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I62 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I63 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I64 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I65 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I66 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I67 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I68 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I69 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I70 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I71 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I72 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I73 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I74 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I75 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I76 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I77 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I78 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I79 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I80 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I81 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I82 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I83 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I84 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I85 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I86 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I87 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I88 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I89 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I90 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I91 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I92 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | S151 | VRG1 | EventMaskLo | UINT32 | RW | 0...4294967295
115 | S152 | VRG1 | EventMaskHi | UINT32 | RW | 0...4294967295

## AQ-210 v2.1.1.3-180
AQ-200 IED EVENT CODES AND SPA EVENTS
FVSPE-v2.1.1.3-180 |  | G-v2.1.1.3-179 | M-v2.1.1.3-179 | R-v2.1.1.3-179 | T-v2.1.1.3-179
NOTE: THIS MAP CAN BE DIFFERENT FROM THE ONE USED BY YOUR DEVICE! TO MAKE SURE YOU HAVE A MAP THAT MATCHES WITH YOUR DEVICE, GET IT FROM THE AQS CONFIGURATION FILE (TOOLS -> EVENTS AND LOGS -> EVENT LIST
Event Code | Block Description | Event Description | SPA Event
1 | SYSTEM | Power on | 0E1
2 | SYSTEM | RTC change | 0E2
3 | SYSTEM | RTC time incorrect | 0E3
4 | SYSTEM | NTP time sync aquired | 0E4
5 | SYSTEM | NTP time change | 0E5
6 | SYSTEM | NTP time sync lost | 0E6
7 | SYSTEM | Measuring system suspended | 0E7
8 | SYSTEM | Measuring system activated | 0E8
9 | SYSTEM | Unknown event | 0E9
26 | SYSTEM | Sync input On | 0E26
27 | SYSTEM | Protection subsystem reset | 0E50
28 | SYSTEM | Storage reinitialized - no contents | 0E28
29 | SYSTEM | Storage reinitialized - new firmware detected | 0E29
30 | SYSTEM | Event buffer clear marker | 0E30
31 | SYSTEM | Event buffer initialized | 0E31
32 | SYSTEM | DblEth LinkA down | 0E32
33 | SYSTEM | DblEth LinkA OK | 0E33
34 | SYSTEM | DblEth LinkB down | 0E34
35 | SYSTEM | DblEth LinkB OK | 0E35
36 | SYSTEM | User access control HMI open | 0E36
37 | SYSTEM | User access control HMI close | 0E37
38 | SYSTEM | User access control settingtool open | 0E38
39 | SYSTEM | User access control settingtool close | 0E39
64 | DIAGNOSTICS | Diagnostic Alarm ON | 1E0
65 | DIAGNOSTICS | Diagnostic Alarm OFF | 1E1
66 | DIAGNOSTICS | Configuration changed | 1E2
67 | DIAGNOSTICS | Configuration changed clear | 1E3
68 | DIAGNOSTICS | Network overload detected On | 1E4
69 | DIAGNOSTICS | Network overload detected Off | 1E5
70 | DIAGNOSTICS | Network loop detected On | 1E6
71 | DIAGNOSTICS | Network loop detected Off | 1E7
128 | IRF | Internal Relay Fault Activated | 2E0
129 | IRF | Internal Relay Fault Deactivated | 2E1
384 | PCS | Switch1 On | 6E0
385 | PCS | Switch1 Off | 6E1
386 | PCS | Switch2 On | 6E2
387 | PCS | Switch2 Off | 6E3
388 | PCS | Switch3 On | 6E4
389 | PCS | Switch3 Off | 6E5
390 | PCS | Switch4 On | 6E6
391 | PCS | Switch4 Off | 6E7
392 | PCS | Switch5 On | 6E8
393 | PCS | Switch5 Off | 6E9
448 | CTRL | Ctrl state REMOTE | 7E0
449 | CTRL | Ctrl state LOCAL | 7E1
512 | LOGIC1 | Logical Out1 On (Logical Output 1) | 8E0
513 | LOGIC1 | Logical Out1 Off (Logical Output 1) | 8E1
514 | LOGIC1 | Logical Out2 On (Logical Output 2) | 8E2
515 | LOGIC1 | Logical Out2 Off (Logical Output 2) | 8E3
516 | LOGIC1 | Logical Out3 On (Logical Output 3) | 8E4
517 | LOGIC1 | Logical Out3 Off (Logical Output 3) | 8E5
518 | LOGIC1 | Logical Out4 On (Logical Output 4) | 8E6
519 | LOGIC1 | Logical Out4 Off (Logical Output 4) | 8E7
520 | LOGIC1 | Logical Out5 On (Logical Output 5) | 8E8
521 | LOGIC1 | Logical Out5 Off (Logical Output 5) | 8E9
522 | LOGIC1 | Logical Out6 On (Logical Output 6) | 8E10
523 | LOGIC1 | Logical Out6 Off (Logical Output 6) | 8E11
524 | LOGIC1 | Logical Out7 On (Logical Output 7) | 8E12
525 | LOGIC1 | Logical Out7 Off (Logical Output 7) | 8E13
526 | LOGIC1 | Logical Out8 On (Logical Output 8) | 8E14
527 | LOGIC1 | Logical Out8 Off (Logical Output 8) | 8E15
528 | LOGIC1 | Logical Out9 On (Logical Output 9) | 8E16
529 | LOGIC1 | Logical Out9 Off (Logical Output 9) | 8E17
530 | LOGIC1 | Logical Out10 On (Logical Output 10) | 8E18
531 | LOGIC1 | Logical Out10 Off (Logical Output 10) | 8E19
532 | LOGIC1 | Logical Out11 On (Logical Output 11) | 8E20
533 | LOGIC1 | Logical Out11 Off (Logical Output 11) | 8E21
534 | LOGIC1 | Logical Out12 On (Logical Output 12) | 8E22
535 | LOGIC1 | Logical Out12 Off (Logical Output 12) | 8E23
536 | LOGIC1 | Logical Out13 On (Logical Output 13) | 8E24
537 | LOGIC1 | Logical Out13 Off (Logical Output 13) | 8E25
538 | LOGIC1 | Logical Out14 On (Logical Output 14) | 8E26
539 | LOGIC1 | Logical Out14 Off (Logical Output 14) | 8E27
540 | LOGIC1 | Logical Out15 On (Logical Output 15) | 8E28
541 | LOGIC1 | Logical Out15 Off (Logical Output 15) | 8E29
542 | LOGIC1 | Logical Out16 On (Logical Output 16) | 8E30
543 | LOGIC1 | Logical Out16 Off (Logical Output 16) | 8E31
544 | LOGIC1 | Logical Out17 On (Logical Output 17) | 8E32
545 | LOGIC1 | Logical Out17 Off (Logical Output 17) | 8E33
546 | LOGIC1 | Logical Out18 On (Logical Output 18) | 8E34
547 | LOGIC1 | Logical Out18 Off (Logical Output 18) | 8E35
548 | LOGIC1 | Logical Out19 On (Logical Output 19) | 8E36
549 | LOGIC1 | Logical Out19 Off (Logical Output 19) | 8E37
550 | LOGIC1 | Logical Out20 On (Logical Output 20) | 8E38
551 | LOGIC1 | Logical Out20 Off (Logical Output 20) | 8E39
552 | LOGIC1 | Logical Out21 On (Logical Output 21) | 8E40
553 | LOGIC1 | Logical Out21 Off (Logical Output 21) | 8E41
554 | LOGIC1 | Logical Out22 On (Logical Output 22) | 8E42
555 | LOGIC1 | Logical Out22 Off (Logical Output 22) | 8E43
556 | LOGIC1 | Logical Out23 On (Logical Output 23) | 8E44
557 | LOGIC1 | Logical Out23 Off (Logical Output 23) | 8E45
558 | LOGIC1 | Logical Out24 On (Logical Output 24) | 8E46
559 | LOGIC1 | Logical Out24 Off (Logical Output 24) | 8E47
560 | LOGIC1 | Logical Out25 On (Logical Output 25) | 8E48
561 | LOGIC1 | Logical Out25 Off (Logical Output 25) | 8E49
562 | LOGIC1 | Logical Out26 On (Logical Output 26) | 8E50
563 | LOGIC1 | Logical Out26 Off (Logical Output 26) | 8E51
564 | LOGIC1 | Logical Out27 On (Logical Output 27) | 8E52
565 | LOGIC1 | Logical Out27 Off (Logical Output 27) | 8E53
566 | LOGIC1 | Logical Out28 On (Logical Output 28) | 8E54
567 | LOGIC1 | Logical Out28 Off (Logical Output 28) | 8E55
568 | LOGIC1 | Logical Out29 On (Logical Output 29) | 8E56
569 | LOGIC1 | Logical Out29 Off (Logical Output 29) | 8E57
570 | LOGIC1 | Logical Out30 On (Logical Output 30) | 8E58
571 | LOGIC1 | Logical Out30 Off (Logical Output 30) | 8E59
572 | LOGIC1 | Logical Out31 On (Logical Output 31) | 8E60
573 | LOGIC1 | Logical Out31 Off (Logical Output 31) | 8E61
574 | LOGIC1 | Logical Out32 On (Logical Output 32) | 8E62
575 | LOGIC1 | Logical Out32 Off (Logical Output 32) | 8E63
576 | LOGIC2 | Logical In1 On (Logical Input 1) | 9E0
577 | LOGIC2 | Logical In1 Off (Logical Input 1) | 9E1
578 | LOGIC2 | Logical In2 On (Logical Input 2) | 9E2
579 | LOGIC2 | Logical In2 Off (Logical Input 2) | 9E3
580 | LOGIC2 | Logical In3 On (Logical Input 3) | 9E4
581 | LOGIC2 | Logical In3 Off (Logical Input 3) | 9E5
582 | LOGIC2 | Logical In4 On (Logical Input 4) | 9E6
583 | LOGIC2 | Logical In4 Off (Logical Input 4) | 9E7
584 | LOGIC2 | Logical In5 On (Logical Input 5) | 9E8
585 | LOGIC2 | Logical In5 Off (Logical Input 5) | 9E9
586 | LOGIC2 | Logical In6 On (Logical Input 6) | 9E10
587 | LOGIC2 | Logical In6 Off (Logical Input 6) | 9E11
588 | LOGIC2 | Logical In7 On (Logical Input 7) | 9E12
589 | LOGIC2 | Logical In7 Off (Logical Input 7) | 9E13
590 | LOGIC2 | Logical In8 On (Logical Input 8) | 9E14
591 | LOGIC2 | Logical In8 Off (Logical Input 8) | 9E15
592 | LOGIC2 | Logical In9 On (Logical Input 9) | 9E16
593 | LOGIC2 | Logical In9 Off (Logical Input 9) | 9E17
594 | LOGIC2 | Logical In10 On (Logical Input 10) | 9E18
595 | LOGIC2 | Logical In10 Off (Logical Input 10) | 9E19
596 | LOGIC2 | Logical In11 On (Logical Input 11) | 9E20
597 | LOGIC2 | Logical In11 Off (Logical Input 11) | 9E21
598 | LOGIC2 | Logical In12 On (Logical Input 12) | 9E22
599 | LOGIC2 | Logical In12 Off (Logical Input 12) | 9E23
600 | LOGIC2 | Logical In13 On (Logical Input 13) | 9E24
601 | LOGIC2 | Logical In13 Off (Logical Input 13) | 9E25
602 | LOGIC2 | Logical In14 On (Logical Input 14) | 9E26
603 | LOGIC2 | Logical In14 Off (Logical Input 14) | 9E27
604 | LOGIC2 | Logical In15 On (Logical Input 15) | 9E28
605 | LOGIC2 | Logical In15 Off (Logical Input 15) | 9E29
606 | LOGIC2 | Logical In16 On (Logical Input 16) | 9E30
607 | LOGIC2 | Logical In16 Off (Logical Input 16) | 9E31
608 | LOGIC2 | Logical In17 On (Logical Input 17) | 9E32
609 | LOGIC2 | Logical In17 Off (Logical Input 17) | 9E33
610 | LOGIC2 | Logical In18 On (Logical Input 18) | 9E34
611 | LOGIC2 | Logical In18 Off (Logical Input 18) | 9E35
612 | LOGIC2 | Logical In19 On (Logical Input 19) | 9E36
613 | LOGIC2 | Logical In19 Off (Logical Input 19) | 9E37
614 | LOGIC2 | Logical In20 On (Logical Input 20) | 9E38
615 | LOGIC2 | Logical In20 Off (Logical Input 20) | 9E39
616 | LOGIC2 | Logical In21 On (Logical Input 21) | 9E40
617 | LOGIC2 | Logical In21 Off (Logical Input 21) | 9E41
618 | LOGIC2 | Logical In22 On (Logical Input 22) | 9E42
619 | LOGIC2 | Logical In22 Off (Logical Input 22) | 9E43
620 | LOGIC2 | Logical In23 On (Logical Input 23) | 9E44
621 | LOGIC2 | Logical In23 Off (Logical Input 23) | 9E45
622 | LOGIC2 | Logical In24 On (Logical Input 24) | 9E46
623 | LOGIC2 | Logical In24 Off (Logical Input 24) | 9E47
624 | LOGIC2 | Logical In25 On (Logical Input 25) | 9E48
625 | LOGIC2 | Logical In25 Off (Logical Input 25) | 9E49
626 | LOGIC2 | Logical In26 On (Logical Input 26) | 9E50
627 | LOGIC2 | Logical In26 Off (Logical Input 26) | 9E51
628 | LOGIC2 | Logical In27 On (Logical Input 27) | 9E52
629 | LOGIC2 | Logical In27 Off (Logical Input 27) | 9E53
630 | LOGIC2 | Logical In28 On (Logical Input 28) | 9E54
631 | LOGIC2 | Logical In28 Off (Logical Input 28) | 9E55
632 | LOGIC2 | Logical In29 On (Logical Input 29) | 9E56
633 | LOGIC2 | Logical In29 Off (Logical Input 29) | 9E57
634 | LOGIC2 | Logical In30 On (Logical Input 30) | 9E58
635 | LOGIC2 | Logical In30 Off (Logical Input 30) | 9E59
636 | LOGIC2 | Logical In31 On (Logical Input 31) | 9E60
637 | LOGIC2 | Logical In31 Off (Logical Input 31) | 9E61
638 | LOGIC2 | Logical In32 On (Logical Input 32) | 9E62
639 | LOGIC2 | Logical In32 Off (Logical Input 32) | 9E63
640 | DIGI | DI 1 On (DI1) | 10E0
641 | DIGI | DI 1 Off (DI1) | 10E1
642 | DIGI | DI 2 On (DI2) | 10E2
643 | DIGI | DI 2 Off (DI2) | 10E3
644 | DIGI | DI 3 On (DI3) | 10E4
645 | DIGI | DI 3 Off (DI3) | 10E5
646 | DIGI | DI 4 On (DI4) | 10E6
647 | DIGI | DI 4 Off (DI4) | 10E7
648 | DIGI | DI 5 On (DI5) | 10E8
649 | DIGI | DI 5 Off (DI5) | 10E9
650 | DIGI | DI 6 On (DI6) | 10E10
651 | DIGI | DI 6 Off (DI6) | 10E11
652 | DIGI | DI 7 On (DI7) | 10E12
653 | DIGI | DI 7 Off (DI7) | 10E13
654 | DIGI | DI 8 On (DI8) | 10E14
655 | DIGI | DI 8 Off (DI8) | 10E15
656 | DIGI | DI 9 On (DI9) | 10E16
657 | DIGI | DI 9 Off (DI9) | 10E17
658 | DIGI | DI 10 On (DI10) | 10E18
659 | DIGI | DI 10 Off (DI10) | 10E19
660 | DIGI | DI 11 On (DI11) | 10E20
661 | DIGI | DI 11 Off (DI11) | 10E21
662 | DIGI | DI 12 On (DI12) | 10E22
663 | DIGI | DI 12 Off (DI12) | 10E23
664 | DIGI | DI 13 On (DI13) | 10E24
665 | DIGI | DI 13 Off (DI13) | 10E25
666 | DIGI | DI 14 On (DI14) | 10E26
667 | DIGI | DI 14 Off (DI14) | 10E27
668 | DIGI | DI 15 On (DI15) | 10E28
669 | DIGI | DI 15 Off (DI15) | 10E29
670 | DIGI | DI 16 On (DI16) | 10E30
671 | DIGI | DI 16 Off (DI16) | 10E31
672 | DIGI | DI 17 On (DI17) | 10E32
673 | DIGI | DI 17 Off (DI17) | 10E33
674 | DIGI | DI 18 On (DI18) | 10E34
675 | DIGI | DI 18 Off (DI18) | 10E35
676 | DIGI | DI 19 On (DI19) | 10E36
677 | DIGI | DI 19 Off (DI19) | 10E37
678 | DIGI | DI 20 On (DI20) | 10E38
679 | DIGI | DI 20 Off (DI20) | 10E39
680 | DIGI | DI 21 On (DI21) | 10E40
681 | DIGI | DI 21 Off (DI21) | 10E41
682 | DIGI | DI 22 On (DI22) | 10E42
683 | DIGI | DI 22 Off (DI22) | 10E43
684 | DIGI | DI 23 On (DI23) | 10E44
685 | DIGI | DI 23 Off (DI23) | 10E45
686 | DIGI | DI 24 On (DI24) | 10E46
687 | DIGI | DI 24 Off (DI24) | 10E47
688 | DIGI | DI 25 On (DI25) | 10E48
689 | DIGI | DI 25 Off (DI25) | 10E49
690 | DIGI | DI 26 On (DI26) | 10E50
691 | DIGI | DI 26 Off (DI26) | 10E51
692 | DIGI | DI 27 On (DI27) | 10E52
693 | DIGI | DI 27 Off (DI27) | 10E53
694 | DIGI | DI 28 On (DI28) | 10E54
695 | DIGI | DI 28 Off (DI28) | 10E55
696 | DIGI | DI 29 On (DI29) | 10E56
697 | DIGI | DI 29 Off (DI29) | 10E57
698 | DIGI | DI 30 On (DI30) | 10E58
699 | DIGI | DI 30 Off (DI30) | 10E59
700 | DIGI | DI 31 On (DI31) | 10E60
701 | DIGI | DI 31 Off (DI31) | 10E61
702 | DIGI | DI 32 On (DI32) | 10E62
703 | DIGI | DI 32 Off (DI32) | 10E63
704 | DIGI2 | DI33 On (DI33) | 11E0
705 | DIGI2 | DI33 Off (DI33) | 11E1
706 | DIGI2 | DI34 On (DI34) | 11E2
707 | DIGI2 | DI34 Off (DI34) | 11E3
708 | DIGI2 | DI35 On (DI35) | 11E4
709 | DIGI2 | DI35 Off (DI35) | 11E5
710 | DIGI2 | DI36 On (DI36) | 11E6
711 | DIGI2 | DI36 Off (DI36) | 11E7
712 | DIGI2 | DI37 On (DI37) | 11E8
713 | DIGI2 | DI37 Off (DI37) | 11E9
714 | DIGI2 | DI38 On (DI38) | 11E10
715 | DIGI2 | DI38 Off (DI38) | 11E11
716 | DIGI2 | DI39 On (DI39) | 11E12
717 | DIGI2 | DI39 Off (DI39) | 11E13
718 | DIGI2 | DI40 On (DI40) | 11E14
719 | DIGI2 | DI40 Off (DI40) | 11E15
720 | DIGI2 | DI41 On (DI41) | 11E16
721 | DIGI2 | DI41 Off (DI41) | 11E17
722 | DIGI2 | DI42 On (DI42) | 11E18
723 | DIGI2 | DI42 Off (DI42) | 11E19
724 | DIGI2 | DI43 On (DI43) | 11E20
725 | DIGI2 | DI43 Off (DI43) | 11E21
726 | DIGI2 | DI44 On (DI44) | 11E22
727 | DIGI2 | DI44 Off (DI44) | 11E23
728 | DIGI2 | DI45 On (DI45) | 11E24
729 | DIGI2 | DI45 Off (DI45) | 11E25
730 | DIGI2 | DI46 On (DI46) | 11E26
731 | DIGI2 | DI46 Off (DI46) | 11E27
732 | DIGI2 | DI47 On (DI47) | 11E28
733 | DIGI2 | DI47 Off (DI47) | 11E29
734 | DIGI2 | DI48 On (DI48) | 11E30
735 | DIGI2 | DI48 Off (DI48) | 11E31
736 | DIGI2 | DI49 On (DI49) | 11E32
737 | DIGI2 | DI49 Off (DI49) | 11E33
738 | DIGI2 | DI50 On (DI50) | 11E34
739 | DIGI2 | DI50 Off (DI50) | 11E35
740 | DIGI2 | DI51 On (DI51) | 11E36
741 | DIGI2 | DI51 Off (DI51) | 11E37
768 | DIGI3 | DI 52 On | 12E0
769 | DIGI3 | DI 52 Off | 12E1
770 | DIGI3 | DI 53 On | 12E2
771 | DIGI3 | DI 53 Off | 12E3
772 | DIGI3 | DI 54 On | 12E4
773 | DIGI3 | DI 54 Off | 12E5
774 | DIGI3 | DI 55 On | 12E6
775 | DIGI3 | DI 55 Off | 12E7
776 | DIGI3 | DI 56 On | 12E8
777 | DIGI3 | DI 56 Off | 12E9
778 | DIGI3 | DI 57 On | 12E10
779 | DIGI3 | DI 57 Off | 12E11
780 | DIGI3 | DI 58 On | 12E12
781 | DIGI3 | DI 58 Off | 12E13
782 | DIGI3 | DI 59 On | 12E14
783 | DIGI3 | DI 59 Off | 12E15
784 | DIGI3 | DI 60 On | 12E16
785 | DIGI3 | DI 60 Off | 12E17
786 | DIGI3 | DI 61 On | 12E18
787 | DIGI3 | DI 61 Off | 12E19
788 | DIGI3 | DI 62 On | 12E20
789 | DIGI3 | DI 62 Off | 12E21
790 | DIGI3 | DI 63 On | 12E22
791 | DIGI3 | DI 63 Off | 12E23
792 | DIGI3 | DI 64 On | 12E24
793 | DIGI3 | DI 64 Off | 12E25
794 | DIGI3 | DI 65 On | 12E26
795 | DIGI3 | DI 65 Off | 12E27
796 | DIGI3 | DI 66 On | 12E28
797 | DIGI3 | DI 66 Off | 12E29
798 | DIGI3 | DI 67 On | 12E30
799 | DIGI3 | DI 67 Off | 12E31
800 | DIGI3 | DI 68 On | 12E32
801 | DIGI3 | DI 68 Off | 12E33
802 | DIGI3 | DI 69 On | 12E34
803 | DIGI3 | DI 69 Off | 12E35
804 | DIGI3 | DI 70 On | 12E36
805 | DIGI3 | DI 70 Off | 12E37
806 | DIGI3 | DI 71 On | 12E38
807 | DIGI3 | DI 71 Off | 12E39
808 | DIGI3 | DI 72 On | 12E40
809 | DIGI3 | DI 72 Off | 12E41
810 | DIGI3 | DI 73 On | 12E42
811 | DIGI3 | DI 73 Off | 12E43
812 | DIGI3 | DI 74 On | 12E44
813 | DIGI3 | DI 74 Off | 12E45
814 | DIGI3 | DI 75 On | 12E46
815 | DIGI3 | DI 75 Off | 12E47
816 | DIGI3 | DI 76 On | 12E48
817 | DIGI3 | DI 76 Off | 12E49
818 | DIGI3 | DI 77 On | 12E50
819 | DIGI3 | DI 77 Off | 12E51
820 | DIGI3 | DI 78 On | 12E52
821 | DIGI3 | DI 78 Off | 12E53
822 | DIGI3 | DI 79 On | 12E54
823 | DIGI3 | DI 79 Off | 12E55
824 | DIGI3 | DI 80 On | 12E56
825 | DIGI3 | DI 80 Off | 12E57
826 | DIGI3 | DI 81 On | 12E58
827 | DIGI3 | DI 81 Off | 12E59
828 | DIGI3 | DI 82 On | 12E60
829 | DIGI3 | DI 82 Off | 12E61
830 | DIGI3 | DI 83 On | 12E62
831 | DIGI3 | DI 83 Off | 12E63
832 | DIGI4 | DI 84 On | 13E0
833 | DIGI4 | DI 84 Off | 13E1
834 | DIGI4 | DI 85 On | 13E2
835 | DIGI4 | DI 85 Off | 13E3
836 | DIGI4 | DI 86 On | 13E4
837 | DIGI4 | DI 86 Off | 13E5
838 | DIGI4 | DI 87 On | 13E6
839 | DIGI4 | DI 87 Off | 13E7
840 | DIGI4 | DI 88 On | 13E8
841 | DIGI4 | DI 88 Off | 13E9
842 | DIGI4 | DI 89 On | 13E10
843 | DIGI4 | DI 89 Off | 13E11
844 | DIGI4 | DI 90 On | 13E12
845 | DIGI4 | DI 90 Off | 13E13
846 | DIGI4 | DI 91 On | 13E14
847 | DIGI4 | DI 91 Off | 13E15
848 | DIGI4 | DI 92 On | 13E16
849 | DIGI4 | DI 92 Off | 13E17
850 | DIGI4 | DI 93 On | 13E18
851 | DIGI4 | DI 93 Off | 13E19
852 | DIGI4 | DI 94 On | 13E20
853 | DIGI4 | DI 94 Off | 13E21
854 | DIGI4 | DI 95 On | 13E22
855 | DIGI4 | DI 95 Off | 13E23
856 | DIGI4 | DI 96 On | 13E24
857 | DIGI4 | DI 96 Off | 13E25
858 | DIGI4 | DI 97 On | 13E26
859 | DIGI4 | DI 97 Off | 13E27
860 | DIGI4 | DI 98 On | 13E28
861 | DIGI4 | DI 98 Off | 13E29
862 | DIGI4 | DI 99 On | 13E30
863 | DIGI4 | DI 99 Off | 13E31
864 | DIGI4 | DI100 On | 13E32
865 | DIGI4 | DI100 Off | 13E33
866 | DIGI4 | DI101 On | 13E34
867 | DIGI4 | DI101 Off | 13E35
868 | DIGI4 | DI102 On | 13E36
869 | DIGI4 | DI102 Off | 13E37
870 | DIGI4 | DI103 On | 13E38
871 | DIGI4 | DI103 Off | 13E39
872 | DIGI4 | DI104 On | 13E40
873 | DIGI4 | DI104 Off | 13E41
874 | DIGI4 | DI105 On | 13E42
875 | DIGI4 | DI105 Off | 13E43
876 | DIGI4 | DI106 On | 13E44
877 | DIGI4 | DI106 Off | 13E45
878 | DIGI4 | DI107 On | 13E46
879 | DIGI4 | DI107 Off | 13E47
880 | DIGI4 | DI108 On | 13E48
881 | DIGI4 | DI108 Off | 13E49
882 | DIGI4 | DI109 On | 13E50
883 | DIGI4 | DI109 Off | 13E51
884 | DIGI4 | DI110 On | 13E52
885 | DIGI4 | DI110 Off | 13E53
886 | DIGI4 | DI111 On | 13E54
887 | DIGI4 | DI111 Off | 13E55
888 | DIGI4 | DI112 On | 13E56
889 | DIGI4 | DI112 Off | 13E57
890 | DIGI4 | DI113 On | 13E58
891 | DIGI4 | DI113 Off | 13E59
892 | DIGI4 | DI114 On | 13E60
893 | DIGI4 | DI114 Off | 13E61
894 | DIGI4 | DI115 On | 13E62
895 | DIGI4 | DI115 Off | 13E63
896 | LOGIC3 | Logical Out33 On | 14E0
897 | LOGIC3 | Logical Out33 Off | 14E1
898 | LOGIC3 | Logical Out34 On | 14E2
899 | LOGIC3 | Logical Out34 Off | 14E3
900 | LOGIC3 | Logical Out35 On | 14E4
901 | LOGIC3 | Logical Out35 Off | 14E5
902 | LOGIC3 | Logical Out36 On | 14E6
903 | LOGIC3 | Logical Out36 Off | 14E7
904 | LOGIC3 | Logical Out37 On | 14E8
905 | LOGIC3 | Logical Out37 Off | 14E9
906 | LOGIC3 | Logical Out38 On | 14E10
907 | LOGIC3 | Logical Out38 Off | 14E11
908 | LOGIC3 | Logical Out39 On | 14E12
909 | LOGIC3 | Logical Out39 Off | 14E13
910 | LOGIC3 | Logical Out40 On | 14E14
911 | LOGIC3 | Logical Out40 Off | 14E15
912 | LOGIC3 | Logical Out41 On | 14E16
913 | LOGIC3 | Logical Out41 Off | 14E17
914 | LOGIC3 | Logical Out42 On | 14E18
915 | LOGIC3 | Logical Out42 Off | 14E19
916 | LOGIC3 | Logical Out43 On | 14E20
917 | LOGIC3 | Logical Out43 Off | 14E21
918 | LOGIC3 | Logical Out44 On | 14E22
919 | LOGIC3 | Logical Out44 Off | 14E23
920 | LOGIC3 | Logical Out45 On | 14E24
921 | LOGIC3 | Logical Out45 Off | 14E25
922 | LOGIC3 | Logical Out46 On | 14E26
923 | LOGIC3 | Logical Out46 Off | 14E27
924 | LOGIC3 | Logical Out47 On | 14E28
925 | LOGIC3 | Logical Out47 Off | 14E29
926 | LOGIC3 | Logical Out48 On | 14E30
927 | LOGIC3 | Logical Out48 Off | 14E31
928 | LOGIC3 | Logical Out49 On | 14E32
929 | LOGIC3 | Logical Out49 Off | 14E33
930 | LOGIC3 | Logical Out50 On | 14E34
931 | LOGIC3 | Logical Out50 Off | 14E35
932 | LOGIC3 | Logical Out51 On | 14E36
933 | LOGIC3 | Logical Out51 Off | 14E37
934 | LOGIC3 | Logical Out52 On | 14E38
935 | LOGIC3 | Logical Out52 Off | 14E39
936 | LOGIC3 | Logical Out53 On | 14E40
937 | LOGIC3 | Logical Out53 Off | 14E41
938 | LOGIC3 | Logical Out54 On | 14E42
939 | LOGIC3 | Logical Out54 Off | 14E43
940 | LOGIC3 | Logical Out55 On | 14E44
941 | LOGIC3 | Logical Out55 Off | 14E45
942 | LOGIC3 | Logical Out56 On | 14E46
943 | LOGIC3 | Logical Out56 Off | 14E47
944 | LOGIC3 | Logical Out57 On | 14E48
945 | LOGIC3 | Logical Out57 Off | 14E49
946 | LOGIC3 | Logical Out58 On | 14E50
947 | LOGIC3 | Logical Out58 Off | 14E51
948 | LOGIC3 | Logical Out59 On | 14E52
949 | LOGIC3 | Logical Out59 Off | 14E53
950 | LOGIC3 | Logical Out60 On | 14E54
951 | LOGIC3 | Logical Out60 Off | 14E55
952 | LOGIC3 | Logical Out61 On | 14E56
953 | LOGIC3 | Logical Out61 Off | 14E57
954 | LOGIC3 | Logical Out62 On | 14E58
955 | LOGIC3 | Logical Out62 Off | 14E59
956 | LOGIC3 | Logical Out63 On | 14E60
957 | LOGIC3 | Logical Out63 Off | 14E61
958 | LOGIC3 | Logical Out64 On | 14E62
959 | LOGIC3 | Logical Out64 Off | 14E63
1024 | GOOSE1 | GOOSE IN1 On (GOOSE IN1) | 16E0
1025 | GOOSE1 | GOOSE IN1 Off (GOOSE IN1) | 16E1
1026 | GOOSE1 | GOOSE IN2 On (GOOSE IN2) | 16E2
1027 | GOOSE1 | GOOSE IN2 Off (GOOSE IN2) | 16E3
1028 | GOOSE1 | GOOSE IN3 On (GOOSE IN3) | 16E4
1029 | GOOSE1 | GOOSE IN3 Off (GOOSE IN3) | 16E5
1030 | GOOSE1 | GOOSE IN4 On (GOOSE IN4) | 16E6
1031 | GOOSE1 | GOOSE IN4 Off (GOOSE IN4) | 16E7
1032 | GOOSE1 | GOOSE IN5 On (GOOSE IN5) | 16E8
1033 | GOOSE1 | GOOSE IN5 Off (GOOSE IN5) | 16E9
1034 | GOOSE1 | GOOSE IN6 On (GOOSE IN6) | 16E10
1035 | GOOSE1 | GOOSE IN6 Off (GOOSE IN6) | 16E11
1036 | GOOSE1 | GOOSE IN7 On (GOOSE IN7) | 16E12
1037 | GOOSE1 | GOOSE IN7 Off (GOOSE IN7) | 16E13
1038 | GOOSE1 | GOOSE IN8 On (GOOSE IN8) | 16E14
1039 | GOOSE1 | GOOSE IN8 Off (GOOSE IN8) | 16E15
1040 | GOOSE1 | GOOSE IN9 On (GOOSE IN9) | 16E16
1041 | GOOSE1 | GOOSE IN9 Off (GOOSE IN9) | 16E17
1042 | GOOSE1 | GOOSE IN10 On (GOOSE IN10) | 16E18
1043 | GOOSE1 | GOOSE IN10 Off (GOOSE IN10) | 16E19
1044 | GOOSE1 | GOOSE IN11 On (GOOSE IN11) | 16E20
1045 | GOOSE1 | GOOSE IN11 Off (GOOSE IN11) | 16E21
1046 | GOOSE1 | GOOSE IN12 On (GOOSE IN12) | 16E22
1047 | GOOSE1 | GOOSE IN12 Off (GOOSE IN12) | 16E23
1048 | GOOSE1 | GOOSE IN13 On (GOOSE IN13) | 16E24
1049 | GOOSE1 | GOOSE IN13 Off (GOOSE IN13) | 16E25
1050 | GOOSE1 | GOOSE IN14 On (GOOSE IN14) | 16E26
1051 | GOOSE1 | GOOSE IN14 Off (GOOSE IN14) | 16E27
1052 | GOOSE1 | GOOSE IN15 On (GOOSE IN15) | 16E28
1053 | GOOSE1 | GOOSE IN15 Off (GOOSE IN15) | 16E29
1054 | GOOSE1 | GOOSE IN16 On (GOOSE IN16) | 16E30
1055 | GOOSE1 | GOOSE IN16 Off (GOOSE IN16) | 16E31
1056 | GOOSE1 | GOOSE IN17 On (GOOSE IN17) | 16E32
1057 | GOOSE1 | GOOSE IN17 Off (GOOSE IN17) | 16E33
1058 | GOOSE1 | GOOSE IN18 On (GOOSE IN18) | 16E34
1059 | GOOSE1 | GOOSE IN18 Off (GOOSE IN18) | 16E35
1060 | GOOSE1 | GOOSE IN19 On (GOOSE IN19) | 16E36
1061 | GOOSE1 | GOOSE IN19 Off (GOOSE IN19) | 16E37
1062 | GOOSE1 | GOOSE IN20 On (GOOSE IN20) | 16E38
1063 | GOOSE1 | GOOSE IN20 Off (GOOSE IN20) | 16E39
1064 | GOOSE1 | GOOSE IN21 On (GOOSE IN21) | 16E40
1065 | GOOSE1 | GOOSE IN21 Off (GOOSE IN21) | 16E41
1066 | GOOSE1 | GOOSE IN22 On (GOOSE IN22) | 16E42
1067 | GOOSE1 | GOOSE IN22 Off (GOOSE IN22) | 16E43
1068 | GOOSE1 | GOOSE IN23 On (GOOSE IN23) | 16E44
1069 | GOOSE1 | GOOSE IN23 Off (GOOSE IN23) | 16E45
1070 | GOOSE1 | GOOSE IN24 On (GOOSE IN24) | 16E46
1071 | GOOSE1 | GOOSE IN24 Off (GOOSE IN24) | 16E47
1072 | GOOSE1 | GOOSE IN25 On (GOOSE IN25) | 16E48
1073 | GOOSE1 | GOOSE IN25 Off (GOOSE IN25) | 16E49
1074 | GOOSE1 | GOOSE IN26 On (GOOSE IN26) | 16E50
1075 | GOOSE1 | GOOSE IN26 Off (GOOSE IN26) | 16E51
1076 | GOOSE1 | GOOSE IN27 On (GOOSE IN27) | 16E52
1077 | GOOSE1 | GOOSE IN27 Off (GOOSE IN27) | 16E53
1078 | GOOSE1 | GOOSE IN28 On (GOOSE IN28) | 16E54
1079 | GOOSE1 | GOOSE IN28 Off (GOOSE IN28) | 16E55
1080 | GOOSE1 | GOOSE IN29 On (GOOSE IN29) | 16E56
1081 | GOOSE1 | GOOSE IN29 Off (GOOSE IN29) | 16E57
1082 | GOOSE1 | GOOSE IN30 On (GOOSE IN30) | 16E58
1083 | GOOSE1 | GOOSE IN30 Off (GOOSE IN30) | 16E59
1084 | GOOSE1 | GOOSE IN31 On (GOOSE IN31) | 16E60
1085 | GOOSE1 | GOOSE IN31 Off (GOOSE IN31) | 16E61
1086 | GOOSE1 | GOOSE IN32 On (GOOSE IN32) | 16E62
1087 | GOOSE1 | GOOSE IN32 Off (GOOSE IN32) | 16E63
1088 | GOOSE2 | GOOSE IN33 On (GOOSE IN33) | 17E0
1089 | GOOSE2 | GOOSE IN33 Off (GOOSE IN33) | 17E1
1090 | GOOSE2 | GOOSE IN34 On (GOOSE IN34) | 17E2
1091 | GOOSE2 | GOOSE IN34 Off (GOOSE IN34) | 17E3
1092 | GOOSE2 | GOOSE IN35 On (GOOSE IN35) | 17E4
1093 | GOOSE2 | GOOSE IN35 Off (GOOSE IN35) | 17E5
1094 | GOOSE2 | GOOSE IN36 On (GOOSE IN36) | 17E6
1095 | GOOSE2 | GOOSE IN36 Off (GOOSE IN36) | 17E7
1096 | GOOSE2 | GOOSE IN37 On (GOOSE IN37) | 17E8
1097 | GOOSE2 | GOOSE IN37 Off (GOOSE IN37) | 17E9
1098 | GOOSE2 | GOOSE IN38 On (GOOSE IN38) | 17E10
1099 | GOOSE2 | GOOSE IN38 Off (GOOSE IN38) | 17E11
1100 | GOOSE2 | GOOSE IN39 On (GOOSE IN39) | 17E12
1101 | GOOSE2 | GOOSE IN39 Off (GOOSE IN39) | 17E13
1102 | GOOSE2 | GOOSE IN40 On (GOOSE IN40) | 17E14
1103 | GOOSE2 | GOOSE IN40 Off (GOOSE IN40) | 17E15
1104 | GOOSE2 | GOOSE IN41 On (GOOSE IN41) | 17E16
1105 | GOOSE2 | GOOSE IN41 Off (GOOSE IN41) | 17E17
1106 | GOOSE2 | GOOSE IN42 On (GOOSE IN42) | 17E18
1107 | GOOSE2 | GOOSE IN42 Off (GOOSE IN42) | 17E19
1108 | GOOSE2 | GOOSE IN43 On (GOOSE IN43) | 17E20
1109 | GOOSE2 | GOOSE IN43 Off (GOOSE IN43) | 17E21
1110 | GOOSE2 | GOOSE IN44 On (GOOSE IN44) | 17E22
1111 | GOOSE2 | GOOSE IN44 Off (GOOSE IN44) | 17E23
1112 | GOOSE2 | GOOSE IN45 On (GOOSE IN45) | 17E24
1113 | GOOSE2 | GOOSE IN45 Off (GOOSE IN45) | 17E25
1114 | GOOSE2 | GOOSE IN46 On (GOOSE IN46) | 17E26
1115 | GOOSE2 | GOOSE IN46 Off (GOOSE IN46) | 17E27
1116 | GOOSE2 | GOOSE IN47 On (GOOSE IN47) | 17E28
1117 | GOOSE2 | GOOSE IN47 Off (GOOSE IN47) | 17E29
1118 | GOOSE2 | GOOSE IN48 On (GOOSE IN48) | 17E30
1119 | GOOSE2 | GOOSE IN48 Off (GOOSE IN48) | 17E31
1120 | GOOSE2 | GOOSE IN49 On (GOOSE IN49) | 17E32
1121 | GOOSE2 | GOOSE IN49 Off (GOOSE IN49) | 17E33
1122 | GOOSE2 | GOOSE IN50 On (GOOSE IN50) | 17E34
1123 | GOOSE2 | GOOSE IN50 Off (GOOSE IN50) | 17E35
1124 | GOOSE2 | GOOSE IN51 On (GOOSE IN51) | 17E36
1125 | GOOSE2 | GOOSE IN51 Off (GOOSE IN51) | 17E37
1126 | GOOSE2 | GOOSE IN52 On (GOOSE IN52) | 17E38
1127 | GOOSE2 | GOOSE IN52 Off (GOOSE IN52) | 17E39
1128 | GOOSE2 | GOOSE IN53 On (GOOSE IN53) | 17E40
1129 | GOOSE2 | GOOSE IN53 Off (GOOSE IN53) | 17E41
1130 | GOOSE2 | GOOSE IN54 On (GOOSE IN54) | 17E42
1131 | GOOSE2 | GOOSE IN54 Off (GOOSE IN54) | 17E43
1132 | GOOSE2 | GOOSE IN55 On (GOOSE IN55) | 17E44
1133 | GOOSE2 | GOOSE IN55 Off (GOOSE IN55) | 17E45
1134 | GOOSE2 | GOOSE IN56 On (GOOSE IN56) | 17E46
1135 | GOOSE2 | GOOSE IN56 Off (GOOSE IN56) | 17E47
1136 | GOOSE2 | GOOSE IN57 On (GOOSE IN57) | 17E48
1137 | GOOSE2 | GOOSE IN57 Off (GOOSE IN57) | 17E49
1138 | GOOSE2 | GOOSE IN58 On (GOOSE IN58) | 17E50
1139 | GOOSE2 | GOOSE IN58 Off (GOOSE IN58) | 17E51
1140 | GOOSE2 | GOOSE IN59 On (GOOSE IN59) | 17E52
1141 | GOOSE2 | GOOSE IN59 Off (GOOSE IN59) | 17E53
1142 | GOOSE2 | GOOSE IN60 On (GOOSE IN60) | 17E54
1143 | GOOSE2 | GOOSE IN60 Off (GOOSE IN60) | 17E55
1144 | GOOSE2 | GOOSE IN61 On (GOOSE IN61) | 17E56
1145 | GOOSE2 | GOOSE IN61 Off (GOOSE IN61) | 17E57
1146 | GOOSE2 | GOOSE IN62 On (GOOSE IN62) | 17E58
1147 | GOOSE2 | GOOSE IN62 Off (GOOSE IN62) | 17E59
1148 | GOOSE2 | GOOSE IN63 On (GOOSE IN63) | 17E60
1149 | GOOSE2 | GOOSE IN63 Off (GOOSE IN63) | 17E61
1150 | GOOSE2 | GOOSE IN64 On (GOOSE IN64) | 17E62
1151 | GOOSE2 | GOOSE IN64 Off (GOOSE IN64) | 17E63
1152 | GOOSE3 | GOOSE IN1 Quality Good (GOOSE IN1) | 18E0
1153 | GOOSE3 | GOOSE IN1 Quality Bad (GOOSE IN1) | 18E1
1154 | GOOSE3 | GOOSE IN2 Quality Good (GOOSE IN2) | 18E2
1155 | GOOSE3 | GOOSE IN2 Quality Bad (GOOSE IN2) | 18E3
1156 | GOOSE3 | GOOSE IN3 Quality Good (GOOSE IN3) | 18E4
1157 | GOOSE3 | GOOSE IN3 Quality Bad (GOOSE IN3) | 18E5
1158 | GOOSE3 | GOOSE IN4 Quality Good (GOOSE IN4) | 18E6
1159 | GOOSE3 | GOOSE IN4 Quality Bad (GOOSE IN4) | 18E7
1160 | GOOSE3 | GOOSE IN5 Quality Good (GOOSE IN5) | 18E8
1161 | GOOSE3 | GOOSE IN5 Quality Bad (GOOSE IN5) | 18E9
1162 | GOOSE3 | GOOSE IN6 Quality Good (GOOSE IN6) | 18E10
1163 | GOOSE3 | GOOSE IN6 Quality Bad (GOOSE IN6) | 18E11
1164 | GOOSE3 | GOOSE IN7 Quality Good (GOOSE IN7) | 18E12
1165 | GOOSE3 | GOOSE IN7 Quality Bad (GOOSE IN7) | 18E13
1166 | GOOSE3 | GOOSE IN8 Quality Good (GOOSE IN8) | 18E14
1167 | GOOSE3 | GOOSE IN8 Quality Bad (GOOSE IN8) | 18E15
1168 | GOOSE3 | GOOSE IN9 Quality Good (GOOSE IN9) | 18E16
1169 | GOOSE3 | GOOSE IN9 Quality Bad (GOOSE IN9) | 18E17
1170 | GOOSE3 | GOOSE IN10 Quality Good (GOOSE IN10) | 18E18
1171 | GOOSE3 | GOOSE IN10 Quality Bad (GOOSE IN10) | 18E19
1172 | GOOSE3 | GOOSE IN11 Quality Good (GOOSE IN11) | 18E20
1173 | GOOSE3 | GOOSE IN11 Quality Bad (GOOSE IN11) | 18E21
1174 | GOOSE3 | GOOSE IN12 Quality Good (GOOSE IN12) | 18E22
1175 | GOOSE3 | GOOSE IN12 Quality Bad (GOOSE IN12) | 18E23
1176 | GOOSE3 | GOOSE IN13 Quality Good (GOOSE IN13) | 18E24
1177 | GOOSE3 | GOOSE IN13 Quality Bad (GOOSE IN13) | 18E25
1178 | GOOSE3 | GOOSE IN14 Quality Good (GOOSE IN14) | 18E26
1179 | GOOSE3 | GOOSE IN14 Quality Bad (GOOSE IN14) | 18E27
1180 | GOOSE3 | GOOSE IN15 Quality Good (GOOSE IN15) | 18E28
1181 | GOOSE3 | GOOSE IN15 Quality Bad (GOOSE IN15) | 18E29
1182 | GOOSE3 | GOOSE IN16 Quality Good (GOOSE IN16) | 18E30
1183 | GOOSE3 | GOOSE IN16 Quality Bad (GOOSE IN16) | 18E31
1184 | GOOSE3 | GOOSE IN17 Quality Good (GOOSE IN17) | 18E32
1185 | GOOSE3 | GOOSE IN17 Quality Bad (GOOSE IN17) | 18E33
1186 | GOOSE3 | GOOSE IN18 Quality Good (GOOSE IN18) | 18E34
1187 | GOOSE3 | GOOSE IN18 Quality Bad (GOOSE IN18) | 18E35
1188 | GOOSE3 | GOOSE IN19 Quality Good (GOOSE IN19) | 18E36
1189 | GOOSE3 | GOOSE IN19 Quality Bad (GOOSE IN19) | 18E37
1190 | GOOSE3 | GOOSE IN20 Quality Good (GOOSE IN20) | 18E38
1191 | GOOSE3 | GOOSE IN20 Quality Bad (GOOSE IN20) | 18E39
1192 | GOOSE3 | GOOSE IN21 Quality Good (GOOSE IN21) | 18E40
1193 | GOOSE3 | GOOSE IN21 Quality Bad (GOOSE IN21) | 18E41
1194 | GOOSE3 | GOOSE IN22 Quality Good (GOOSE IN22) | 18E42
1195 | GOOSE3 | GOOSE IN22 Quality Bad (GOOSE IN22) | 18E43
1196 | GOOSE3 | GOOSE IN23 Quality Good (GOOSE IN23) | 18E44
1197 | GOOSE3 | GOOSE IN23 Quality Bad (GOOSE IN23) | 18E45
1198 | GOOSE3 | GOOSE IN24 Quality Good (GOOSE IN24) | 18E46
1199 | GOOSE3 | GOOSE IN24 Quality Bad (GOOSE IN24) | 18E47
1200 | GOOSE3 | GOOSE IN25 Quality Good (GOOSE IN25) | 18E48
1201 | GOOSE3 | GOOSE IN25 Quality Bad (GOOSE IN25) | 18E49
1202 | GOOSE3 | GOOSE IN26 Quality Good (GOOSE IN26) | 18E50
1203 | GOOSE3 | GOOSE IN26 Quality Bad (GOOSE IN26) | 18E51
1204 | GOOSE3 | GOOSE IN27 Quality Good (GOOSE IN27) | 18E52
1205 | GOOSE3 | GOOSE IN27 Quality Bad (GOOSE IN27) | 18E53
1206 | GOOSE3 | GOOSE IN28 Quality Good (GOOSE IN28) | 18E54
1207 | GOOSE3 | GOOSE IN28 Quality Bad (GOOSE IN28) | 18E55
1208 | GOOSE3 | GOOSE IN29 Quality Good (GOOSE IN29) | 18E56
1209 | GOOSE3 | GOOSE IN29 Quality Bad (GOOSE IN29) | 18E57
1210 | GOOSE3 | GOOSE IN30 Quality Good (GOOSE IN30) | 18E58
1211 | GOOSE3 | GOOSE IN30 Quality Bad (GOOSE IN30) | 18E59
1212 | GOOSE3 | GOOSE IN31 Quality Good (GOOSE IN31) | 18E60
1213 | GOOSE3 | GOOSE IN31 Quality Bad (GOOSE IN31) | 18E61
1214 | GOOSE3 | GOOSE IN32 Quality Good (GOOSE IN32) | 18E62
1215 | GOOSE3 | GOOSE IN32 Quality Bad (GOOSE IN32) | 18E63
1216 | GOOSE4 | GOOSE IN33 Quality Good (GOOSE IN33) | 19E0
1217 | GOOSE4 | GOOSE IN33 Quality Bad (GOOSE IN33) | 19E1
1218 | GOOSE4 | GOOSE IN34 Quality Good (GOOSE IN34) | 19E2
1219 | GOOSE4 | GOOSE IN34 Quality Bad (GOOSE IN34) | 19E3
1220 | GOOSE4 | GOOSE IN35 Quality Good (GOOSE IN35) | 19E4
1221 | GOOSE4 | GOOSE IN35 Quality Bad (GOOSE IN35) | 19E5
1222 | GOOSE4 | GOOSE IN36 Quality Good (GOOSE IN36) | 19E6
1223 | GOOSE4 | GOOSE IN36 Quality Bad (GOOSE IN36) | 19E7
1224 | GOOSE4 | GOOSE IN37 Quality Good (GOOSE IN37) | 19E8
1225 | GOOSE4 | GOOSE IN37 Quality Bad (GOOSE IN37) | 19E9
1226 | GOOSE4 | GOOSE IN38 Quality Good (GOOSE IN38) | 19E10
1227 | GOOSE4 | GOOSE IN38 Quality Bad (GOOSE IN38) | 19E11
1228 | GOOSE4 | GOOSE IN39 Quality Good (GOOSE IN39) | 19E12
1229 | GOOSE4 | GOOSE IN39 Quality Bad (GOOSE IN39) | 19E13
1230 | GOOSE4 | GOOSE IN40 Quality Good (GOOSE IN40) | 19E14
1231 | GOOSE4 | GOOSE IN40 Quality Bad (GOOSE IN40) | 19E15
1232 | GOOSE4 | GOOSE IN41 Quality Good (GOOSE IN41) | 19E16
1233 | GOOSE4 | GOOSE IN41 Quality Bad (GOOSE IN41) | 19E17
1234 | GOOSE4 | GOOSE IN42 Quality Good (GOOSE IN42) | 19E18
1235 | GOOSE4 | GOOSE IN42 Quality Bad (GOOSE IN42) | 19E19
1236 | GOOSE4 | GOOSE IN43 Quality Good (GOOSE IN43) | 19E20
1237 | GOOSE4 | GOOSE IN43 Quality Bad (GOOSE IN43) | 19E21
1238 | GOOSE4 | GOOSE IN44 Quality Good (GOOSE IN44) | 19E22
1239 | GOOSE4 | GOOSE IN44 Quality Bad (GOOSE IN44) | 19E23
1240 | GOOSE4 | GOOSE IN45 Quality Good (GOOSE IN45) | 19E24
1241 | GOOSE4 | GOOSE IN45 Quality Bad (GOOSE IN45) | 19E25
1242 | GOOSE4 | GOOSE IN46 Quality Good (GOOSE IN46) | 19E26
1243 | GOOSE4 | GOOSE IN46 Quality Bad (GOOSE IN46) | 19E27
1244 | GOOSE4 | GOOSE IN47 Quality Good (GOOSE IN47) | 19E28
1245 | GOOSE4 | GOOSE IN47 Quality Bad (GOOSE IN47) | 19E29
1246 | GOOSE4 | GOOSE IN48 Quality Good (GOOSE IN48) | 19E30
1247 | GOOSE4 | GOOSE IN48 Quality Bad (GOOSE IN48) | 19E31
1248 | GOOSE4 | GOOSE IN49 Quality Good (GOOSE IN49) | 19E32
1249 | GOOSE4 | GOOSE IN49 Quality Bad (GOOSE IN49) | 19E33
1250 | GOOSE4 | GOOSE IN50 Quality Good (GOOSE IN50) | 19E34
1251 | GOOSE4 | GOOSE IN50 Quality Bad (GOOSE IN50) | 19E35
1252 | GOOSE4 | GOOSE IN51 Quality Good (GOOSE IN51) | 19E36
1253 | GOOSE4 | GOOSE IN51 Quality Bad (GOOSE IN51) | 19E37
1254 | GOOSE4 | GOOSE IN52 Quality Good (GOOSE IN52) | 19E38
1255 | GOOSE4 | GOOSE IN52 Quality Bad (GOOSE IN52) | 19E39
1256 | GOOSE4 | GOOSE IN53 Quality Good (GOOSE IN53) | 19E40
1257 | GOOSE4 | GOOSE IN53 Quality Bad (GOOSE IN53) | 19E41
1258 | GOOSE4 | GOOSE IN54 Quality Good (GOOSE IN54) | 19E42
1259 | GOOSE4 | GOOSE IN54 Quality Bad (GOOSE IN54) | 19E43
1260 | GOOSE4 | GOOSE IN55 Quality Good (GOOSE IN55) | 19E44
1261 | GOOSE4 | GOOSE IN55 Quality Bad (GOOSE IN55) | 19E45
1262 | GOOSE4 | GOOSE IN56 Quality Good (GOOSE IN56) | 19E46
1263 | GOOSE4 | GOOSE IN56 Quality Bad (GOOSE IN56) | 19E47
1264 | GOOSE4 | GOOSE IN57 Quality Good (GOOSE IN57) | 19E48
1265 | GOOSE4 | GOOSE IN57 Quality Bad (GOOSE IN57) | 19E49
1266 | GOOSE4 | GOOSE IN58 Quality Good (GOOSE IN58) | 19E50
1267 | GOOSE4 | GOOSE IN58 Quality Bad (GOOSE IN58) | 19E51
1268 | GOOSE4 | GOOSE IN59 Quality Good (GOOSE IN59) | 19E52
1269 | GOOSE4 | GOOSE IN59 Quality Bad (GOOSE IN59) | 19E53
1270 | GOOSE4 | GOOSE IN60 Quality Good (GOOSE IN60) | 19E54
1271 | GOOSE4 | GOOSE IN60 Quality Bad (GOOSE IN60) | 19E55
1272 | GOOSE4 | GOOSE IN61 Quality Good (GOOSE IN61) | 19E56
1273 | GOOSE4 | GOOSE IN61 Quality Bad (GOOSE IN61) | 19E57
1274 | GOOSE4 | GOOSE IN62 Quality Good (GOOSE IN62) | 19E58
1275 | GOOSE4 | GOOSE IN62 Quality Bad (GOOSE IN62) | 19E59
1276 | GOOSE4 | GOOSE IN63 Quality Good (GOOSE IN63) | 19E60
1277 | GOOSE4 | GOOSE IN63 Quality Bad (GOOSE IN63) | 19E61
1278 | GOOSE4 | GOOSE IN64 Quality Good (GOOSE IN64) | 19E62
1279 | GOOSE4 | GOOSE IN64 Quality Bad (GOOSE IN64) | 19E63
1280 | NOC1 | Start ON | 20E0
1281 | NOC1 | Start OFF | 20E1
1282 | NOC1 | Trip ON | 20E2
1283 | NOC1 | Trip OFF | 20E3
1284 | NOC1 | Block ON | 20E4
1285 | NOC1 | Block OFF | 20E5
1286 | NOC1 | Phase A Start On | 20E6
1287 | NOC1 | Phase A Start Off | 20E7
1288 | NOC1 | Phase B Start On | 20E8
1289 | NOC1 | Phase B Start Off | 20E9
1290 | NOC1 | Phase C Start On | 20E10
1291 | NOC1 | Phase C Start Off | 20E11
1292 | NOC1 | Phase A Trip On | 20E12
1293 | NOC1 | Phase A Trip Off | 20E13
1294 | NOC1 | Phase B Trip On | 20E14
1295 | NOC1 | Phase B Trip Off | 20E15
1296 | NOC1 | Phase C Trip On | 20E16
1297 | NOC1 | Phase C Trip Off | 20E17
1344 | NOC2 | Start ON | 21E0
1345 | NOC2 | Start OFF | 21E1
1346 | NOC2 | Trip ON | 21E2
1347 | NOC2 | Trip OFF | 21E3
1348 | NOC2 | Block ON | 21E4
1349 | NOC2 | Block OFF | 21E5
1350 | NOC2 | Phase A Start On | 21E6
1351 | NOC2 | Phase A Start Off | 21E7
1352 | NOC2 | Phase B Start On | 21E8
1353 | NOC2 | Phase B Start Off | 21E9
1354 | NOC2 | Phase C Start On | 21E10
1355 | NOC2 | Phase C Start Off | 21E11
1356 | NOC2 | Phase A Trip On | 21E12
1357 | NOC2 | Phase A Trip Off | 21E13
1358 | NOC2 | Phase B Trip On | 21E14
1359 | NOC2 | Phase B Trip Off | 21E15
1360 | NOC2 | Phase C Trip On | 21E16
1361 | NOC2 | Phase C Trip Off | 21E17
1408 | NOC3 | Start ON | 22E0
1409 | NOC3 | Start OFF | 22E1
1410 | NOC3 | Trip ON | 22E2
1411 | NOC3 | Trip OFF | 22E3
1412 | NOC3 | Block ON | 22E4
1413 | NOC3 | Block OFF | 22E5
1414 | NOC3 | Phase A Start On | 22E6
1415 | NOC3 | Phase A Start Off | 22E7
1416 | NOC3 | Phase B Start On | 22E8
1417 | NOC3 | Phase B Start Off | 22E9
1418 | NOC3 | Phase C Start On | 22E10
1419 | NOC3 | Phase C Start Off | 22E11
1420 | NOC3 | Phase A Trip On | 22E12
1421 | NOC3 | Phase A Trip Off | 22E13
1422 | NOC3 | Phase B Trip On | 22E14
1423 | NOC3 | Phase B Trip Off | 22E15
1424 | NOC3 | Phase C Trip On | 22E16
1425 | NOC3 | Phase C Trip Off | 22E17
1472 | NOC4 | Start ON | 23E0
1473 | NOC4 | Start OFF | 23E1
1474 | NOC4 | Trip ON | 23E2
1475 | NOC4 | Trip OFF | 23E3
1476 | NOC4 | Block ON | 23E4
1477 | NOC4 | Block OFF | 23E5
1478 | NOC4 | Phase A Start On | 23E6
1479 | NOC4 | Phase A Start Off | 23E7
1480 | NOC4 | Phase B Start On | 23E8
1481 | NOC4 | Phase B Start Off | 23E9
1482 | NOC4 | Phase C Start On | 23E10
1483 | NOC4 | Phase C Start Off | 23E11
1484 | NOC4 | Phase A Trip On | 23E12
1485 | NOC4 | Phase A Trip Off | 23E13
1486 | NOC4 | Phase B Trip On | 23E14
1487 | NOC4 | Phase B Trip Off | 23E15
1488 | NOC4 | Phase C Trip On | 23E16
1489 | NOC4 | Phase C Trip Off | 23E17
1664 | NEF1 | Start ON | 26E0
1665 | NEF1 | Start OFF | 26E1
1666 | NEF1 | Trip ON | 26E2
1667 | NEF1 | Trip OFF | 26E3
1668 | NEF1 | Block ON | 26E4
1669 | NEF1 | Block OFF | 26E5
1728 | NEF2 | Start ON | 27E0
1729 | NEF2 | Start OFF | 27E1
1730 | NEF2 | Trip ON | 27E2
1731 | NEF2 | Trip OFF | 27E3
1732 | NEF2 | Block ON | 27E4
1733 | NEF2 | Block OFF | 27E5
1792 | NEF3 | Start ON | 28E0
1793 | NEF3 | Start OFF | 28E1
1794 | NEF3 | Trip ON | 28E2
1795 | NEF3 | Trip OFF | 28E3
1796 | NEF3 | Block ON | 28E4
1797 | NEF3 | Block OFF | 28E5
1856 | NEF4 | Start ON | 29E0
1857 | NEF4 | Start OFF | 29E1
1858 | NEF4 | Trip ON | 29E2
1859 | NEF4 | Trip OFF | 29E3
1860 | NEF4 | Block ON | 29E4
1861 | NEF4 | Block OFF | 29E5
2048 | CUB1 | Start ON | 32E0
2049 | CUB1 | Start OFF | 32E1
2050 | CUB1 | Trip ON | 32E2
2051 | CUB1 | Trip OFF | 32E3
2052 | CUB1 | Block ON | 32E4
2053 | CUB1 | Block OFF | 32E5
2112 | CUB2 | Start ON | 33E0
2113 | CUB2 | Start OFF | 33E1
2114 | CUB2 | Trip ON | 33E2
2115 | CUB2 | Trip OFF | 33E3
2116 | CUB2 | Block ON | 33E4
2117 | CUB2 | Block OFF | 33E5
2176 | CUB3 | Start ON | 34E0
2177 | CUB3 | Start OFF | 34E1
2178 | CUB3 | Trip ON | 34E2
2179 | CUB3 | Trip OFF | 34E3
2180 | CUB3 | Block ON | 34E4
2181 | CUB3 | Block OFF | 34E5
2240 | CUB4 | Start ON | 35E0
2241 | CUB4 | Start OFF | 35E1
2242 | CUB4 | Trip ON | 35E2
2243 | CUB4 | Trip OFF | 35E3
2244 | CUB4 | Block ON | 35E4
2245 | CUB4 | Block OFF | 35E5
2368 | HOC1 | Start ON | 37E0
2369 | HOC1 | Start OFF | 37E1
2370 | HOC1 | Trip ON | 37E2
2371 | HOC1 | Trip OFF | 37E3
2372 | HOC1 | Block ON | 37E4
2373 | HOC1 | Block OFF | 37E5
2432 | HOC2 | Start ON | 38E0
2433 | HOC2 | Start OFF | 38E1
2434 | HOC2 | Trip ON | 38E2
2435 | HOC2 | Trip OFF | 38E3
2436 | HOC2 | Block ON | 38E4
2437 | HOC2 | Block OFF | 38E5
2496 | HOC3 | Start ON | 39E0
2497 | HOC3 | Start OFF | 39E1
2498 | HOC3 | Trip ON | 39E2
2499 | HOC3 | Trip OFF | 39E3
2500 | HOC3 | Block ON | 39E4
2501 | HOC3 | Block OFF | 39E5
2560 | HOC4 | Start ON | 40E0
2561 | HOC4 | Start OFF | 40E1
2562 | HOC4 | Trip ON | 40E2
2563 | HOC4 | Trip OFF | 40E3
2564 | HOC4 | Block ON | 40E4
2565 | HOC4 | Block OFF | 40E5
2688 | CLP1 | LowStart ON | 42E0
2689 | CLP1 | LowStart OFF | 42E1
2690 | CLP1 | HighStart ON | 42E2
2691 | CLP1 | HighStart OFF | 42E3
2692 | CLP1 | LoadNormal ON | 42E4
2693 | CLP1 | LoadNormal OFF | 42E5
2694 | CLP1 | Overcurrent ON | 42E6
2695 | CLP1 | Overcurrent OFF | 42E7
2696 | CLP1 | CLPUActivated ON | 42E8
2697 | CLP1 | CLPUActivated OFF | 42E9
2698 | CLP1 | Block ON | 42E10
2699 | CLP1 | Block OFF | 42E11
2752 | FLX1 | Flocator triggered On | 43E0
2753 | FLX1 | Flocator triggered Off | 43E1
2754 | FLX1 | Flocator Calculation On | 43E2
2755 | FLX1 | Flocator Calculation Off | 43E3
2816 | CBF1 | Start ON | 44E0
2817 | CBF1 | Start OFF | 44E1
2818 | CBF1 | Retrip ON | 44E2
2819 | CBF1 | Retrip OFF | 44E3
2820 | CBF1 | CBFP ON | 44E4
2821 | CBF1 | CBFP OFF | 44E5
2822 | CBF1 | Block ON | 44E6
2823 | CBF1 | Block OFF | 44E7
2824 | CBF1 | DO monitor On | 44E8
2825 | CBF1 | DO monitor Off | 44E9
2826 | CBF1 | Signal On | 44E10
2827 | CBF1 | Signal Off | 44E11
2828 | CBF1 | Phase current On | 44E12
2829 | CBF1 | Phase current Off | 44E13
2830 | CBF1 | Res current On | 44E14
2831 | CBF1 | Res current Off | 44E15
2880 | SYN1 | SYN1 Blocked On | 45E0
2881 | SYN1 | SYN1 Blocked Off | 45E1
2882 | SYN1 | SYN1 Ok On | 45E2
2883 | SYN1 | SYN1 Ok Off | 45E3
2884 | SYN1 | SYN1 Bypass On | 45E4
2885 | SYN1 | SYN1 Bypass Off | 45E5
2886 | SYN1 | SYN1 Volt condition OK | 45E6
2887 | SYN1 | SYN1 Volt cond not match | 45E7
2888 | SYN1 | SYN1 Volt diff Ok | 45E8
2889 | SYN1 | SYN1 Volt diff out of setting | 45E9
2890 | SYN1 | SYN1 Angle diff Ok | 45E10
2891 | SYN1 | SYN1 Angle diff out of setting | 45E11
2892 | SYN1 | SYN1 Frequency diff Ok | 45E12
2893 | SYN1 | SYN1 Frequency diff out of setting | 45E13
2894 | SYN1 | SYN2 Blocked On | 45E14
2895 | SYN1 | SYN2 Blocked Off | 45E15
2896 | SYN1 | SYN2 Ok On | 45E16
2897 | SYN1 | SYN2 Ok Off | 45E17
2898 | SYN1 | SYN2 Bypass On | 45E18
2899 | SYN1 | SYN2 Bypass Off | 45E19
2900 | SYN1 | SYN2 Volt condition OK | 45E20
2901 | SYN1 | SYN2 Volt cond not match | 45E21
2902 | SYN1 | SYN2 Volt diff Ok | 45E22
2903 | SYN1 | SYN2 Volt diff out of setting | 45E23
2904 | SYN1 | SYN2 Angle diff Ok | 45E24
2905 | SYN1 | SYN2 Angle diff out of setting | 45E25
2906 | SYN1 | SYN2 Frequency diff Ok | 45E26
2907 | SYN1 | SYN2 Frequency diff out of setting | 45E27
2908 | SYN1 | SYN3 Blocked On | 45E28
2909 | SYN1 | SYN3 Blocked Off | 45E29
2910 | SYN1 | SYN3 Ok On | 45E30
2911 | SYN1 | SYN3 Ok Off | 45E31
2912 | SYN1 | SYN3 Bypass On | 45E32
2913 | SYN1 | SYN3 Bypass Off | 45E33
2914 | SYN1 | SYN3 Volt condition OK | 45E34
2915 | SYN1 | SYN3 Volt cond not match | 45E35
2916 | SYN1 | SYN3 Volt diff Ok | 45E36
2917 | SYN1 | SYN3 Volt diff out of setting | 45E37
2918 | SYN1 | SYN3 Angle diff Ok | 45E38
2919 | SYN1 | SYN3 Angle diff out of setting | 45E39
2920 | SYN1 | SYN3 Frequency diff Ok | 45E40
2921 | SYN1 | SYN3 Frequency diff out of setting | 45E41
2922 | SYN1 | SYN1 Switch On | 45E42
2923 | SYN1 | SYN1 Switch Off | 45E43
2924 | SYN1 | SYN2 Switch On | 45E44
2925 | SYN1 | SYN2 Switch Off | 45E45
2926 | SYN1 | SYN3 Switch On | 45E46
2927 | SYN1 | SYN3 Switch Off | 45E47
2944 | OBJ1 | Object Intermediate | 46E0
2945 | OBJ1 | Object Open | 46E1
2946 | OBJ1 | Object Close | 46E2
2947 | OBJ1 | Object Bad | 46E3
2948 | OBJ1 | WD Intermediate | 46E4
2949 | OBJ1 | WD Out | 46E5
2950 | OBJ1 | WD in | 46E6
2951 | OBJ1 | WD Bad | 46E7
2952 | OBJ1 | Open Request On | 46E8
2953 | OBJ1 | Open Request Off | 46E9
2954 | OBJ1 | Open Command On | 46E10
2955 | OBJ1 | Open Command Off | 46E11
2956 | OBJ1 | Close Request On | 46E12
2957 | OBJ1 | Close Request Off | 46E13
2958 | OBJ1 | Close Command On | 46E14
2959 | OBJ1 | Close Command Off | 46E15
2960 | OBJ1 | Open Blocked On | 46E16
2961 | OBJ1 | Open Blocked Off | 46E17
2962 | OBJ1 | Close Blocked On | 46E18
2963 | OBJ1 | Close Blocked Off | 46E19
2964 | OBJ1 | Object Ready | 46E20
2965 | OBJ1 | Object Not Ready | 46E21
2966 | OBJ1 | Sync Ok | 46E22
2967 | OBJ1 | Sync Not Ok | 46E23
2968 | OBJ1 | Open Command Fail | 46E24
2969 | OBJ1 | Close Command Fail | 46E25
2970 | OBJ1 | Final trip On | 46E26
2971 | OBJ1 | Final trip Off | 46E27
3008 | OBJ2 | Object Intermediate | 47E0
3009 | OBJ2 | Object Open | 47E1
3010 | OBJ2 | Object Close | 47E2
3011 | OBJ2 | Object Bad | 47E3
3012 | OBJ2 | WD Intermediate | 47E4
3013 | OBJ2 | WD Out | 47E5
3014 | OBJ2 | WD in | 47E6
3015 | OBJ2 | WD Bad | 47E7
3016 | OBJ2 | Open Request On | 47E8
3017 | OBJ2 | Open Request Off | 47E9
3018 | OBJ2 | Open Command On | 47E10
3019 | OBJ2 | Open Command Off | 47E11
3020 | OBJ2 | Close Request On | 47E12
3021 | OBJ2 | Close Request Off | 47E13
3022 | OBJ2 | Close Command On | 47E14
3023 | OBJ2 | Close Command Off | 47E15
3024 | OBJ2 | Open Blocked On | 47E16
3025 | OBJ2 | Open Blocked Off | 47E17
3026 | OBJ2 | Close Blocked On | 47E18
3027 | OBJ2 | Close Blocked Off | 47E19
3028 | OBJ2 | Object Ready | 47E20
3029 | OBJ2 | Object Not Ready | 47E21
3030 | OBJ2 | Sync Ok | 47E22
3031 | OBJ2 | Sync Not Ok | 47E23
3032 | OBJ2 | Open Command Fail | 47E24
3033 | OBJ2 | Close Command Fail | 47E25
3034 | OBJ2 | Final trip On | 47E26
3035 | OBJ2 | Final trip Off | 47E27
3072 | OBJ3 | Object Intermediate | 48E0
3073 | OBJ3 | Object Open | 48E1
3074 | OBJ3 | Object Close | 48E2
3075 | OBJ3 | Object Bad | 48E3
3076 | OBJ3 | WD Intermediate | 48E4
3077 | OBJ3 | WD Out | 48E5
3078 | OBJ3 | WD in | 48E6
3079 | OBJ3 | WD Bad | 48E7
3080 | OBJ3 | Open Request On | 48E8
3081 | OBJ3 | Open Request Off | 48E9
3082 | OBJ3 | Open Command On | 48E10
3083 | OBJ3 | Open Command Off | 48E11
3084 | OBJ3 | Close Request On | 48E12
3085 | OBJ3 | Close Request Off | 48E13
3086 | OBJ3 | Close Command On | 48E14
3087 | OBJ3 | Close Command Off | 48E15
3088 | OBJ3 | Open Blocked On | 48E16
3089 | OBJ3 | Open Blocked Off | 48E17
3090 | OBJ3 | Close Blocked On | 48E18
3091 | OBJ3 | Close Blocked Off | 48E19
3092 | OBJ3 | Object Ready | 48E20
3093 | OBJ3 | Object Not Ready | 48E21
3094 | OBJ3 | Sync Ok | 48E22
3095 | OBJ3 | Sync Not Ok | 48E23
3096 | OBJ3 | Open Command Fail | 48E24
3097 | OBJ3 | Close Command Fail | 48E25
3098 | OBJ3 | Final trip On | 48E26
3099 | OBJ3 | Final trip Off | 48E27
3136 | OBJ4 | Object Intermediate | 49E0
3137 | OBJ4 | Object Open | 49E1
3138 | OBJ4 | Object Close | 49E2
3139 | OBJ4 | Object Bad | 49E3
3140 | OBJ4 | WD Intermediate | 49E4
3141 | OBJ4 | WD Out | 49E5
3142 | OBJ4 | WD in | 49E6
3143 | OBJ4 | WD Bad | 49E7
3144 | OBJ4 | Open Request On | 49E8
3145 | OBJ4 | Open Request Off | 49E9
3146 | OBJ4 | Open Command On | 49E10
3147 | OBJ4 | Open Command Off | 49E11
3148 | OBJ4 | Close Request On | 49E12
3149 | OBJ4 | Close Request Off | 49E13
3150 | OBJ4 | Close Command On | 49E14
3151 | OBJ4 | Close Command Off | 49E15
3152 | OBJ4 | Open Blocked On | 49E16
3153 | OBJ4 | Open Blocked Off | 49E17
3154 | OBJ4 | Close Blocked On | 49E18
3155 | OBJ4 | Close Blocked Off | 49E19
3156 | OBJ4 | Object Ready | 49E20
3157 | OBJ4 | Object Not Ready | 49E21
3158 | OBJ4 | Sync Ok | 49E22
3159 | OBJ4 | Sync Not Ok | 49E23
3160 | OBJ4 | Open Command Fail | 49E24
3161 | OBJ4 | Close Command Fail | 49E25
3162 | OBJ4 | Final trip On | 49E26
3163 | OBJ4 | Final trip Off | 49E27
3200 | OBJ5 | Object Intermediate | 50E0
3201 | OBJ5 | Object Open | 50E1
3202 | OBJ5 | Object Close | 50E2
3203 | OBJ5 | Object Bad | 50E3
3204 | OBJ5 | WD Intermediate | 50E4
3205 | OBJ5 | WD Out | 50E5
3206 | OBJ5 | WD in | 50E6
3207 | OBJ5 | WD Bad | 50E7
3208 | OBJ5 | Open Request On | 50E8
3209 | OBJ5 | Open Request Off | 50E9
3210 | OBJ5 | Open Command On | 50E10
3211 | OBJ5 | Open Command Off | 50E11
3212 | OBJ5 | Close Request On | 50E12
3213 | OBJ5 | Close Request Off | 50E13
3214 | OBJ5 | Close Command On | 50E14
3215 | OBJ5 | Close Command Off | 50E15
3216 | OBJ5 | Open Blocked On | 50E16
3217 | OBJ5 | Open Blocked Off | 50E17
3218 | OBJ5 | Close Blocked On | 50E18
3219 | OBJ5 | Close Blocked Off | 50E19
3220 | OBJ5 | Object Ready | 50E20
3221 | OBJ5 | Object Not Ready | 50E21
3222 | OBJ5 | Sync Ok | 50E22
3223 | OBJ5 | Sync Not Ok | 50E23
3224 | OBJ5 | Open Command Fail | 50E24
3225 | OBJ5 | Close Command Fail | 50E25
3226 | OBJ5 | Final trip On | 50E26
3227 | OBJ5 | Final trip Off | 50E27
3264 | HSHC | HSI1 On | 51E0
3265 | HSHC | HSI1 Off | 51E1
3266 | HSHC | HSI2 On | 51E2
3267 | HSHC | HSI2 Off | 51E3
3268 | HSHC | HSI3 On | 51E4
3269 | HSHC | HSI3 Off | 51E5
3270 | HSHC | HSI4 On | 51E6
3271 | HSHC | HSI4 Off | 51E7
3272 | HSHC | HSI5 On | 51E8
3273 | HSHC | HSI5 Off | 51E9
3274 | HSHC | HSI6 On | 51E10
3275 | HSHC | HSI6 Off | 51E11
3276 | HSHC | HSI7 On | 51E12
3277 | HSHC | HSI7 Off | 51E13
3278 | HSHC | HSI8 On | 51E14
3279 | HSHC | HSI8 Off | 51E15
3280 | HSHC | HSI9 On | 51E16
3281 | HSHC | HSI9 Off | 51E17
3282 | HSHC | HSI10 On | 51E18
3283 | HSHC | HSI10 Off | 51E19
3284 | HSHC | HSI11 On | 51E20
3285 | HSHC | HSI11 Off | 51E21
3286 | HSHC | HSI12 On | 51E22
3287 | HSHC | HSI12 Off | 51E23
3328 | CTS1 | Alarm On | 52E0
3329 | CTS1 | Alarm Off | 52E1
3330 | CTS1 | Block On | 52E2
3331 | CTS1 | Block Off | 52E3
3392 | VTS1 | Bus VT fail Start On | 53E0
3393 | VTS1 | Bus VT fail Start Off | 53E1
3394 | VTS1 | Bus VT fail Trip On | 53E2
3395 | VTS1 | Bus VT fail Trip Off | 53E3
3396 | VTS1 | Bus VT fail Block On | 53E4
3397 | VTS1 | Bus VT fail Block Off | 53E5
3398 | VTS1 | Line VT fail On | 53E6
3399 | VTS1 | Line VT fail Off | 53E7
3400 | VTS1 | Bus Fuse fail On | 53E8
3401 | VTS1 | Bus Fuse fail Off | 53E9
3402 | VTS1 | Line Fuse fail On | 53E10
3403 | VTS1 | Line Fuse fail Off | 53E11
3456 | CTS2 | Alarm On | 54E0
3457 | CTS2 | Alarm Off | 54E1
3458 | CTS2 | Block On | 54E2
3459 | CTS2 | Block Off | 54E3
3520 | THD1 | THD Start Phase On | 55E0
3521 | THD1 | THD Start Phase Off | 55E1
3522 | THD1 | THD Start I01 On | 55E2
3523 | THD1 | THD Start I01 Off | 55E3
3524 | THD1 | THD Start I02 On | 55E4
3525 | THD1 | THD Start I02 Off | 55E5
3526 | THD1 | THD Alarm Phase On | 55E6
3527 | THD1 | THD Alarm Phase Off | 55E7
3528 | THD1 | THD Alarm I01 On | 55E8
3529 | THD1 | THD Alarm I01 Off | 55E9
3530 | THD1 | THD Alarm I02 On | 55E10
3531 | THD1 | THD Alarm I02 Off | 55E11
3532 | THD1 | Blocked On | 55E12
3533 | THD1 | Blocked Off | 55E13
3584 | FSP1 | Alarm On | 56E0
3585 | FSP1 | Alarm Off | 56E1
3586 | FSP1 | Inhibit On | 56E2
3587 | FSP1 | Inhibit Off | 56E3
3588 | FSP1 | Blocked On | 56E4
3589 | FSP1 | Blocked Off | 56E5
3648 | LCR1 | Max.Start time exceed On | 57E0
3649 | LCR1 | Max.Start time exceed Off | 57E1
3650 | LCR1 | Set start time exceed On | 57E2
3651 | LCR1 | Set start time exceed Off | 57E3
3652 | LCR1 | Speed Switch not received On | 57E4
3653 | LCR1 | Speed Switch not received Off | 57E5
3654 | LCR1 | Start On | 57E6
3655 | LCR1 | Start Off | 57E7
3656 | LCR1 | Set time Trip On | 57E8
3657 | LCR1 | Set time Trip Off | 57E9
3658 | LCR1 | Max cap Trip On | 57E10
3659 | LCR1 | Max cap Trip Off | 57E11
3660 | LCR1 | Blocked On | 57E12
3661 | LCR1 | Blocked Off | 57E13
3712 | CBW1 | CBWEAR1 Triggered | 58E0
3713 | CBW1 | CBWEAR1 Alarm1 On | 58E1
3714 | CBW1 | CBWEAR1 Alarm1 Off | 58E2
3715 | CBW1 | CBWEAR1 Alarm2 On | 58E3
3716 | CBW1 | CBWEAR1 Alarm2 Off | 58E4
3776 | MJP1 | Start ON | 59E0
3777 | MJP1 | Start OFF | 59E1
3778 | MJP1 | Trip ON | 59E2
3779 | MJP1 | Trip OFF | 59E3
3780 | MJP1 | Block ON | 59E4
3781 | MJP1 | Block OFF | 59E5
3840 | NUC1 | Start ON | 60E0
3841 | NUC1 | Start OFF | 60E1
3842 | NUC1 | Trip ON | 60E2
3843 | NUC1 | Trip OFF | 60E3
3844 | NUC1 | Block ON | 60E4
3845 | NUC1 | Block OFF | 60E5
3904 | SOF1 | SOTF Init On | 61E0
3905 | SOF1 | SOTF Init Off | 61E1
3906 | SOF1 | SOTF Block On | 61E2
3907 | SOF1 | SOTF Block Off | 61E3
3908 | SOF1 | SOTF Active On | 61E4
3909 | SOF1 | SOTF Active Off | 61E5
3910 | SOF1 | SOTF Trip On | 61E6
3911 | SOF1 | SOTF Trip Off | 61E7
3968 | MST1 | Motor Stopped On | 62E0
3969 | MST1 | Motor Stopped Off | 62E1
3970 | MST1 | Motor Starting On | 62E2
3971 | MST1 | Motor Starting Off | 62E3
3972 | MST1 | Motor Running On | 62E4
3973 | MST1 | Motor Running Off | 62E5
3974 | MST1 | Motor Stalled On | 62E6
3975 | MST1 | Motor Stalled Off | 62E7
3976 | MST1 | Load not symm On | 62E8
3977 | MST1 | Load not symm Off | 62E9
3978 | MST1 | Load normal On | 62E10
3979 | MST1 | Load normal Off | 62E11
3980 | MST1 | Overload On | 62E12
3981 | MST1 | Overload Off | 62E13
3982 | MST1 | High Overcurrent On | 62E14
3983 | MST1 | High Overcurrent Off | 62E15
4032 | AR1 | AR Ready On | 63E0
4033 | AR1 | AR Ready Off | 63E1
4034 | AR1 | AR Locked Reset | 63E2
4035 | AR1 | AR Reclosing request rejected On | 63E3
4036 | AR1 | AR Reclosing request rejected Off | 63E4
4037 | AR1 | AR Reclosing request On | 63E5
4038 | AR1 | AR Reclosing request Off | 63E6
4039 | AR1 | User Operated Obj AR halted and reset | 63E7
4040 | AR1 | Object failure, AR locked | 63E8
4041 | AR1 | Shot Failed | 63E9
4042 | AR1 | AR cycle end due to Discr request | 63E10
4043 | AR1 | AR Shot Clear | 63E11
4044 | AR1 | Object Close Request On | 63E12
4045 | AR1 | Object Open Request | 63E13
4046 | AR1 | Inhibit condition On | 63E14
4047 | AR1 | Inhibit condition Off | 63E15
4048 | AR1 | Locking condition On | 63E16
4049 | AR1 | Locking condition Off | 63E17
4050 | AR1 | Reserved | 63E18
4051 | AR1 | AR1 Request On | 63E19
4052 | AR1 | AR1 Request Off | 63E20
4053 | AR1 | AR2 Request On | 63E21
4054 | AR1 | AR2 Request Off | 63E22
4055 | AR1 | AR3 Request On | 63E23
4056 | AR1 | AR3 Request Off | 63E24
4057 | AR1 | AR4 Request On | 63E25
4058 | AR1 | AR4 Request Off | 63E26
4059 | AR1 | AR5 Request On | 63E27
4060 | AR1 | AR5 Request Off | 63E28
4061 | AR1 | Critical Request On | 63E29
4062 | AR1 | Critical Request Off | 63E30
4063 | AR1 | AR Running On | 63E31
4064 | AR1 | AR Running Off | 63E32
4065 | AR1 | Shot 1 Execute On | 63E33
4066 | AR1 | Shot 1 Execute Off | 63E34
4067 | AR1 | Shot 2 Execute On | 63E35
4068 | AR1 | Shot 2 Execute Off | 63E36
4069 | AR1 | Shot 3 Execute On | 63E37
4070 | AR1 | Shot 3 Execute Off | 63E38
4071 | AR1 | Shot 4 Execute On | 63E39
4072 | AR1 | Shot 4 Execute Off | 63E40
4073 | AR1 | Shot 5 Execute On | 63E41
4074 | AR1 | Shot 5 Execute Off | 63E42
4075 | AR1 | Seq Finished Final Trip Armed On | 63E43
4076 | AR1 | Final Trip Executed | 63E44
4077 | AR1 | Lock Out Time On | 63E45
4078 | AR1 | Lock Out Time Off | 63E46
4079 | AR1 | General Reclaim time On | 63E47
4080 | AR1 | General Reclaim time Off | 63E48
4081 | AR1 | Shot Start Time On | 63E49
4082 | AR1 | Shot Start Time Off | 63E50
4083 | AR1 | Dead Time On | 63E51
4084 | AR1 | Dead Time Off | 63E52
4085 | AR1 | Arc Discr Time On | 63E53
4086 | AR1 | Arc Discr Time Off | 63E54
4087 | AR1 | Shot Reclaim Time On | 63E55
4088 | AR1 | Shot Reclaim Time Off | 63E56
4089 | AR1 | Seq. finished Off | 63E57
4090 | AR1 | Final Trip Executed Off | 63E58
4091 | AR1 | Object Close Request Off | 63E59
4092 | AR1 | AR On | 63E60
4093 | AR1 | AR Off | 63E61
4094 | AR1 | AR Running (DT) On | 63E62
4095 | AR1 | AR Running (DT) Off | 63E63
4096 | DR1 | Recorder triggered On | 64E0
4097 | DR1 | Recorder triggered Off | 64E1
4098 | DR1 | Recorder memory cleared | 64E2
4099 | DR1 | Oldest record cleared | 64E3
4100 | DR1 | Recorder memory full On | 64E4
4101 | DR1 | Recorder memory full Off | 64E5
4102 | DR1 | Recording On | 64E6
4103 | DR1 | Recording Off | 64E7
4104 | DR1 | Storing recording On | 64E8
4105 | DR1 | Storing recording Off | 64E9
4106 | DR1 | Newest record cleared | 64E10
4160 | SGS | SG2 Enabled | 65E0
4161 | SGS | SG2 Disabled | 65E1
4162 | SGS | SG3 Enabled | 65E2
4163 | SGS | SG3 Disabled | 65E3
4164 | SGS | SG4 Enabled | 65E4
4165 | SGS | SG4 Disabled | 65E5
4166 | SGS | SG5 Enabled | 65E6
4167 | SGS | SG5 Disabled | 65E7
4168 | SGS | SG6 Enabled | 65E8
4169 | SGS | SG6 Disabled | 65E9
4170 | SGS | SG7 Enabled | 65E10
4171 | SGS | SG7 Disabled | 65E11
4172 | SGS | SG8 Enabled | 65E12
4173 | SGS | SG8 Disabled | 65E13
4174 | SGS | SG1 Request On | 65E14
4175 | SGS | SG1 Request Off | 65E15
4176 | SGS | SG2 Request On | 65E16
4177 | SGS | SG2 Request Off | 65E17
4178 | SGS | SG3 Request On | 65E18
4179 | SGS | SG3 Request Off | 65E19
4180 | SGS | SG4 Request On | 65E20
4181 | SGS | SG4 Request Off | 65E21
4182 | SGS | SG5 Request On | 65E22
4183 | SGS | SG5 Request Off | 65E23
4184 | SGS | SG6 Request On | 65E24
4185 | SGS | SG6 Request Off | 65E25
4186 | SGS | SG7 Request On | 65E26
4187 | SGS | SG7 Request Off | 65E27
4188 | SGS | SG8 Request On | 65E28
4189 | SGS | SG8 Request Off | 65E29
4190 | SGS | Remote Change SG Req On | 65E30
4191 | SGS | Remote Change SG Req Off | 65E31
4192 | SGS | Local Change SG Req On | 65E32
4193 | SGS | Local Change SG Req On | 65E33
4194 | SGS | Force Change SG On | 65E34
4195 | SGS | Force Change SG Off | 65E35
4196 | SGS | SG Req. Fail Not configured SG On | 65E36
4197 | SGS | SG Req. Fail Not configured SG On | 65E37
4198 | SGS | Force Req. Fail Force not On | 65E38
4199 | SGS | Force Req. Fail Off | 65E39
4200 | SGS | SG Req. Fail Lower priority Req. On | 65E40
4201 | SGS | SG Req. Fail Lower priority Req. Off | 65E41
4202 | SGS | SG1 Active On | 65E42
4203 | SGS | SG1 Active Off | 65E43
4204 | SGS | SG2 Active On | 65E44
4205 | SGS | SG2 Active Off | 65E45
4206 | SGS | SG3 Active On | 65E46
4207 | SGS | SG3 Active Off | 65E47
4208 | SGS | SG4 Active On | 65E48
4209 | SGS | SG4 Active Off | 65E49
4210 | SGS | SG5 Active On | 65E50
4211 | SGS | SG5 Active Off | 65E51
4212 | SGS | SG6 Active On | 65E52
4213 | SGS | SG6 Active Off | 65E53
4214 | SGS | SG7 Active On | 65E54
4215 | SGS | SG7 Active Off | 65E55
4216 | SGS | SG8 Active On | 65E56
4217 | SGS | SG8 Active Off | 65E57
4224 | REF1 | REF Trip On | 66E0
4225 | REF1 | REF Trip Off | 66E1
4226 | REF1 | REF Block On | 66E2
4227 | REF1 | REF Block Off | 66E3
4288 | TOLF1 | Alarm1 On | 67E0
4289 | TOLF1 | Alarm1 Off | 67E1
4290 | TOLF1 | Alarm2 On | 67E2
4291 | TOLF1 | Alarm2 Off | 67E3
4292 | TOLF1 | Inhibit On | 67E4
4293 | TOLF1 | Inhibit Off | 67E5
4294 | TOLF1 | Trip On | 67E6
4295 | TOLF1 | Trip Off | 67E7
4296 | TOLF1 | Block On | 67E8
4297 | TOLF1 | Block Off | 67E9
4352 | TOLM1 | Alarm1 On | 68E0
4353 | TOLM1 | Alarm1 Off | 68E1
4354 | TOLM1 | Alarm2 On | 68E2
4355 | TOLM1 | Alarm2 Off | 68E3
4356 | TOLM1 | Inhibit On | 68E4
4357 | TOLM1 | Inhibit Off | 68E5
4358 | TOLM1 | Trip On | 68E6
4359 | TOLM1 | Trip Off | 68E7
4360 | TOLM1 | Block On | 68E8
4361 | TOLM1 | Block Off | 68E9
4416 | RTD1 | S1 Alarm1 On | 69E0
4417 | RTD1 | S1 Alarm1 Off | 69E1
4418 | RTD1 | S1 Alarm2 On | 69E2
4419 | RTD1 | S1 Alarm2 Off | 69E3
4420 | RTD1 | S2 Alarm1 On | 69E4
4421 | RTD1 | S2 Alarm1 Off | 69E5
4422 | RTD1 | S2 Alarm2 On | 69E6
4423 | RTD1 | S2 Alarm2 Off | 69E7
4424 | RTD1 | S3 Alarm1 On | 69E8
4425 | RTD1 | S3 Alarm1 Off | 69E9
4426 | RTD1 | S3 Alarm2 On | 69E10
4427 | RTD1 | S3 Alarm2 Off | 69E11
4428 | RTD1 | S4 Alarm1 On | 69E12
4429 | RTD1 | S4 Alarm1 Off | 69E13
4430 | RTD1 | S4 Alarm2 On | 69E14
4431 | RTD1 | S4 Alarm2 Off | 69E15
4432 | RTD1 | S5 Alarm1 On | 69E16
4433 | RTD1 | S5 Alarm1 Off | 69E17
4434 | RTD1 | S5 Alarm2 On | 69E18
4435 | RTD1 | S5 Alarm2 Off | 69E19
4436 | RTD1 | S6 Alarm1 On | 69E20
4437 | RTD1 | S6 Alarm1 Off | 69E21
4438 | RTD1 | S6 Alarm2 On | 69E22
4439 | RTD1 | S6 Alarm2 Off | 69E23
4440 | RTD1 | S7 Alarm1 On | 69E24
4441 | RTD1 | S7 Alarm1 Off | 69E25
4442 | RTD1 | S7 Alarm2 On | 69E26
4443 | RTD1 | S7 Alarm2 Off | 69E27
4444 | RTD1 | S8 Alarm1 On | 69E28
4445 | RTD1 | S8 Alarm1 Off | 69E29
4446 | RTD1 | S8 Alarm2 On | 69E30
4447 | RTD1 | S8 Alarm2 Off | 69E31
4448 | RTD1 | S9 Alarm1 On | 69E32
4449 | RTD1 | S9 Alarm1 Off | 69E33
4450 | RTD1 | S9 Alarm2 On | 69E34
4451 | RTD1 | S9 Alarm2 Off | 69E35
4452 | RTD1 | S10 Alarm1 On | 69E36
4453 | RTD1 | S10 Alarm1 Off | 69E37
4454 | RTD1 | S10 Alarm2 On | 69E38
4455 | RTD1 | S10 Alarm2 Off | 69E39
4456 | RTD1 | S11 Alarm1 On | 69E40
4457 | RTD1 | S11 Alarm1 Off | 69E41
4458 | RTD1 | S11 Alarm2 On | 69E42
4459 | RTD1 | S11 Alarm2 Off | 69E43
4460 | RTD1 | S12 Alarm1 On | 69E44
4461 | RTD1 | S12 Alarm1 Off | 69E45
4462 | RTD1 | S12 Alarm2 On | 69E46
4463 | RTD1 | S12 Alarm2 Off | 69E47
4464 | RTD1 | S13 Alarm1 On | 69E48
4465 | RTD1 | S13 Alarm1 Off | 69E49
4466 | RTD1 | S13 Alarm2 On | 69E50
4467 | RTD1 | S13 Alarm2 Off | 69E51
4468 | RTD1 | S14 Alarm1 On | 69E52
4469 | RTD1 | S14 Alarm1 Off | 69E53
4470 | RTD1 | S14 Alarm2 On | 69E54
4471 | RTD1 | S14 Alarm2 Off | 69E55
4472 | RTD1 | S15 Alarm1 On | 69E56
4473 | RTD1 | S15 Alarm1 Off | 69E57
4474 | RTD1 | S15 Alarm2 On | 69E58
4475 | RTD1 | S15 Alarm2 Off | 69E59
4476 | RTD1 | S16 Alarm1 On | 69E60
4477 | RTD1 | S16 Alarm1 Off | 69E61
4478 | RTD1 | S16 Alarm2 On | 69E62
4479 | RTD1 | S16 Alarm2 Off | 69E63
4480 | RTD2 | S1 Meas Ok | 70E0
4481 | RTD2 | S1 Meas Invalid | 70E1
4482 | RTD2 | S2 Meas Ok | 70E2
4483 | RTD2 | S2 Meas Invalid | 70E3
4484 | RTD2 | S3 Meas Ok | 70E4
4485 | RTD2 | S3 Meas Invalid | 70E5
4486 | RTD2 | S4 Meas Ok | 70E6
4487 | RTD2 | S4 Meas Invalid | 70E7
4488 | RTD2 | S5 Meas Ok | 70E8
4489 | RTD2 | S5 Meas Invalid | 70E9
4490 | RTD2 | S6 Meas Ok | 70E10
4491 | RTD2 | S6 Meas Invalid | 70E11
4492 | RTD2 | S7 Meas Ok | 70E12
4493 | RTD2 | S7 Meas Invalid | 70E13
4494 | RTD2 | S8 Meas Ok | 70E14
4495 | RTD2 | S8 Meas Invalid | 70E15
4496 | RTD2 | S9 Meas Ok | 70E16
4497 | RTD2 | S9 Meas Invalid | 70E17
4498 | RTD2 | S10 Meas Ok | 70E18
4499 | RTD2 | S10 Meas Invalid | 70E19
4500 | RTD2 | S11 Meas Ok | 70E20
4501 | RTD2 | S11 Meas Invalid | 70E21
4502 | RTD2 | S12 Meas Ok | 70E22
4503 | RTD2 | S12 Meas Invalid | 70E23
4504 | RTD2 | S13 Meas Ok | 70E24
4505 | RTD2 | S13 Meas Invalid | 70E25
4506 | RTD2 | S14 Meas Ok | 70E26
4507 | RTD2 | S14 Meas Invalid | 70E27
4508 | RTD2 | S15 Meas Ok | 70E28
4509 | RTD2 | S15 Meas Invalid | 70E29
4510 | RTD2 | S16 Meas Ok | 70E30
4511 | RTD2 | S16 Meas Invalid | 70E31
4544 | DIF1 | Idb> Trip On | 71E0
4545 | DIF1 | Idb> Trip Off | 71E1
4546 | DIF1 | Idb> Blocked (ext) On | 71E2
4547 | DIF1 | Idb> Blocked (ext) Off | 71E3
4548 | DIF1 | Idi> Trip On | 71E4
4549 | DIF1 | Idi> Trip Off | 71E5
4550 | DIF1 | Idi> Blocked (ext) On | 71E6
4551 | DIF1 | Idi> Blocked (ext) Off | 71E7
4552 | DIF1 | 2.nd Harmonic Block On | 71E8
4553 | DIF1 | 2.nd Harmonic Block Off | 71E9
4554 | DIF1 | 5.th Harmonic Block On | 71E10
4555 | DIF1 | 5.th Harmonic Block Off | 71E11
4556 | DIF1 | L1 2.nd harm On | 71E12
4557 | DIF1 | L1 2.nd harm Off | 71E13
4558 | DIF1 | L2 2.nd harm On | 71E14
4559 | DIF1 | L2 2.nd harm Off | 71E15
4560 | DIF1 | L3 2.nd harm On | 71E16
4561 | DIF1 | L3 2.nd harm Off | 71E17
4562 | DIF1 | L1 5.th harm On | 71E18
4563 | DIF1 | L1 5.th harm Off | 71E19
4564 | DIF1 | L2 5.th harm On | 71E20
4565 | DIF1 | L2 5.th harm Off | 71E21
4566 | DIF1 | L3 5.th harm On | 71E22
4567 | DIF1 | L3 5.th harm Off | 71E23
4568 | DIF1 | HV I0d> Block On | 71E24
4569 | DIF1 | HV I0d> Block Off | 71E25
4570 | DIF1 | HV I0d> Trip On | 71E26
4571 | DIF1 | HV I0d> Trip Off | 71E27
4572 | DIF1 | LV I0d> Block On | 71E28
4573 | DIF1 | LV I0d> Block Off | 71E29
4574 | DIF1 | LV I0d> Trip On | 71E30
4575 | DIF1 | LV I0d> Trip Off | 71E31
4608 | TRF1 | Light/No load On | 72E0
4609 | TRF1 | Light/No load Off | 72E1
4610 | TRF1 | HV side inrush On | 72E2
4611 | TRF1 | HV side inrush Off | 72E3
4612 | TRF1 | LV side inrush On | 72E4
4613 | TRF1 | LV side inrush Off | 72E5
4614 | TRF1 | Load normal On | 72E6
4615 | TRF1 | Load normal Off | 72E7
4616 | TRF1 | Overloading On | 72E8
4617 | TRF1 | Overloading Off | 72E9
4618 | TRF1 | High overload On | 72E10
4619 | TRF1 | High overload Off | 72E11
4620 | TRF1 | Setting changes, calculating new trafo data | 72E12
4621 | TRF1 | Calculation finished, possible restart | 72E13
4672 | TOLT1 | Alarm1 On | 73E0
4673 | TOLT1 | Alarm1 Off | 73E1
4674 | TOLT1 | Alarm2 On | 73E2
4675 | TOLT1 | Alarm2 Off | 73E3
4676 | TOLT1 | Inhibit On | 73E4
4677 | TOLT1 | Inhibit Off | 73E5
4678 | TOLT1 | Trip On | 73E6
4679 | TOLT1 | Trip Off | 73E7
4680 | TOLT1 | Block On | 73E8
4681 | TOLT1 | Block Off | 73E9
4736 | ARC1 | Zone1 Trip On | 74E0
4737 | ARC1 | Zone1 Trip Off | 74E1
4738 | ARC1 | Zone1 Block On | 74E2
4739 | ARC1 | Zone1 BlockOff | 74E3
4740 | ARC1 | Zone2 Trip On | 74E4
4741 | ARC1 | Zone2 Trip Off | 74E5
4742 | ARC1 | Zone2 Block On | 74E6
4743 | ARC1 | Zone2 BlockOff | 74E7
4744 | ARC1 | Zone3 Trip On | 74E8
4745 | ARC1 | Zone3 Trip Off | 74E9
4746 | ARC1 | Zone3 Block On | 74E10
4747 | ARC1 | Zone3 BlockOff | 74E11
4748 | ARC1 | Zone4 Trip On | 74E12
4749 | ARC1 | Zone4 Trip Off | 74E13
4750 | ARC1 | Zone4 Block On | 74E14
4751 | ARC1 | Zone4 BlockOff | 74E15
4752 | ARC1 | Ph Current Blocked On | 74E16
4753 | ARC1 | Ph Current Blocked Off | 74E17
4754 | ARC1 | Ph Current Start On | 74E18
4755 | ARC1 | Ph Current Start Off | 74E19
4756 | ARC1 | Res Current Blocked On | 74E20
4757 | ARC1 | Res Current Blocked Off | 74E21
4758 | ARC1 | Res Current Start On | 74E22
4759 | ARC1 | Res Current Start Off | 74E23
4760 | ARC1 | Channel 1 Light On | 74E24
4761 | ARC1 | Channel 1 Light Off | 74E25
4762 | ARC1 | Channel 1 Pressure On | 74E26
4763 | ARC1 | Channel 1 Pressure Off | 74E27
4764 | ARC1 | Channel 2 Light On | 74E28
4765 | ARC1 | Channel 2 Light Off | 74E29
4766 | ARC1 | Channel 2 Pressure On | 74E30
4767 | ARC1 | Channel 2 Pressure Off | 74E31
4768 | ARC1 | Channel 3 Light On | 74E32
4769 | ARC1 | Channel 3 Light Off | 74E33
4770 | ARC1 | Channel 3 Pressure On | 74E34
4771 | ARC1 | Channel 3 Pressure Off | 74E35
4772 | ARC1 | Channel 4 Light On | 74E36
4773 | ARC1 | Channel 4 Light Off | 74E37
4774 | ARC1 | Channel 4 Pressure On | 74E38
4775 | ARC1 | Channel 4 Pressure Off | 74E39
4776 | ARC1 | DI Signal On | 74E40
4777 | ARC1 | DI Signal Off | 74E41
4800 | DOC1 | Start ON | 75E0
4801 | DOC1 | Start OFF | 75E1
4802 | DOC1 | Trip ON | 75E2
4803 | DOC1 | Trip OFF | 75E3
4804 | DOC1 | Block ON | 75E4
4805 | DOC1 | Block OFF | 75E5
4806 | DOC1 | No voltage, Protection locked On | 75E6
4807 | DOC1 | Voltage measurable, Protection locked Off | 75E7
4808 | DOC1 | Measuring live angle On | 75E8
4809 | DOC1 | Measuring live angle Off | 75E9
4810 | DOC1 | Using voltmem On | 75E10
4811 | DOC1 | Using voltmem Off | 75E11
4813 | DOC1 | Voltage mem Off Emergency non dir On | 75E13
4814 | DOC1 | Voltage mem Off Emergency non dir Off | 75E14
4864 | DOC2 | Start ON | 76E0
4865 | DOC2 | Start OFF | 76E1
4866 | DOC2 | Trip ON | 76E2
4867 | DOC2 | Trip OFF | 76E3
4868 | DOC2 | Block ON | 76E4
4869 | DOC2 | Block OFF | 76E5
4870 | DOC2 | No voltage, Protection locked On | 76E6
4871 | DOC2 | Voltage measurable, Protection locked Off | 76E7
4872 | DOC2 | Measuring live angle On | 76E8
4873 | DOC2 | Measuring live angle Off | 76E9
4874 | DOC2 | Using voltmem On | 76E10
4875 | DOC2 | Using voltmem Off | 76E11
4877 | DOC2 | Voltage mem Off Emergency non dir On | 76E13
4878 | DOC2 | Voltage mem Off Emergency non dir Off | 76E14
4928 | DOC3 | Start ON | 77E0
4929 | DOC3 | Start OFF | 77E1
4930 | DOC3 | Trip ON | 77E2
4931 | DOC3 | Trip OFF | 77E3
4932 | DOC3 | Block ON | 77E4
4933 | DOC3 | Block OFF | 77E5
4934 | DOC3 | No voltage, Protection locked On | 77E6
4935 | DOC3 | Voltage measurable, Protection locked Off | 77E7
4936 | DOC3 | Measuring live angle On | 77E8
4937 | DOC3 | Measuring live angle Off | 77E9
4938 | DOC3 | Using voltmem On | 77E10
4939 | DOC3 | Using voltmem Off | 77E11
4941 | DOC3 | Voltage mem Off Emergency non dir On | 77E13
4942 | DOC3 | Voltage mem Off Emergency non dir Off | 77E14
4992 | DOC4 | Start ON | 78E0
4993 | DOC4 | Start OFF | 78E1
4994 | DOC4 | Trip ON | 78E2
4995 | DOC4 | Trip OFF | 78E3
4996 | DOC4 | Block ON | 78E4
4997 | DOC4 | Block OFF | 78E5
4998 | DOC4 | No voltage, Protection locked On | 78E6
4999 | DOC4 | Voltage measurable, Protection locked Off | 78E7
5000 | DOC4 | Measuring live angle On | 78E8
5001 | DOC4 | Measuring live angle Off | 78E9
5002 | DOC4 | Using voltmem On | 78E10
5003 | DOC4 | Using voltmem Off | 78E11
5005 | DOC4 | Voltage mem Off Emergency non dir On | 78E13
5006 | DOC4 | Voltage mem Off Emergency non dir Off | 78E14
5184 | DEF1 | Start ON | 81E0
5185 | DEF1 | Start OFF | 81E1
5186 | DEF1 | Trip ON | 81E2
5187 | DEF1 | Trip OFF | 81E3
5188 | DEF1 | Block ON | 81E4
5189 | DEF1 | Block OFF | 81E5
5190 | DEF1 | I0Cosfi Start On | 81E6
5191 | DEF1 | I0Cosfi Start Off | 81E7
5192 | DEF1 | I0Sinfi Start On | 81E8
5193 | DEF1 | I0Sinfi Start Off | 81E9
5194 | DEF1 | I0Cosfi Trip On | 81E10
5195 | DEF1 | I0Cosfi Trip Off | 81E11
5196 | DEF1 | I0Sinfi Trip On | 81E12
5197 | DEF1 | I0Sinfi Trip Off | 81E13
5248 | DEF2 | Start ON | 82E0
5249 | DEF2 | Start OFF | 82E1
5250 | DEF2 | Trip ON | 82E2
5251 | DEF2 | Trip OFF | 82E3
5252 | DEF2 | Block ON | 82E4
5253 | DEF2 | Block OFF | 82E5
5254 | DEF2 | I0Cosfi Start On | 82E6
5255 | DEF2 | I0Cosfi Start Off | 82E7
5256 | DEF2 | I0Sinfi Start On | 82E8
5257 | DEF2 | I0Sinfi Start Off | 82E9
5258 | DEF2 | I0Cosfi Trip On | 82E10
5259 | DEF2 | I0Cosfi Trip Off | 82E11
5260 | DEF2 | I0Sinfi Trip On | 82E12
5261 | DEF2 | I0Sinfi Trip Off | 82E13
5312 | DEF3 | Start ON | 83E0
5313 | DEF3 | Start OFF | 83E1
5314 | DEF3 | Trip ON | 83E2
5315 | DEF3 | Trip OFF | 83E3
5316 | DEF3 | Block ON | 83E4
5317 | DEF3 | Block OFF | 83E5
5318 | DEF3 | I0Cosfi Start On | 83E6
5319 | DEF3 | I0Cosfi Start Off | 83E7
5320 | DEF3 | I0Sinfi Start On | 83E8
5321 | DEF3 | I0Sinfi Start Off | 83E9
5322 | DEF3 | I0Cosfi Trip On | 83E10
5323 | DEF3 | I0Cosfi Trip Off | 83E11
5324 | DEF3 | I0Sinfi Trip On | 83E12
5325 | DEF3 | I0Sinfi Trip Off | 83E13
5376 | DEF4 | Start ON | 84E0
5377 | DEF4 | Start OFF | 84E1
5378 | DEF4 | Trip ON | 84E2
5379 | DEF4 | Trip OFF | 84E3
5380 | DEF4 | Block ON | 84E4
5381 | DEF4 | Block OFF | 84E5
5382 | DEF4 | I0Cosfi Start On | 84E6
5383 | DEF4 | I0Cosfi Start Off | 84E7
5384 | DEF4 | I0Sinfi Start On | 84E8
5385 | DEF4 | I0Sinfi Start Off | 84E9
5386 | DEF4 | I0Cosfi Trip On | 84E10
5387 | DEF4 | I0Cosfi Trip Off | 84E11
5388 | DEF4 | I0Sinfi Trip On | 84E12
5389 | DEF4 | I0Sinfi Trip Off | 84E13
5440 | OV1 | Start ON | 85E0
5441 | OV1 | Start OFF | 85E1
5442 | OV1 | Trip ON | 85E2
5443 | OV1 | Trip OFF | 85E3
5444 | OV1 | Block ON | 85E4
5445 | OV1 | Block OFF | 85E5
5504 | OV2 | Start ON | 86E0
5505 | OV2 | Start OFF | 86E1
5506 | OV2 | Trip ON | 86E2
5507 | OV2 | Trip OFF | 86E3
5508 | OV2 | Block ON | 86E4
5509 | OV2 | Block OFF | 86E5
5568 | OV3 | Start ON | 87E0
5569 | OV3 | Start OFF | 87E1
5570 | OV3 | Trip ON | 87E2
5571 | OV3 | Trip OFF | 87E3
5572 | OV3 | Block ON | 87E4
5573 | OV3 | Block OFF | 87E5
5632 | OV4 | Start ON | 88E0
5633 | OV4 | Start OFF | 88E1
5634 | OV4 | Trip ON | 88E2
5635 | OV4 | Trip OFF | 88E3
5636 | OV4 | Block ON | 88E4
5637 | OV4 | Block OFF | 88E5
5696 | UV1 | Start ON | 89E0
5697 | UV1 | Start OFF | 89E1
5698 | UV1 | Trip ON | 89E2
5699 | UV1 | Trip OFF | 89E3
5700 | UV1 | Block ON | 89E4
5701 | UV1 | Block OFF | 89E5
5702 | UV1 | Undervoltage Block On | 89E6
5703 | UV1 | Undervoltage Block Off | 89E7
5760 | UV2 | Start ON | 90E0
5761 | UV2 | Start OFF | 90E1
5762 | UV2 | Trip ON | 90E2
5763 | UV2 | Trip OFF | 90E3
5764 | UV2 | Block ON | 90E4
5765 | UV2 | Block OFF | 90E5
5766 | UV2 | Undervoltage Block On | 90E6
5767 | UV2 | Undervoltage Block Off | 90E7
5824 | UV3 | Start ON | 91E0
5825 | UV3 | Start OFF | 91E1
5826 | UV3 | Trip ON | 91E2
5827 | UV3 | Trip OFF | 91E3
5828 | UV3 | Block ON | 91E4
5829 | UV3 | Block OFF | 91E5
5830 | UV3 | Undervoltage Block On | 91E6
5831 | UV3 | Undervoltage Block Off | 91E7
5888 | UV4 | Start ON | 92E0
5889 | UV4 | Start OFF | 92E1
5890 | UV4 | Trip ON | 92E2
5891 | UV4 | Trip OFF | 92E3
5892 | UV4 | Block ON | 92E4
5893 | UV4 | Block OFF | 92E5
5894 | UV4 | Undervoltage Block On | 92E6
5895 | UV4 | Undervoltage Block Off | 92E7
5952 | NOV1 | Start ON | 93E0
5953 | NOV1 | Start OFF | 93E1
5954 | NOV1 | Trip ON | 93E2
5955 | NOV1 | Trip OFF | 93E3
5956 | NOV1 | Block ON | 93E4
5957 | NOV1 | Block OFF | 93E5
6016 | NOV2 | Start ON | 94E0
6017 | NOV2 | Start OFF | 94E1
6018 | NOV2 | Trip ON | 94E2
6019 | NOV2 | Trip OFF | 94E3
6020 | NOV2 | Block ON | 94E4
6021 | NOV2 | Block OFF | 94E5
6080 | NOV3 | Start ON | 95E0
6081 | NOV3 | Start OFF | 95E1
6082 | NOV3 | Trip ON | 95E2
6083 | NOV3 | Trip OFF | 95E3
6084 | NOV3 | Block ON | 95E4
6085 | NOV3 | Block OFF | 95E5
6144 | NOV4 | Start ON | 96E0
6145 | NOV4 | Start OFF | 96E1
6146 | NOV4 | Trip ON | 96E2
6147 | NOV4 | Trip OFF | 96E3
6148 | NOV4 | Block ON | 96E4
6149 | NOV4 | Block OFF | 96E5
6208 | NJK1 | U0RECL Request On | 97E0
6209 | NJK1 | U0RECL Request Off | 97E1
6210 | NJK1 | U0RECL Blocked On | 97E2
6211 | NJK1 | U0RECL Blocked Off | 97E3
6212 | NJK1 | U0RECL Active On | 97E4
6213 | NJK1 | U0RECL Active Off | 97E5
6214 | NJK1 | U0RECL Breaker close request On | 97E6
6215 | NJK1 | U0RECL Breaker close request Off | 97E7
6216 | NJK1 | U0RECL U0 Blocking On | 97E8
6217 | NJK1 | U0RECL U0 Blocking Off | 97E9
6272 | FRQC1 | f> [Curr] Start ON | 98E0
6273 | FRQC1 | f> [Curr] Start OFF | 98E1
6274 | FRQC1 | f> [Curr] Trip ON | 98E2
6275 | FRQC1 | f> [Curr] Trip OFF | 98E3
6276 | FRQC1 | f>>[Curr] Start ON | 98E4
6277 | FRQC1 | f>> [Curr] Start OFF | 98E5
6278 | FRQC1 | f>> [Curr] Trip ON | 98E6
6279 | FRQC1 | f>> [Curr] Trip OFF | 98E7
6280 | FRQC1 | f>>> [Curr] Start ON | 98E8
6281 | FRQC1 | f>>> [Curr] Start OFF | 98E9
6282 | FRQC1 | f>>> [Curr] Trip ON | 98E10
6283 | FRQC1 | f>>> [Curr] Trip OFF | 98E11
6284 | FRQC1 | f>>>> [Curr] Start ON | 98E12
6285 | FRQC1 | f>>>> [Curr] Start OFF | 98E13
6286 | FRQC1 | f>>>> [Curr] Trip ON | 98E14
6287 | FRQC1 | f>>>> [Curr] Trip OFF | 98E15
6288 | FRQC1 | f< [Curr] Start ON | 98E16
6289 | FRQC1 | f< [Curr] Start OFF | 98E17
6290 | FRQC1 | f< [Curr] Trip ON | 98E18
6291 | FRQC1 | f< [Curr] Trip OFF | 98E19
6292 | FRQC1 | f<< [Curr] Start ON | 98E20
6293 | FRQC1 | f<< [Curr] Start OFF | 98E21
6294 | FRQC1 | f<< [Curr] Trip ON | 98E22
6295 | FRQC1 | f<< [Curr] Trip OFF | 98E23
6296 | FRQC1 | f<<< [Curr] Start ON | 98E24
6297 | FRQC1 | f<<< [Curr] Start OFF | 98E25
6298 | FRQC1 | f<<< [Curr] Trip ON | 98E26
6299 | FRQC1 | f<<< [Curr] Trip OFF | 98E27
6300 | FRQC1 | f<<<< [Curr] Start ON | 98E28
6301 | FRQC1 | f<<<< [Curr] Start OFF | 98E29
6302 | FRQC1 | f<<<< [Curr] Trip ON | 98E30
6303 | FRQC1 | f<<<< [Curr] Trip OFF | 98E31
6304 | FRQC1 | f> [Curr] Block ON | 98E32
6305 | FRQC1 | f> [Curr] Block OFF | 98E33
6306 | FRQC1 | f>> [Curr] Block ON | 98E34
6307 | FRQC1 | f>> [Curr] Block OFF | 98E35
6308 | FRQC1 | f>>> [Curr] Block ON | 98E36
6309 | FRQC1 | f>>> [Curr] Block OFF | 98E37
6310 | FRQC1 | f>>>> [Curr] Block ON | 98E38
6311 | FRQC1 | f>>>> [Curr] Block OFF | 98E39
6312 | FRQC1 | f< [Curr] Block ON | 98E40
6313 | FRQC1 | f< [Curr] Block OFF | 98E41
6314 | FRQC1 | f<< [Curr] Block ON | 98E42
6315 | FRQC1 | f<< [Curr] Block OFF | 98E43
6316 | FRQC1 | f<<< [Curr] Block ON | 98E44
6317 | FRQC1 | f<<< [Curr] Block OFF | 98E45
6318 | FRQC1 | f<<<< [Curr] Block ON | 98E46
6319 | FRQC1 | f<<<< [Curr] Block OFF | 98E47
6320 | FRQC1 | Meas Curr Ok for f [curr] | 98E48
6321 | FRQC1 | Meas Curr too low, f [curr] blocked | 98E49
6336 | FRQV1 | f> Start ON | 99E0
6337 | FRQV1 | f> Start OFF | 99E1
6338 | FRQV1 | f> Trip ON | 99E2
6339 | FRQV1 | f> Trip OFF | 99E3
6340 | FRQV1 | f>> Start ON | 99E4
6341 | FRQV1 | f>> Start OFF | 99E5
6342 | FRQV1 | f>> Trip ON | 99E6
6343 | FRQV1 | f>> Trip OFF | 99E7
6344 | FRQV1 | f>>> Start ON | 99E8
6345 | FRQV1 | f>>> Start OFF | 99E9
6346 | FRQV1 | f>>> Trip ON | 99E10
6347 | FRQV1 | f>>> Trip OFF | 99E11
6348 | FRQV1 | f>>>> Start ON | 99E12
6349 | FRQV1 | f>>>> Start OFF | 99E13
6350 | FRQV1 | f>>>> Trip ON | 99E14
6351 | FRQV1 | f>>>> Trip OFF | 99E15
6352 | FRQV1 | f< Start ON | 99E16
6353 | FRQV1 | f< Start OFF | 99E17
6354 | FRQV1 | f< Trip ON | 99E18
6355 | FRQV1 | f< Trip OFF | 99E19
6356 | FRQV1 | f<< Start ON | 99E20
6357 | FRQV1 | f<< Start OFF | 99E21
6358 | FRQV1 | f<< Trip ON | 99E22
6359 | FRQV1 | f<< Trip OFF | 99E23
6360 | FRQV1 | f<<< Start ON | 99E24
6361 | FRQV1 | f<<< Start OFF | 99E25
6362 | FRQV1 | f<<< Trip ON | 99E26
6363 | FRQV1 | f<<< Trip OFF | 99E27
6364 | FRQV1 | f<<<< Start ON | 99E28
6365 | FRQV1 | f<<<< Start OFF | 99E29
6366 | FRQV1 | f<<<< Trip ON | 99E30
6367 | FRQV1 | f<<<< Trip OFF | 99E31
6368 | FRQV1 | f> Block ON | 99E32
6369 | FRQV1 | f> Block OFF | 99E33
6370 | FRQV1 | f>> Block ON | 99E34
6371 | FRQV1 | f>> Block OFF | 99E35
6372 | FRQV1 | f>>> Block ON | 99E36
6373 | FRQV1 | f>>> Block OFF | 99E37
6374 | FRQV1 | f>>>> Block ON | 99E38
6375 | FRQV1 | f>>>> Block OFF | 99E39
6376 | FRQV1 | f< Block ON | 99E40
6377 | FRQV1 | f< Block OFF | 99E41
6378 | FRQV1 | f<< Block ON | 99E42
6379 | FRQV1 | f<< Block OFF | 99E43
6380 | FRQV1 | f<<< Block ON | 99E44
6381 | FRQV1 | f<<< Block OFF | 99E45
6382 | FRQV1 | f<<<< Block ON | 99E46
6383 | FRQV1 | f<<<< Block OFF | 99E47
6400 | OPW1 | Start ON | 100E0
6401 | OPW1 | Start OFF | 100E1
6402 | OPW1 | Trip ON | 100E2
6403 | OPW1 | Trip OFF | 100E3
6404 | OPW1 | Block ON | 100E4
6405 | OPW1 | Block OFF | 100E5
6464 | UPW1 | Start ON | 101E0
6465 | UPW1 | Start OFF | 101E1
6466 | UPW1 | Trip ON | 101E2
6467 | UPW1 | Trip OFF | 101E3
6468 | UPW1 | Block ON | 101E4
6469 | UPW1 | Block OFF | 101E5
6528 | RPW1 | Start ON | 102E0
6529 | RPW1 | Start OFF | 102E1
6530 | RPW1 | Trip ON | 102E2
6531 | RPW1 | Trip OFF | 102E3
6532 | RPW1 | Block ON | 102E4
6533 | RPW1 | Block OFF | 102E5
6592 | DFT1 | df/dt </> (1) Start ON | 103E0
6593 | DFT1 | df/dt </> (1) Start OFF | 103E1
6594 | DFT1 | df/dt </> (1) Trip ON | 103E2
6595 | DFT1 | df/dt </> (1) Trip OFF | 103E3
6596 | DFT1 | df/dt </> (2) Start ON | 103E4
6597 | DFT1 | df/dt </> (2) Start OFF | 103E5
6598 | DFT1 | df/dt </> (2) Trip ON | 103E6
6599 | DFT1 | df/dt </> (2) Trip OFF | 103E7
6600 | DFT1 | df/dt </> (3) Start ON | 103E8
6601 | DFT1 | df/dt </> (3) Start OFF | 103E9
6602 | DFT1 | df/dt </> (3) Trip ON | 103E10
6603 | DFT1 | df/dt </> (3) Trip OFF | 103E11
6604 | DFT1 | df/dt </> (4) Start ON | 103E12
6605 | DFT1 | df/dt </> (4) Start OFF | 103E13
6606 | DFT1 | df/dt </> (4) Trip ON | 103E14
6607 | DFT1 | df/dt </> (4) Trip OFF | 103E15
6608 | DFT1 | df/dt </> (5) Start ON | 103E16
6609 | DFT1 | df/dt </> (5) Start OFF | 103E17
6610 | DFT1 | df/dt </> (5) Trip ON | 103E18
6611 | DFT1 | df/dt </> (5) Trip OFF | 103E19
6612 | DFT1 | df/dt </> (6) Start ON | 103E20
6613 | DFT1 | df/dt </> (6) Start OFF | 103E21
6614 | DFT1 | df/dt </> (6) Trip ON | 103E22
6615 | DFT1 | df/dt </> (6) Trip OFF | 103E23
6616 | DFT1 | df/dt </> (7) Start ON | 103E24
6617 | DFT1 | df/dt </> (7) Start OFF | 103E25
6618 | DFT1 | df/dt </> (7) Trip ON | 103E26
6619 | DFT1 | df/dt </> (7) Trip OFF | 103E27
6620 | DFT1 | df/dt </> (8) Start ON | 103E28
6621 | DFT1 | df/dt </> (8) Start OFF | 103E29
6622 | DFT1 | df/dt </> (8) Trip ON | 103E30
6623 | DFT1 | df/dt </> (8) Trip OFF | 103E31
6624 | DFT1 | df/dt </> (1) Block ON | 103E32
6625 | DFT1 | df/dt </> (1) Block OFF | 103E33
6626 | DFT1 | df/dt </> (2) Block ON | 103E34
6627 | DFT1 | df/dt </> (2) Block OFF | 103E35
6628 | DFT1 | df/dt </> (3) Block ON | 103E36
6629 | DFT1 | df/dt </> (3) Block OFF | 103E37
6630 | DFT1 | df/dt </> (4) Block ON | 103E38
6631 | DFT1 | df/dt </> (4) Block OFF | 103E39
6632 | DFT1 | df/dt </> (5) Block ON | 103E40
6633 | DFT1 | df/dt </> (5) Block OFF | 103E41
6634 | DFT1 | df/dt </> (6) Block ON | 103E42
6635 | DFT1 | df/dt </> (6) Block OFF | 103E43
6636 | DFT1 | df/dt </> (7) Block ON | 103E44
6637 | DFT1 | df/dt </> (7) Block OFF | 103E45
6638 | DFT1 | df/dt </> (8) Block ON | 103E46
6639 | DFT1 | df/dt </> (8) Block OFF | 103E47
6656 | CIN1 | Intermediate | 104E0
6657 | CIN1 | Open | 104E1
6658 | CIN1 | Close | 104E2
6659 | CIN1 | Bad | 104E3
6720 | CIN2 | Intermediate | 105E0
6721 | CIN2 | Open | 105E1
6722 | CIN2 | Close | 105E2
6723 | CIN2 | Bad | 105E3
6784 | CIN3 | Intermediate | 106E0
6785 | CIN3 | Open | 106E1
6786 | CIN3 | Close | 106E2
6787 | CIN3 | Bad | 106E3
6848 | CIN4 | Intermediate | 107E0
6849 | CIN4 | Open | 107E1
6850 | CIN4 | Close | 107E2
6851 | CIN4 | Bad | 107E3
6912 | CIN5 | Intermediate | 108E0
6913 | CIN5 | Open | 108E1
6914 | CIN5 | Close | 108E2
6915 | CIN5 | Bad | 108E3
6976 | UEX1 | Start ON | 109E0
6977 | UEX1 | Start OFF | 109E1
6978 | UEX1 | Trip ON | 109E2
6979 | UEX1 | Trip OFF | 109E3
6980 | UEX1 | Block ON | 109E4
6981 | UEX1 | Block OFF | 109E5
7040 | SEF1 | Start ON | 110E0
7041 | SEF1 | Start OFF | 110E1
7042 | SEF1 | Trip ON | 110E2
7043 | SEF1 | Trip OFF | 110E3
7044 | SEF1 | Block ON | 110E4
7045 | SEF1 | Block OFF | 110E5
7104 | UIM1 | Start ON | 111E0
7105 | UIM1 | Start OFF | 111E1
7106 | UIM1 | Trip ON | 111E2
7107 | UIM1 | Trip OFF | 111E3
7108 | UIM1 | Block ON | 111E4
7109 | UIM1 | Block OFF | 111E5
7168 | VOC1 | Start ON | 112E0
7169 | VOC1 | Start OFF | 112E1
7170 | VOC1 | Trip ON | 112E2
7171 | VOC1 | Trip OFF | 112E3
7172 | VOC1 | Block ON | 112E4
7173 | VOC1 | Block OFF | 112E5
7232 | GST1 | Light/No load On | 113E0
7233 | GST1 | Light/No load Off | 113E1
7234 | GST1 | HV side inrush On | 113E2
7235 | GST1 | HV side inrush Off | 113E3
7236 | GST1 | LV side inrush On | 113E4
7237 | GST1 | LV side inrush Off | 113E5
7238 | GST1 | Load normal On | 113E6
7239 | GST1 | Load normal Off | 113E7
7240 | GST1 | Overloading On | 113E8
7241 | GST1 | Overloading Off | 113E9
7242 | GST1 | High overload On | 113E10
7243 | GST1 | High overload Off | 113E11
7244 | GST1 | Setting changes, calculating new trafo data | 113E12
7245 | GST1 | Calculation finished, possible restart | 113E13
7296 | IEF1 | Start FWD ON | 114E0
7297 | IEF1 | Start FWD OFF | 114E1
7298 | IEF1 | Start REV ON | 114E2
7299 | IEF1 | Start REV OFF | 114E3
7300 | IEF1 | Trip ON | 114E4
7301 | IEF1 | Trip OFF | 114E5
7302 | IEF1 | Block ON | 114E6
7303 | IEF1 | Block OFF | 114E7
7304 | IEF1 | Intermittent EF detected ON | 114E8
7305 | IEF1 | Intermittent EF detected OFF | 114E9
7306 | IEF1 | Normal earthfault detected | 114E10
7307 | IEF1 | Intermittent EF Locked | 114E11
7360 | VRG1 | Tap Raise command On | 115E0
7361 | VRG1 | Tap Raise command Off | 115E1
7362 | VRG1 | Tap Lower command On | 115E2
7363 | VRG1 | Tap Lower command Off | 115E3
7364 | VRG1 | Block operation On | 115E4
7365 | VRG1 | Block Operation Off | 115E5
7366 | VRG1 | Block Output commands On | 115E6
7367 | VRG1 | Block Output commands Off | 115E7
7368 | VRG1 | Low voltage blocking On | 115E8
7369 | VRG1 | Low voltage blocking Off | 115E9
7370 | VRG1 | Overcurrent blocking On | 115E10
7371 | VRG1 | Overcurrent blocking Off | 115E11
7372 | VRG1 | Tap on highlimit On | 115E12
7373 | VRG1 | Tap on highlimit Off | 115E13
7374 | VRG1 | Tap on lowlimit On | 115E14
7375 | VRG1 | Tap on lowlimit Off | 115E15
7376 | VRG1 | Operation blocked On | 115E16
7377 | VRG1 | Operation blocked Off | 115E17
7378 | VRG1 | U>/< Start On | 115E18
7379 | VRG1 | U>/< Start Off | 115E19
7380 | VRG1 | U>>/<< Start On | 115E20
7381 | VRG1 | U>>/<< Start Off | 115E21
7382 | VRG1 | Control wait time On | 115E22
7383 | VRG1 | Control wait time Off | 115E23
7384 | VRG1 | Manual control On | 115E24
7385 | VRG1 | Automatic control On | 115E25
7386 | VRG1 | Tap raise requested On | 115E26
7387 | VRG1 | Tap raise requested Off | 115E27
7388 | VRG1 | Tap lower requested On | 115E28
7389 | VRG1 | Tap lower requested Off | 115E29
8192 | VHZ1 | (1)Start ON | 128E0
8193 | VHZ1 | (1)Start OFF | 128E1
8194 | VHZ1 | (1)Alarm ON | 128E2
8195 | VHZ1 | (1)Alarm OFF | 128E3
8196 | VHZ1 | (1)Trip ON | 128E4
8197 | VHZ1 | (1)Trip OFF | 128E5
8198 | VHZ1 | (1)Block ON | 128E6
8199 | VHZ1 | (1)Block OFF | 128E7
8200 | VHZ1 | (2)Start ON | 128E8
8201 | VHZ1 | (2)Start OFF | 128E9
8202 | VHZ1 | (2)Alarm ON | 128E10
8203 | VHZ1 | (2)AlarmOFF | 128E11
8204 | VHZ1 | (2)Trip ON | 128E12
8205 | VHZ1 | (2)Trip OFF | 128E13
8206 | VHZ1 | (2)Block ON | 128E14
8207 | VHZ1 | (2)Block OFF | 128E15
8256 | UPF1 | Block On | 129E0
8257 | UPF1 | Block Off | 129E1
8258 | UPF1 | Start On | 129E2
8259 | UPF1 | Start Off | 129E3
8260 | UPF1 | Trip On | 129E4
8261 | UPF1 | Trip Off | 129E5
8262 | UPF1 | Alarm Start On | 129E6
8263 | UPF1 | Alarm Start Off | 129E7
8264 | UPF1 | Alarm On | 129E8
8265 | UPF1 | Alarm Off | 129E9
8320 | VUB1 | Start ON | 130E0
8321 | VUB1 | Start OFF | 130E1
8322 | VUB1 | Trip ON | 130E2
8323 | VUB1 | Trip OFF | 130E3
8324 | VUB1 | Block ON | 130E4
8325 | VUB1 | Block OFF | 130E5
8384 | VUB2 | Start ON | 131E0
8385 | VUB2 | Start OFF | 131E1
8386 | VUB2 | Trip ON | 131E2
8387 | VUB2 | Trip OFF | 131E3
8388 | VUB2 | Block ON | 131E4
8389 | VUB2 | Block OFF | 131E5
8448 | VUB3 | Start ON | 132E0
8449 | VUB3 | Start OFF | 132E1
8450 | VUB3 | Trip ON | 132E2
8451 | VUB3 | Trip OFF | 132E3
8452 | VUB3 | Block ON | 132E4
8453 | VUB3 | Block OFF | 132E5
8512 | VUB4 | Start ON | 133E0
8513 | VUB4 | Start OFF | 133E1
8514 | VUB4 | Trip ON | 133E2
8515 | VUB4 | Trip OFF | 133E3
8516 | VUB4 | Block ON | 133E4
8517 | VUB4 | Block OFF | 133E5
8576 | PGS1 | PS1 >/< Start ON | 134E0
8577 | PGS1 | PS1 >/< Start OFF | 134E1
8578 | PGS1 | PS1 >/< Trip ON | 134E2
8579 | PGS1 | PS1 >/< Trip OFF | 134E3
8580 | PGS1 | PS1 >/< Block ON | 134E4
8581 | PGS1 | PS1 >/< Block OFF | 134E5
8582 | PGS1 | PS2 >/< Start ON | 134E6
8583 | PGS1 | PS2 >/< Start OFF | 134E7
8584 | PGS1 | PS2 >/< Trip ON | 134E8
8585 | PGS1 | PS2 >/< Trip OFF | 134E9
8586 | PGS1 | PS2 >/< Block ON | 134E10
8587 | PGS1 | PS2 >/< Block OFF | 134E11
8588 | PGS1 | PS3 >/< Start ON | 134E12
8589 | PGS1 | PS3 >/< Start OFF | 134E13
8590 | PGS1 | PS3 >/< Trip ON | 134E14
8591 | PGS1 | PS3 >/< Trip OFF | 134E15
8592 | PGS1 | PS3 >/< Block ON | 134E16
8593 | PGS1 | PS3 >/< Block OFF | 134E17
8594 | PGS1 | PS4 >/< Start ON | 134E18
8595 | PGS1 | PS4 >/< Start OFF | 134E19
8596 | PGS1 | PS4 >/< Trip ON | 134E20
8597 | PGS1 | PS4 >/< Trip OFF | 134E21
8598 | PGS1 | PS4 >/< Block ON | 134E22
8599 | PGS1 | PS4 >/< Block OFF | 134E23
8600 | PGS1 | PS5 >/< Start ON | 134E24
8601 | PGS1 | PS5 >/< Start OFF | 134E25
8602 | PGS1 | PS5 >/< Trip ON | 134E26
8603 | PGS1 | PS5 >/< Trip OFF | 134E27
8604 | PGS1 | PS5 >/< Block ON | 134E28
8605 | PGS1 | PS5 >/< Block OFF | 134E29
8606 | PGS1 | reserved | 134E30
8607 | PGS1 | reserved | 134E31
8608 | PGS1 | PS6 >/< Start ON | 134E32
8609 | PGS1 | PS6 >/< Start OFF | 134E33
8610 | PGS1 | PS6 >/< Trip ON | 134E34
8611 | PGS1 | PS6 >/< Trip OFF | 134E35
8612 | PGS1 | PS6 >/< Block ON | 134E36
8613 | PGS1 | PS6 >/< Block OFF | 134E37
8614 | PGS1 | PS7 >/< Start ON | 134E38
8615 | PGS1 | PS7 >/< Start OFF | 134E39
8616 | PGS1 | PS7 >/< Trip ON | 134E40
8617 | PGS1 | PS7 >/< Trip OFF | 134E41
8618 | PGS1 | PS7 >/< Block ON | 134E42
8619 | PGS1 | PS7 >/< Block OFF | 134E43
8620 | PGS1 | PS8 >/< Start ON | 134E44
8621 | PGS1 | PS8 >/< Start OFF | 134E45
8622 | PGS1 | PS8 >/< Trip ON | 134E46
8623 | PGS1 | PS8 >/< Trip OFF | 134E47
8624 | PGS1 | PS8 >/< Block ON | 134E48
8625 | PGS1 | PS8 >/< Block OFF | 134E49
8626 | PGS1 | PS9 >/< Start ON | 134E50
8627 | PGS1 | PS9 >/< Start OFF | 134E51
8628 | PGS1 | PS9 >/< Trip ON | 134E52
8629 | PGS1 | PS9 >/< Trip OFF | 134E53
8630 | PGS1 | PS9 >/< Block ON | 134E54
8631 | PGS1 | PS9 >/< Block OFF | 134E55
8632 | PGS1 | PS10 >/< Start ON | 134E56
8633 | PGS1 | PS10 >/< Start OFF | 134E57
8634 | PGS1 | PS10 >/< Trip ON | 134E58
8635 | PGS1 | PS10 >/< Trip OFF | 134E59
8636 | PGS1 | PS10 >/< Block ON | 134E60
8637 | PGS1 | PS10 >/< Block OFF | 134E61
8640 | EMON1 | I> (50) Detect On | 135E0
8641 | EMON1 | I> (50) Detect Off | 135E1
8642 | EMON1 | I0> (50N) Detect On | 135E2
8643 | EMON1 | I0> (50N) Detect Off | 135E3
8644 | EMON1 | Idir> (67) Detect On | 135E4
8645 | EMON1 | Idir> (67) Detect Off | 135E5
8646 | EMON1 | I0dir> (67N) Detect On | 135E6
8647 | EMON1 | I0dir> (67N) Detect Off | 135E7
8648 | EMON1 | I0Int> (67NT) Detect FWD On | 135E8
8649 | EMON1 | I0Int> (67NT) Detect FWD Off | 135E9
8650 | EMON1 | I0Int> (67NT) Detect REV On | 135E10
8651 | EMON1 | I0Int> (67NT) Detect REV Off | 135E11
8652 | EMON1 | U< (27) Undervoltage detected On | 135E12
8653 | EMON1 | U< (27) Undervoltage detected Off | 135E13
8654 | EMON1 | U< (27) No voltage detected On | 135E14
8655 | EMON1 | U< (27) No voltage detected Off | 135E15
8656 | EMON1 | U0> (59N) Overvoltage detected On | 135E16
8657 | EMON1 | U0> (59N) Overvoltage detected Off | 135E17
8658 | EMON1 | FL (21FL) Triggered On | 135E18
8659 | EMON1 | FL (21FL) Triggered On | 135E19
8832 | MBIO | ModuleA Ch1 Invalid ON | 138E0
8833 | MBIO | ModuleA Ch1 Invalid OFF | 138E1
8834 | MBIO | ModuleA Ch2 Invalid ON | 138E2
8835 | MBIO | ModuleA Ch2 Invalid OFF | 138E3
8836 | MBIO | ModuleA Ch3 Invalid ON | 138E4
8837 | MBIO | ModuleA Ch3 Invalid OFF | 138E5
8838 | MBIO | ModuleA Ch4 Invalid ON | 138E6
8839 | MBIO | ModuleA Ch4 Invalid OFF | 138E7
8840 | MBIO | ModuleA Ch5 Invalid ON | 138E8
8841 | MBIO | ModuleA Ch5 Invalid OFF | 138E9
8842 | MBIO | ModuleA Ch6 Invalid ON | 138E10
8843 | MBIO | ModuleA Ch6 Invalid OFF | 138E11
8844 | MBIO | ModuleA Ch7 Invalid ON | 138E12
8845 | MBIO | ModuleA Ch7 Invalid OFF | 138E13
8846 | MBIO | ModuleA Ch8 Invalid ON | 138E14
8847 | MBIO | ModuleA Ch8 Invalid OFF | 138E15
8848 | MBIO | ModuleB Ch1 Invalid ON | 138E16
8849 | MBIO | ModuleB Ch1 Invalid OFF | 138E17
8850 | MBIO | ModuleB Ch2 Invalid ON | 138E18
8851 | MBIO | ModuleB Ch2 Invalid OFF | 138E19
8852 | MBIO | ModuleB Ch3 Invalid ON | 138E20
8853 | MBIO | ModuleB Ch3 Invalid OFF | 138E21
8854 | MBIO | ModuleB Ch4 Invalid ON | 138E22
8855 | MBIO | ModuleB Ch4 Invalid OFF | 138E23
8856 | MBIO | ModuleB Ch5 Invalid ON | 138E24
8857 | MBIO | ModuleB Ch5 Invalid OFF | 138E25
8858 | MBIO | ModuleB Ch6 Invalid ON | 138E26
8859 | MBIO | ModuleB Ch6 Invalid OFF | 138E27
8860 | MBIO | ModuleB Ch7 Invalid ON | 138E28
8861 | MBIO | ModuleB Ch7 Invalid OFF | 138E29
8862 | MBIO | ModuleB Ch8 Invalid ON | 138E30
8863 | MBIO | ModuleB Ch8 Invalid OFF | 138E31
8864 | MBIO | ModuleC Ch1 Invalid ON | 138E32
8865 | MBIO | ModuleC Ch1 Invalid OFF | 138E33
8866 | MBIO | ModuleC Ch2 Invalid ON | 138E34
8867 | MBIO | ModuleC Ch2 Invalid OFF | 138E35
8868 | MBIO | ModuleC Ch3 Invalid ON | 138E36
8869 | MBIO | ModuleC Ch3 Invalid OFF | 138E37
8870 | MBIO | ModuleC Ch4 Invalid ON | 138E38
8871 | MBIO | ModuleC Ch4 Invalid OFF | 138E39
8872 | MBIO | ModuleC Ch5 Invalid ON | 138E40
8873 | MBIO | ModuleC Ch5 Invalid OFF | 138E41
8874 | MBIO | ModuleC Ch6 Invalid ON | 138E42
8875 | MBIO | ModuleC Ch6 Invalid OFF | 138E43
8876 | MBIO | ModuleC Ch7 Invalid ON | 138E44
8877 | MBIO | ModuleC Ch7 Invalid OFF | 138E45
8878 | MBIO | ModuleC Ch8 Invalid ON | 138E46
8879 | MBIO | ModuleC Ch8 Invalid OFF | 138E47
9536 | UIM2 | Start ON | 149E0
9537 | UIM2 | Start OFF | 149E1
9538 | UIM2 | Trip ON | 149E2
9539 | UIM2 | Trip OFF | 149E3
9540 | UIM2 | Block ON | 149E4
9541 | UIM2 | Block OFF | 149E5
9600 | OBJ6 | Object Intermediate | 150E0
9601 | OBJ6 | Object Open | 150E1
9602 | OBJ6 | Object Close | 150E2
9603 | OBJ6 | Object Bad | 150E3
9604 | OBJ6 | WD Intermediate | 150E4
9605 | OBJ6 | WD Out | 150E5
9606 | OBJ6 | WD in | 150E6
9607 | OBJ6 | WD Bad | 150E7
9608 | OBJ6 | Open Request On | 150E8
9609 | OBJ6 | Open Request Off | 150E9
9610 | OBJ6 | Open Command On | 150E10
9611 | OBJ6 | Open Command Off | 150E11
9612 | OBJ6 | Close Request On | 150E12
9613 | OBJ6 | Close Request Off | 150E13
9614 | OBJ6 | Close Command On | 150E14
9615 | OBJ6 | Close Command Off | 150E15
9616 | OBJ6 | Open Blocked On | 150E16
9617 | OBJ6 | Open Blocked Off | 150E17
9618 | OBJ6 | Close Blocked On | 150E18
9619 | OBJ6 | Close Blocked Off | 150E19
9620 | OBJ6 | Object Ready | 150E20
9621 | OBJ6 | Object Not Ready | 150E21
9622 | OBJ6 | Sync Ok | 150E22
9623 | OBJ6 | Sync Not Ok | 150E23
9624 | OBJ6 | Open Command Fail | 150E24
9625 | OBJ6 | Close Command Fail | 150E25
9626 | OBJ6 | Final trip On | 150E26
9627 | OBJ6 | Final trip Off | 150E27
9664 | OBJ7 | Object Intermediate | 151E0
9665 | OBJ7 | Object Open | 151E1
9666 | OBJ7 | Object Close | 151E2
9667 | OBJ7 | Object Bad | 151E3
9668 | OBJ7 | WD Intermediate | 151E4
9669 | OBJ7 | WD Out | 151E5
9670 | OBJ7 | WD in | 151E6
9671 | OBJ7 | WD Bad | 151E7
9672 | OBJ7 | Open Request On | 151E8
9673 | OBJ7 | Open Request Off | 151E9
9674 | OBJ7 | Open Command On | 151E10
9675 | OBJ7 | Open Command Off | 151E11
9676 | OBJ7 | Close Request On | 151E12
9677 | OBJ7 | Close Request Off | 151E13
9678 | OBJ7 | Close Command On | 151E14
9679 | OBJ7 | Close Command Off | 151E15
9680 | OBJ7 | Open Blocked On | 151E16
9681 | OBJ7 | Open Blocked Off | 151E17
9682 | OBJ7 | Close Blocked On | 151E18
9683 | OBJ7 | Close Blocked Off | 151E19
9684 | OBJ7 | Object Ready | 151E20
9685 | OBJ7 | Object Not Ready | 151E21
9686 | OBJ7 | Sync Ok | 151E22
9687 | OBJ7 | Sync Not Ok | 151E23
9688 | OBJ7 | Open Command Fail | 151E24
9689 | OBJ7 | Close Command Fail | 151E25
9690 | OBJ7 | Final trip On | 151E26
9691 | OBJ7 | Final trip Off | 151E27
9728 | OBJ8 | Object Intermediate | 152E0
9729 | OBJ8 | Object Open | 152E1
9730 | OBJ8 | Object Close | 152E2
9731 | OBJ8 | Object Bad | 152E3
9732 | OBJ8 | WD Intermediate | 152E4
9733 | OBJ8 | WD Out | 152E5
9734 | OBJ8 | WD in | 152E6
9735 | OBJ8 | WD Bad | 152E7
9736 | OBJ8 | Open Request On | 152E8
9737 | OBJ8 | Open Request Off | 152E9
9738 | OBJ8 | Open Command On | 152E10
9739 | OBJ8 | Open Command Off | 152E11
9740 | OBJ8 | Close Request On | 152E12
9741 | OBJ8 | Close Request Off | 152E13
9742 | OBJ8 | Close Command On | 152E14
9743 | OBJ8 | Close Command Off | 152E15
9744 | OBJ8 | Open Blocked On | 152E16
9745 | OBJ8 | Open Blocked Off | 152E17
9746 | OBJ8 | Close Blocked On | 152E18
9747 | OBJ8 | Close Blocked Off | 152E19
9748 | OBJ8 | Object Ready | 152E20
9749 | OBJ8 | Object Not Ready | 152E21
9750 | OBJ8 | Sync Ok | 152E22
9751 | OBJ8 | Sync Not Ok | 152E23
9752 | OBJ8 | Open Command Fail | 152E24
9753 | OBJ8 | Close Command Fail | 152E25
9754 | OBJ8 | Final trip On | 152E26
9755 | OBJ8 | Final trip Off | 152E27
9792 | OBJ9 | Object Intermediate | 153E0
9793 | OBJ9 | Object Open | 153E1
9794 | OBJ9 | Object Close | 153E2
9795 | OBJ9 | Object Bad | 153E3
9796 | OBJ9 | WD Intermediate | 153E4
9797 | OBJ9 | WD Out | 153E5
9798 | OBJ9 | WD in | 153E6
9799 | OBJ9 | WD Bad | 153E7
9800 | OBJ9 | Open Request On | 153E8
9801 | OBJ9 | Open Request Off | 153E9
9802 | OBJ9 | Open Command On | 153E10
9803 | OBJ9 | Open Command Off | 153E11
9804 | OBJ9 | Close Request On | 153E12
9805 | OBJ9 | Close Request Off | 153E13
9806 | OBJ9 | Close Command On | 153E14
9807 | OBJ9 | Close Command Off | 153E15
9808 | OBJ9 | Open Blocked On | 153E16
9809 | OBJ9 | Open Blocked Off | 153E17
9810 | OBJ9 | Close Blocked On | 153E18
9811 | OBJ9 | Close Blocked Off | 153E19
9812 | OBJ9 | Object Ready | 153E20
9813 | OBJ9 | Object Not Ready | 153E21
9814 | OBJ9 | Sync Ok | 153E22
9815 | OBJ9 | Sync Not Ok | 153E23
9816 | OBJ9 | Open Command Fail | 153E24
9817 | OBJ9 | Close Command Fail | 153E25
9818 | OBJ9 | Final trip On | 153E26
9819 | OBJ9 | Final trip Off | 153E27
9856 | OBJ10 | Object Intermediate | 154E0
9857 | OBJ10 | Object Open | 154E1
9858 | OBJ10 | Object Close | 154E2
9859 | OBJ10 | Object Bad | 154E3
9860 | OBJ10 | WD Intermediate | 154E4
9861 | OBJ10 | WD Out | 154E5
9862 | OBJ10 | WD in | 154E6
9863 | OBJ10 | WD Bad | 154E7
9864 | OBJ10 | Open Request On | 154E8
9865 | OBJ10 | Open Request Off | 154E9
9866 | OBJ10 | Open Command On | 154E10
9867 | OBJ10 | Open Command Off | 154E11
9868 | OBJ10 | Close Request On | 154E12
9869 | OBJ10 | Close Request Off | 154E13
9870 | OBJ10 | Close Command On | 154E14
9871 | OBJ10 | Close Command Off | 154E15
9872 | OBJ10 | Open Blocked On | 154E16
9873 | OBJ10 | Open Blocked Off | 154E17
9874 | OBJ10 | Close Blocked On | 154E18
9875 | OBJ10 | Close Blocked Off | 154E19
9876 | OBJ10 | Object Ready | 154E20
9877 | OBJ10 | Object Not Ready | 154E21
9878 | OBJ10 | Sync Ok | 154E22
9879 | OBJ10 | Sync Not Ok | 154E23
9880 | OBJ10 | Open Command Fail | 154E24
9881 | OBJ10 | Close Command Fail | 154E25
9882 | OBJ10 | Final trip On | 154E26
9883 | OBJ10 | Final trip Off | 154E27
9920 | VJP1 | Block On | 155E0
9921 | VJP1 | Block Off | 155E1
9922 | VJP1 | Trip On | 155E2
9923 | VJP1 | Trip Off | 155E3
9924 | VJP1 | Alarm On | 155E4
9925 | VJP1 | Alarm Off | 155E5
9984 | GMAG | FCL on limit On | 156E0
9985 | GMAG | FCL on limit Off | 156E1
9986 | GMAG | UEL in operation On | 156E2
9987 | GMAG | UEL in operation Off | 156E3
9988 | GMAG | SCL Overexcitation On | 156E4
9989 | GMAG | SCL Overexcitation Off | 156E5
9990 | GMAG | SCL Underexcitation On | 156E6
9991 | GMAG | SCL Underexcitation Off | 156E7
9992 | GMAG | High IP On | 156E8
9993 | GMAG | High IP Off | 156E9
9994 | GMAG | Inst FCL On | 156E10
9995 | GMAG | Inst FCL Off | 156E11
9996 | GMAG | Low supply voltage On | 156E12
9997 | GMAG | Low supply voltage Off | 156E13
9998 | GMAG | FCR Mode On | 156E14
9999 | GMAG | FCR Mode Off | 156E15
10000 | GMAG | AVR Mode On | 156E16
10001 | GMAG | AVR Mode Off | 156E17
10002 | GMAG | Low meas volt On | 156E18
10003 | GMAG | Low meas volt Off | 156E19
10004 | GMAG | IGBT Shorted On | 156E20
10005 | GMAG | IGBT Shorted Off | 156E21
10006 | GMAG | PWM Enable On | 156E22
10007 | GMAG | PWM Enable Off | 156E23
10008 | GMAG | PWM DO1 On | 156E24
10009 | GMAG | PWM DO1 Off | 156E25
10010 | GMAG | PWM DO2 On | 156E26
10011 | GMAG | PWM DO2 Off | 156E27
10012 | GMAG | Rectifier trip On | 156E28
10013 | GMAG | Rectifier trip Off | 156E29
10014 | GMAG | Temp high breaker 1 On | 156E30
10015 | GMAG | Temp high breaker 1 Off | 156E31
10016 | GMAG | Temp high breaker 2 On | 156E32
10017 | GMAG | Temp high breaker 2 Off | 156E33
10018 | GMAG | Excitation On | 156E34
10019 | GMAG | Exc On Cmd Off | 156E35
10020 | GMAG | Excitation Off | 156E36
10021 | GMAG | Exc Off Cmd Off | 156E37
10022 | GMAG | Diode fault On | 156E38
10023 | GMAG | Diode fault Off | 156E39
10024 | GMAG | Overcurrent On | 156E40
10025 | GMAG | Overcurrent Off | 156E41
10026 | GMAG | PWM DI1 On | 156E42
10027 | GMAG | PWM DI1 Off | 156E43
10028 | GMAG | PWM DI2 On | 156E44
10029 | GMAG | PWM DI2 Off | 156E45
10030 | GMAG | PWM DI3 On | 156E46
10031 | GMAG | PWM DI3 Off | 156E47
10032 | GMAG | PWM DI4 On | 156E48
10033 | GMAG | PWM DI4 Off | 156E49
10034 | GMAG | PWM DI5 On | 156E50
10035 | GMAG | PWM DI5 Off | 156E51
10036 | GMAG | PWM DI6 On | 156E52
10037 | GMAG | PWM DI6 Off | 156E53
10038 | GMAG | PWM DI7 On | 156E54
10039 | GMAG | PWM DI7 Off | 156E55
10040 | GMAG | PWM DI8 On | 156E56
10041 | GMAG | PWM DI8 Off | 156E57
10048 | GMAG1 | Synchronised On | 157E0
10049 | GMAG1 | Synchronised Off | 157E1
10050 | GMAG1 | Islandmode On | 157E2
10051 | GMAG1 | Islandmode Off | 157E3
10052 | GMAG1 | FB is Open On | 157E4
10053 | GMAG1 | FB is Open Off | 157E5
10054 | GMAG1 | FB is Closed On | 157E6
10055 | GMAG1 | FB is Closed Off | 157E7
10056 | GMAG1 | Field flashing On | 157E8
10057 | GMAG1 | Field flashing Off | 157E9
10058 | GMAG1 | Long field flashing On | 157E10
10059 | GMAG1 | Long field flashing Off | 157E11
10060 | GMAG1 | Test mode On | 157E12
10061 | GMAG1 | Test mode Off | 157E13
10062 | GMAG1 | Phase retard On | 157E14
10063 | GMAG1 | Phase retard Off | 157E15
10064 | GMAG1 | Reset On | 157E16
10065 | GMAG1 | Reset Off | 157E17
10066 | GMAG1 | Command AVR On | 157E18
10067 | GMAG1 | Command AVR Off | 157E19
10068 | GMAG1 | Command FCR On | 157E20
10069 | GMAG1 | Command FCR Off | 157E21
10070 | GMAG1 | Command MVar On | 157E22
10071 | GMAG1 | Command MVar Off | 157E23
10072 | GMAG1 | Command PF On | 157E24
10073 | GMAG1 | Command PF Off | 157E25
10074 | GMAG1 | Excitation run order On | 157E26
10075 | GMAG1 | Excitation run order Off | 157E27
10076 | GMAG1 | Increase On | 157E28
10077 | GMAG1 | Increase Off | 157E29
10078 | GMAG1 | Decrease On | 157E30
10079 | GMAG1 | Decrease Off | 157E31
10080 | GMAG1 | AVR Bus On | 157E32
10081 | GMAG1 | AVR Bus Off | 157E33
10082 | GMAG1 | FCR Bus On | 157E34
10083 | GMAG1 | FCR Bus Off | 157E35
10084 | GMAG1 | MVar Bus On | 157E36
10085 | GMAG1 | MVar Bus Off | 157E37
10086 | GMAG1 | PF Bus On | 157E38
10087 | GMAG1 | PF Bus Off | 157E39
10088 | GMAG1 | Overriding control On | 157E40
10089 | GMAG1 | Overriding control Off | 157E41
10090 | GMAG1 | Increase MVAR/PF On | 157E42
10091 | GMAG1 | Increase MVAR/PF Off | 157E43
10092 | GMAG1 | Decrease MVAR/PF On | 157E44
10093 | GMAG1 | Decrease MVAR/PF Off | 157E45
10094 | GMAG1 | Low Q error On | 157E46
10095 | GMAG1 | Low Q error Off | 157E47
10096 | GMAG1 | AVR ref on lowlim On | 157E48
10097 | GMAG1 | AVR ref on lowlim Off | 157E49
10098 | GMAG1 | AVR ref on highlim On | 157E50
10099 | GMAG1 | AVR ref on highlim Off | 157E51
10100 | GMAG1 | FCR ref on lowlim On | 157E52
10101 | GMAG1 | FCR ref on lowlim Off | 157E53
10102 | GMAG1 | FCR ref on highlim On | 157E54
10103 | GMAG1 | FCR ref on highlim Off | 157E55
10104 | GMAG1 | VHZ limit active On | 157E56
10105 | GMAG1 | VHZ limit active Off | 157E57
10106 | GMAG1 | Process panel activated On | 157E58
10107 | GMAG1 | Process panel activated Off | 157E59
10108 | GMAG1 | Parameters active On | 157E60
10109 | GMAG1 | Parameters active Off | 157E61
10110 | GMAG1 | Bus activated On | 157E62
10111 | GMAG1 | Bus activated Off | 157E63
10112 | GMAG2 | Reset and excitation off On | 158E0
10113 | GMAG2 | Reset and excitation off Off | 158E1
10114 | GMAG2 | Field breaker does not open On | 158E2
10115 | GMAG2 | Field breaker does not open Off | 158E3
10116 | GMAG2 | New reference start On | 158E4
10117 | GMAG2 | New reference start Off | 158E5
10118 | GMAG2 | GB is closed On | 158E6
10119 | GMAG2 | GB is closed Off | 158E7
10120 | GMAG2 | FB off GB on On | 158E8
10121 | GMAG2 | FB off GB on Off | 158E9
10122 | GMAG2 | Disturbed mode On | 158E10
10123 | GMAG2 | Disturbed mode Off | 158E11
10124 | GMAG2 | Disturbed mode pulse On | 158E12
10125 | GMAG2 | Disturbed mode pulse Off | 158E13
10126 | GMAG2 | Following line voltage On | 158E14
10127 | GMAG2 | Following line voltage Off | 158E15
10128 | GMAG2 | Test Square enable On | 158E16
10129 | GMAG2 | Test Square enable Off | 158E17
10130 | GMAG2 | Order open FB On | 158E18
10131 | GMAG2 | Order open FB Off | 158E19
10132 | GMAG2 | Order close FB On | 158E20
10133 | GMAG2 | Order close FB Off | 158E21
10134 | GMAG2 | Q unloaded On | 158E22
10135 | GMAG2 | Q unloaded Off | 158E23
10136 | GMAG2 | MVAR ref on high On | 158E24
10137 | GMAG2 | MVAR ref on high Off | 158E25
10138 | GMAG2 | MVAR ref on low On | 158E26
10139 | GMAG2 | MVAR ref on low Off | 158E27
10140 | GMAG2 | PF ref on high On | 158E28
10141 | GMAG2 | PF ref on high Off | 158E29
10142 | GMAG2 | PF ref on low On | 158E30
10143 | GMAG2 | PF ref on low Off | 158E31
10144 | GMAG2 | AVR start Ref On | 158E32
10145 | GMAG2 | AVR start Ref Off | 158E33
10146 | GMAG2 | FCR start Ref On | 158E34
10147 | GMAG2 | FCR start Ref Off | 158E35
10148 | GMAG2 | Unload MVAR On | 158E36
10149 | GMAG2 | Unload MVAR Off | 158E37
10150 | GMAG2 | PWM DO3 On | 158E38
10151 | GMAG2 | PWM DO3 Off | 158E39
10152 | GMAG2 | PWM DO4 On | 158E40
10153 | GMAG2 | PWM DO4 Off | 158E41
10154 | GMAG2 | MVAR Mode On | 158E42
10155 | GMAG2 | MVAR Mode Off | 158E43
10156 | GMAG2 | PF Mode On | 158E44
10157 | GMAG2 | PF Mode Off | 158E45
10158 | GMAG2 | PSS Enabled On | 158E46
10159 | GMAG2 | PSS Enabled Off | 158E47
10160 | GMAG2 | PSS Blocked On | 158E48
10161 | GMAG2 | PSS Blocked Off | 158E49
10176 | ALARM1 | Alarm 1 On (Alarm 1) | 159E0
10177 | ALARM1 | Alarm 1 Off (Alarm 1) | 159E1
10178 | ALARM1 | Alarm 2 On (Alarm 2) | 159E2
10179 | ALARM1 | Alarm 2 Off (Alarm 2) | 159E3
10180 | ALARM1 | Alarm 3 On (Alarm 3) | 159E4
10181 | ALARM1 | Alarm 3 Off (Alarm 3) | 159E5
10182 | ALARM1 | Alarm 4 On (Alarm 4) | 159E6
10183 | ALARM1 | Alarm 4 Off (Alarm 4) | 159E7
10184 | ALARM1 | Alarm 5 On (Alarm 5) | 159E8
10185 | ALARM1 | Alarm 5 Off (Alarm 5) | 159E9
10186 | ALARM1 | Alarm 6 On (Alarm 6) | 159E10
10187 | ALARM1 | Alarm 6 Off (Alarm 6) | 159E11
10188 | ALARM1 | Alarm 7 On (Alarm 7) | 159E12
10189 | ALARM1 | Alarm 7 Off (Alarm 7) | 159E13
10190 | ALARM1 | Alarm 8 On (Alarm 8) | 159E14
10191 | ALARM1 | Alarm 8 Off (Alarm 8) | 159E15
10192 | ALARM1 | Alarm 9 On (Alarm 9) | 159E16
10193 | ALARM1 | Alarm 9 Off (Alarm 9) | 159E17
10194 | ALARM1 | Alarm 10 On (Alarm 10) | 159E18
10195 | ALARM1 | Alarm 10 Off (Alarm 10) | 159E19
10196 | ALARM1 | Alarm 11 On (Alarm 11) | 159E20
10197 | ALARM1 | Alarm 11 Off (Alarm 11) | 159E21
10198 | ALARM1 | Alarm 12 On (Alarm 12) | 159E22
10199 | ALARM1 | Alarm 12 Off (Alarm 12) | 159E23
10200 | ALARM1 | Alarm 13 On (Alarm 13) | 159E24
10201 | ALARM1 | Alarm 13 Off (Alarm 13) | 159E25
10202 | ALARM1 | Alarm 14 On (Alarm 14) | 159E26
10203 | ALARM1 | Alarm 14 Off (Alarm 14) | 159E27
10204 | ALARM1 | Alarm 15 On (Alarm 15) | 159E28
10205 | ALARM1 | Alarm 15 Off (Alarm 15) | 159E29
10206 | ALARM1 | Alarm 16 On (Alarm 16) | 159E30
10207 | ALARM1 | Alarm 16 Off (Alarm 16) | 159E31
10208 | ALARM1 | Alarm 17 On (Alarm 17) | 159E32
10209 | ALARM1 | Alarm 17 Off (Alarm 17) | 159E33
10210 | ALARM1 | Alarm 18 On (Alarm 18) | 159E34
10211 | ALARM1 | Alarm 18 Off (Alarm 18) | 159E35
10212 | ALARM1 | Alarm 19 On (Alarm 19) | 159E36
10213 | ALARM1 | Alarm 19 Off (Alarm 19) | 159E37
10214 | ALARM1 | Alarm 20 On (Alarm 20) | 159E38
10215 | ALARM1 | Alarm 20 Off (Alarm 20) | 159E39
10216 | ALARM1 | Alarm 21 On (Alarm 21) | 159E40
10217 | ALARM1 | Alarm 21 Off (Alarm 21) | 159E41
10218 | ALARM1 | Alarm 22 On (Alarm 22) | 159E42
10219 | ALARM1 | Alarm 22 Off (Alarm 22) | 159E43
10220 | ALARM1 | Alarm 23 On (Alarm 23) | 159E44
10221 | ALARM1 | Alarm 23 Off (Alarm 23) | 159E45
10222 | ALARM1 | Alarm 24 On (Alarm 24) | 159E46
10223 | ALARM1 | Alarm 24 Off (Alarm 24) | 159E47
10224 | ALARM1 | Alarm 25 On (Alarm 25) | 159E48
10225 | ALARM1 | Alarm 25 Off (Alarm 25) | 159E49
10226 | ALARM1 | Alarm 26 On (Alarm 26) | 159E50
10227 | ALARM1 | Alarm 26 Off (Alarm 26) | 159E51
10228 | ALARM1 | Alarm 27 On (Alarm 27) | 159E52
10229 | ALARM1 | Alarm 27 Off (Alarm 27) | 159E53
10230 | ALARM1 | Alarm 28 On (Alarm 28) | 159E54
10231 | ALARM1 | Alarm 28 Off (Alarm 28) | 159E55
10232 | ALARM1 | Alarm 29 On (Alarm 29) | 159E56
10233 | ALARM1 | Alarm 29 Off (Alarm 29) | 159E57
10234 | ALARM1 | Alarm 30 On (Alarm 30) | 159E58
10235 | ALARM1 | Alarm 30 Off (Alarm 30) | 159E59
10236 | ALARM1 | Alarm 31 On (Alarm 31) | 159E60
10237 | ALARM1 | Alarm 31 Off (Alarm 31) | 159E61
10238 | ALARM1 | Alarm 32 On (Alarm 32) | 159E62
10239 | ALARM1 | Alarm 32 Off (Alarm 32) | 159E63
10240 | ALARM2 | Alarm 33 On (Alarm 33) | 160E0
10241 | ALARM2 | Alarm 33 Off (Alarm 33) | 160E1
10242 | ALARM2 | Alarm 34 On (Alarm 34) | 160E2
10243 | ALARM2 | Alarm 34 Off (Alarm 34) | 160E3
10244 | ALARM2 | Alarm 35 On (Alarm 35) | 160E4
10245 | ALARM2 | Alarm 35 Off (Alarm 35) | 160E5
10246 | ALARM2 | Alarm 36 On (Alarm 36) | 160E6
10247 | ALARM2 | Alarm 36 Off (Alarm 36) | 160E7
10248 | ALARM2 | Alarm 37 On (Alarm 37) | 160E8
10249 | ALARM2 | Alarm 37 Off (Alarm 37) | 160E9
10250 | ALARM2 | Alarm 38 On (Alarm 38) | 160E10
10251 | ALARM2 | Alarm 38 Off (Alarm 38) | 160E11
10252 | ALARM2 | Alarm 39 On (Alarm 39) | 160E12
10253 | ALARM2 | Alarm 39 Off (Alarm 39) | 160E13
10254 | ALARM2 | Alarm 40 On (Alarm 40) | 160E14
10255 | ALARM2 | Alarm 40 Off (Alarm 40) | 160E15
10256 | ALARM2 | Alarm 41 On (Alarm 41) | 160E16
10257 | ALARM2 | Alarm 41 Off (Alarm 41) | 160E17
10258 | ALARM2 | Alarm 42 On (Alarm 42) | 160E18
10259 | ALARM2 | Alarm 42 Off (Alarm 42) | 160E19
10260 | ALARM2 | Alarm 43 On (Alarm 43) | 160E20
10261 | ALARM2 | Alarm 43 Off (Alarm 43) | 160E21
10262 | ALARM2 | Alarm 44 On (Alarm 44) | 160E22
10263 | ALARM2 | Alarm 44 Off (Alarm 44) | 160E23
10264 | ALARM2 | Alarm 45 On (Alarm 45) | 160E24
10265 | ALARM2 | Alarm 45 Off (Alarm 45) | 160E25
10266 | ALARM2 | Alarm 46 On (Alarm 46) | 160E26
10267 | ALARM2 | Alarm 46 Off (Alarm 46) | 160E27
10268 | ALARM2 | Alarm 47 On (Alarm 47) | 160E28
10269 | ALARM2 | Alarm 47 Off (Alarm 47) | 160E29
10270 | ALARM2 | Alarm 48 On (Alarm 48) | 160E30
10271 | ALARM2 | Alarm 48 Off (Alarm 48) | 160E31
10272 | ALARM2 | Alarm 49 On (Alarm 49) | 160E32
10273 | ALARM2 | Alarm 49 Off (Alarm 49) | 160E33
10274 | ALARM2 | Alarm 50 On (Alarm 50) | 160E34
10275 | ALARM2 | Alarm 50 Off (Alarm 50) | 160E35
10276 | ALARM2 | Alarm 51 On (Alarm 51) | 160E36
10277 | ALARM2 | Alarm 51 Off (Alarm 51) | 160E37
10278 | ALARM2 | Alarm 52 On (Alarm 52) | 160E38
10279 | ALARM2 | Alarm 52 Off (Alarm 52) | 160E39
10280 | ALARM2 | Alarm 53 On (Alarm 53) | 160E40
10281 | ALARM2 | Alarm 53 Off (Alarm 53) | 160E41
10282 | ALARM2 | Alarm 54 On (Alarm 54) | 160E42
10283 | ALARM2 | Alarm 54 Off (Alarm 54) | 160E43
10284 | ALARM2 | Alarm 55 On (Alarm 55) | 160E44
10285 | ALARM2 | Alarm 55 Off (Alarm 55) | 160E45
10286 | ALARM2 | Alarm 56 On (Alarm 56) | 160E46
10287 | ALARM2 | Alarm 56 Off (Alarm 56) | 160E47
10288 | ALARM2 | Alarm 57 On (Alarm 57) | 160E48
10289 | ALARM2 | Alarm 57 Off (Alarm 57) | 160E49
10290 | ALARM2 | Alarm 58 On (Alarm 58) | 160E50
10291 | ALARM2 | Alarm 58 Off (Alarm 58) | 160E51
10292 | ALARM2 | Alarm 59 On (Alarm 59) | 160E52
10293 | ALARM2 | Alarm 59 Off (Alarm 59) | 160E53
10294 | ALARM2 | Alarm 60 On (Alarm 60) | 160E54
10295 | ALARM2 | Alarm 60 Off (Alarm 60) | 160E55
10296 | ALARM2 | Alarm 61 On (Alarm 61) | 160E56
10297 | ALARM2 | Alarm 61 Off (Alarm 61) | 160E57
10298 | ALARM2 | Alarm 62 On (Alarm 62) | 160E58
10299 | ALARM2 | Alarm 62 Off (Alarm 62) | 160E59
10300 | ALARM2 | Alarm 63 On (Alarm 63) | 160E60
10301 | ALARM2 | Alarm 63 Off (Alarm 63) | 160E61
10302 | ALARM2 | Alarm 64 On (Alarm 64) | 160E62
10303 | ALARM2 | Alarm 64 Off (Alarm 64) | 160E63
10304 | IAE1 | Start ON | 161E0
10305 | IAE1 | Start OFF | 161E1
10306 | IAE1 | Trip ON | 161E2
10307 | IAE1 | Trip OFF | 161E3
10308 | IAE1 | Block ON | 161E4
10309 | IAE1 | Block OFF | 161E5
10310 | IAE1 | Low Current On | 161E6
10311 | IAE1 | Low Current Off | 161E7
10312 | IAE1 | Low Voltage On | 161E8
10313 | IAE1 | Low Voltage On | 161E9
10368 | GSYN | Synchronizing Blocked On | 162E0
10369 | GSYN | Synchronizing Blocked Off | 162E1
10370 | GSYN | Synchronizing Running On | 162E2
10371 | GSYN | Synchronizing Running Off | 162E3
10372 | GSYN | Synchr. Increase Voltage On | 162E4
10373 | GSYN | Synchr. Increase Voltage Off | 162E5
10374 | GSYN | Synchr. Decrease Voltage On | 162E6
10375 | GSYN | Synchr. Decrease Voltage Off | 162E7
10376 | GSYN | Synchr. Increase Frequency On | 162E8
10377 | GSYN | Synchr. Increase Frequency Off | 162E9
10378 | GSYN | Synchr. Decrease Frequency On | 162E10
10379 | GSYN | Synchr. Decrease Frequency Off | 162E11
10380 | GSYN | Synchronizer BRK Close On | 162E12
10381 | GSYN | Synchronizer BRK Close Off | 162E13
10382 | GSYN | Synchronizer Long Sync. Time On | 162E14
10383 | GSYN | Synchronizer Long Sync. Time Off | 162E15
10384 | GSYN | Synchroswitch Close fail Re-init On | 162E16
10385 | GSYN | Synchroswitch Close fail Re-init Off | 162E17
10386 | GSYN | Synchroswitching requested On | 162E18
10387 | GSYN | Synchroswitching requested Off | 162E19
10432 | VREC | Trigger On | 163E0
10433 | VREC | Trigger Off | 163E1
10496 | PWR1 | Start ON | 164E0
10497 | PWR1 | Start OFF | 164E1
10498 | PWR1 | Trip ON | 164E2
10499 | PWR1 | Trip OFF | 164E3
10500 | PWR1 | Block ON | 164E4
10501 | PWR1 | Block OFF | 164E5
10560 | PWR2 | Start ON | 165E0
10561 | PWR2 | Start OFF | 165E1
10562 | PWR2 | Trip ON | 165E2
10563 | PWR2 | Trip OFF | 165E3
10564 | PWR2 | Block ON | 165E4
10565 | PWR2 | Block OFF | 165E5
10624 | PWR3 | Start ON | 166E0
10625 | PWR3 | Start OFF | 166E1
10626 | PWR3 | Trip ON | 166E2
10627 | PWR3 | Trip OFF | 166E3
10628 | PWR3 | Block ON | 166E4
10629 | PWR3 | Block OFF | 166E5
10688 | PWR4 | Start ON | 167E0
10689 | PWR4 | Start OFF | 167E1
10690 | PWR4 | Trip ON | 167E2
10691 | PWR4 | Trip OFF | 167E3
10692 | PWR4 | Block ON | 167E4
10693 | PWR4 | Block OFF | 167E5
10752 | CIN6 | Intermediate | 168E0
10753 | CIN6 | Open | 168E1
10754 | CIN6 | Close | 168E2
10755 | CIN6 | Bad | 168E3
10816 | CIN7 | Intermediate | 169E0
10817 | CIN7 | Open | 169E1
10818 | CIN7 | Close | 169E2
10819 | CIN7 | Bad | 169E3
10880 | CIN8 | Intermediate | 170E0
10881 | CIN8 | Open | 170E1
10882 | CIN8 | Close | 170E2
10883 | CIN8 | Bad | 170E3
10944 | CIN9 | Intermediate | 171E0
10945 | CIN9 | Open | 171E1
10946 | CIN9 | Close | 171E2
10947 | CIN9 | Bad | 171E3
11008 | CIN10 | Intermediate | 172E0
11009 | CIN10 | Open | 172E1
11010 | CIN10 | Close | 172E2
11011 | CIN10 | Bad | 172E3
11072 | CIN11 | Intermediate | 173E0
11073 | CIN11 | Open | 173E1
11074 | CIN11 | Close | 173E2
11075 | CIN11 | Bad | 173E3
11136 | CIN12 | Intermediate | 174E0
11137 | CIN12 | Open | 174E1
11138 | CIN12 | Close | 174E2
11139 | CIN12 | Bad | 174E3
11200 | CIN13 | Intermediate | 175E0
11201 | CIN13 | Open | 175E1
11202 | CIN13 | Close | 175E2
11203 | CIN13 | Bad | 175E3
11264 | CIN14 | Intermediate | 176E0
11265 | CIN14 | Open | 176E1
11266 | CIN14 | Close | 176E2
11267 | CIN14 | Bad | 176E3
11328 | CIN15 | Intermediate | 177E0
11329 | CIN15 | Open | 177E1
11330 | CIN15 | Close | 177E2
11331 | CIN15 | Bad | 177E3
11392 | CIN16 | Intermediate | 178E0
11393 | CIN16 | Open | 178E1
11394 | CIN16 | Close | 178E2
11395 | CIN16 | Bad | 178E3
11456 | CIN17 | Intermediate | 179E0
11457 | CIN17 | Open | 179E1
11458 | CIN17 | Close | 179E2
11459 | CIN17 | Bad | 179E3
11520 | CIN18 | Intermediate | 180E0
11521 | CIN18 | Open | 180E1
11522 | CIN18 | Close | 180E2
11523 | CIN18 | Bad | 180E3
11584 | CIN19 | Intermediate | 181E0
11585 | CIN19 | Open | 181E1
11586 | CIN19 | Close | 181E2
11587 | CIN19 | Bad | 181E3
11648 | CIN20 | Intermediate | 182E0
11649 | CIN20 | Open | 182E1
11650 | CIN20 | Close | 182E2
11651 | CIN20 | Bad | 182E3
11712 | RHC1 | Running hour counter On | 183E0
11713 | RHC1 | Running hour counter Off | 183E1
11714 | RHC1 | Running hour counter cleared On | 183E2
11715 | RHC1 | Running hour counter cleared Off | 183E3
11776 | ALARM3 | Alarm 65 On | 184E0
11777 | ALARM3 | Alarm 65 Off | 184E1
11778 | ALARM3 | Alarm 66 On | 184E2
11779 | ALARM3 | Alarm 66 Off | 184E3
11780 | ALARM3 | Alarm 67 On | 184E4
11781 | ALARM3 | Alarm 67 Off | 184E5
11782 | ALARM3 | Alarm 68 On | 184E6
11783 | ALARM3 | Alarm 68 Off | 184E7
11784 | ALARM3 | Alarm 69 On | 184E8
11785 | ALARM3 | Alarm 69 Off | 184E9
11786 | ALARM3 | Alarm 70 On | 184E10
11787 | ALARM3 | Alarm 70 Off | 184E11
11788 | ALARM3 | Alarm 71 On | 184E12
11789 | ALARM3 | Alarm 71 Off | 184E13
11790 | ALARM3 | Alarm 72 On | 184E14
11791 | ALARM3 | Alarm 72 Off | 184E15
11792 | ALARM3 | Alarm 73 On | 184E16
11793 | ALARM3 | Alarm 73 Off | 184E17
11794 | ALARM3 | Alarm 74 On | 184E18
11795 | ALARM3 | Alarm 74 Off | 184E19
11796 | ALARM3 | Alarm 75 On | 184E20
11797 | ALARM3 | Alarm 75 Off | 184E21
11798 | ALARM3 | Alarm 76 On | 184E22
11799 | ALARM3 | Alarm 76 Off | 184E23
11800 | ALARM3 | Alarm 77 On | 184E24
11801 | ALARM3 | Alarm 77 Off | 184E25
11802 | ALARM3 | Alarm 78 On | 184E26
11803 | ALARM3 | Alarm 78 Off | 184E27
11804 | ALARM3 | Alarm 79 On | 184E28
11805 | ALARM3 | Alarm 79 Off | 184E29
11806 | ALARM3 | Alarm 80 On | 184E30
11807 | ALARM3 | Alarm 80 Off | 184E31
11808 | ALARM3 | Alarm 81 On | 184E32
11809 | ALARM3 | Alarm 81 Off | 184E33
11810 | ALARM3 | Alarm 82 On | 184E34
11811 | ALARM3 | Alarm 82 Off | 184E35
11812 | ALARM3 | Alarm 83 On | 184E36
11813 | ALARM3 | Alarm 83 Off | 184E37
11814 | ALARM3 | Alarm 84 On | 184E38
11815 | ALARM3 | Alarm 84 Off | 184E39
11816 | ALARM3 | Alarm 85 On | 184E40
11817 | ALARM3 | Alarm 85 Off | 184E41
11818 | ALARM3 | Alarm 86 On | 184E42
11819 | ALARM3 | Alarm 86 Off | 184E43
11820 | ALARM3 | Alarm 87 On | 184E44
11821 | ALARM3 | Alarm 87 Off | 184E45
11822 | ALARM3 | Alarm 88 On | 184E46
11823 | ALARM3 | Alarm 88 Off | 184E47
11824 | ALARM3 | Alarm 89 On | 184E48
11825 | ALARM3 | Alarm 89 Off | 184E49
11826 | ALARM3 | Alarm 90 On | 184E50
11827 | ALARM3 | Alarm 90 Off | 184E51
11828 | ALARM3 | Alarm 91 On | 184E52
11829 | ALARM3 | Alarm 91 Off | 184E53
11830 | ALARM3 | Alarm 92 On | 184E54
11831 | ALARM3 | Alarm 92 Off | 184E55
11832 | ALARM3 | Alarm 93 On | 184E56
11833 | ALARM3 | Alarm 93 Off | 184E57
11834 | ALARM3 | Alarm 94 On | 184E58
11835 | ALARM3 | Alarm 94 Off | 184E59
11836 | ALARM3 | Alarm 95 On | 184E60
11837 | ALARM3 | Alarm 95 Off | 184E61
11838 | ALARM3 | Alarm 96 On | 184E62
11839 | ALARM3 | Alarm 96 Off | 184E63
11840 | ALARM4 | Alarm 97 On | 185E0
11841 | ALARM4 | Alarm 97 Off | 185E1
11842 | ALARM4 | Alarm 98 On | 185E2
11843 | ALARM4 | Alarm 98 Off | 185E3
11844 | ALARM4 | Alarm 99 On | 185E4
11845 | ALARM4 | Alarm 99 Off | 185E5
11846 | ALARM4 | Alarm 100 On | 185E6
11847 | ALARM4 | Alarm 100 Off | 185E7
11848 | ALARM4 | Alarm 101 On | 185E8
11849 | ALARM4 | Alarm 101 Off | 185E9
11850 | ALARM4 | Alarm 102 On | 185E10
11851 | ALARM4 | Alarm 102 Off | 185E11
11852 | ALARM4 | Alarm 103 On | 185E12
11853 | ALARM4 | Alarm 103 Off | 185E13
11854 | ALARM4 | Alarm 104 On | 185E14
11855 | ALARM4 | Alarm 104 Off | 185E15
11856 | ALARM4 | Alarm 105 On | 185E16
11857 | ALARM4 | Alarm 105 Off | 185E17
11858 | ALARM4 | Alarm 106 On | 185E18
11859 | ALARM4 | Alarm 106 Off | 185E19
11860 | ALARM4 | Alarm 107 On | 185E20
11861 | ALARM4 | Alarm 107 Off | 185E21
11862 | ALARM4 | Alarm 108 On | 185E22
11863 | ALARM4 | Alarm 108 Off | 185E23
11864 | ALARM4 | Alarm 109 On | 185E24
11865 | ALARM4 | Alarm 109 Off | 185E25
11866 | ALARM4 | Alarm 110 On | 185E26
11867 | ALARM4 | Alarm 110 Off | 185E27
11868 | ALARM4 | Alarm 111 On | 185E28
11869 | ALARM4 | Alarm 111 Off | 185E29
11870 | ALARM4 | Alarm 112 On | 185E30
11871 | ALARM4 | Alarm 112 Off | 185E31
11872 | ALARM4 | Alarm 113 On | 185E32
11873 | ALARM4 | Alarm 113 Off | 185E33
11874 | ALARM4 | Alarm 114 On | 185E34
11875 | ALARM4 | Alarm 114 Off | 185E35
11876 | ALARM4 | Alarm 115 On | 185E36
11877 | ALARM4 | Alarm 115 Off | 185E37
11878 | ALARM4 | Alarm 116 On | 185E38
11879 | ALARM4 | Alarm 116 Off | 185E39
11880 | ALARM4 | Alarm 117 On | 185E40
11881 | ALARM4 | Alarm 117 Off | 185E41
11882 | ALARM4 | Alarm 118 On | 185E42
11883 | ALARM4 | Alarm 118 Off | 185E43
11884 | ALARM4 | Alarm 119 On | 185E44
11885 | ALARM4 | Alarm 119 Off | 185E45
11886 | ALARM4 | Alarm 120 On | 185E46
11887 | ALARM4 | Alarm 120 Off | 185E47
11888 | ALARM4 | Alarm 121 On | 185E48
11889 | ALARM4 | Alarm 121 Off | 185E49
11890 | ALARM4 | Alarm 122 On | 185E50
11891 | ALARM4 | Alarm 122 Off | 185E51
11892 | ALARM4 | Alarm 123 On | 185E52
11893 | ALARM4 | Alarm 123 Off | 185E53
11894 | ALARM4 | Alarm 124 On | 185E54
11895 | ALARM4 | Alarm 124 Off | 185E55
11896 | ALARM4 | Alarm 125 On | 185E56
11897 | ALARM4 | Alarm 125 Off | 185E57
11898 | ALARM4 | Alarm 126 On | 185E58
11899 | ALARM4 | Alarm 126 Off | 185E59
11900 | ALARM4 | Alarm 127 On | 185E60
11901 | ALARM4 | Alarm 127 Off | 185E61
11902 | ALARM4 | Alarm 128 On | 185E62
11903 | ALARM4 | Alarm 128 Off | 185E63
12096 | LDIF1 | Idb> Trip On | 189E0
12097 | LDIF1 | Idb> Trip Off | 189E1
12098 | LDIF1 | Idb> Blocked (ext) On | 189E2
12099 | LDIF1 | Idb> Blocked (ext) Off | 189E3
12100 | LDIF1 | Idi> Trip On | 189E4
12101 | LDIF1 | Idi> Trip Off | 189E5
12102 | LDIF1 | Idi> Blocked (ext) On | 189E6
12103 | LDIF1 | Idi> Blocked (ext) Off | 189E7
12104 | LDIF1 | 2.nd Harmonic Block On | 189E8
12105 | LDIF1 | 2.nd Harmonic Block Off | 189E9
12106 | LDIF1 | 5.th Harmonic Block On | 189E10
12107 | LDIF1 | 5.th Harmonic Block Off | 189E11
12108 | LDIF1 | L1 2.nd harm On | 189E12
12109 | LDIF1 | L1 2.nd harm Off | 189E13
12110 | LDIF1 | L2 2.nd harm On | 189E14
12111 | LDIF1 | L2 2.nd harm Off | 189E15
12112 | LDIF1 | L3 2.nd harm On | 189E16
12113 | LDIF1 | L3 2.nd harm Off | 189E17
12114 | LDIF1 | L1 5.th harm On | 189E18
12115 | LDIF1 | L1 5.th harm Off | 189E19
12116 | LDIF1 | L2 5.th harm On | 189E20
12117 | LDIF1 | L2 5.th harm Off | 189E21
12118 | LDIF1 | L3 5.th harm On | 189E22
12119 | LDIF1 | L3 5.th harm Off | 189E23
12160 | M1VT1 | Voltage memory enabled | 190E0
12161 | M1VT1 | Voltage memory disabled | 190E1
12162 | M1VT1 | Voltage low detected On | 190E2
12163 | M1VT1 | Voltage low detected Off | 190E3
12164 | M1VT1 | Current high detected On | 190E4
12165 | M1VT1 | Current high detected Off | 190E5
12166 | M1VT1 | Frequency tracked from CT On | 190E6
12167 | M1VT1 | Frequency tracked from CT Off | 190E7
12168 | M1VT1 | Using Voltage memory On | 190E8
12169 | M1VT1 | Using Voltage memory Off | 190E9
12170 | M1VT1 | Voltage memory blocked On | 190E10
12171 | M1VT1 | Voltage memory blocked Off | 190E11
12288 | NOCS1 | Start ON | 192E0
12289 | NOCS1 | Start OFF | 192E1
12290 | NOCS1 | Trip ON | 192E2
12291 | NOCS1 | Trip OFF | 192E3
12292 | NOCS1 | Block ON | 192E4
12293 | NOCS1 | Block OFF | 192E5
12294 | NOCS1 | L1 Start ON | 192E6
12295 | NOCS1 | L1 Start OFF | 192E7
12296 | NOCS1 | L2 Start ON | 192E8
12297 | NOCS1 | L2 Start OFF | 192E9
12298 | NOCS1 | L3 Start ON | 192E10
12299 | NOCS1 | L3 Start OFF | 192E11
12300 | NOCS1 | L1 Trip ON | 192E12
12301 | NOCS1 | L1 Trip OFF | 192E13
12302 | NOCS1 | L2 Trip ON | 192E14
12303 | NOCS1 | L2 Trip OFF | 192E15
12304 | NOCS1 | L3 Trip ON | 192E16
12305 | NOCS1 | L3 Trip OFF | 192E17
12352 | OBJS1 | Object A(L1) Intermediate | 193E0
12353 | OBJS1 | Object A(L1) Open | 193E1
12354 | OBJS1 | Object A(L1) Close | 193E2
12355 | OBJS1 | Object A(L1) Bad | 193E3
12356 | OBJS1 | Object B(L2) Open | 193E4
12357 | OBJS1 | Object B(L2) Close | 193E5
12358 | OBJS1 | Object B(L2) Bad | 193E6
12359 | OBJS1 | Object B(L2) Intermediate | 193E7
12360 | OBJS1 | Object C(L3) Open | 193E8
12361 | OBJS1 | Object C(L3) Close | 193E9
12362 | OBJS1 | Object C(L3) Bad | 193E10
12363 | OBJS1 | Object C(L3) Intermediate | 193E11
12364 | OBJS1 | WD Cart Intermediate | 193E12
12365 | OBJS1 | WD Cart Open | 193E13
12366 | OBJS1 | WD Cart Close | 193E14
12367 | OBJS1 | WD Cart Bad | 193E15
12368 | OBJS1 | Object A(L1) Open Command On | 193E16
12369 | OBJS1 | Object A(L1) Open Command Off | 193E17
12370 | OBJS1 | Object B(L2) Open Command On | 193E18
12371 | OBJS1 | Object B(L2) Open Command Off | 193E19
12372 | OBJS1 | Object C(L3) Open Command On | 193E20
12373 | OBJS1 | Object C(L3) Open Command Off | 193E21
12374 | OBJS1 | Close Command On | 193E22
12375 | OBJS1 | Close Command Off | 193E23
12376 | OBJS1 | Open Commands Blocked | 193E24
12377 | OBJS1 | Open Commands Allowed | 193E25
12378 | OBJS1 | Close Commands Blocked | 193E26
12379 | OBJS1 | Close Commands Allowed | 193E27
12380 | OBJS1 | Object Is Ready | 193E28
12381 | OBJS1 | Object Not Ready, Wait for Ready | 193E29
12382 | OBJS1 | Sync Is Ok | 193E30
12383 | OBJS1 | Sync Not Ok Wait for sync | 193E31
12384 | OBJS1 | Final Trip On | 193E32
12385 | OBJS1 | Final Trip Off | 193E33
12386 | OBJS1 | Open Command Fail On | 193E34
12387 | OBJS1 | Open Command Fail Off | 193E35
12388 | OBJS1 | Close Command Fail On | 193E36
12389 | OBJS1 | Close Command Fail Off | 193E37
12390 | OBJS1 | L1 Open Command Timeout On | 193E38
12391 | OBJS1 | L1 Open Command Timeout On | 193E39
12392 | OBJS1 | L2 Open Command Timeout On | 193E40
12393 | OBJS1 | L2 Open Command Timeout On | 193E41
12394 | OBJS1 | L3 Open Command Timeout On | 193E42
12395 | OBJS1 | L3 Open Command Timeout On | 193E43
12396 | OBJS1 | Close Command Timeout On | 193E44
12397 | OBJS1 | Close Command Timeout On | 193E45
12416 | NOCS2 | Start ON | 194E0
12417 | NOCS2 | Start OFF | 194E1
12418 | NOCS2 | Trip ON | 194E2
12419 | NOCS2 | Trip OFF | 194E3
12420 | NOCS2 | Block ON | 194E4
12421 | NOCS2 | Block OFF | 194E5
12422 | NOCS2 | L1 Start ON | 194E6
12423 | NOCS2 | L1 Start OFF | 194E7
12424 | NOCS2 | L2 Start ON | 194E8
12425 | NOCS2 | L2 Start OFF | 194E9
12426 | NOCS2 | L3 Start ON | 194E10
12427 | NOCS2 | L3 Start OFF | 194E11
12428 | NOCS2 | L1 Trip ON | 194E12
12429 | NOCS2 | L1 Trip OFF | 194E13
12430 | NOCS2 | L2 Trip ON | 194E14
12431 | NOCS2 | L2 Trip OFF | 194E15
12432 | NOCS2 | L3 Trip ON | 194E16
12433 | NOCS2 | L3 Trip OFF | 194E17
12480 | SGS2 | SG2 Enabled | 195E0
12481 | SGS2 | SG2 Disabled | 195E1
12482 | SGS2 | SG3 Enabled | 195E2
12483 | SGS2 | SG3 Disabled | 195E3
12484 | SGS2 | SG4 Enabled | 195E4
12485 | SGS2 | SG4 Disabled | 195E5
12486 | SGS2 | SG5 Enabled | 195E6
12487 | SGS2 | SG5 Disabled | 195E7
12488 | SGS2 | SG6 Enabled | 195E8
12489 | SGS2 | SG6 Disabled | 195E9
12490 | SGS2 | SG7 Enabled | 195E10
12491 | SGS2 | SG7 Disabled | 195E11
12492 | SGS2 | SG8 Enabled | 195E12
12493 | SGS2 | SG8 Disabled | 195E13
12494 | SGS2 | SG1 Request On | 195E14
12495 | SGS2 | SG1 Request Off | 195E15
12496 | SGS2 | SG2 Request On | 195E16
12497 | SGS2 | SG2 Request Off | 195E17
12498 | SGS2 | SG3 Request On | 195E18
12499 | SGS2 | SG3 Request Off | 195E19
12500 | SGS2 | SG4 Request On | 195E20
12501 | SGS2 | SG4 Request Off | 195E21
12502 | SGS2 | SG5 Request On | 195E22
12503 | SGS2 | SG5 Request Off | 195E23
12504 | SGS2 | SG6 Request On | 195E24
12505 | SGS2 | SG6 Request Off | 195E25
12506 | SGS2 | SG7 Request On | 195E26
12507 | SGS2 | SG7 Request Off | 195E27
12508 | SGS2 | SG8 Request On | 195E28
12509 | SGS2 | SG8 Request Off | 195E29
12510 | SGS2 | Remote Change SG Req On | 195E30
12511 | SGS2 | Remote Change SG Req Off | 195E31
12512 | SGS2 | Local Change SG Req On | 195E32
12513 | SGS2 | Local Change SG Req On | 195E33
12514 | SGS2 | Force Change SG On | 195E34
12515 | SGS2 | Force Change SG Off | 195E35
12516 | SGS2 | SG Req. Fail Not configured SG On | 195E36
12517 | SGS2 | SG Req. Fail Not configured SG On | 195E37
12518 | SGS2 | Force Req. Fail Force not On | 195E38
12519 | SGS2 | Force Req. Fail Off | 195E39
12520 | SGS2 | SG Req. Fail Lower priority Req. On | 195E40
12521 | SGS2 | SG Req. Fail Lower priority Req. Off | 195E41
12522 | SGS2 | SG1 Active On | 195E42
12523 | SGS2 | SG1 Active Off | 195E43
12524 | SGS2 | SG2 Active On | 195E44
12525 | SGS2 | SG2 Active Off | 195E45
12526 | SGS2 | SG3 Active On | 195E46
12527 | SGS2 | SG3 Active Off | 195E47
12528 | SGS2 | SG4 Active On | 195E48
12529 | SGS2 | SG4 Active Off | 195E49
12530 | SGS2 | SG5 Active On | 195E50
12531 | SGS2 | SG5 Active Off | 195E51
12532 | SGS2 | SG6 Active On | 195E52
12533 | SGS2 | SG6 Active Off | 195E53
12534 | SGS2 | SG7 Active On | 195E54
12535 | SGS2 | SG7 Active Off | 195E55
12536 | SGS2 | SG8 Active On | 195E56
12537 | SGS2 | SG8 Active Off | 195E57
12544 | URX1 | Start ON | 196E0
12545 | URX1 | Start OFF | 196E1
12546 | URX1 | Trip ON | 196E2
12547 | URX1 | Trip OFF | 196E3
12548 | URX1 | Block ON | 196E4
12549 | URX1 | Block OFF | 196E5
12608 | URX2 | Start ON | 197E0
12609 | URX2 | Start OFF | 197E1
12610 | URX2 | Trip ON | 197E2
12611 | URX2 | Trip OFF | 197E3
12612 | URX2 | Block ON | 197E4
12613 | URX2 | Block OFF | 197E5
12736 | MGWB1 | On Bit 1 | 199E0
12737 | MGWB1 | Off Bit 1 | 199E1
12738 | MGWB1 | On Bit 2 | 199E2
12739 | MGWB1 | Off Bit 2 | 199E3
12740 | MGWB1 | On Bit 3 | 199E4
12741 | MGWB1 | Off Bit 3 | 199E5
12742 | MGWB1 | On Bit 4 | 199E6
12743 | MGWB1 | Off Bit 4 | 199E7
12744 | MGWB1 | On Bit 5 | 199E8
12745 | MGWB1 | Off Bit 5 | 199E9
12746 | MGWB1 | On Bit 6 | 199E10
12747 | MGWB1 | Off Bit 6 | 199E11
12748 | MGWB1 | On Bit 7 | 199E12
12749 | MGWB1 | Off Bit 7 | 199E13
12750 | MGWB1 | On Bit 8 | 199E14
12751 | MGWB1 | Off Bit 8 | 199E15
12752 | MGWB1 | On Bit 9 | 199E16
12753 | MGWB1 | Off Bit 9 | 199E17
12754 | MGWB1 | On Bit 10 | 199E18
12755 | MGWB1 | Off Bit 10 | 199E19
12756 | MGWB1 | On Bit 11 | 199E20
12757 | MGWB1 | Off Bit 11 | 199E21
12758 | MGWB1 | On Bit 12 | 199E22
12759 | MGWB1 | Off Bit 12 | 199E23
12760 | MGWB1 | On Bit 13 | 199E24
12761 | MGWB1 | Off Bit 13 | 199E25
12762 | MGWB1 | On Bit 14 | 199E26
12763 | MGWB1 | Off Bit 14 | 199E27
12764 | MGWB1 | On Bit 15 | 199E28
12765 | MGWB1 | Off Bit 15 | 199E29
12766 | MGWB1 | On Bit 16 | 199E30
12767 | MGWB1 | Off Bit 16 | 199E31
12768 | MGWB1 | On Bit 17 | 199E32
12769 | MGWB1 | Off Bit 17 | 199E33
12770 | MGWB1 | On Bit 18 | 199E34
12771 | MGWB1 | Off Bit 18 | 199E35
12772 | MGWB1 | On Bit 19 | 199E36
12773 | MGWB1 | Off Bit 19 | 199E37
12774 | MGWB1 | On Bit 20 | 199E38
12775 | MGWB1 | Off Bit 20 | 199E39
12776 | MGWB1 | On Bit 21 | 199E40
12777 | MGWB1 | Off Bit 21 | 199E41
12778 | MGWB1 | On Bit 22 | 199E42
12779 | MGWB1 | Off Bit 22 | 199E43
12780 | MGWB1 | On Bit 23 | 199E44
12781 | MGWB1 | Off Bit 23 | 199E45
12782 | MGWB1 | On Bit 24 | 199E46
12783 | MGWB1 | Off Bit 24 | 199E47
12784 | MGWB1 | On Bit 25 | 199E48
12785 | MGWB1 | Off Bit 25 | 199E49
12786 | MGWB1 | On Bit 26 | 199E50
12787 | MGWB1 | Off Bit 26 | 199E51
12788 | MGWB1 | On Bit 27 | 199E52
12789 | MGWB1 | Off Bit 27 | 199E53
12790 | MGWB1 | On Bit 28 | 199E54
12791 | MGWB1 | Off Bit 28 | 199E55
12792 | MGWB1 | On Bit 29 | 199E56
12793 | MGWB1 | Off Bit 29 | 199E57
12794 | MGWB1 | On Bit 30 | 199E58
12795 | MGWB1 | Off Bit 30 | 199E59
12796 | MGWB1 | On Bit 31 | 199E60
12797 | MGWB1 | Off Bit 31 | 199E61
12798 | MGWB1 | On Bit 32 | 199E62
12799 | MGWB1 | Off Bit 32 | 199E63
12800 | MGWB2 | On Bit 33 | 200E0
12801 | MGWB2 | Off Bit 33 | 200E1
12802 | MGWB2 | On Bit 34 | 200E2
12803 | MGWB2 | Off Bit 34 | 200E3
12804 | MGWB2 | On Bit 35 | 200E4
12805 | MGWB2 | Off Bit 35 | 200E5
12806 | MGWB2 | On Bit 36 | 200E6
12807 | MGWB2 | Off Bit 36 | 200E7
12808 | MGWB2 | On Bit 37 | 200E8
12809 | MGWB2 | Off Bit 37 | 200E9
12810 | MGWB2 | On Bit 38 | 200E10
12811 | MGWB2 | Off Bit 38 | 200E11
12812 | MGWB2 | On Bit 39 | 200E12
12813 | MGWB2 | Off Bit 39 | 200E13
12814 | MGWB2 | On Bit 40 | 200E14
12815 | MGWB2 | Off Bit 40 | 200E15
12816 | MGWB2 | On Bit 41 | 200E16
12817 | MGWB2 | Off Bit 41 | 200E17
12818 | MGWB2 | On Bit 42 | 200E18
12819 | MGWB2 | Off Bit 42 | 200E19
12820 | MGWB2 | On Bit 43 | 200E20
12821 | MGWB2 | Off Bit 43 | 200E21
12822 | MGWB2 | On Bit 44 | 200E22
12823 | MGWB2 | Off Bit 44 | 200E23
12824 | MGWB2 | On Bit 45 | 200E24
12825 | MGWB2 | Off Bit 45 | 200E25
12826 | MGWB2 | On Bit 46 | 200E26
12827 | MGWB2 | Off Bit 46 | 200E27
12828 | MGWB2 | On Bit 47 | 200E28
12829 | MGWB2 | Off Bit 47 | 200E29
12830 | MGWB2 | On Bit 48 | 200E30
12831 | MGWB2 | Off Bit 48 | 200E31
12832 | MGWB2 | On Bit 49 | 200E32
12833 | MGWB2 | Off Bit 49 | 200E33
12834 | MGWB2 | On Bit 50 | 200E34
12835 | MGWB2 | Off Bit 50 | 200E35
12836 | MGWB2 | On Bit 51 | 200E36
12837 | MGWB2 | Off Bit 51 | 200E37
12838 | MGWB2 | On Bit 52 | 200E38
12839 | MGWB2 | Off Bit 52 | 200E39
12840 | MGWB2 | On Bit 53 | 200E40
12841 | MGWB2 | Off Bit 53 | 200E41
12842 | MGWB2 | On Bit 54 | 200E42
12843 | MGWB2 | Off Bit 54 | 200E43
12844 | MGWB2 | On Bit 55 | 200E44
12845 | MGWB2 | Off Bit 55 | 200E45
12846 | MGWB2 | On Bit 56 | 200E46
12847 | MGWB2 | Off Bit 56 | 200E47
12848 | MGWB2 | On Bit 57 | 200E48
12849 | MGWB2 | Off Bit 57 | 200E49
12850 | MGWB2 | On Bit 58 | 200E50
12851 | MGWB2 | Off Bit 58 | 200E51
12852 | MGWB2 | On Bit 59 | 200E52
12853 | MGWB2 | Off Bit 59 | 200E53
12854 | MGWB2 | On Bit 60 | 200E54
12855 | MGWB2 | Off Bit 60 | 200E55
12856 | MGWB2 | On Bit 61 | 200E56
12857 | MGWB2 | Off Bit 61 | 200E57
12858 | MGWB2 | On Bit 62 | 200E58
12859 | MGWB2 | Off Bit 62 | 200E59
12860 | MGWB2 | On Bit 63 | 200E60
12861 | MGWB2 | Off Bit 63 | 200E61
12862 | MGWB2 | On Bit 64 | 200E62
12863 | MGWB2 | Off Bit 64 | 200E63
12864 | MGWB3 | On Bit 65 | 201E0
12865 | MGWB3 | Off Bit 65 | 201E1
12866 | MGWB3 | On Bit 66 | 201E2
12867 | MGWB3 | Off Bit 66 | 201E3
12868 | MGWB3 | On Bit 67 | 201E4
12869 | MGWB3 | Off Bit 67 | 201E5
12870 | MGWB3 | On Bit 68 | 201E6
12871 | MGWB3 | Off Bit 68 | 201E7
12872 | MGWB3 | On Bit 69 | 201E8
12873 | MGWB3 | Off Bit 69 | 201E9
12874 | MGWB3 | On Bit 70 | 201E10
12875 | MGWB3 | Off Bit 70 | 201E11
12876 | MGWB3 | On Bit 71 | 201E12
12877 | MGWB3 | Off Bit 71 | 201E13
12878 | MGWB3 | On Bit 72 | 201E14
12879 | MGWB3 | Off Bit 72 | 201E15
12880 | MGWB3 | On Bit 73 | 201E16
12881 | MGWB3 | Off Bit 73 | 201E17
12882 | MGWB3 | On Bit 74 | 201E18
12883 | MGWB3 | Off Bit 74 | 201E19
12884 | MGWB3 | On Bit 75 | 201E20
12885 | MGWB3 | Off Bit 75 | 201E21
12886 | MGWB3 | On Bit 76 | 201E22
12887 | MGWB3 | Off Bit 76 | 201E23
12888 | MGWB3 | On Bit 77 | 201E24
12889 | MGWB3 | Off Bit 77 | 201E25
12890 | MGWB3 | On Bit 78 | 201E26
12891 | MGWB3 | Off Bit 78 | 201E27
12892 | MGWB3 | On Bit 79 | 201E28
12893 | MGWB3 | Off Bit 79 | 201E29
12894 | MGWB3 | On Bit 80 | 201E30
12895 | MGWB3 | Off Bit 80 | 201E31
12896 | MGWB3 | On Bit 81 | 201E32
12897 | MGWB3 | Off Bit 81 | 201E33
12898 | MGWB3 | On Bit 82 | 201E34
12899 | MGWB3 | Off Bit 82 | 201E35
12900 | MGWB3 | On Bit 83 | 201E36
12901 | MGWB3 | Off Bit 83 | 201E37
12902 | MGWB3 | On Bit 84 | 201E38
12903 | MGWB3 | Off Bit 84 | 201E39
12904 | MGWB3 | On Bit 85 | 201E40
12905 | MGWB3 | Off Bit 85 | 201E41
12906 | MGWB3 | On Bit 86 | 201E42
12907 | MGWB3 | Off Bit 86 | 201E43
12908 | MGWB3 | On Bit 87 | 201E44
12909 | MGWB3 | Off Bit 87 | 201E45
12910 | MGWB3 | On Bit 88 | 201E46
12911 | MGWB3 | Off Bit 88 | 201E47
12912 | MGWB3 | On Bit 89 | 201E48
12913 | MGWB3 | Off Bit 89 | 201E49
12914 | MGWB3 | On Bit 90 | 201E50
12915 | MGWB3 | Off Bit 90 | 201E51
12916 | MGWB3 | On Bit 91 | 201E52
12917 | MGWB3 | Off Bit 91 | 201E53
12918 | MGWB3 | On Bit 92 | 201E54
12919 | MGWB3 | Off Bit 92 | 201E55
12920 | MGWB3 | On Bit 93 | 201E56
12921 | MGWB3 | Off Bit 93 | 201E57
12922 | MGWB3 | On Bit 94 | 201E58
12923 | MGWB3 | Off Bit 94 | 201E59
12924 | MGWB3 | On Bit 95 | 201E60
12925 | MGWB3 | Off Bit 95 | 201E61
12926 | MGWB3 | On Bit 96 | 201E62
12927 | MGWB3 | Off Bit 96 | 201E63
12928 | MGWB4 | On Bit 97 | 202E0
12929 | MGWB4 | Off Bit 97 | 202E1
12930 | MGWB4 | On Bit 98 | 202E2
12931 | MGWB4 | Off Bit 98 | 202E3
12932 | MGWB4 | On Bit 99 | 202E4
12933 | MGWB4 | Off Bit 99 | 202E5
12934 | MGWB4 | On Bit 100 | 202E6
12935 | MGWB4 | Off Bit 100 | 202E7
12936 | MGWB4 | On Bit 101 | 202E8
12937 | MGWB4 | Off Bit 101 | 202E9
12938 | MGWB4 | On Bit 102 | 202E10
12939 | MGWB4 | Off Bit 102 | 202E11
12940 | MGWB4 | On Bit 103 | 202E12
12941 | MGWB4 | Off Bit 103 | 202E13
12942 | MGWB4 | On Bit 104 | 202E14
12943 | MGWB4 | Off Bit 104 | 202E15
12944 | MGWB4 | On Bit 105 | 202E16
12945 | MGWB4 | Off Bit 105 | 202E17
12946 | MGWB4 | On Bit 106 | 202E18
12947 | MGWB4 | Off Bit 106 | 202E19
12948 | MGWB4 | On Bit 107 | 202E20
12949 | MGWB4 | Off Bit 107 | 202E21
12950 | MGWB4 | On Bit 108 | 202E22
12951 | MGWB4 | Off Bit 108 | 202E23
12952 | MGWB4 | On Bit 109 | 202E24
12953 | MGWB4 | Off Bit 109 | 202E25
12954 | MGWB4 | On Bit 110 | 202E26
12955 | MGWB4 | Off Bit 110 | 202E27
12956 | MGWB4 | On Bit 111 | 202E28
12957 | MGWB4 | Off Bit 111 | 202E29
12958 | MGWB4 | On Bit 112 | 202E30
12959 | MGWB4 | Off Bit 112 | 202E31
12960 | MGWB4 | On Bit 113 | 202E32
12961 | MGWB4 | Off Bit 113 | 202E33
12962 | MGWB4 | On Bit 114 | 202E34
12963 | MGWB4 | Off Bit 114 | 202E35
12964 | MGWB4 | On Bit 115 | 202E36
12965 | MGWB4 | Off Bit 115 | 202E37
12966 | MGWB4 | On Bit 116 | 202E38
12967 | MGWB4 | Off Bit 116 | 202E39
12968 | MGWB4 | On Bit 117 | 202E40
12969 | MGWB4 | Off Bit 117 | 202E41
12970 | MGWB4 | On Bit 118 | 202E42
12971 | MGWB4 | Off Bit 118 | 202E43
12972 | MGWB4 | On Bit 119 | 202E44
12973 | MGWB4 | Off Bit 119 | 202E45
12974 | MGWB4 | On Bit 120 | 202E46
12975 | MGWB4 | Off Bit 120 | 202E47
12976 | MGWB4 | On Bit 121 | 202E48
12977 | MGWB4 | Off Bit 121 | 202E49
12978 | MGWB4 | On Bit 122 | 202E50
12979 | MGWB4 | Off Bit 122 | 202E51
12980 | MGWB4 | On Bit 123 | 202E52
12981 | MGWB4 | Off Bit 123 | 202E53
12982 | MGWB4 | On Bit 124 | 202E54
12983 | MGWB4 | Off Bit 124 | 202E55
12984 | MGWB4 | On Bit 125 | 202E56
12985 | MGWB4 | Off Bit 125 | 202E57
12986 | MGWB4 | On Bit 126 | 202E58
12987 | MGWB4 | Off Bit 126 | 202E59
12988 | MGWB4 | On Bit 127 | 202E60
12989 | MGWB4 | Off Bit 127 | 202E61
12990 | MGWB4 | On Bit 128 | 202E62
12991 | MGWB4 | Off Bit 128 | 202E63
12992 | MGWD1 | Off Off Double Bit 1 | 203E0
12993 | MGWD1 | On Off Double Bit 1 | 203E1
12994 | MGWD1 | Off On Double Bit 1 | 203E2
12995 | MGWD1 | On On Double Bit 1 | 203E3
12996 | MGWD1 | Off Off Double Bit 2 | 203E4
12997 | MGWD1 | On Off Double Bit 2 | 203E5
12998 | MGWD1 | Off On Double Bit 2 | 203E6
12999 | MGWD1 | On On Double Bit 2 | 203E7
13000 | MGWD1 | Off Off Double Bit 3 | 203E8
13001 | MGWD1 | On Off Double Bit 3 | 203E9
13002 | MGWD1 | Off On Double Bit 3 | 203E10
13003 | MGWD1 | On On Double Bit 3 | 203E11
13004 | MGWD1 | Off Off Double Bit 4 | 203E12
13005 | MGWD1 | On Off Double Bit 4 | 203E13
13006 | MGWD1 | Off On Double Bit 4 | 203E14
13007 | MGWD1 | On On Double Bit 4 | 203E15
13008 | MGWD1 | Off Off Double Bit 5 | 203E16
13009 | MGWD1 | On Off Double Bit 5 | 203E17
13010 | MGWD1 | Off On Double Bit 5 | 203E18
13011 | MGWD1 | On On Double Bit 5 | 203E19
13012 | MGWD1 | Off Off Double Bit 6 | 203E20
13013 | MGWD1 | On Off Double Bit 6 | 203E21
13014 | MGWD1 | Off On Double Bit 6 | 203E22
13015 | MGWD1 | On On Double Bit 6 | 203E23
13016 | MGWD1 | Off Off Double Bit 7 | 203E24
13017 | MGWD1 | On Off Double Bit 7 | 203E25
13018 | MGWD1 | Off On Double Bit 7 | 203E26
13019 | MGWD1 | On On Double Bit 7 | 203E27
13020 | MGWD1 | Off Off Double Bit 8 | 203E28
13021 | MGWD1 | On Off Double Bit 8 | 203E29
13022 | MGWD1 | Off On Double Bit 8 | 203E30
13023 | MGWD1 | On On Double Bit 8 | 203E31
13024 | MGWD1 | Off Off Double Bit 9 | 203E32
13025 | MGWD1 | On Off Double Bit 9 | 203E33
13026 | MGWD1 | Off On Double Bit 9 | 203E34
13027 | MGWD1 | On On Double Bit 9 | 203E35
13028 | MGWD1 | Off Off Double Bit 10 | 203E36
13029 | MGWD1 | On Off Double Bit 10 | 203E37
13030 | MGWD1 | Off On Double Bit 10 | 203E38
13031 | MGWD1 | On On Double Bit 10 | 203E39
13032 | MGWD1 | Off Off Double Bit 11 | 203E40
13033 | MGWD1 | On Off Double Bit 11 | 203E41
13034 | MGWD1 | Off On Double Bit 11 | 203E42
13035 | MGWD1 | On On Double Bit 11 | 203E43
13036 | MGWD1 | Off Off Double Bit 12 | 203E44
13037 | MGWD1 | On Off Double Bit 12 | 203E45
13038 | MGWD1 | Off On Double Bit 12 | 203E46
13039 | MGWD1 | On On Double Bit 12 | 203E47
13040 | MGWD1 | Off Off Double Bit 13 | 203E48
13041 | MGWD1 | On Off Double Bit 13 | 203E49
13042 | MGWD1 | Off On Double Bit 13 | 203E50
13043 | MGWD1 | On On Double Bit 13 | 203E51
13044 | MGWD1 | Off Off Double Bit 14 | 203E52
13045 | MGWD1 | On Off Double Bit 14 | 203E53
13046 | MGWD1 | Off On Double Bit 14 | 203E54
13047 | MGWD1 | On On Double Bit 14 | 203E55
13048 | MGWD1 | Off Off Double Bit 15 | 203E56
13049 | MGWD1 | On Off Double Bit 15 | 203E57
13050 | MGWD1 | Off On Double Bit 15 | 203E58
13051 | MGWD1 | On On Double Bit 15 | 203E59
13052 | MGWD1 | Off Off Double Bit 16 | 203E60
13053 | MGWD1 | On Off Double Bit 16 | 203E61
13054 | MGWD1 | Off On Double Bit 16 | 203E62
13055 | MGWD1 | On On Double Bit 16 | 203E63
13056 | MGWD2 | Off Off Double Bit 17 | 204E0
13057 | MGWD2 | On Off Double Bit 17 | 204E1
13058 | MGWD2 | Off On Double Bit 17 | 204E2
13059 | MGWD2 | On On Double Bit 17 | 204E3
13060 | MGWD2 | Off Off Double Bit 18 | 204E4
13061 | MGWD2 | On Off Double Bit 18 | 204E5
13062 | MGWD2 | Off On Double Bit 18 | 204E6
13063 | MGWD2 | On On Double Bit 18 | 204E7
13064 | MGWD2 | Off Off Double Bit 19 | 204E8
13065 | MGWD2 | On Off Double Bit 19 | 204E9
13066 | MGWD2 | Off On Double Bit 19 | 204E10
13067 | MGWD2 | On On Double Bit 19 | 204E11
13068 | MGWD2 | Off Off Double Bit 20 | 204E12
13069 | MGWD2 | On Off Double Bit 20 | 204E13
13070 | MGWD2 | Off On Double Bit 20 | 204E14
13071 | MGWD2 | On On Double Bit 20 | 204E15
13072 | MGWD2 | Off Off Double Bit 21 | 204E16
13073 | MGWD2 | On Off Double Bit 21 | 204E17
13074 | MGWD2 | Off On Double Bit 21 | 204E18
13075 | MGWD2 | On On Double Bit 21 | 204E19
13076 | MGWD2 | Off Off Double Bit 22 | 204E20
13077 | MGWD2 | On Off Double Bit 22 | 204E21
13078 | MGWD2 | Off On Double Bit 22 | 204E22
13079 | MGWD2 | On On Double Bit 22 | 204E23
13080 | MGWD2 | Off Off Double Bit 23 | 204E24
13081 | MGWD2 | On Off Double Bit 23 | 204E25
13082 | MGWD2 | Off On Double Bit 23 | 204E26
13083 | MGWD2 | On On Double Bit 23 | 204E27
13084 | MGWD2 | Off Off Double Bit 24 | 204E28
13085 | MGWD2 | On Off Double Bit 24 | 204E29
13086 | MGWD2 | Off On Double Bit 24 | 204E30
13087 | MGWD2 | On On Double Bit 24 | 204E31
13088 | MGWD2 | Off Off Double Bit 25 | 204E32
13089 | MGWD2 | On Off Double Bit 25 | 204E33
13090 | MGWD2 | Off On Double Bit 25 | 204E34
13091 | MGWD2 | On On Double Bit 25 | 204E35
13092 | MGWD2 | Off Off Double Bit 26 | 204E36
13093 | MGWD2 | On Off Double Bit 26 | 204E37
13094 | MGWD2 | Off On Double Bit 26 | 204E38
13095 | MGWD2 | On On Double Bit 26 | 204E39
13096 | MGWD2 | Off Off Double Bit 27 | 204E40
13097 | MGWD2 | On Off Double Bit 27 | 204E41
13098 | MGWD2 | Off On Double Bit 27 | 204E42
13099 | MGWD2 | On On Double Bit 27 | 204E43
13100 | MGWD2 | Off Off Double Bit 28 | 204E44
13101 | MGWD2 | On Off Double Bit 28 | 204E45
13102 | MGWD2 | Off On Double Bit 28 | 204E46
13103 | MGWD2 | On On Double Bit 28 | 204E47
13104 | MGWD2 | Off Off Double Bit 29 | 204E48
13105 | MGWD2 | On Off Double Bit 29 | 204E49
13106 | MGWD2 | Off On Double Bit 29 | 204E50
13107 | MGWD2 | On On Double Bit 29 | 204E51
13108 | MGWD2 | Off Off Double Bit 30 | 204E52
13109 | MGWD2 | On Off Double Bit 30 | 204E53
13110 | MGWD2 | Off On Double Bit 30 | 204E54
13111 | MGWD2 | On On Double Bit 30 | 204E55
13112 | MGWD2 | Off Off Double Bit 31 | 204E56
13113 | MGWD2 | On Off Double Bit 31 | 204E57
13114 | MGWD2 | Off On Double Bit 31 | 204E58
13115 | MGWD2 | On On Double Bit 31 | 204E59
13116 | MGWD2 | Off Off Double Bit 32 | 204E60
13117 | MGWD2 | On Off Double Bit 32 | 204E61
13118 | MGWD2 | Off On Double Bit 32 | 204E62
13119 | MGWD2 | On On Double Bit 32 | 204E63
13120 | ROC1 | Start ON | 205E0
13121 | ROC1 | Start OFF | 205E1
13122 | ROC1 | Trip ON | 205E2
13123 | ROC1 | Trip OFF | 205E3
13124 | ROC1 | Block ON | 205E4
13125 | ROC1 | Block OFF | 205E5
13184 | ROC2 | Start ON | 206E0
13185 | ROC2 | Start OFF | 206E1
13186 | ROC2 | Trip ON | 206E2
13187 | ROC2 | Trip OFF | 206E3
13188 | ROC2 | Block ON | 206E4
13189 | ROC2 | Block OFF | 206E5
13248 | ROC3 | Start ON | 207E0
13249 | ROC3 | Start OFF | 207E1
13250 | ROC3 | Trip ON | 207E2
13251 | ROC3 | Trip OFF | 207E3
13252 | ROC3 | Block ON | 207E4
13253 | ROC3 | Block OFF | 207E5
13312 | ROC4 | Start ON | 208E0
13313 | ROC4 | Start OFF | 208E1
13314 | ROC4 | Trip ON | 208E2
13315 | ROC4 | Trip OFF | 208E3
13316 | ROC4 | Block ON | 208E4
13317 | ROC4 | Block OFF | 208E5
13376 | ROC5 | Start ON | 209E0
13377 | ROC5 | Start OFF | 209E1
13378 | ROC5 | Trip ON | 209E2
13379 | ROC5 | Trip OFF | 209E3
13380 | ROC5 | Block ON | 209E4
13381 | ROC5 | Block OFF | 209E5
13440 | ROC6 | Start ON | 210E0
13441 | ROC6 | Start OFF | 210E1
13442 | ROC6 | Trip ON | 210E2
13443 | ROC6 | Trip OFF | 210E3
13444 | ROC6 | Block ON | 210E4
13445 | ROC6 | Block OFF | 210E5
13504 | ROC7 | Start ON | 211E0
13505 | ROC7 | Start OFF | 211E1
13506 | ROC7 | Trip ON | 211E2
13507 | ROC7 | Trip OFF | 211E3
13508 | ROC7 | Block ON | 211E4
13509 | ROC7 | Block OFF | 211E5
13568 | ROC8 | Start ON | 212E0
13569 | ROC8 | Start OFF | 212E1
13570 | ROC8 | Trip ON | 212E2
13571 | ROC8 | Trip OFF | 212E3
13572 | ROC8 | Block ON | 212E4
13573 | ROC8 | Block OFF | 212E5
13632 | ROV1 | Start ON | 213E0
13633 | ROV1 | Start OFF | 213E1
13634 | ROV1 | Trip ON | 213E2
13635 | ROV1 | Trip OFF | 213E3
13636 | ROV1 | Block ON | 213E4
13637 | ROV1 | Block OFF | 213E5
13696 | ROV2 | Start ON | 214E0
13697 | ROV2 | Start OFF | 214E1
13698 | ROV2 | Trip ON | 214E2
13699 | ROV2 | Trip OFF | 214E3
13700 | ROV2 | Block ON | 214E4
13701 | ROV2 | Block OFF | 214E5
13760 | ROV3 | Start ON | 215E0
13761 | ROV3 | Start OFF | 215E1
13762 | ROV3 | Trip ON | 215E2
13763 | ROV3 | Trip OFF | 215E3
13764 | ROV3 | Block ON | 215E4
13765 | ROV3 | Block OFF | 215E5
13824 | ROV4 | Start ON | 216E0
13825 | ROV4 | Start OFF | 216E1
13826 | ROV4 | Trip ON | 216E2
13827 | ROV4 | Trip OFF | 216E3
13828 | ROV4 | Block ON | 216E4
13829 | ROV4 | Block OFF | 216E5
13888 | UCP1 | Alarm Start ON | 217E0
13889 | UCP1 | Alarm Start OFF | 217E1
13890 | UCP1 | Alarm ON | 217E2
13891 | UCP1 | Alarm OFF | 217E3
13892 | UCP1 | Start ON | 217E4
13893 | UCP1 | Start OFF | 217E5
13894 | UCP1 | Trip ON | 217E6
13895 | UCP1 | Trip OFF | 217E7
13896 | UCP1 | Block ON | 217E8
13897 | UCP1 | Block OFF | 217E9
13898 | UCP1 | Harmonic block ON | 217E10
13899 | UCP1 | Harmonic block OFF | 217E11
13952 | PGS1B | PS6 >/< Start ON | 218E0
13953 | PGS1B | PS6 >/< Start OFF | 218E1
13954 | PGS1B | PS6 >/< Trip ON | 218E2
13955 | PGS1B | PS6 >/< Trip OFF | 218E3
13956 | PGS1B | PS6 >/< Block ON | 218E4
13957 | PGS1B | PS6 >/< Block OFF | 218E5
13958 | PGS1B | PS7 >/< Start ON | 218E6
13959 | PGS1B | PS7 >/< Start OFF | 218E7
13960 | PGS1B | PS7 >/< Trip ON | 218E8
13961 | PGS1B | PS7 >/< Trip OFF | 218E9
13962 | PGS1B | PS7 >/< Block ON | 218E10
13963 | PGS1B | PS7 >/< Block OFF | 218E11
13964 | PGS1B | PS8 >/< Start ON | 218E12
13965 | PGS1B | PS8 >/< Start OFF | 218E13
13966 | PGS1B | PS8 >/< Trip ON | 218E14
13967 | PGS1B | PS8 >/< Trip OFF | 218E15
13968 | PGS1B | PS8 >/< Block ON | 218E16
13969 | PGS1B | PS8 >/< Block OFF | 218E17
13970 | PGS1B | PS9 >/< Start ON | 218E18
13971 | PGS1B | PS9 >/< Start OFF | 218E19
13972 | PGS1B | PS9 >/< Trip ON | 218E20
13973 | PGS1B | PS9 >/< Trip OFF | 218E21
13974 | PGS1B | PS9 >/< Block ON | 218E22
13975 | PGS1B | PS9 >/< Block OFF | 218E23
13976 | PGS1B | PS10 >/< Start ON | 218E24
13977 | PGS1B | PS10 >/< Start OFF | 218E25
13978 | PGS1B | PS10 >/< Trip ON | 218E26
13979 | PGS1B | PS10 >/< Trip OFF | 218E27
13980 | PGS1B | PS10 >/< Block ON | 218E28
13981 | PGS1B | PS10 >/< Block OFF | 218E29

## AQ-210 v2.1.1.3-233
AQ-200 IED EVENT CODES AND SPA EVENTS
FVSPE |  | G | M | R | T
NOTE: THIS MAP CAN BE DIFFERENT FROM THE ONE USED BY YOUR DEVICE! TO MAKE SURE YOU HAVE A MAP THAT MATCHES WITH YOUR DEVICE, GET IT FROM THE AQS CONFIGURATION FILE (TOOLS -> EVENTS AND LOGS -> EVENT LIST
Event Code | Block Description | Event Description | SPA Event
1 | SYSTEM | Power on | 0E1
2 | SYSTEM | RTC change | 0E2
3 | SYSTEM | RTC time incorrect | 0E3
4 | SYSTEM | NTP time sync aquired | 0E4
5 | SYSTEM | NTP time change | 0E5
6 | SYSTEM | NTP time sync lost | 0E6
7 | SYSTEM | Measuring system suspended | 0E7
8 | SYSTEM | Measuring system activated | 0E8
9 | SYSTEM | Unknown event | 0E9
26 | SYSTEM | Sync input On | 0E26
27 | SYSTEM | Protection subsystem reset | 0E50
28 | SYSTEM | Storage reinitialized - no contents | 0E28
29 | SYSTEM | Storage reinitialized - new firmware detected | 0E29
30 | SYSTEM | Event buffer clear marker | 0E30
31 | SYSTEM | Event buffer initialized | 0E31
32 | SYSTEM | DblEth LinkA down | 0E32
33 | SYSTEM | DblEth LinkA OK | 0E33
34 | SYSTEM | DblEth LinkB down | 0E34
35 | SYSTEM | DblEth LinkB OK | 0E35
36 | SYSTEM | User access control HMI open | 0E36
37 | SYSTEM | User access control HMI close | 0E37
38 | SYSTEM | User access control settingtool open | 0E38
39 | SYSTEM | User access control settingtool close | 0E39
64 | DIAGNOSTICS | Diagnostic Alarm ON | 1E0
65 | DIAGNOSTICS | Diagnostic Alarm OFF | 1E1
66 | DIAGNOSTICS | Configuration changed | 1E2
67 | DIAGNOSTICS | Configuration changed clear | 1E3
68 | DIAGNOSTICS | Network overload detected On | 1E4
69 | DIAGNOSTICS | Network overload detected Off | 1E5
70 | DIAGNOSTICS | Network loop detected On | 1E6
71 | DIAGNOSTICS | Network loop detected Off | 1E7
128 | IRF | Internal Relay Fault Activated | 2E0
129 | IRF | Internal Relay Fault Deactivated | 2E1
384 | PCS | Switch1 On | 6E0
385 | PCS | Switch1 Off | 6E1
386 | PCS | Switch2 On | 6E2
387 | PCS | Switch2 Off | 6E3
388 | PCS | Switch3 On | 6E4
389 | PCS | Switch3 Off | 6E5
390 | PCS | Switch4 On | 6E6
391 | PCS | Switch4 Off | 6E7
392 | PCS | Switch5 On | 6E8
393 | PCS | Switch5 Off | 6E9
448 | CTRL | Ctrl state REMOTE | 7E0
449 | CTRL | Ctrl state LOCAL | 7E1
512 | LOGIC1 | Logical Out1 On (Logical Output 1) | 8E0
513 | LOGIC1 | Logical Out1 Off (Logical Output 1) | 8E1
514 | LOGIC1 | Logical Out2 On (Logical Output 2) | 8E2
515 | LOGIC1 | Logical Out2 Off (Logical Output 2) | 8E3
516 | LOGIC1 | Logical Out3 On (Logical Output 3) | 8E4
517 | LOGIC1 | Logical Out3 Off (Logical Output 3) | 8E5
518 | LOGIC1 | Logical Out4 On (Logical Output 4) | 8E6
519 | LOGIC1 | Logical Out4 Off (Logical Output 4) | 8E7
520 | LOGIC1 | Logical Out5 On (Logical Output 5) | 8E8
521 | LOGIC1 | Logical Out5 Off (Logical Output 5) | 8E9
522 | LOGIC1 | Logical Out6 On (Logical Output 6) | 8E10
523 | LOGIC1 | Logical Out6 Off (Logical Output 6) | 8E11
524 | LOGIC1 | Logical Out7 On (Logical Output 7) | 8E12
525 | LOGIC1 | Logical Out7 Off (Logical Output 7) | 8E13
526 | LOGIC1 | Logical Out8 On (Logical Output 8) | 8E14
527 | LOGIC1 | Logical Out8 Off (Logical Output 8) | 8E15
528 | LOGIC1 | Logical Out9 On (Logical Output 9) | 8E16
529 | LOGIC1 | Logical Out9 Off (Logical Output 9) | 8E17
530 | LOGIC1 | Logical Out10 On (Logical Output 10) | 8E18
531 | LOGIC1 | Logical Out10 Off (Logical Output 10) | 8E19
532 | LOGIC1 | Logical Out11 On (Logical Output 11) | 8E20
533 | LOGIC1 | Logical Out11 Off (Logical Output 11) | 8E21
534 | LOGIC1 | Logical Out12 On (Logical Output 12) | 8E22
535 | LOGIC1 | Logical Out12 Off (Logical Output 12) | 8E23
536 | LOGIC1 | Logical Out13 On (Logical Output 13) | 8E24
537 | LOGIC1 | Logical Out13 Off (Logical Output 13) | 8E25
538 | LOGIC1 | Logical Out14 On (Logical Output 14) | 8E26
539 | LOGIC1 | Logical Out14 Off (Logical Output 14) | 8E27
540 | LOGIC1 | Logical Out15 On (Logical Output 15) | 8E28
541 | LOGIC1 | Logical Out15 Off (Logical Output 15) | 8E29
542 | LOGIC1 | Logical Out16 On (Logical Output 16) | 8E30
543 | LOGIC1 | Logical Out16 Off (Logical Output 16) | 8E31
544 | LOGIC1 | Logical Out17 On (Logical Output 17) | 8E32
545 | LOGIC1 | Logical Out17 Off (Logical Output 17) | 8E33
546 | LOGIC1 | Logical Out18 On (Logical Output 18) | 8E34
547 | LOGIC1 | Logical Out18 Off (Logical Output 18) | 8E35
548 | LOGIC1 | Logical Out19 On (Logical Output 19) | 8E36
549 | LOGIC1 | Logical Out19 Off (Logical Output 19) | 8E37
550 | LOGIC1 | Logical Out20 On (Logical Output 20) | 8E38
551 | LOGIC1 | Logical Out20 Off (Logical Output 20) | 8E39
552 | LOGIC1 | Logical Out21 On (Logical Output 21) | 8E40
553 | LOGIC1 | Logical Out21 Off (Logical Output 21) | 8E41
554 | LOGIC1 | Logical Out22 On (Logical Output 22) | 8E42
555 | LOGIC1 | Logical Out22 Off (Logical Output 22) | 8E43
556 | LOGIC1 | Logical Out23 On (Logical Output 23) | 8E44
557 | LOGIC1 | Logical Out23 Off (Logical Output 23) | 8E45
558 | LOGIC1 | Logical Out24 On (Logical Output 24) | 8E46
559 | LOGIC1 | Logical Out24 Off (Logical Output 24) | 8E47
560 | LOGIC1 | Logical Out25 On (Logical Output 25) | 8E48
561 | LOGIC1 | Logical Out25 Off (Logical Output 25) | 8E49
562 | LOGIC1 | Logical Out26 On (Logical Output 26) | 8E50
563 | LOGIC1 | Logical Out26 Off (Logical Output 26) | 8E51
564 | LOGIC1 | Logical Out27 On (Logical Output 27) | 8E52
565 | LOGIC1 | Logical Out27 Off (Logical Output 27) | 8E53
566 | LOGIC1 | Logical Out28 On (Logical Output 28) | 8E54
567 | LOGIC1 | Logical Out28 Off (Logical Output 28) | 8E55
568 | LOGIC1 | Logical Out29 On (Logical Output 29) | 8E56
569 | LOGIC1 | Logical Out29 Off (Logical Output 29) | 8E57
570 | LOGIC1 | Logical Out30 On (Logical Output 30) | 8E58
571 | LOGIC1 | Logical Out30 Off (Logical Output 30) | 8E59
572 | LOGIC1 | Logical Out31 On (Logical Output 31) | 8E60
573 | LOGIC1 | Logical Out31 Off (Logical Output 31) | 8E61
574 | LOGIC1 | Logical Out32 On (Logical Output 32) | 8E62
575 | LOGIC1 | Logical Out32 Off (Logical Output 32) | 8E63
576 | LOGIC2 | Logical In1 On (Logical Input 1) | 9E0
577 | LOGIC2 | Logical In1 Off (Logical Input 1) | 9E1
578 | LOGIC2 | Logical In2 On (Logical Input 2) | 9E2
579 | LOGIC2 | Logical In2 Off (Logical Input 2) | 9E3
580 | LOGIC2 | Logical In3 On (Logical Input 3) | 9E4
581 | LOGIC2 | Logical In3 Off (Logical Input 3) | 9E5
582 | LOGIC2 | Logical In4 On (Logical Input 4) | 9E6
583 | LOGIC2 | Logical In4 Off (Logical Input 4) | 9E7
584 | LOGIC2 | Logical In5 On (Logical Input 5) | 9E8
585 | LOGIC2 | Logical In5 Off (Logical Input 5) | 9E9
586 | LOGIC2 | Logical In6 On (Logical Input 6) | 9E10
587 | LOGIC2 | Logical In6 Off (Logical Input 6) | 9E11
588 | LOGIC2 | Logical In7 On (Logical Input 7) | 9E12
589 | LOGIC2 | Logical In7 Off (Logical Input 7) | 9E13
590 | LOGIC2 | Logical In8 On (Logical Input 8) | 9E14
591 | LOGIC2 | Logical In8 Off (Logical Input 8) | 9E15
592 | LOGIC2 | Logical In9 On (Logical Input 9) | 9E16
593 | LOGIC2 | Logical In9 Off (Logical Input 9) | 9E17
594 | LOGIC2 | Logical In10 On (Logical Input 10) | 9E18
595 | LOGIC2 | Logical In10 Off (Logical Input 10) | 9E19
596 | LOGIC2 | Logical In11 On (Logical Input 11) | 9E20
597 | LOGIC2 | Logical In11 Off (Logical Input 11) | 9E21
598 | LOGIC2 | Logical In12 On (Logical Input 12) | 9E22
599 | LOGIC2 | Logical In12 Off (Logical Input 12) | 9E23
600 | LOGIC2 | Logical In13 On (Logical Input 13) | 9E24
601 | LOGIC2 | Logical In13 Off (Logical Input 13) | 9E25
602 | LOGIC2 | Logical In14 On (Logical Input 14) | 9E26
603 | LOGIC2 | Logical In14 Off (Logical Input 14) | 9E27
604 | LOGIC2 | Logical In15 On (Logical Input 15) | 9E28
605 | LOGIC2 | Logical In15 Off (Logical Input 15) | 9E29
606 | LOGIC2 | Logical In16 On (Logical Input 16) | 9E30
607 | LOGIC2 | Logical In16 Off (Logical Input 16) | 9E31
608 | LOGIC2 | Logical In17 On (Logical Input 17) | 9E32
609 | LOGIC2 | Logical In17 Off (Logical Input 17) | 9E33
610 | LOGIC2 | Logical In18 On (Logical Input 18) | 9E34
611 | LOGIC2 | Logical In18 Off (Logical Input 18) | 9E35
612 | LOGIC2 | Logical In19 On (Logical Input 19) | 9E36
613 | LOGIC2 | Logical In19 Off (Logical Input 19) | 9E37
614 | LOGIC2 | Logical In20 On (Logical Input 20) | 9E38
615 | LOGIC2 | Logical In20 Off (Logical Input 20) | 9E39
616 | LOGIC2 | Logical In21 On (Logical Input 21) | 9E40
617 | LOGIC2 | Logical In21 Off (Logical Input 21) | 9E41
618 | LOGIC2 | Logical In22 On (Logical Input 22) | 9E42
619 | LOGIC2 | Logical In22 Off (Logical Input 22) | 9E43
620 | LOGIC2 | Logical In23 On (Logical Input 23) | 9E44
621 | LOGIC2 | Logical In23 Off (Logical Input 23) | 9E45
622 | LOGIC2 | Logical In24 On (Logical Input 24) | 9E46
623 | LOGIC2 | Logical In24 Off (Logical Input 24) | 9E47
624 | LOGIC2 | Logical In25 On (Logical Input 25) | 9E48
625 | LOGIC2 | Logical In25 Off (Logical Input 25) | 9E49
626 | LOGIC2 | Logical In26 On (Logical Input 26) | 9E50
627 | LOGIC2 | Logical In26 Off (Logical Input 26) | 9E51
628 | LOGIC2 | Logical In27 On (Logical Input 27) | 9E52
629 | LOGIC2 | Logical In27 Off (Logical Input 27) | 9E53
630 | LOGIC2 | Logical In28 On (Logical Input 28) | 9E54
631 | LOGIC2 | Logical In28 Off (Logical Input 28) | 9E55
632 | LOGIC2 | Logical In29 On (Logical Input 29) | 9E56
633 | LOGIC2 | Logical In29 Off (Logical Input 29) | 9E57
634 | LOGIC2 | Logical In30 On (Logical Input 30) | 9E58
635 | LOGIC2 | Logical In30 Off (Logical Input 30) | 9E59
636 | LOGIC2 | Logical In31 On (Logical Input 31) | 9E60
637 | LOGIC2 | Logical In31 Off (Logical Input 31) | 9E61
638 | LOGIC2 | Logical In32 On (Logical Input 32) | 9E62
639 | LOGIC2 | Logical In32 Off (Logical Input 32) | 9E63
640 | DIGI | DI 1 On (DI1) | 10E0
641 | DIGI | DI 1 Off (DI1) | 10E1
642 | DIGI | DI 2 On (DI2) | 10E2
643 | DIGI | DI 2 Off (DI2) | 10E3
644 | DIGI | DI 3 On (DI3) | 10E4
645 | DIGI | DI 3 Off (DI3) | 10E5
646 | DIGI | DI 4 On (DI4) | 10E6
647 | DIGI | DI 4 Off (DI4) | 10E7
648 | DIGI | DI 5 On (DI5) | 10E8
649 | DIGI | DI 5 Off (DI5) | 10E9
650 | DIGI | DI 6 On (DI6) | 10E10
651 | DIGI | DI 6 Off (DI6) | 10E11
652 | DIGI | DI 7 On (DI7) | 10E12
653 | DIGI | DI 7 Off (DI7) | 10E13
654 | DIGI | DI 8 On (DI8) | 10E14
655 | DIGI | DI 8 Off (DI8) | 10E15
656 | DIGI | DI 9 On (DI9) | 10E16
657 | DIGI | DI 9 Off (DI9) | 10E17
658 | DIGI | DI 10 On (DI10) | 10E18
659 | DIGI | DI 10 Off (DI10) | 10E19
660 | DIGI | DI 11 On (DI11) | 10E20
661 | DIGI | DI 11 Off (DI11) | 10E21
662 | DIGI | DI 12 On (DI12) | 10E22
663 | DIGI | DI 12 Off (DI12) | 10E23
664 | DIGI | DI 13 On (DI13) | 10E24
665 | DIGI | DI 13 Off (DI13) | 10E25
666 | DIGI | DI 14 On (DI14) | 10E26
667 | DIGI | DI 14 Off (DI14) | 10E27
668 | DIGI | DI 15 On (DI15) | 10E28
669 | DIGI | DI 15 Off (DI15) | 10E29
670 | DIGI | DI 16 On (DI16) | 10E30
671 | DIGI | DI 16 Off (DI16) | 10E31
672 | DIGI | DI 17 On (DI17) | 10E32
673 | DIGI | DI 17 Off (DI17) | 10E33
674 | DIGI | DI 18 On (DI18) | 10E34
675 | DIGI | DI 18 Off (DI18) | 10E35
676 | DIGI | DI 19 On (DI19) | 10E36
677 | DIGI | DI 19 Off (DI19) | 10E37
678 | DIGI | DI 20 On (DI20) | 10E38
679 | DIGI | DI 20 Off (DI20) | 10E39
680 | DIGI | DI 21 On (DI21) | 10E40
681 | DIGI | DI 21 Off (DI21) | 10E41
682 | DIGI | DI 22 On (DI22) | 10E42
683 | DIGI | DI 22 Off (DI22) | 10E43
684 | DIGI | DI 23 On (DI23) | 10E44
685 | DIGI | DI 23 Off (DI23) | 10E45
686 | DIGI | DI 24 On (DI24) | 10E46
687 | DIGI | DI 24 Off (DI24) | 10E47
688 | DIGI | DI 25 On (DI25) | 10E48
689 | DIGI | DI 25 Off (DI25) | 10E49
690 | DIGI | DI 26 On (DI26) | 10E50
691 | DIGI | DI 26 Off (DI26) | 10E51
692 | DIGI | DI 27 On (DI27) | 10E52
693 | DIGI | DI 27 Off (DI27) | 10E53
694 | DIGI | DI 28 On (DI28) | 10E54
695 | DIGI | DI 28 Off (DI28) | 10E55
696 | DIGI | DI 29 On (DI29) | 10E56
697 | DIGI | DI 29 Off (DI29) | 10E57
698 | DIGI | DI 30 On (DI30) | 10E58
699 | DIGI | DI 30 Off (DI30) | 10E59
700 | DIGI | DI 31 On (DI31) | 10E60
701 | DIGI | DI 31 Off (DI31) | 10E61
702 | DIGI | DI 32 On (DI32) | 10E62
703 | DIGI | DI 32 Off (DI32) | 10E63
704 | DIGI2 | DI33 On (DI33) | 11E0
705 | DIGI2 | DI33 Off (DI33) | 11E1
706 | DIGI2 | DI34 On (DI34) | 11E2
707 | DIGI2 | DI34 Off (DI34) | 11E3
708 | DIGI2 | DI35 On (DI35) | 11E4
709 | DIGI2 | DI35 Off (DI35) | 11E5
710 | DIGI2 | DI36 On (DI36) | 11E6
711 | DIGI2 | DI36 Off (DI36) | 11E7
712 | DIGI2 | DI37 On (DI37) | 11E8
713 | DIGI2 | DI37 Off (DI37) | 11E9
714 | DIGI2 | DI38 On (DI38) | 11E10
715 | DIGI2 | DI38 Off (DI38) | 11E11
716 | DIGI2 | DI39 On (DI39) | 11E12
717 | DIGI2 | DI39 Off (DI39) | 11E13
718 | DIGI2 | DI40 On (DI40) | 11E14
719 | DIGI2 | DI40 Off (DI40) | 11E15
720 | DIGI2 | DI41 On (DI41) | 11E16
721 | DIGI2 | DI41 Off (DI41) | 11E17
722 | DIGI2 | DI42 On (DI42) | 11E18
723 | DIGI2 | DI42 Off (DI42) | 11E19
724 | DIGI2 | DI43 On (DI43) | 11E20
725 | DIGI2 | DI43 Off (DI43) | 11E21
726 | DIGI2 | DI44 On (DI44) | 11E22
727 | DIGI2 | DI44 Off (DI44) | 11E23
728 | DIGI2 | DI45 On (DI45) | 11E24
729 | DIGI2 | DI45 Off (DI45) | 11E25
730 | DIGI2 | DI46 On (DI46) | 11E26
731 | DIGI2 | DI46 Off (DI46) | 11E27
732 | DIGI2 | DI47 On (DI47) | 11E28
733 | DIGI2 | DI47 Off (DI47) | 11E29
734 | DIGI2 | DI48 On (DI48) | 11E30
735 | DIGI2 | DI48 Off (DI48) | 11E31
736 | DIGI2 | DI49 On (DI49) | 11E32
737 | DIGI2 | DI49 Off (DI49) | 11E33
738 | DIGI2 | DI50 On (DI50) | 11E34
739 | DIGI2 | DI50 Off (DI50) | 11E35
740 | DIGI2 | DI51 On (DI51) | 11E36
741 | DIGI2 | DI51 Off (DI51) | 11E37
768 | DIGI3 | DI 52 On | 12E0
769 | DIGI3 | DI 52 Off | 12E1
770 | DIGI3 | DI 53 On | 12E2
771 | DIGI3 | DI 53 Off | 12E3
772 | DIGI3 | DI 54 On | 12E4
773 | DIGI3 | DI 54 Off | 12E5
774 | DIGI3 | DI 55 On | 12E6
775 | DIGI3 | DI 55 Off | 12E7
776 | DIGI3 | DI 56 On | 12E8
777 | DIGI3 | DI 56 Off | 12E9
778 | DIGI3 | DI 57 On | 12E10
779 | DIGI3 | DI 57 Off | 12E11
780 | DIGI3 | DI 58 On | 12E12
781 | DIGI3 | DI 58 Off | 12E13
782 | DIGI3 | DI 59 On | 12E14
783 | DIGI3 | DI 59 Off | 12E15
784 | DIGI3 | DI 60 On | 12E16
785 | DIGI3 | DI 60 Off | 12E17
786 | DIGI3 | DI 61 On | 12E18
787 | DIGI3 | DI 61 Off | 12E19
788 | DIGI3 | DI 62 On | 12E20
789 | DIGI3 | DI 62 Off | 12E21
790 | DIGI3 | DI 63 On | 12E22
791 | DIGI3 | DI 63 Off | 12E23
792 | DIGI3 | DI 64 On | 12E24
793 | DIGI3 | DI 64 Off | 12E25
794 | DIGI3 | DI 65 On | 12E26
795 | DIGI3 | DI 65 Off | 12E27
796 | DIGI3 | DI 66 On | 12E28
797 | DIGI3 | DI 66 Off | 12E29
798 | DIGI3 | DI 67 On | 12E30
799 | DIGI3 | DI 67 Off | 12E31
800 | DIGI3 | DI 68 On | 12E32
801 | DIGI3 | DI 68 Off | 12E33
802 | DIGI3 | DI 69 On | 12E34
803 | DIGI3 | DI 69 Off | 12E35
804 | DIGI3 | DI 70 On | 12E36
805 | DIGI3 | DI 70 Off | 12E37
806 | DIGI3 | DI 71 On | 12E38
807 | DIGI3 | DI 71 Off | 12E39
808 | DIGI3 | DI 72 On | 12E40
809 | DIGI3 | DI 72 Off | 12E41
810 | DIGI3 | DI 73 On | 12E42
811 | DIGI3 | DI 73 Off | 12E43
812 | DIGI3 | DI 74 On | 12E44
813 | DIGI3 | DI 74 Off | 12E45
814 | DIGI3 | DI 75 On | 12E46
815 | DIGI3 | DI 75 Off | 12E47
816 | DIGI3 | DI 76 On | 12E48
817 | DIGI3 | DI 76 Off | 12E49
818 | DIGI3 | DI 77 On | 12E50
819 | DIGI3 | DI 77 Off | 12E51
820 | DIGI3 | DI 78 On | 12E52
821 | DIGI3 | DI 78 Off | 12E53
822 | DIGI3 | DI 79 On | 12E54
823 | DIGI3 | DI 79 Off | 12E55
824 | DIGI3 | DI 80 On | 12E56
825 | DIGI3 | DI 80 Off | 12E57
826 | DIGI3 | DI 81 On | 12E58
827 | DIGI3 | DI 81 Off | 12E59
828 | DIGI3 | DI 82 On | 12E60
829 | DIGI3 | DI 82 Off | 12E61
830 | DIGI3 | DI 83 On | 12E62
831 | DIGI3 | DI 83 Off | 12E63
832 | DIGI4 | DI 84 On | 13E0
833 | DIGI4 | DI 84 Off | 13E1
834 | DIGI4 | DI 85 On | 13E2
835 | DIGI4 | DI 85 Off | 13E3
836 | DIGI4 | DI 86 On | 13E4
837 | DIGI4 | DI 86 Off | 13E5
838 | DIGI4 | DI 87 On | 13E6
839 | DIGI4 | DI 87 Off | 13E7
840 | DIGI4 | DI 88 On | 13E8
841 | DIGI4 | DI 88 Off | 13E9
842 | DIGI4 | DI 89 On | 13E10
843 | DIGI4 | DI 89 Off | 13E11
844 | DIGI4 | DI 90 On | 13E12
845 | DIGI4 | DI 90 Off | 13E13
846 | DIGI4 | DI 91 On | 13E14
847 | DIGI4 | DI 91 Off | 13E15
848 | DIGI4 | DI 92 On | 13E16
849 | DIGI4 | DI 92 Off | 13E17
850 | DIGI4 | DI 93 On | 13E18
851 | DIGI4 | DI 93 Off | 13E19
852 | DIGI4 | DI 94 On | 13E20
853 | DIGI4 | DI 94 Off | 13E21
854 | DIGI4 | DI 95 On | 13E22
855 | DIGI4 | DI 95 Off | 13E23
856 | DIGI4 | DI 96 On | 13E24
857 | DIGI4 | DI 96 Off | 13E25
858 | DIGI4 | DI 97 On | 13E26
859 | DIGI4 | DI 97 Off | 13E27
860 | DIGI4 | DI 98 On | 13E28
861 | DIGI4 | DI 98 Off | 13E29
862 | DIGI4 | DI 99 On | 13E30
863 | DIGI4 | DI 99 Off | 13E31
864 | DIGI4 | DI100 On | 13E32
865 | DIGI4 | DI100 Off | 13E33
866 | DIGI4 | DI101 On | 13E34
867 | DIGI4 | DI101 Off | 13E35
868 | DIGI4 | DI102 On | 13E36
869 | DIGI4 | DI102 Off | 13E37
870 | DIGI4 | DI103 On | 13E38
871 | DIGI4 | DI103 Off | 13E39
872 | DIGI4 | DI104 On | 13E40
873 | DIGI4 | DI104 Off | 13E41
874 | DIGI4 | DI105 On | 13E42
875 | DIGI4 | DI105 Off | 13E43
876 | DIGI4 | DI106 On | 13E44
877 | DIGI4 | DI106 Off | 13E45
878 | DIGI4 | DI107 On | 13E46
879 | DIGI4 | DI107 Off | 13E47
880 | DIGI4 | DI108 On | 13E48
881 | DIGI4 | DI108 Off | 13E49
882 | DIGI4 | DI109 On | 13E50
883 | DIGI4 | DI109 Off | 13E51
884 | DIGI4 | DI110 On | 13E52
885 | DIGI4 | DI110 Off | 13E53
886 | DIGI4 | DI111 On | 13E54
887 | DIGI4 | DI111 Off | 13E55
888 | DIGI4 | DI112 On | 13E56
889 | DIGI4 | DI112 Off | 13E57
890 | DIGI4 | DI113 On | 13E58
891 | DIGI4 | DI113 Off | 13E59
892 | DIGI4 | DI114 On | 13E60
893 | DIGI4 | DI114 Off | 13E61
894 | DIGI4 | DI115 On | 13E62
895 | DIGI4 | DI115 Off | 13E63
896 | LOGIC3 | Logical Out33 On | 14E0
897 | LOGIC3 | Logical Out33 Off | 14E1
898 | LOGIC3 | Logical Out34 On | 14E2
899 | LOGIC3 | Logical Out34 Off | 14E3
900 | LOGIC3 | Logical Out35 On | 14E4
901 | LOGIC3 | Logical Out35 Off | 14E5
902 | LOGIC3 | Logical Out36 On | 14E6
903 | LOGIC3 | Logical Out36 Off | 14E7
904 | LOGIC3 | Logical Out37 On | 14E8
905 | LOGIC3 | Logical Out37 Off | 14E9
906 | LOGIC3 | Logical Out38 On | 14E10
907 | LOGIC3 | Logical Out38 Off | 14E11
908 | LOGIC3 | Logical Out39 On | 14E12
909 | LOGIC3 | Logical Out39 Off | 14E13
910 | LOGIC3 | Logical Out40 On | 14E14
911 | LOGIC3 | Logical Out40 Off | 14E15
912 | LOGIC3 | Logical Out41 On | 14E16
913 | LOGIC3 | Logical Out41 Off | 14E17
914 | LOGIC3 | Logical Out42 On | 14E18
915 | LOGIC3 | Logical Out42 Off | 14E19
916 | LOGIC3 | Logical Out43 On | 14E20
917 | LOGIC3 | Logical Out43 Off | 14E21
918 | LOGIC3 | Logical Out44 On | 14E22
919 | LOGIC3 | Logical Out44 Off | 14E23
920 | LOGIC3 | Logical Out45 On | 14E24
921 | LOGIC3 | Logical Out45 Off | 14E25
922 | LOGIC3 | Logical Out46 On | 14E26
923 | LOGIC3 | Logical Out46 Off | 14E27
924 | LOGIC3 | Logical Out47 On | 14E28
925 | LOGIC3 | Logical Out47 Off | 14E29
926 | LOGIC3 | Logical Out48 On | 14E30
927 | LOGIC3 | Logical Out48 Off | 14E31
928 | LOGIC3 | Logical Out49 On | 14E32
929 | LOGIC3 | Logical Out49 Off | 14E33
930 | LOGIC3 | Logical Out50 On | 14E34
931 | LOGIC3 | Logical Out50 Off | 14E35
932 | LOGIC3 | Logical Out51 On | 14E36
933 | LOGIC3 | Logical Out51 Off | 14E37
934 | LOGIC3 | Logical Out52 On | 14E38
935 | LOGIC3 | Logical Out52 Off | 14E39
936 | LOGIC3 | Logical Out53 On | 14E40
937 | LOGIC3 | Logical Out53 Off | 14E41
938 | LOGIC3 | Logical Out54 On | 14E42
939 | LOGIC3 | Logical Out54 Off | 14E43
940 | LOGIC3 | Logical Out55 On | 14E44
941 | LOGIC3 | Logical Out55 Off | 14E45
942 | LOGIC3 | Logical Out56 On | 14E46
943 | LOGIC3 | Logical Out56 Off | 14E47
944 | LOGIC3 | Logical Out57 On | 14E48
945 | LOGIC3 | Logical Out57 Off | 14E49
946 | LOGIC3 | Logical Out58 On | 14E50
947 | LOGIC3 | Logical Out58 Off | 14E51
948 | LOGIC3 | Logical Out59 On | 14E52
949 | LOGIC3 | Logical Out59 Off | 14E53
950 | LOGIC3 | Logical Out60 On | 14E54
951 | LOGIC3 | Logical Out60 Off | 14E55
952 | LOGIC3 | Logical Out61 On | 14E56
953 | LOGIC3 | Logical Out61 Off | 14E57
954 | LOGIC3 | Logical Out62 On | 14E58
955 | LOGIC3 | Logical Out62 Off | 14E59
956 | LOGIC3 | Logical Out63 On | 14E60
957 | LOGIC3 | Logical Out63 Off | 14E61
958 | LOGIC3 | Logical Out64 On | 14E62
959 | LOGIC3 | Logical Out64 Off | 14E63
1024 | GOOSE1 | GOOSE IN1 On (GOOSE IN1) | 16E0
1025 | GOOSE1 | GOOSE IN1 Off (GOOSE IN1) | 16E1
1026 | GOOSE1 | GOOSE IN2 On (GOOSE IN2) | 16E2
1027 | GOOSE1 | GOOSE IN2 Off (GOOSE IN2) | 16E3
1028 | GOOSE1 | GOOSE IN3 On (GOOSE IN3) | 16E4
1029 | GOOSE1 | GOOSE IN3 Off (GOOSE IN3) | 16E5
1030 | GOOSE1 | GOOSE IN4 On (GOOSE IN4) | 16E6
1031 | GOOSE1 | GOOSE IN4 Off (GOOSE IN4) | 16E7
1032 | GOOSE1 | GOOSE IN5 On (GOOSE IN5) | 16E8
1033 | GOOSE1 | GOOSE IN5 Off (GOOSE IN5) | 16E9
1034 | GOOSE1 | GOOSE IN6 On (GOOSE IN6) | 16E10
1035 | GOOSE1 | GOOSE IN6 Off (GOOSE IN6) | 16E11
1036 | GOOSE1 | GOOSE IN7 On (GOOSE IN7) | 16E12
1037 | GOOSE1 | GOOSE IN7 Off (GOOSE IN7) | 16E13
1038 | GOOSE1 | GOOSE IN8 On (GOOSE IN8) | 16E14
1039 | GOOSE1 | GOOSE IN8 Off (GOOSE IN8) | 16E15
1040 | GOOSE1 | GOOSE IN9 On (GOOSE IN9) | 16E16
1041 | GOOSE1 | GOOSE IN9 Off (GOOSE IN9) | 16E17
1042 | GOOSE1 | GOOSE IN10 On (GOOSE IN10) | 16E18
1043 | GOOSE1 | GOOSE IN10 Off (GOOSE IN10) | 16E19
1044 | GOOSE1 | GOOSE IN11 On (GOOSE IN11) | 16E20
1045 | GOOSE1 | GOOSE IN11 Off (GOOSE IN11) | 16E21
1046 | GOOSE1 | GOOSE IN12 On (GOOSE IN12) | 16E22
1047 | GOOSE1 | GOOSE IN12 Off (GOOSE IN12) | 16E23
1048 | GOOSE1 | GOOSE IN13 On (GOOSE IN13) | 16E24
1049 | GOOSE1 | GOOSE IN13 Off (GOOSE IN13) | 16E25
1050 | GOOSE1 | GOOSE IN14 On (GOOSE IN14) | 16E26
1051 | GOOSE1 | GOOSE IN14 Off (GOOSE IN14) | 16E27
1052 | GOOSE1 | GOOSE IN15 On (GOOSE IN15) | 16E28
1053 | GOOSE1 | GOOSE IN15 Off (GOOSE IN15) | 16E29
1054 | GOOSE1 | GOOSE IN16 On (GOOSE IN16) | 16E30
1055 | GOOSE1 | GOOSE IN16 Off (GOOSE IN16) | 16E31
1056 | GOOSE1 | GOOSE IN17 On (GOOSE IN17) | 16E32
1057 | GOOSE1 | GOOSE IN17 Off (GOOSE IN17) | 16E33
1058 | GOOSE1 | GOOSE IN18 On (GOOSE IN18) | 16E34
1059 | GOOSE1 | GOOSE IN18 Off (GOOSE IN18) | 16E35
1060 | GOOSE1 | GOOSE IN19 On (GOOSE IN19) | 16E36
1061 | GOOSE1 | GOOSE IN19 Off (GOOSE IN19) | 16E37
1062 | GOOSE1 | GOOSE IN20 On (GOOSE IN20) | 16E38
1063 | GOOSE1 | GOOSE IN20 Off (GOOSE IN20) | 16E39
1064 | GOOSE1 | GOOSE IN21 On (GOOSE IN21) | 16E40
1065 | GOOSE1 | GOOSE IN21 Off (GOOSE IN21) | 16E41
1066 | GOOSE1 | GOOSE IN22 On (GOOSE IN22) | 16E42
1067 | GOOSE1 | GOOSE IN22 Off (GOOSE IN22) | 16E43
1068 | GOOSE1 | GOOSE IN23 On (GOOSE IN23) | 16E44
1069 | GOOSE1 | GOOSE IN23 Off (GOOSE IN23) | 16E45
1070 | GOOSE1 | GOOSE IN24 On (GOOSE IN24) | 16E46
1071 | GOOSE1 | GOOSE IN24 Off (GOOSE IN24) | 16E47
1072 | GOOSE1 | GOOSE IN25 On (GOOSE IN25) | 16E48
1073 | GOOSE1 | GOOSE IN25 Off (GOOSE IN25) | 16E49
1074 | GOOSE1 | GOOSE IN26 On (GOOSE IN26) | 16E50
1075 | GOOSE1 | GOOSE IN26 Off (GOOSE IN26) | 16E51
1076 | GOOSE1 | GOOSE IN27 On (GOOSE IN27) | 16E52
1077 | GOOSE1 | GOOSE IN27 Off (GOOSE IN27) | 16E53
1078 | GOOSE1 | GOOSE IN28 On (GOOSE IN28) | 16E54
1079 | GOOSE1 | GOOSE IN28 Off (GOOSE IN28) | 16E55
1080 | GOOSE1 | GOOSE IN29 On (GOOSE IN29) | 16E56
1081 | GOOSE1 | GOOSE IN29 Off (GOOSE IN29) | 16E57
1082 | GOOSE1 | GOOSE IN30 On (GOOSE IN30) | 16E58
1083 | GOOSE1 | GOOSE IN30 Off (GOOSE IN30) | 16E59
1084 | GOOSE1 | GOOSE IN31 On (GOOSE IN31) | 16E60
1085 | GOOSE1 | GOOSE IN31 Off (GOOSE IN31) | 16E61
1086 | GOOSE1 | GOOSE IN32 On (GOOSE IN32) | 16E62
1087 | GOOSE1 | GOOSE IN32 Off (GOOSE IN32) | 16E63
1088 | GOOSE2 | GOOSE IN33 On (GOOSE IN33) | 17E0
1089 | GOOSE2 | GOOSE IN33 Off (GOOSE IN33) | 17E1
1090 | GOOSE2 | GOOSE IN34 On (GOOSE IN34) | 17E2
1091 | GOOSE2 | GOOSE IN34 Off (GOOSE IN34) | 17E3
1092 | GOOSE2 | GOOSE IN35 On (GOOSE IN35) | 17E4
1093 | GOOSE2 | GOOSE IN35 Off (GOOSE IN35) | 17E5
1094 | GOOSE2 | GOOSE IN36 On (GOOSE IN36) | 17E6
1095 | GOOSE2 | GOOSE IN36 Off (GOOSE IN36) | 17E7
1096 | GOOSE2 | GOOSE IN37 On (GOOSE IN37) | 17E8
1097 | GOOSE2 | GOOSE IN37 Off (GOOSE IN37) | 17E9
1098 | GOOSE2 | GOOSE IN38 On (GOOSE IN38) | 17E10
1099 | GOOSE2 | GOOSE IN38 Off (GOOSE IN38) | 17E11
1100 | GOOSE2 | GOOSE IN39 On (GOOSE IN39) | 17E12
1101 | GOOSE2 | GOOSE IN39 Off (GOOSE IN39) | 17E13
1102 | GOOSE2 | GOOSE IN40 On (GOOSE IN40) | 17E14
1103 | GOOSE2 | GOOSE IN40 Off (GOOSE IN40) | 17E15
1104 | GOOSE2 | GOOSE IN41 On (GOOSE IN41) | 17E16
1105 | GOOSE2 | GOOSE IN41 Off (GOOSE IN41) | 17E17
1106 | GOOSE2 | GOOSE IN42 On (GOOSE IN42) | 17E18
1107 | GOOSE2 | GOOSE IN42 Off (GOOSE IN42) | 17E19
1108 | GOOSE2 | GOOSE IN43 On (GOOSE IN43) | 17E20
1109 | GOOSE2 | GOOSE IN43 Off (GOOSE IN43) | 17E21
1110 | GOOSE2 | GOOSE IN44 On (GOOSE IN44) | 17E22
1111 | GOOSE2 | GOOSE IN44 Off (GOOSE IN44) | 17E23
1112 | GOOSE2 | GOOSE IN45 On (GOOSE IN45) | 17E24
1113 | GOOSE2 | GOOSE IN45 Off (GOOSE IN45) | 17E25
1114 | GOOSE2 | GOOSE IN46 On (GOOSE IN46) | 17E26
1115 | GOOSE2 | GOOSE IN46 Off (GOOSE IN46) | 17E27
1116 | GOOSE2 | GOOSE IN47 On (GOOSE IN47) | 17E28
1117 | GOOSE2 | GOOSE IN47 Off (GOOSE IN47) | 17E29
1118 | GOOSE2 | GOOSE IN48 On (GOOSE IN48) | 17E30
1119 | GOOSE2 | GOOSE IN48 Off (GOOSE IN48) | 17E31
1120 | GOOSE2 | GOOSE IN49 On (GOOSE IN49) | 17E32
1121 | GOOSE2 | GOOSE IN49 Off (GOOSE IN49) | 17E33
1122 | GOOSE2 | GOOSE IN50 On (GOOSE IN50) | 17E34
1123 | GOOSE2 | GOOSE IN50 Off (GOOSE IN50) | 17E35
1124 | GOOSE2 | GOOSE IN51 On (GOOSE IN51) | 17E36
1125 | GOOSE2 | GOOSE IN51 Off (GOOSE IN51) | 17E37
1126 | GOOSE2 | GOOSE IN52 On (GOOSE IN52) | 17E38
1127 | GOOSE2 | GOOSE IN52 Off (GOOSE IN52) | 17E39
1128 | GOOSE2 | GOOSE IN53 On (GOOSE IN53) | 17E40
1129 | GOOSE2 | GOOSE IN53 Off (GOOSE IN53) | 17E41
1130 | GOOSE2 | GOOSE IN54 On (GOOSE IN54) | 17E42
1131 | GOOSE2 | GOOSE IN54 Off (GOOSE IN54) | 17E43
1132 | GOOSE2 | GOOSE IN55 On (GOOSE IN55) | 17E44
1133 | GOOSE2 | GOOSE IN55 Off (GOOSE IN55) | 17E45
1134 | GOOSE2 | GOOSE IN56 On (GOOSE IN56) | 17E46
1135 | GOOSE2 | GOOSE IN56 Off (GOOSE IN56) | 17E47
1136 | GOOSE2 | GOOSE IN57 On (GOOSE IN57) | 17E48
1137 | GOOSE2 | GOOSE IN57 Off (GOOSE IN57) | 17E49
1138 | GOOSE2 | GOOSE IN58 On (GOOSE IN58) | 17E50
1139 | GOOSE2 | GOOSE IN58 Off (GOOSE IN58) | 17E51
1140 | GOOSE2 | GOOSE IN59 On (GOOSE IN59) | 17E52
1141 | GOOSE2 | GOOSE IN59 Off (GOOSE IN59) | 17E53
1142 | GOOSE2 | GOOSE IN60 On (GOOSE IN60) | 17E54
1143 | GOOSE2 | GOOSE IN60 Off (GOOSE IN60) | 17E55
1144 | GOOSE2 | GOOSE IN61 On (GOOSE IN61) | 17E56
1145 | GOOSE2 | GOOSE IN61 Off (GOOSE IN61) | 17E57
1146 | GOOSE2 | GOOSE IN62 On (GOOSE IN62) | 17E58
1147 | GOOSE2 | GOOSE IN62 Off (GOOSE IN62) | 17E59
1148 | GOOSE2 | GOOSE IN63 On (GOOSE IN63) | 17E60
1149 | GOOSE2 | GOOSE IN63 Off (GOOSE IN63) | 17E61
1150 | GOOSE2 | GOOSE IN64 On (GOOSE IN64) | 17E62
1151 | GOOSE2 | GOOSE IN64 Off (GOOSE IN64) | 17E63
1152 | GOOSE3 | GOOSE IN1 Quality Good (GOOSE IN1) | 18E0
1153 | GOOSE3 | GOOSE IN1 Quality Bad (GOOSE IN1) | 18E1
1154 | GOOSE3 | GOOSE IN2 Quality Good (GOOSE IN2) | 18E2
1155 | GOOSE3 | GOOSE IN2 Quality Bad (GOOSE IN2) | 18E3
1156 | GOOSE3 | GOOSE IN3 Quality Good (GOOSE IN3) | 18E4
1157 | GOOSE3 | GOOSE IN3 Quality Bad (GOOSE IN3) | 18E5
1158 | GOOSE3 | GOOSE IN4 Quality Good (GOOSE IN4) | 18E6
1159 | GOOSE3 | GOOSE IN4 Quality Bad (GOOSE IN4) | 18E7
1160 | GOOSE3 | GOOSE IN5 Quality Good (GOOSE IN5) | 18E8
1161 | GOOSE3 | GOOSE IN5 Quality Bad (GOOSE IN5) | 18E9
1162 | GOOSE3 | GOOSE IN6 Quality Good (GOOSE IN6) | 18E10
1163 | GOOSE3 | GOOSE IN6 Quality Bad (GOOSE IN6) | 18E11
1164 | GOOSE3 | GOOSE IN7 Quality Good (GOOSE IN7) | 18E12
1165 | GOOSE3 | GOOSE IN7 Quality Bad (GOOSE IN7) | 18E13
1166 | GOOSE3 | GOOSE IN8 Quality Good (GOOSE IN8) | 18E14
1167 | GOOSE3 | GOOSE IN8 Quality Bad (GOOSE IN8) | 18E15
1168 | GOOSE3 | GOOSE IN9 Quality Good (GOOSE IN9) | 18E16
1169 | GOOSE3 | GOOSE IN9 Quality Bad (GOOSE IN9) | 18E17
1170 | GOOSE3 | GOOSE IN10 Quality Good (GOOSE IN10) | 18E18
1171 | GOOSE3 | GOOSE IN10 Quality Bad (GOOSE IN10) | 18E19
1172 | GOOSE3 | GOOSE IN11 Quality Good (GOOSE IN11) | 18E20
1173 | GOOSE3 | GOOSE IN11 Quality Bad (GOOSE IN11) | 18E21
1174 | GOOSE3 | GOOSE IN12 Quality Good (GOOSE IN12) | 18E22
1175 | GOOSE3 | GOOSE IN12 Quality Bad (GOOSE IN12) | 18E23
1176 | GOOSE3 | GOOSE IN13 Quality Good (GOOSE IN13) | 18E24
1177 | GOOSE3 | GOOSE IN13 Quality Bad (GOOSE IN13) | 18E25
1178 | GOOSE3 | GOOSE IN14 Quality Good (GOOSE IN14) | 18E26
1179 | GOOSE3 | GOOSE IN14 Quality Bad (GOOSE IN14) | 18E27
1180 | GOOSE3 | GOOSE IN15 Quality Good (GOOSE IN15) | 18E28
1181 | GOOSE3 | GOOSE IN15 Quality Bad (GOOSE IN15) | 18E29
1182 | GOOSE3 | GOOSE IN16 Quality Good (GOOSE IN16) | 18E30
1183 | GOOSE3 | GOOSE IN16 Quality Bad (GOOSE IN16) | 18E31
1184 | GOOSE3 | GOOSE IN17 Quality Good (GOOSE IN17) | 18E32
1185 | GOOSE3 | GOOSE IN17 Quality Bad (GOOSE IN17) | 18E33
1186 | GOOSE3 | GOOSE IN18 Quality Good (GOOSE IN18) | 18E34
1187 | GOOSE3 | GOOSE IN18 Quality Bad (GOOSE IN18) | 18E35
1188 | GOOSE3 | GOOSE IN19 Quality Good (GOOSE IN19) | 18E36
1189 | GOOSE3 | GOOSE IN19 Quality Bad (GOOSE IN19) | 18E37
1190 | GOOSE3 | GOOSE IN20 Quality Good (GOOSE IN20) | 18E38
1191 | GOOSE3 | GOOSE IN20 Quality Bad (GOOSE IN20) | 18E39
1192 | GOOSE3 | GOOSE IN21 Quality Good (GOOSE IN21) | 18E40
1193 | GOOSE3 | GOOSE IN21 Quality Bad (GOOSE IN21) | 18E41
1194 | GOOSE3 | GOOSE IN22 Quality Good (GOOSE IN22) | 18E42
1195 | GOOSE3 | GOOSE IN22 Quality Bad (GOOSE IN22) | 18E43
1196 | GOOSE3 | GOOSE IN23 Quality Good (GOOSE IN23) | 18E44
1197 | GOOSE3 | GOOSE IN23 Quality Bad (GOOSE IN23) | 18E45
1198 | GOOSE3 | GOOSE IN24 Quality Good (GOOSE IN24) | 18E46
1199 | GOOSE3 | GOOSE IN24 Quality Bad (GOOSE IN24) | 18E47
1200 | GOOSE3 | GOOSE IN25 Quality Good (GOOSE IN25) | 18E48
1201 | GOOSE3 | GOOSE IN25 Quality Bad (GOOSE IN25) | 18E49
1202 | GOOSE3 | GOOSE IN26 Quality Good (GOOSE IN26) | 18E50
1203 | GOOSE3 | GOOSE IN26 Quality Bad (GOOSE IN26) | 18E51
1204 | GOOSE3 | GOOSE IN27 Quality Good (GOOSE IN27) | 18E52
1205 | GOOSE3 | GOOSE IN27 Quality Bad (GOOSE IN27) | 18E53
1206 | GOOSE3 | GOOSE IN28 Quality Good (GOOSE IN28) | 18E54
1207 | GOOSE3 | GOOSE IN28 Quality Bad (GOOSE IN28) | 18E55
1208 | GOOSE3 | GOOSE IN29 Quality Good (GOOSE IN29) | 18E56
1209 | GOOSE3 | GOOSE IN29 Quality Bad (GOOSE IN29) | 18E57
1210 | GOOSE3 | GOOSE IN30 Quality Good (GOOSE IN30) | 18E58
1211 | GOOSE3 | GOOSE IN30 Quality Bad (GOOSE IN30) | 18E59
1212 | GOOSE3 | GOOSE IN31 Quality Good (GOOSE IN31) | 18E60
1213 | GOOSE3 | GOOSE IN31 Quality Bad (GOOSE IN31) | 18E61
1214 | GOOSE3 | GOOSE IN32 Quality Good (GOOSE IN32) | 18E62
1215 | GOOSE3 | GOOSE IN32 Quality Bad (GOOSE IN32) | 18E63
1216 | GOOSE4 | GOOSE IN33 Quality Good (GOOSE IN33) | 19E0
1217 | GOOSE4 | GOOSE IN33 Quality Bad (GOOSE IN33) | 19E1
1218 | GOOSE4 | GOOSE IN34 Quality Good (GOOSE IN34) | 19E2
1219 | GOOSE4 | GOOSE IN34 Quality Bad (GOOSE IN34) | 19E3
1220 | GOOSE4 | GOOSE IN35 Quality Good (GOOSE IN35) | 19E4
1221 | GOOSE4 | GOOSE IN35 Quality Bad (GOOSE IN35) | 19E5
1222 | GOOSE4 | GOOSE IN36 Quality Good (GOOSE IN36) | 19E6
1223 | GOOSE4 | GOOSE IN36 Quality Bad (GOOSE IN36) | 19E7
1224 | GOOSE4 | GOOSE IN37 Quality Good (GOOSE IN37) | 19E8
1225 | GOOSE4 | GOOSE IN37 Quality Bad (GOOSE IN37) | 19E9
1226 | GOOSE4 | GOOSE IN38 Quality Good (GOOSE IN38) | 19E10
1227 | GOOSE4 | GOOSE IN38 Quality Bad (GOOSE IN38) | 19E11
1228 | GOOSE4 | GOOSE IN39 Quality Good (GOOSE IN39) | 19E12
1229 | GOOSE4 | GOOSE IN39 Quality Bad (GOOSE IN39) | 19E13
1230 | GOOSE4 | GOOSE IN40 Quality Good (GOOSE IN40) | 19E14
1231 | GOOSE4 | GOOSE IN40 Quality Bad (GOOSE IN40) | 19E15
1232 | GOOSE4 | GOOSE IN41 Quality Good (GOOSE IN41) | 19E16
1233 | GOOSE4 | GOOSE IN41 Quality Bad (GOOSE IN41) | 19E17
1234 | GOOSE4 | GOOSE IN42 Quality Good (GOOSE IN42) | 19E18
1235 | GOOSE4 | GOOSE IN42 Quality Bad (GOOSE IN42) | 19E19
1236 | GOOSE4 | GOOSE IN43 Quality Good (GOOSE IN43) | 19E20
1237 | GOOSE4 | GOOSE IN43 Quality Bad (GOOSE IN43) | 19E21
1238 | GOOSE4 | GOOSE IN44 Quality Good (GOOSE IN44) | 19E22
1239 | GOOSE4 | GOOSE IN44 Quality Bad (GOOSE IN44) | 19E23
1240 | GOOSE4 | GOOSE IN45 Quality Good (GOOSE IN45) | 19E24
1241 | GOOSE4 | GOOSE IN45 Quality Bad (GOOSE IN45) | 19E25
1242 | GOOSE4 | GOOSE IN46 Quality Good (GOOSE IN46) | 19E26
1243 | GOOSE4 | GOOSE IN46 Quality Bad (GOOSE IN46) | 19E27
1244 | GOOSE4 | GOOSE IN47 Quality Good (GOOSE IN47) | 19E28
1245 | GOOSE4 | GOOSE IN47 Quality Bad (GOOSE IN47) | 19E29
1246 | GOOSE4 | GOOSE IN48 Quality Good (GOOSE IN48) | 19E30
1247 | GOOSE4 | GOOSE IN48 Quality Bad (GOOSE IN48) | 19E31
1248 | GOOSE4 | GOOSE IN49 Quality Good (GOOSE IN49) | 19E32
1249 | GOOSE4 | GOOSE IN49 Quality Bad (GOOSE IN49) | 19E33
1250 | GOOSE4 | GOOSE IN50 Quality Good (GOOSE IN50) | 19E34
1251 | GOOSE4 | GOOSE IN50 Quality Bad (GOOSE IN50) | 19E35
1252 | GOOSE4 | GOOSE IN51 Quality Good (GOOSE IN51) | 19E36
1253 | GOOSE4 | GOOSE IN51 Quality Bad (GOOSE IN51) | 19E37
1254 | GOOSE4 | GOOSE IN52 Quality Good (GOOSE IN52) | 19E38
1255 | GOOSE4 | GOOSE IN52 Quality Bad (GOOSE IN52) | 19E39
1256 | GOOSE4 | GOOSE IN53 Quality Good (GOOSE IN53) | 19E40
1257 | GOOSE4 | GOOSE IN53 Quality Bad (GOOSE IN53) | 19E41
1258 | GOOSE4 | GOOSE IN54 Quality Good (GOOSE IN54) | 19E42
1259 | GOOSE4 | GOOSE IN54 Quality Bad (GOOSE IN54) | 19E43
1260 | GOOSE4 | GOOSE IN55 Quality Good (GOOSE IN55) | 19E44
1261 | GOOSE4 | GOOSE IN55 Quality Bad (GOOSE IN55) | 19E45
1262 | GOOSE4 | GOOSE IN56 Quality Good (GOOSE IN56) | 19E46
1263 | GOOSE4 | GOOSE IN56 Quality Bad (GOOSE IN56) | 19E47
1264 | GOOSE4 | GOOSE IN57 Quality Good (GOOSE IN57) | 19E48
1265 | GOOSE4 | GOOSE IN57 Quality Bad (GOOSE IN57) | 19E49
1266 | GOOSE4 | GOOSE IN58 Quality Good (GOOSE IN58) | 19E50
1267 | GOOSE4 | GOOSE IN58 Quality Bad (GOOSE IN58) | 19E51
1268 | GOOSE4 | GOOSE IN59 Quality Good (GOOSE IN59) | 19E52
1269 | GOOSE4 | GOOSE IN59 Quality Bad (GOOSE IN59) | 19E53
1270 | GOOSE4 | GOOSE IN60 Quality Good (GOOSE IN60) | 19E54
1271 | GOOSE4 | GOOSE IN60 Quality Bad (GOOSE IN60) | 19E55
1272 | GOOSE4 | GOOSE IN61 Quality Good (GOOSE IN61) | 19E56
1273 | GOOSE4 | GOOSE IN61 Quality Bad (GOOSE IN61) | 19E57
1274 | GOOSE4 | GOOSE IN62 Quality Good (GOOSE IN62) | 19E58
1275 | GOOSE4 | GOOSE IN62 Quality Bad (GOOSE IN62) | 19E59
1276 | GOOSE4 | GOOSE IN63 Quality Good (GOOSE IN63) | 19E60
1277 | GOOSE4 | GOOSE IN63 Quality Bad (GOOSE IN63) | 19E61
1278 | GOOSE4 | GOOSE IN64 Quality Good (GOOSE IN64) | 19E62
1279 | GOOSE4 | GOOSE IN64 Quality Bad (GOOSE IN64) | 19E63
1280 | NOC1 | Start ON | 20E0
1281 | NOC1 | Start OFF | 20E1
1282 | NOC1 | Trip ON | 20E2
1283 | NOC1 | Trip OFF | 20E3
1284 | NOC1 | Block ON | 20E4
1285 | NOC1 | Block OFF | 20E5
1286 | NOC1 | Phase A Start On | 20E6
1287 | NOC1 | Phase A Start Off | 20E7
1288 | NOC1 | Phase B Start On | 20E8
1289 | NOC1 | Phase B Start Off | 20E9
1290 | NOC1 | Phase C Start On | 20E10
1291 | NOC1 | Phase C Start Off | 20E11
1292 | NOC1 | Phase A Trip On | 20E12
1293 | NOC1 | Phase A Trip Off | 20E13
1294 | NOC1 | Phase B Trip On | 20E14
1295 | NOC1 | Phase B Trip Off | 20E15
1296 | NOC1 | Phase C Trip On | 20E16
1297 | NOC1 | Phase C Trip Off | 20E17
1344 | NOC2 | Start ON | 21E0
1345 | NOC2 | Start OFF | 21E1
1346 | NOC2 | Trip ON | 21E2
1347 | NOC2 | Trip OFF | 21E3
1348 | NOC2 | Block ON | 21E4
1349 | NOC2 | Block OFF | 21E5
1350 | NOC2 | Phase A Start On | 21E6
1351 | NOC2 | Phase A Start Off | 21E7
1352 | NOC2 | Phase B Start On | 21E8
1353 | NOC2 | Phase B Start Off | 21E9
1354 | NOC2 | Phase C Start On | 21E10
1355 | NOC2 | Phase C Start Off | 21E11
1356 | NOC2 | Phase A Trip On | 21E12
1357 | NOC2 | Phase A Trip Off | 21E13
1358 | NOC2 | Phase B Trip On | 21E14
1359 | NOC2 | Phase B Trip Off | 21E15
1360 | NOC2 | Phase C Trip On | 21E16
1361 | NOC2 | Phase C Trip Off | 21E17
1408 | NOC3 | Start ON | 22E0
1409 | NOC3 | Start OFF | 22E1
1410 | NOC3 | Trip ON | 22E2
1411 | NOC3 | Trip OFF | 22E3
1412 | NOC3 | Block ON | 22E4
1413 | NOC3 | Block OFF | 22E5
1414 | NOC3 | Phase A Start On | 22E6
1415 | NOC3 | Phase A Start Off | 22E7
1416 | NOC3 | Phase B Start On | 22E8
1417 | NOC3 | Phase B Start Off | 22E9
1418 | NOC3 | Phase C Start On | 22E10
1419 | NOC3 | Phase C Start Off | 22E11
1420 | NOC3 | Phase A Trip On | 22E12
1421 | NOC3 | Phase A Trip Off | 22E13
1422 | NOC3 | Phase B Trip On | 22E14
1423 | NOC3 | Phase B Trip Off | 22E15
1424 | NOC3 | Phase C Trip On | 22E16
1425 | NOC3 | Phase C Trip Off | 22E17
1472 | NOC4 | Start ON | 23E0
1473 | NOC4 | Start OFF | 23E1
1474 | NOC4 | Trip ON | 23E2
1475 | NOC4 | Trip OFF | 23E3
1476 | NOC4 | Block ON | 23E4
1477 | NOC4 | Block OFF | 23E5
1478 | NOC4 | Phase A Start On | 23E6
1479 | NOC4 | Phase A Start Off | 23E7
1480 | NOC4 | Phase B Start On | 23E8
1481 | NOC4 | Phase B Start Off | 23E9
1482 | NOC4 | Phase C Start On | 23E10
1483 | NOC4 | Phase C Start Off | 23E11
1484 | NOC4 | Phase A Trip On | 23E12
1485 | NOC4 | Phase A Trip Off | 23E13
1486 | NOC4 | Phase B Trip On | 23E14
1487 | NOC4 | Phase B Trip Off | 23E15
1488 | NOC4 | Phase C Trip On | 23E16
1489 | NOC4 | Phase C Trip Off | 23E17
1664 | NEF1 | Start ON | 26E0
1665 | NEF1 | Start OFF | 26E1
1666 | NEF1 | Trip ON | 26E2
1667 | NEF1 | Trip OFF | 26E3
1668 | NEF1 | Block ON | 26E4
1669 | NEF1 | Block OFF | 26E5
1728 | NEF2 | Start ON | 27E0
1729 | NEF2 | Start OFF | 27E1
1730 | NEF2 | Trip ON | 27E2
1731 | NEF2 | Trip OFF | 27E3
1732 | NEF2 | Block ON | 27E4
1733 | NEF2 | Block OFF | 27E5
1792 | NEF3 | Start ON | 28E0
1793 | NEF3 | Start OFF | 28E1
1794 | NEF3 | Trip ON | 28E2
1795 | NEF3 | Trip OFF | 28E3
1796 | NEF3 | Block ON | 28E4
1797 | NEF3 | Block OFF | 28E5
1856 | NEF4 | Start ON | 29E0
1857 | NEF4 | Start OFF | 29E1
1858 | NEF4 | Trip ON | 29E2
1859 | NEF4 | Trip OFF | 29E3
1860 | NEF4 | Block ON | 29E4
1861 | NEF4 | Block OFF | 29E5
2048 | CUB1 | Start ON | 32E0
2049 | CUB1 | Start OFF | 32E1
2050 | CUB1 | Trip ON | 32E2
2051 | CUB1 | Trip OFF | 32E3
2052 | CUB1 | Block ON | 32E4
2053 | CUB1 | Block OFF | 32E5
2112 | CUB2 | Start ON | 33E0
2113 | CUB2 | Start OFF | 33E1
2114 | CUB2 | Trip ON | 33E2
2115 | CUB2 | Trip OFF | 33E3
2116 | CUB2 | Block ON | 33E4
2117 | CUB2 | Block OFF | 33E5
2176 | CUB3 | Start ON | 34E0
2177 | CUB3 | Start OFF | 34E1
2178 | CUB3 | Trip ON | 34E2
2179 | CUB3 | Trip OFF | 34E3
2180 | CUB3 | Block ON | 34E4
2181 | CUB3 | Block OFF | 34E5
2240 | CUB4 | Start ON | 35E0
2241 | CUB4 | Start OFF | 35E1
2242 | CUB4 | Trip ON | 35E2
2243 | CUB4 | Trip OFF | 35E3
2244 | CUB4 | Block ON | 35E4
2245 | CUB4 | Block OFF | 35E5
2368 | HOC1 | Start ON | 37E0
2369 | HOC1 | Start OFF | 37E1
2370 | HOC1 | Trip ON | 37E2
2371 | HOC1 | Trip OFF | 37E3
2372 | HOC1 | Block ON | 37E4
2373 | HOC1 | Block OFF | 37E5
2432 | HOC2 | Start ON | 38E0
2433 | HOC2 | Start OFF | 38E1
2434 | HOC2 | Trip ON | 38E2
2435 | HOC2 | Trip OFF | 38E3
2436 | HOC2 | Block ON | 38E4
2437 | HOC2 | Block OFF | 38E5
2496 | HOC3 | Start ON | 39E0
2497 | HOC3 | Start OFF | 39E1
2498 | HOC3 | Trip ON | 39E2
2499 | HOC3 | Trip OFF | 39E3
2500 | HOC3 | Block ON | 39E4
2501 | HOC3 | Block OFF | 39E5
2560 | HOC4 | Start ON | 40E0
2561 | HOC4 | Start OFF | 40E1
2562 | HOC4 | Trip ON | 40E2
2563 | HOC4 | Trip OFF | 40E3
2564 | HOC4 | Block ON | 40E4
2565 | HOC4 | Block OFF | 40E5
2688 | CLP1 | LowStart ON | 42E0
2689 | CLP1 | LowStart OFF | 42E1
2690 | CLP1 | HighStart ON | 42E2
2691 | CLP1 | HighStart OFF | 42E3
2692 | CLP1 | LoadNormal ON | 42E4
2693 | CLP1 | LoadNormal OFF | 42E5
2694 | CLP1 | Overcurrent ON | 42E6
2695 | CLP1 | Overcurrent OFF | 42E7
2696 | CLP1 | CLPUActivated ON | 42E8
2697 | CLP1 | CLPUActivated OFF | 42E9
2698 | CLP1 | Block ON | 42E10
2699 | CLP1 | Block OFF | 42E11
2752 | FLX1 | Flocator triggered On | 43E0
2753 | FLX1 | Flocator triggered Off | 43E1
2754 | FLX1 | Flocator Calculation On | 43E2
2755 | FLX1 | Flocator Calculation Off | 43E3
2816 | CBF1 | Start ON | 44E0
2817 | CBF1 | Start OFF | 44E1
2818 | CBF1 | Retrip ON | 44E2
2819 | CBF1 | Retrip OFF | 44E3
2820 | CBF1 | CBFP ON | 44E4
2821 | CBF1 | CBFP OFF | 44E5
2822 | CBF1 | Block ON | 44E6
2823 | CBF1 | Block OFF | 44E7
2824 | CBF1 | DO monitor On | 44E8
2825 | CBF1 | DO monitor Off | 44E9
2826 | CBF1 | Signal On | 44E10
2827 | CBF1 | Signal Off | 44E11
2828 | CBF1 | Phase current On | 44E12
2829 | CBF1 | Phase current Off | 44E13
2830 | CBF1 | Res current On | 44E14
2831 | CBF1 | Res current Off | 44E15
2880 | SYN1 | SYN1 Blocked On | 45E0
2881 | SYN1 | SYN1 Blocked Off | 45E1
2882 | SYN1 | SYN1 Ok On | 45E2
2883 | SYN1 | SYN1 Ok Off | 45E3
2884 | SYN1 | SYN1 Bypass On | 45E4
2885 | SYN1 | SYN1 Bypass Off | 45E5
2886 | SYN1 | SYN1 Volt condition OK | 45E6
2887 | SYN1 | SYN1 Volt cond not match | 45E7
2888 | SYN1 | SYN1 Volt diff Ok | 45E8
2889 | SYN1 | SYN1 Volt diff out of setting | 45E9
2890 | SYN1 | SYN1 Angle diff Ok | 45E10
2891 | SYN1 | SYN1 Angle diff out of setting | 45E11
2892 | SYN1 | SYN1 Frequency diff Ok | 45E12
2893 | SYN1 | SYN1 Frequency diff out of setting | 45E13
2894 | SYN1 | SYN2 Blocked On | 45E14
2895 | SYN1 | SYN2 Blocked Off | 45E15
2896 | SYN1 | SYN2 Ok On | 45E16
2897 | SYN1 | SYN2 Ok Off | 45E17
2898 | SYN1 | SYN2 Bypass On | 45E18
2899 | SYN1 | SYN2 Bypass Off | 45E19
2900 | SYN1 | SYN2 Volt condition OK | 45E20
2901 | SYN1 | SYN2 Volt cond not match | 45E21
2902 | SYN1 | SYN2 Volt diff Ok | 45E22
2903 | SYN1 | SYN2 Volt diff out of setting | 45E23
2904 | SYN1 | SYN2 Angle diff Ok | 45E24
2905 | SYN1 | SYN2 Angle diff out of setting | 45E25
2906 | SYN1 | SYN2 Frequency diff Ok | 45E26
2907 | SYN1 | SYN2 Frequency diff out of setting | 45E27
2908 | SYN1 | SYN3 Blocked On | 45E28
2909 | SYN1 | SYN3 Blocked Off | 45E29
2910 | SYN1 | SYN3 Ok On | 45E30
2911 | SYN1 | SYN3 Ok Off | 45E31
2912 | SYN1 | SYN3 Bypass On | 45E32
2913 | SYN1 | SYN3 Bypass Off | 45E33
2914 | SYN1 | SYN3 Volt condition OK | 45E34
2915 | SYN1 | SYN3 Volt cond not match | 45E35
2916 | SYN1 | SYN3 Volt diff Ok | 45E36
2917 | SYN1 | SYN3 Volt diff out of setting | 45E37
2918 | SYN1 | SYN3 Angle diff Ok | 45E38
2919 | SYN1 | SYN3 Angle diff out of setting | 45E39
2920 | SYN1 | SYN3 Frequency diff Ok | 45E40
2921 | SYN1 | SYN3 Frequency diff out of setting | 45E41
2922 | SYN1 | SYN1 Switch On | 45E42
2923 | SYN1 | SYN1 Switch Off | 45E43
2924 | SYN1 | SYN2 Switch On | 45E44
2925 | SYN1 | SYN2 Switch Off | 45E45
2926 | SYN1 | SYN3 Switch On | 45E46
2927 | SYN1 | SYN3 Switch Off | 45E47
2944 | OBJ1 | Object Intermediate | 46E0
2945 | OBJ1 | Object Open | 46E1
2946 | OBJ1 | Object Close | 46E2
2947 | OBJ1 | Object Bad | 46E3
2948 | OBJ1 | WD Intermediate | 46E4
2949 | OBJ1 | WD Out | 46E5
2950 | OBJ1 | WD in | 46E6
2951 | OBJ1 | WD Bad | 46E7
2952 | OBJ1 | Open Request On | 46E8
2953 | OBJ1 | Open Request Off | 46E9
2954 | OBJ1 | Open Command On | 46E10
2955 | OBJ1 | Open Command Off | 46E11
2956 | OBJ1 | Close Request On | 46E12
2957 | OBJ1 | Close Request Off | 46E13
2958 | OBJ1 | Close Command On | 46E14
2959 | OBJ1 | Close Command Off | 46E15
2960 | OBJ1 | Open Blocked On | 46E16
2961 | OBJ1 | Open Blocked Off | 46E17
2962 | OBJ1 | Close Blocked On | 46E18
2963 | OBJ1 | Close Blocked Off | 46E19
2964 | OBJ1 | Object Ready | 46E20
2965 | OBJ1 | Object Not Ready | 46E21
2966 | OBJ1 | Sync Ok | 46E22
2967 | OBJ1 | Sync Not Ok | 46E23
2968 | OBJ1 | Open Command Fail | 46E24
2969 | OBJ1 | Close Command Fail | 46E25
2970 | OBJ1 | Final trip On | 46E26
2971 | OBJ1 | Final trip Off | 46E27
3008 | OBJ2 | Object Intermediate | 47E0
3009 | OBJ2 | Object Open | 47E1
3010 | OBJ2 | Object Close | 47E2
3011 | OBJ2 | Object Bad | 47E3
3012 | OBJ2 | WD Intermediate | 47E4
3013 | OBJ2 | WD Out | 47E5
3014 | OBJ2 | WD in | 47E6
3015 | OBJ2 | WD Bad | 47E7
3016 | OBJ2 | Open Request On | 47E8
3017 | OBJ2 | Open Request Off | 47E9
3018 | OBJ2 | Open Command On | 47E10
3019 | OBJ2 | Open Command Off | 47E11
3020 | OBJ2 | Close Request On | 47E12
3021 | OBJ2 | Close Request Off | 47E13
3022 | OBJ2 | Close Command On | 47E14
3023 | OBJ2 | Close Command Off | 47E15
3024 | OBJ2 | Open Blocked On | 47E16
3025 | OBJ2 | Open Blocked Off | 47E17
3026 | OBJ2 | Close Blocked On | 47E18
3027 | OBJ2 | Close Blocked Off | 47E19
3028 | OBJ2 | Object Ready | 47E20
3029 | OBJ2 | Object Not Ready | 47E21
3030 | OBJ2 | Sync Ok | 47E22
3031 | OBJ2 | Sync Not Ok | 47E23
3032 | OBJ2 | Open Command Fail | 47E24
3033 | OBJ2 | Close Command Fail | 47E25
3034 | OBJ2 | Final trip On | 47E26
3035 | OBJ2 | Final trip Off | 47E27
3072 | OBJ3 | Object Intermediate | 48E0
3073 | OBJ3 | Object Open | 48E1
3074 | OBJ3 | Object Close | 48E2
3075 | OBJ3 | Object Bad | 48E3
3076 | OBJ3 | WD Intermediate | 48E4
3077 | OBJ3 | WD Out | 48E5
3078 | OBJ3 | WD in | 48E6
3079 | OBJ3 | WD Bad | 48E7
3080 | OBJ3 | Open Request On | 48E8
3081 | OBJ3 | Open Request Off | 48E9
3082 | OBJ3 | Open Command On | 48E10
3083 | OBJ3 | Open Command Off | 48E11
3084 | OBJ3 | Close Request On | 48E12
3085 | OBJ3 | Close Request Off | 48E13
3086 | OBJ3 | Close Command On | 48E14
3087 | OBJ3 | Close Command Off | 48E15
3088 | OBJ3 | Open Blocked On | 48E16
3089 | OBJ3 | Open Blocked Off | 48E17
3090 | OBJ3 | Close Blocked On | 48E18
3091 | OBJ3 | Close Blocked Off | 48E19
3092 | OBJ3 | Object Ready | 48E20
3093 | OBJ3 | Object Not Ready | 48E21
3094 | OBJ3 | Sync Ok | 48E22
3095 | OBJ3 | Sync Not Ok | 48E23
3096 | OBJ3 | Open Command Fail | 48E24
3097 | OBJ3 | Close Command Fail | 48E25
3098 | OBJ3 | Final trip On | 48E26
3099 | OBJ3 | Final trip Off | 48E27
3136 | OBJ4 | Object Intermediate | 49E0
3137 | OBJ4 | Object Open | 49E1
3138 | OBJ4 | Object Close | 49E2
3139 | OBJ4 | Object Bad | 49E3
3140 | OBJ4 | WD Intermediate | 49E4
3141 | OBJ4 | WD Out | 49E5
3142 | OBJ4 | WD in | 49E6
3143 | OBJ4 | WD Bad | 49E7
3144 | OBJ4 | Open Request On | 49E8
3145 | OBJ4 | Open Request Off | 49E9
3146 | OBJ4 | Open Command On | 49E10
3147 | OBJ4 | Open Command Off | 49E11
3148 | OBJ4 | Close Request On | 49E12
3149 | OBJ4 | Close Request Off | 49E13
3150 | OBJ4 | Close Command On | 49E14
3151 | OBJ4 | Close Command Off | 49E15
3152 | OBJ4 | Open Blocked On | 49E16
3153 | OBJ4 | Open Blocked Off | 49E17
3154 | OBJ4 | Close Blocked On | 49E18
3155 | OBJ4 | Close Blocked Off | 49E19
3156 | OBJ4 | Object Ready | 49E20
3157 | OBJ4 | Object Not Ready | 49E21
3158 | OBJ4 | Sync Ok | 49E22
3159 | OBJ4 | Sync Not Ok | 49E23
3160 | OBJ4 | Open Command Fail | 49E24
3161 | OBJ4 | Close Command Fail | 49E25
3162 | OBJ4 | Final trip On | 49E26
3163 | OBJ4 | Final trip Off | 49E27
3200 | OBJ5 | Object Intermediate | 50E0
3201 | OBJ5 | Object Open | 50E1
3202 | OBJ5 | Object Close | 50E2
3203 | OBJ5 | Object Bad | 50E3
3204 | OBJ5 | WD Intermediate | 50E4
3205 | OBJ5 | WD Out | 50E5
3206 | OBJ5 | WD in | 50E6
3207 | OBJ5 | WD Bad | 50E7
3208 | OBJ5 | Open Request On | 50E8
3209 | OBJ5 | Open Request Off | 50E9
3210 | OBJ5 | Open Command On | 50E10
3211 | OBJ5 | Open Command Off | 50E11
3212 | OBJ5 | Close Request On | 50E12
3213 | OBJ5 | Close Request Off | 50E13
3214 | OBJ5 | Close Command On | 50E14
3215 | OBJ5 | Close Command Off | 50E15
3216 | OBJ5 | Open Blocked On | 50E16
3217 | OBJ5 | Open Blocked Off | 50E17
3218 | OBJ5 | Close Blocked On | 50E18
3219 | OBJ5 | Close Blocked Off | 50E19
3220 | OBJ5 | Object Ready | 50E20
3221 | OBJ5 | Object Not Ready | 50E21
3222 | OBJ5 | Sync Ok | 50E22
3223 | OBJ5 | Sync Not Ok | 50E23
3224 | OBJ5 | Open Command Fail | 50E24
3225 | OBJ5 | Close Command Fail | 50E25
3226 | OBJ5 | Final trip On | 50E26
3227 | OBJ5 | Final trip Off | 50E27
3264 | HSHC | HSI1 On | 51E0
3265 | HSHC | HSI1 Off | 51E1
3266 | HSHC | HSI2 On | 51E2
3267 | HSHC | HSI2 Off | 51E3
3268 | HSHC | HSI3 On | 51E4
3269 | HSHC | HSI3 Off | 51E5
3270 | HSHC | HSI4 On | 51E6
3271 | HSHC | HSI4 Off | 51E7
3272 | HSHC | HSI5 On | 51E8
3273 | HSHC | HSI5 Off | 51E9
3274 | HSHC | HSI6 On | 51E10
3275 | HSHC | HSI6 Off | 51E11
3276 | HSHC | HSI7 On | 51E12
3277 | HSHC | HSI7 Off | 51E13
3278 | HSHC | HSI8 On | 51E14
3279 | HSHC | HSI8 Off | 51E15
3280 | HSHC | HSI9 On | 51E16
3281 | HSHC | HSI9 Off | 51E17
3282 | HSHC | HSI10 On | 51E18
3283 | HSHC | HSI10 Off | 51E19
3284 | HSHC | HSI11 On | 51E20
3285 | HSHC | HSI11 Off | 51E21
3286 | HSHC | HSI12 On | 51E22
3287 | HSHC | HSI12 Off | 51E23
3328 | CTS1 | Alarm On | 52E0
3329 | CTS1 | Alarm Off | 52E1
3330 | CTS1 | Block On | 52E2
3331 | CTS1 | Block Off | 52E3
3392 | VTS1 | Bus VT fail Start On | 53E0
3393 | VTS1 | Bus VT fail Start Off | 53E1
3394 | VTS1 | Bus VT fail Trip On | 53E2
3395 | VTS1 | Bus VT fail Trip Off | 53E3
3396 | VTS1 | Bus VT fail Block On | 53E4
3397 | VTS1 | Bus VT fail Block Off | 53E5
3398 | VTS1 | Line VT fail On | 53E6
3399 | VTS1 | Line VT fail Off | 53E7
3400 | VTS1 | Bus Fuse fail On | 53E8
3401 | VTS1 | Bus Fuse fail Off | 53E9
3402 | VTS1 | Line Fuse fail On | 53E10
3403 | VTS1 | Line Fuse fail Off | 53E11
3456 | CTS2 | Alarm On | 54E0
3457 | CTS2 | Alarm Off | 54E1
3458 | CTS2 | Block On | 54E2
3459 | CTS2 | Block Off | 54E3
3520 | THD1 | THD Start Phase On | 55E0
3521 | THD1 | THD Start Phase Off | 55E1
3522 | THD1 | THD Start I01 On | 55E2
3523 | THD1 | THD Start I01 Off | 55E3
3524 | THD1 | THD Start I02 On | 55E4
3525 | THD1 | THD Start I02 Off | 55E5
3526 | THD1 | THD Alarm Phase On | 55E6
3527 | THD1 | THD Alarm Phase Off | 55E7
3528 | THD1 | THD Alarm I01 On | 55E8
3529 | THD1 | THD Alarm I01 Off | 55E9
3530 | THD1 | THD Alarm I02 On | 55E10
3531 | THD1 | THD Alarm I02 Off | 55E11
3532 | THD1 | Blocked On | 55E12
3533 | THD1 | Blocked Off | 55E13
3584 | FSP1 | Alarm On | 56E0
3585 | FSP1 | Alarm Off | 56E1
3586 | FSP1 | Inhibit On | 56E2
3587 | FSP1 | Inhibit Off | 56E3
3588 | FSP1 | Blocked On | 56E4
3589 | FSP1 | Blocked Off | 56E5
3648 | LCR1 | Max.Start time exceed On | 57E0
3649 | LCR1 | Max.Start time exceed Off | 57E1
3650 | LCR1 | Set start time exceed On | 57E2
3651 | LCR1 | Set start time exceed Off | 57E3
3652 | LCR1 | Speed Switch not received On | 57E4
3653 | LCR1 | Speed Switch not received Off | 57E5
3654 | LCR1 | Start On | 57E6
3655 | LCR1 | Start Off | 57E7
3656 | LCR1 | Set time Trip On | 57E8
3657 | LCR1 | Set time Trip Off | 57E9
3658 | LCR1 | Max cap Trip On | 57E10
3659 | LCR1 | Max cap Trip Off | 57E11
3660 | LCR1 | Blocked On | 57E12
3661 | LCR1 | Blocked Off | 57E13
3712 | CBW1 | CBWEAR1 Triggered | 58E0
3713 | CBW1 | CBWEAR1 Alarm1 On | 58E1
3714 | CBW1 | CBWEAR1 Alarm1 Off | 58E2
3715 | CBW1 | CBWEAR1 Alarm2 On | 58E3
3716 | CBW1 | CBWEAR1 Alarm2 Off | 58E4
3776 | MJP1 | Start ON | 59E0
3777 | MJP1 | Start OFF | 59E1
3778 | MJP1 | Trip ON | 59E2
3779 | MJP1 | Trip OFF | 59E3
3780 | MJP1 | Block ON | 59E4
3781 | MJP1 | Block OFF | 59E5
3840 | NUC1 | Start ON | 60E0
3841 | NUC1 | Start OFF | 60E1
3842 | NUC1 | Trip ON | 60E2
3843 | NUC1 | Trip OFF | 60E3
3844 | NUC1 | Block ON | 60E4
3845 | NUC1 | Block OFF | 60E5
3904 | SOF1 | SOTF Init On | 61E0
3905 | SOF1 | SOTF Init Off | 61E1
3906 | SOF1 | SOTF Block On | 61E2
3907 | SOF1 | SOTF Block Off | 61E3
3908 | SOF1 | SOTF Active On | 61E4
3909 | SOF1 | SOTF Active Off | 61E5
3910 | SOF1 | SOTF Trip On | 61E6
3911 | SOF1 | SOTF Trip Off | 61E7
3968 | MST1 | Motor Stopped On | 62E0
3969 | MST1 | Motor Stopped Off | 62E1
3970 | MST1 | Motor Starting On | 62E2
3971 | MST1 | Motor Starting Off | 62E3
3972 | MST1 | Motor Running On | 62E4
3973 | MST1 | Motor Running Off | 62E5
3974 | MST1 | Motor Stalled On | 62E6
3975 | MST1 | Motor Stalled Off | 62E7
3976 | MST1 | Load not symm On | 62E8
3977 | MST1 | Load not symm Off | 62E9
3978 | MST1 | Load normal On | 62E10
3979 | MST1 | Load normal Off | 62E11
3980 | MST1 | Overload On | 62E12
3981 | MST1 | Overload Off | 62E13
3982 | MST1 | High Overcurrent On | 62E14
3983 | MST1 | High Overcurrent Off | 62E15
4032 | AR1 | AR Ready On | 63E0
4033 | AR1 | AR Ready Off | 63E1
4034 | AR1 | AR Locked Reset | 63E2
4035 | AR1 | AR Reclosing request rejected On | 63E3
4036 | AR1 | AR Reclosing request rejected Off | 63E4
4037 | AR1 | AR Reclosing request On | 63E5
4038 | AR1 | AR Reclosing request Off | 63E6
4039 | AR1 | User Operated Obj AR halted and reset | 63E7
4040 | AR1 | Object failure, AR locked | 63E8
4041 | AR1 | Shot Failed | 63E9
4042 | AR1 | AR cycle end due to Discr request | 63E10
4043 | AR1 | AR Shot Clear | 63E11
4044 | AR1 | Object Close Request On | 63E12
4045 | AR1 | Object Open Request | 63E13
4046 | AR1 | Inhibit condition On | 63E14
4047 | AR1 | Inhibit condition Off | 63E15
4048 | AR1 | Locking condition On | 63E16
4049 | AR1 | Locking condition Off | 63E17
4050 | AR1 | Reserved | 63E18
4051 | AR1 | AR1 Request On | 63E19
4052 | AR1 | AR1 Request Off | 63E20
4053 | AR1 | AR2 Request On | 63E21
4054 | AR1 | AR2 Request Off | 63E22
4055 | AR1 | AR3 Request On | 63E23
4056 | AR1 | AR3 Request Off | 63E24
4057 | AR1 | AR4 Request On | 63E25
4058 | AR1 | AR4 Request Off | 63E26
4059 | AR1 | AR5 Request On | 63E27
4060 | AR1 | AR5 Request Off | 63E28
4061 | AR1 | Critical Request On | 63E29
4062 | AR1 | Critical Request Off | 63E30
4063 | AR1 | AR Running On | 63E31
4064 | AR1 | AR Running Off | 63E32
4065 | AR1 | Shot 1 Execute On | 63E33
4066 | AR1 | Shot 1 Execute Off | 63E34
4067 | AR1 | Shot 2 Execute On | 63E35
4068 | AR1 | Shot 2 Execute Off | 63E36
4069 | AR1 | Shot 3 Execute On | 63E37
4070 | AR1 | Shot 3 Execute Off | 63E38
4071 | AR1 | Shot 4 Execute On | 63E39
4072 | AR1 | Shot 4 Execute Off | 63E40
4073 | AR1 | Shot 5 Execute On | 63E41
4074 | AR1 | Shot 5 Execute Off | 63E42
4075 | AR1 | Seq Finished Final Trip Armed On | 63E43
4076 | AR1 | Final Trip Executed | 63E44
4077 | AR1 | Lock Out Time On | 63E45
4078 | AR1 | Lock Out Time Off | 63E46
4079 | AR1 | General Reclaim time On | 63E47
4080 | AR1 | General Reclaim time Off | 63E48
4081 | AR1 | Shot Start Time On | 63E49
4082 | AR1 | Shot Start Time Off | 63E50
4083 | AR1 | Dead Time On | 63E51
4084 | AR1 | Dead Time Off | 63E52
4085 | AR1 | Arc Discr Time On | 63E53
4086 | AR1 | Arc Discr Time Off | 63E54
4087 | AR1 | Shot Reclaim Time On | 63E55
4088 | AR1 | Shot Reclaim Time Off | 63E56
4089 | AR1 | Seq. finished Off | 63E57
4090 | AR1 | Final Trip Executed Off | 63E58
4091 | AR1 | Object Close Request Off | 63E59
4092 | AR1 | AR On | 63E60
4093 | AR1 | AR Off | 63E61
4094 | AR1 | AR Running (DT) On | 63E62
4095 | AR1 | AR Running (DT) Off | 63E63
4096 | DR1 | Recorder triggered On | 64E0
4097 | DR1 | Recorder triggered Off | 64E1
4098 | DR1 | Recorder memory cleared | 64E2
4099 | DR1 | Oldest record cleared | 64E3
4100 | DR1 | Recorder memory full On | 64E4
4101 | DR1 | Recorder memory full Off | 64E5
4102 | DR1 | Recording On | 64E6
4103 | DR1 | Recording Off | 64E7
4104 | DR1 | Storing recording On | 64E8
4105 | DR1 | Storing recording Off | 64E9
4106 | DR1 | Newest record cleared | 64E10
4160 | SGS | SG2 Enabled | 65E0
4161 | SGS | SG2 Disabled | 65E1
4162 | SGS | SG3 Enabled | 65E2
4163 | SGS | SG3 Disabled | 65E3
4164 | SGS | SG4 Enabled | 65E4
4165 | SGS | SG4 Disabled | 65E5
4166 | SGS | SG5 Enabled | 65E6
4167 | SGS | SG5 Disabled | 65E7
4168 | SGS | SG6 Enabled | 65E8
4169 | SGS | SG6 Disabled | 65E9
4170 | SGS | SG7 Enabled | 65E10
4171 | SGS | SG7 Disabled | 65E11
4172 | SGS | SG8 Enabled | 65E12
4173 | SGS | SG8 Disabled | 65E13
4174 | SGS | SG1 Request On | 65E14
4175 | SGS | SG1 Request Off | 65E15
4176 | SGS | SG2 Request On | 65E16
4177 | SGS | SG2 Request Off | 65E17
4178 | SGS | SG3 Request On | 65E18
4179 | SGS | SG3 Request Off | 65E19
4180 | SGS | SG4 Request On | 65E20
4181 | SGS | SG4 Request Off | 65E21
4182 | SGS | SG5 Request On | 65E22
4183 | SGS | SG5 Request Off | 65E23
4184 | SGS | SG6 Request On | 65E24
4185 | SGS | SG6 Request Off | 65E25
4186 | SGS | SG7 Request On | 65E26
4187 | SGS | SG7 Request Off | 65E27
4188 | SGS | SG8 Request On | 65E28
4189 | SGS | SG8 Request Off | 65E29
4190 | SGS | Remote Change SG Req On | 65E30
4191 | SGS | Remote Change SG Req Off | 65E31
4192 | SGS | Local Change SG Req On | 65E32
4193 | SGS | Local Change SG Req On | 65E33
4194 | SGS | Force Change SG On | 65E34
4195 | SGS | Force Change SG Off | 65E35
4196 | SGS | SG Req. Fail Not configured SG On | 65E36
4197 | SGS | SG Req. Fail Not configured SG On | 65E37
4198 | SGS | Force Req. Fail Force not On | 65E38
4199 | SGS | Force Req. Fail Off | 65E39
4200 | SGS | SG Req. Fail Lower priority Req. On | 65E40
4201 | SGS | SG Req. Fail Lower priority Req. Off | 65E41
4202 | SGS | SG1 Active On | 65E42
4203 | SGS | SG1 Active Off | 65E43
4204 | SGS | SG2 Active On | 65E44
4205 | SGS | SG2 Active Off | 65E45
4206 | SGS | SG3 Active On | 65E46
4207 | SGS | SG3 Active Off | 65E47
4208 | SGS | SG4 Active On | 65E48
4209 | SGS | SG4 Active Off | 65E49
4210 | SGS | SG5 Active On | 65E50
4211 | SGS | SG5 Active Off | 65E51
4212 | SGS | SG6 Active On | 65E52
4213 | SGS | SG6 Active Off | 65E53
4214 | SGS | SG7 Active On | 65E54
4215 | SGS | SG7 Active Off | 65E55
4216 | SGS | SG8 Active On | 65E56
4217 | SGS | SG8 Active Off | 65E57
4224 | REF1 | REF Trip On | 66E0
4225 | REF1 | REF Trip Off | 66E1
4226 | REF1 | REF Block On | 66E2
4227 | REF1 | REF Block Off | 66E3
4288 | TOLF1 | Alarm1 On | 67E0
4289 | TOLF1 | Alarm1 Off | 67E1
4290 | TOLF1 | Alarm2 On | 67E2
4291 | TOLF1 | Alarm2 Off | 67E3
4292 | TOLF1 | Inhibit On | 67E4
4293 | TOLF1 | Inhibit Off | 67E5
4294 | TOLF1 | Trip On | 67E6
4295 | TOLF1 | Trip Off | 67E7
4296 | TOLF1 | Block On | 67E8
4297 | TOLF1 | Block Off | 67E9
4352 | TOLM1 | Alarm1 On | 68E0
4353 | TOLM1 | Alarm1 Off | 68E1
4354 | TOLM1 | Alarm2 On | 68E2
4355 | TOLM1 | Alarm2 Off | 68E3
4356 | TOLM1 | Inhibit On | 68E4
4357 | TOLM1 | Inhibit Off | 68E5
4358 | TOLM1 | Trip On | 68E6
4359 | TOLM1 | Trip Off | 68E7
4360 | TOLM1 | Block On | 68E8
4361 | TOLM1 | Block Off | 68E9
4416 | RTD1 | S1 Alarm1 On | 69E0
4417 | RTD1 | S1 Alarm1 Off | 69E1
4418 | RTD1 | S1 Alarm2 On | 69E2
4419 | RTD1 | S1 Alarm2 Off | 69E3
4420 | RTD1 | S2 Alarm1 On | 69E4
4421 | RTD1 | S2 Alarm1 Off | 69E5
4422 | RTD1 | S2 Alarm2 On | 69E6
4423 | RTD1 | S2 Alarm2 Off | 69E7
4424 | RTD1 | S3 Alarm1 On | 69E8
4425 | RTD1 | S3 Alarm1 Off | 69E9
4426 | RTD1 | S3 Alarm2 On | 69E10
4427 | RTD1 | S3 Alarm2 Off | 69E11
4428 | RTD1 | S4 Alarm1 On | 69E12
4429 | RTD1 | S4 Alarm1 Off | 69E13
4430 | RTD1 | S4 Alarm2 On | 69E14
4431 | RTD1 | S4 Alarm2 Off | 69E15
4432 | RTD1 | S5 Alarm1 On | 69E16
4433 | RTD1 | S5 Alarm1 Off | 69E17
4434 | RTD1 | S5 Alarm2 On | 69E18
4435 | RTD1 | S5 Alarm2 Off | 69E19
4436 | RTD1 | S6 Alarm1 On | 69E20
4437 | RTD1 | S6 Alarm1 Off | 69E21
4438 | RTD1 | S6 Alarm2 On | 69E22
4439 | RTD1 | S6 Alarm2 Off | 69E23
4440 | RTD1 | S7 Alarm1 On | 69E24
4441 | RTD1 | S7 Alarm1 Off | 69E25
4442 | RTD1 | S7 Alarm2 On | 69E26
4443 | RTD1 | S7 Alarm2 Off | 69E27
4444 | RTD1 | S8 Alarm1 On | 69E28
4445 | RTD1 | S8 Alarm1 Off | 69E29
4446 | RTD1 | S8 Alarm2 On | 69E30
4447 | RTD1 | S8 Alarm2 Off | 69E31
4448 | RTD1 | S9 Alarm1 On | 69E32
4449 | RTD1 | S9 Alarm1 Off | 69E33
4450 | RTD1 | S9 Alarm2 On | 69E34
4451 | RTD1 | S9 Alarm2 Off | 69E35
4452 | RTD1 | S10 Alarm1 On | 69E36
4453 | RTD1 | S10 Alarm1 Off | 69E37
4454 | RTD1 | S10 Alarm2 On | 69E38
4455 | RTD1 | S10 Alarm2 Off | 69E39
4456 | RTD1 | S11 Alarm1 On | 69E40
4457 | RTD1 | S11 Alarm1 Off | 69E41
4458 | RTD1 | S11 Alarm2 On | 69E42
4459 | RTD1 | S11 Alarm2 Off | 69E43
4460 | RTD1 | S12 Alarm1 On | 69E44
4461 | RTD1 | S12 Alarm1 Off | 69E45
4462 | RTD1 | S12 Alarm2 On | 69E46
4463 | RTD1 | S12 Alarm2 Off | 69E47
4464 | RTD1 | S13 Alarm1 On | 69E48
4465 | RTD1 | S13 Alarm1 Off | 69E49
4466 | RTD1 | S13 Alarm2 On | 69E50
4467 | RTD1 | S13 Alarm2 Off | 69E51
4468 | RTD1 | S14 Alarm1 On | 69E52
4469 | RTD1 | S14 Alarm1 Off | 69E53
4470 | RTD1 | S14 Alarm2 On | 69E54
4471 | RTD1 | S14 Alarm2 Off | 69E55
4472 | RTD1 | S15 Alarm1 On | 69E56
4473 | RTD1 | S15 Alarm1 Off | 69E57
4474 | RTD1 | S15 Alarm2 On | 69E58
4475 | RTD1 | S15 Alarm2 Off | 69E59
4476 | RTD1 | S16 Alarm1 On | 69E60
4477 | RTD1 | S16 Alarm1 Off | 69E61
4478 | RTD1 | S16 Alarm2 On | 69E62
4479 | RTD1 | S16 Alarm2 Off | 69E63
4480 | RTD2 | S1 Meas Ok | 70E0
4481 | RTD2 | S1 Meas Invalid | 70E1
4482 | RTD2 | S2 Meas Ok | 70E2
4483 | RTD2 | S2 Meas Invalid | 70E3
4484 | RTD2 | S3 Meas Ok | 70E4
4485 | RTD2 | S3 Meas Invalid | 70E5
4486 | RTD2 | S4 Meas Ok | 70E6
4487 | RTD2 | S4 Meas Invalid | 70E7
4488 | RTD2 | S5 Meas Ok | 70E8
4489 | RTD2 | S5 Meas Invalid | 70E9
4490 | RTD2 | S6 Meas Ok | 70E10
4491 | RTD2 | S6 Meas Invalid | 70E11
4492 | RTD2 | S7 Meas Ok | 70E12
4493 | RTD2 | S7 Meas Invalid | 70E13
4494 | RTD2 | S8 Meas Ok | 70E14
4495 | RTD2 | S8 Meas Invalid | 70E15
4496 | RTD2 | S9 Meas Ok | 70E16
4497 | RTD2 | S9 Meas Invalid | 70E17
4498 | RTD2 | S10 Meas Ok | 70E18
4499 | RTD2 | S10 Meas Invalid | 70E19
4500 | RTD2 | S11 Meas Ok | 70E20
4501 | RTD2 | S11 Meas Invalid | 70E21
4502 | RTD2 | S12 Meas Ok | 70E22
4503 | RTD2 | S12 Meas Invalid | 70E23
4504 | RTD2 | S13 Meas Ok | 70E24
4505 | RTD2 | S13 Meas Invalid | 70E25
4506 | RTD2 | S14 Meas Ok | 70E26
4507 | RTD2 | S14 Meas Invalid | 70E27
4508 | RTD2 | S15 Meas Ok | 70E28
4509 | RTD2 | S15 Meas Invalid | 70E29
4510 | RTD2 | S16 Meas Ok | 70E30
4511 | RTD2 | S16 Meas Invalid | 70E31
4544 | DIF1 | Idb> Trip On | 71E0
4545 | DIF1 | Idb> Trip Off | 71E1
4546 | DIF1 | Idb> Blocked (ext) On | 71E2
4547 | DIF1 | Idb> Blocked (ext) Off | 71E3
4548 | DIF1 | Idi> Trip On | 71E4
4549 | DIF1 | Idi> Trip Off | 71E5
4550 | DIF1 | Idi> Blocked (ext) On | 71E6
4551 | DIF1 | Idi> Blocked (ext) Off | 71E7
4552 | DIF1 | 2.nd Harmonic Block On | 71E8
4553 | DIF1 | 2.nd Harmonic Block Off | 71E9
4554 | DIF1 | 5.th Harmonic Block On | 71E10
4555 | DIF1 | 5.th Harmonic Block Off | 71E11
4556 | DIF1 | L1 2.nd harm On | 71E12
4557 | DIF1 | L1 2.nd harm Off | 71E13
4558 | DIF1 | L2 2.nd harm On | 71E14
4559 | DIF1 | L2 2.nd harm Off | 71E15
4560 | DIF1 | L3 2.nd harm On | 71E16
4561 | DIF1 | L3 2.nd harm Off | 71E17
4562 | DIF1 | L1 5.th harm On | 71E18
4563 | DIF1 | L1 5.th harm Off | 71E19
4564 | DIF1 | L2 5.th harm On | 71E20
4565 | DIF1 | L2 5.th harm Off | 71E21
4566 | DIF1 | L3 5.th harm On | 71E22
4567 | DIF1 | L3 5.th harm Off | 71E23
4568 | DIF1 | HV I0d> Block On | 71E24
4569 | DIF1 | HV I0d> Block Off | 71E25
4570 | DIF1 | HV I0d> Trip On | 71E26
4571 | DIF1 | HV I0d> Trip Off | 71E27
4572 | DIF1 | LV I0d> Block On | 71E28
4573 | DIF1 | LV I0d> Block Off | 71E29
4574 | DIF1 | LV I0d> Trip On | 71E30
4575 | DIF1 | LV I0d> Trip Off | 71E31
4608 | TRF1 | Light/No load On | 72E0
4609 | TRF1 | Light/No load Off | 72E1
4610 | TRF1 | HV side inrush On | 72E2
4611 | TRF1 | HV side inrush Off | 72E3
4612 | TRF1 | LV side inrush On | 72E4
4613 | TRF1 | LV side inrush Off | 72E5
4614 | TRF1 | Load normal On | 72E6
4615 | TRF1 | Load normal Off | 72E7
4616 | TRF1 | Overloading On | 72E8
4617 | TRF1 | Overloading Off | 72E9
4618 | TRF1 | High overload On | 72E10
4619 | TRF1 | High overload Off | 72E11
4620 | TRF1 | Setting changes, calculating new trafo data | 72E12
4621 | TRF1 | Calculation finished, possible restart | 72E13
4672 | TOLT1 | Alarm1 On | 73E0
4673 | TOLT1 | Alarm1 Off | 73E1
4674 | TOLT1 | Alarm2 On | 73E2
4675 | TOLT1 | Alarm2 Off | 73E3
4676 | TOLT1 | Inhibit On | 73E4
4677 | TOLT1 | Inhibit Off | 73E5
4678 | TOLT1 | Trip On | 73E6
4679 | TOLT1 | Trip Off | 73E7
4680 | TOLT1 | Block On | 73E8
4681 | TOLT1 | Block Off | 73E9
4736 | ARC1 | Zone1 Trip On | 74E0
4737 | ARC1 | Zone1 Trip Off | 74E1
4738 | ARC1 | Zone1 Block On | 74E2
4739 | ARC1 | Zone1 BlockOff | 74E3
4740 | ARC1 | Zone2 Trip On | 74E4
4741 | ARC1 | Zone2 Trip Off | 74E5
4742 | ARC1 | Zone2 Block On | 74E6
4743 | ARC1 | Zone2 BlockOff | 74E7
4744 | ARC1 | Zone3 Trip On | 74E8
4745 | ARC1 | Zone3 Trip Off | 74E9
4746 | ARC1 | Zone3 Block On | 74E10
4747 | ARC1 | Zone3 BlockOff | 74E11
4748 | ARC1 | Zone4 Trip On | 74E12
4749 | ARC1 | Zone4 Trip Off | 74E13
4750 | ARC1 | Zone4 Block On | 74E14
4751 | ARC1 | Zone4 BlockOff | 74E15
4752 | ARC1 | Ph Current Blocked On | 74E16
4753 | ARC1 | Ph Current Blocked Off | 74E17
4754 | ARC1 | Ph Current Start On | 74E18
4755 | ARC1 | Ph Current Start Off | 74E19
4756 | ARC1 | Res Current Blocked On | 74E20
4757 | ARC1 | Res Current Blocked Off | 74E21
4758 | ARC1 | Res Current Start On | 74E22
4759 | ARC1 | Res Current Start Off | 74E23
4760 | ARC1 | Channel 1 Light On | 74E24
4761 | ARC1 | Channel 1 Light Off | 74E25
4762 | ARC1 | Channel 1 Pressure On | 74E26
4763 | ARC1 | Channel 1 Pressure Off | 74E27
4764 | ARC1 | Channel 2 Light On | 74E28
4765 | ARC1 | Channel 2 Light Off | 74E29
4766 | ARC1 | Channel 2 Pressure On | 74E30
4767 | ARC1 | Channel 2 Pressure Off | 74E31
4768 | ARC1 | Channel 3 Light On | 74E32
4769 | ARC1 | Channel 3 Light Off | 74E33
4770 | ARC1 | Channel 3 Pressure On | 74E34
4771 | ARC1 | Channel 3 Pressure Off | 74E35
4772 | ARC1 | Channel 4 Light On | 74E36
4773 | ARC1 | Channel 4 Light Off | 74E37
4774 | ARC1 | Channel 4 Pressure On | 74E38
4775 | ARC1 | Channel 4 Pressure Off | 74E39
4776 | ARC1 | DI Signal On | 74E40
4777 | ARC1 | DI Signal Off | 74E41
4800 | DOC1 | Start ON | 75E0
4801 | DOC1 | Start OFF | 75E1
4802 | DOC1 | Trip ON | 75E2
4803 | DOC1 | Trip OFF | 75E3
4804 | DOC1 | Block ON | 75E4
4805 | DOC1 | Block OFF | 75E5
4806 | DOC1 | No voltage, Protection locked On | 75E6
4807 | DOC1 | Voltage measurable, Protection locked Off | 75E7
4808 | DOC1 | Measuring live angle On | 75E8
4809 | DOC1 | Measuring live angle Off | 75E9
4810 | DOC1 | Using voltmem On | 75E10
4811 | DOC1 | Using voltmem Off | 75E11
4813 | DOC1 | Voltage mem Off Emergency non dir On | 75E13
4814 | DOC1 | Voltage mem Off Emergency non dir Off | 75E14
4864 | DOC2 | Start ON | 76E0
4865 | DOC2 | Start OFF | 76E1
4866 | DOC2 | Trip ON | 76E2
4867 | DOC2 | Trip OFF | 76E3
4868 | DOC2 | Block ON | 76E4
4869 | DOC2 | Block OFF | 76E5
4870 | DOC2 | No voltage, Protection locked On | 76E6
4871 | DOC2 | Voltage measurable, Protection locked Off | 76E7
4872 | DOC2 | Measuring live angle On | 76E8
4873 | DOC2 | Measuring live angle Off | 76E9
4874 | DOC2 | Using voltmem On | 76E10
4875 | DOC2 | Using voltmem Off | 76E11
4877 | DOC2 | Voltage mem Off Emergency non dir On | 76E13
4878 | DOC2 | Voltage mem Off Emergency non dir Off | 76E14
4928 | DOC3 | Start ON | 77E0
4929 | DOC3 | Start OFF | 77E1
4930 | DOC3 | Trip ON | 77E2
4931 | DOC3 | Trip OFF | 77E3
4932 | DOC3 | Block ON | 77E4
4933 | DOC3 | Block OFF | 77E5
4934 | DOC3 | No voltage, Protection locked On | 77E6
4935 | DOC3 | Voltage measurable, Protection locked Off | 77E7
4936 | DOC3 | Measuring live angle On | 77E8
4937 | DOC3 | Measuring live angle Off | 77E9
4938 | DOC3 | Using voltmem On | 77E10
4939 | DOC3 | Using voltmem Off | 77E11
4941 | DOC3 | Voltage mem Off Emergency non dir On | 77E13
4942 | DOC3 | Voltage mem Off Emergency non dir Off | 77E14
4992 | DOC4 | Start ON | 78E0
4993 | DOC4 | Start OFF | 78E1
4994 | DOC4 | Trip ON | 78E2
4995 | DOC4 | Trip OFF | 78E3
4996 | DOC4 | Block ON | 78E4
4997 | DOC4 | Block OFF | 78E5
4998 | DOC4 | No voltage, Protection locked On | 78E6
4999 | DOC4 | Voltage measurable, Protection locked Off | 78E7
5000 | DOC4 | Measuring live angle On | 78E8
5001 | DOC4 | Measuring live angle Off | 78E9
5002 | DOC4 | Using voltmem On | 78E10
5003 | DOC4 | Using voltmem Off | 78E11
5005 | DOC4 | Voltage mem Off Emergency non dir On | 78E13
5006 | DOC4 | Voltage mem Off Emergency non dir Off | 78E14
5184 | DEF1 | Start ON | 81E0
5185 | DEF1 | Start OFF | 81E1
5186 | DEF1 | Trip ON | 81E2
5187 | DEF1 | Trip OFF | 81E3
5188 | DEF1 | Block ON | 81E4
5189 | DEF1 | Block OFF | 81E5
5190 | DEF1 | I0Cosfi Start On | 81E6
5191 | DEF1 | I0Cosfi Start Off | 81E7
5192 | DEF1 | I0Sinfi Start On | 81E8
5193 | DEF1 | I0Sinfi Start Off | 81E9
5194 | DEF1 | I0Cosfi Trip On | 81E10
5195 | DEF1 | I0Cosfi Trip Off | 81E11
5196 | DEF1 | I0Sinfi Trip On | 81E12
5197 | DEF1 | I0Sinfi Trip Off | 81E13
5248 | DEF2 | Start ON | 82E0
5249 | DEF2 | Start OFF | 82E1
5250 | DEF2 | Trip ON | 82E2
5251 | DEF2 | Trip OFF | 82E3
5252 | DEF2 | Block ON | 82E4
5253 | DEF2 | Block OFF | 82E5
5254 | DEF2 | I0Cosfi Start On | 82E6
5255 | DEF2 | I0Cosfi Start Off | 82E7
5256 | DEF2 | I0Sinfi Start On | 82E8
5257 | DEF2 | I0Sinfi Start Off | 82E9
5258 | DEF2 | I0Cosfi Trip On | 82E10
5259 | DEF2 | I0Cosfi Trip Off | 82E11
5260 | DEF2 | I0Sinfi Trip On | 82E12
5261 | DEF2 | I0Sinfi Trip Off | 82E13
5312 | DEF3 | Start ON | 83E0
5313 | DEF3 | Start OFF | 83E1
5314 | DEF3 | Trip ON | 83E2
5315 | DEF3 | Trip OFF | 83E3
5316 | DEF3 | Block ON | 83E4
5317 | DEF3 | Block OFF | 83E5
5318 | DEF3 | I0Cosfi Start On | 83E6
5319 | DEF3 | I0Cosfi Start Off | 83E7
5320 | DEF3 | I0Sinfi Start On | 83E8
5321 | DEF3 | I0Sinfi Start Off | 83E9
5322 | DEF3 | I0Cosfi Trip On | 83E10
5323 | DEF3 | I0Cosfi Trip Off | 83E11
5324 | DEF3 | I0Sinfi Trip On | 83E12
5325 | DEF3 | I0Sinfi Trip Off | 83E13
5376 | DEF4 | Start ON | 84E0
5377 | DEF4 | Start OFF | 84E1
5378 | DEF4 | Trip ON | 84E2
5379 | DEF4 | Trip OFF | 84E3
5380 | DEF4 | Block ON | 84E4
5381 | DEF4 | Block OFF | 84E5
5382 | DEF4 | I0Cosfi Start On | 84E6
5383 | DEF4 | I0Cosfi Start Off | 84E7
5384 | DEF4 | I0Sinfi Start On | 84E8
5385 | DEF4 | I0Sinfi Start Off | 84E9
5386 | DEF4 | I0Cosfi Trip On | 84E10
5387 | DEF4 | I0Cosfi Trip Off | 84E11
5388 | DEF4 | I0Sinfi Trip On | 84E12
5389 | DEF4 | I0Sinfi Trip Off | 84E13
5440 | OV1 | Start ON | 85E0
5441 | OV1 | Start OFF | 85E1
5442 | OV1 | Trip ON | 85E2
5443 | OV1 | Trip OFF | 85E3
5444 | OV1 | Block ON | 85E4
5445 | OV1 | Block OFF | 85E5
5504 | OV2 | Start ON | 86E0
5505 | OV2 | Start OFF | 86E1
5506 | OV2 | Trip ON | 86E2
5507 | OV2 | Trip OFF | 86E3
5508 | OV2 | Block ON | 86E4
5509 | OV2 | Block OFF | 86E5
5568 | OV3 | Start ON | 87E0
5569 | OV3 | Start OFF | 87E1
5570 | OV3 | Trip ON | 87E2
5571 | OV3 | Trip OFF | 87E3
5572 | OV3 | Block ON | 87E4
5573 | OV3 | Block OFF | 87E5
5632 | OV4 | Start ON | 88E0
5633 | OV4 | Start OFF | 88E1
5634 | OV4 | Trip ON | 88E2
5635 | OV4 | Trip OFF | 88E3
5636 | OV4 | Block ON | 88E4
5637 | OV4 | Block OFF | 88E5
5696 | UV1 | Start ON | 89E0
5697 | UV1 | Start OFF | 89E1
5698 | UV1 | Trip ON | 89E2
5699 | UV1 | Trip OFF | 89E3
5700 | UV1 | Block ON | 89E4
5701 | UV1 | Block OFF | 89E5
5702 | UV1 | Undervoltage Block On | 89E6
5703 | UV1 | Undervoltage Block Off | 89E7
5760 | UV2 | Start ON | 90E0
5761 | UV2 | Start OFF | 90E1
5762 | UV2 | Trip ON | 90E2
5763 | UV2 | Trip OFF | 90E3
5764 | UV2 | Block ON | 90E4
5765 | UV2 | Block OFF | 90E5
5766 | UV2 | Undervoltage Block On | 90E6
5767 | UV2 | Undervoltage Block Off | 90E7
5824 | UV3 | Start ON | 91E0
5825 | UV3 | Start OFF | 91E1
5826 | UV3 | Trip ON | 91E2
5827 | UV3 | Trip OFF | 91E3
5828 | UV3 | Block ON | 91E4
5829 | UV3 | Block OFF | 91E5
5830 | UV3 | Undervoltage Block On | 91E6
5831 | UV3 | Undervoltage Block Off | 91E7
5888 | UV4 | Start ON | 92E0
5889 | UV4 | Start OFF | 92E1
5890 | UV4 | Trip ON | 92E2
5891 | UV4 | Trip OFF | 92E3
5892 | UV4 | Block ON | 92E4
5893 | UV4 | Block OFF | 92E5
5894 | UV4 | Undervoltage Block On | 92E6
5895 | UV4 | Undervoltage Block Off | 92E7
5952 | NOV1 | Start ON | 93E0
5953 | NOV1 | Start OFF | 93E1
5954 | NOV1 | Trip ON | 93E2
5955 | NOV1 | Trip OFF | 93E3
5956 | NOV1 | Block ON | 93E4
5957 | NOV1 | Block OFF | 93E5
6016 | NOV2 | Start ON | 94E0
6017 | NOV2 | Start OFF | 94E1
6018 | NOV2 | Trip ON | 94E2
6019 | NOV2 | Trip OFF | 94E3
6020 | NOV2 | Block ON | 94E4
6021 | NOV2 | Block OFF | 94E5
6080 | NOV3 | Start ON | 95E0
6081 | NOV3 | Start OFF | 95E1
6082 | NOV3 | Trip ON | 95E2
6083 | NOV3 | Trip OFF | 95E3
6084 | NOV3 | Block ON | 95E4
6085 | NOV3 | Block OFF | 95E5
6144 | NOV4 | Start ON | 96E0
6145 | NOV4 | Start OFF | 96E1
6146 | NOV4 | Trip ON | 96E2
6147 | NOV4 | Trip OFF | 96E3
6148 | NOV4 | Block ON | 96E4
6149 | NOV4 | Block OFF | 96E5
6208 | NJK1 | U0RECL Request On | 97E0
6209 | NJK1 | U0RECL Request Off | 97E1
6210 | NJK1 | U0RECL Blocked On | 97E2
6211 | NJK1 | U0RECL Blocked Off | 97E3
6212 | NJK1 | U0RECL Active On | 97E4
6213 | NJK1 | U0RECL Active Off | 97E5
6214 | NJK1 | U0RECL Breaker close request On | 97E6
6215 | NJK1 | U0RECL Breaker close request Off | 97E7
6216 | NJK1 | U0RECL U0 Blocking On | 97E8
6217 | NJK1 | U0RECL U0 Blocking Off | 97E9
6272 | FRQC1 | f> [Curr] Start ON | 98E0
6273 | FRQC1 | f> [Curr] Start OFF | 98E1
6274 | FRQC1 | f> [Curr] Trip ON | 98E2
6275 | FRQC1 | f> [Curr] Trip OFF | 98E3
6276 | FRQC1 | f>>[Curr] Start ON | 98E4
6277 | FRQC1 | f>> [Curr] Start OFF | 98E5
6278 | FRQC1 | f>> [Curr] Trip ON | 98E6
6279 | FRQC1 | f>> [Curr] Trip OFF | 98E7
6280 | FRQC1 | f>>> [Curr] Start ON | 98E8
6281 | FRQC1 | f>>> [Curr] Start OFF | 98E9
6282 | FRQC1 | f>>> [Curr] Trip ON | 98E10
6283 | FRQC1 | f>>> [Curr] Trip OFF | 98E11
6284 | FRQC1 | f>>>> [Curr] Start ON | 98E12
6285 | FRQC1 | f>>>> [Curr] Start OFF | 98E13
6286 | FRQC1 | f>>>> [Curr] Trip ON | 98E14
6287 | FRQC1 | f>>>> [Curr] Trip OFF | 98E15
6288 | FRQC1 | f< [Curr] Start ON | 98E16
6289 | FRQC1 | f< [Curr] Start OFF | 98E17
6290 | FRQC1 | f< [Curr] Trip ON | 98E18
6291 | FRQC1 | f< [Curr] Trip OFF | 98E19
6292 | FRQC1 | f<< [Curr] Start ON | 98E20
6293 | FRQC1 | f<< [Curr] Start OFF | 98E21
6294 | FRQC1 | f<< [Curr] Trip ON | 98E22
6295 | FRQC1 | f<< [Curr] Trip OFF | 98E23
6296 | FRQC1 | f<<< [Curr] Start ON | 98E24
6297 | FRQC1 | f<<< [Curr] Start OFF | 98E25
6298 | FRQC1 | f<<< [Curr] Trip ON | 98E26
6299 | FRQC1 | f<<< [Curr] Trip OFF | 98E27
6300 | FRQC1 | f<<<< [Curr] Start ON | 98E28
6301 | FRQC1 | f<<<< [Curr] Start OFF | 98E29
6302 | FRQC1 | f<<<< [Curr] Trip ON | 98E30
6303 | FRQC1 | f<<<< [Curr] Trip OFF | 98E31
6304 | FRQC1 | f> [Curr] Block ON | 98E32
6305 | FRQC1 | f> [Curr] Block OFF | 98E33
6306 | FRQC1 | f>> [Curr] Block ON | 98E34
6307 | FRQC1 | f>> [Curr] Block OFF | 98E35
6308 | FRQC1 | f>>> [Curr] Block ON | 98E36
6309 | FRQC1 | f>>> [Curr] Block OFF | 98E37
6310 | FRQC1 | f>>>> [Curr] Block ON | 98E38
6311 | FRQC1 | f>>>> [Curr] Block OFF | 98E39
6312 | FRQC1 | f< [Curr] Block ON | 98E40
6313 | FRQC1 | f< [Curr] Block OFF | 98E41
6314 | FRQC1 | f<< [Curr] Block ON | 98E42
6315 | FRQC1 | f<< [Curr] Block OFF | 98E43
6316 | FRQC1 | f<<< [Curr] Block ON | 98E44
6317 | FRQC1 | f<<< [Curr] Block OFF | 98E45
6318 | FRQC1 | f<<<< [Curr] Block ON | 98E46
6319 | FRQC1 | f<<<< [Curr] Block OFF | 98E47
6320 | FRQC1 | Meas Curr Ok for f [curr] | 98E48
6321 | FRQC1 | Meas Curr too low, f [curr] blocked | 98E49
6336 | FRQV1 | f> Start ON | 99E0
6337 | FRQV1 | f> Start OFF | 99E1
6338 | FRQV1 | f> Trip ON | 99E2
6339 | FRQV1 | f> Trip OFF | 99E3
6340 | FRQV1 | f>> Start ON | 99E4
6341 | FRQV1 | f>> Start OFF | 99E5
6342 | FRQV1 | f>> Trip ON | 99E6
6343 | FRQV1 | f>> Trip OFF | 99E7
6344 | FRQV1 | f>>> Start ON | 99E8
6345 | FRQV1 | f>>> Start OFF | 99E9
6346 | FRQV1 | f>>> Trip ON | 99E10
6347 | FRQV1 | f>>> Trip OFF | 99E11
6348 | FRQV1 | f>>>> Start ON | 99E12
6349 | FRQV1 | f>>>> Start OFF | 99E13
6350 | FRQV1 | f>>>> Trip ON | 99E14
6351 | FRQV1 | f>>>> Trip OFF | 99E15
6352 | FRQV1 | f< Start ON | 99E16
6353 | FRQV1 | f< Start OFF | 99E17
6354 | FRQV1 | f< Trip ON | 99E18
6355 | FRQV1 | f< Trip OFF | 99E19
6356 | FRQV1 | f<< Start ON | 99E20
6357 | FRQV1 | f<< Start OFF | 99E21
6358 | FRQV1 | f<< Trip ON | 99E22
6359 | FRQV1 | f<< Trip OFF | 99E23
6360 | FRQV1 | f<<< Start ON | 99E24
6361 | FRQV1 | f<<< Start OFF | 99E25
6362 | FRQV1 | f<<< Trip ON | 99E26
6363 | FRQV1 | f<<< Trip OFF | 99E27
6364 | FRQV1 | f<<<< Start ON | 99E28
6365 | FRQV1 | f<<<< Start OFF | 99E29
6366 | FRQV1 | f<<<< Trip ON | 99E30
6367 | FRQV1 | f<<<< Trip OFF | 99E31
6368 | FRQV1 | f> Block ON | 99E32
6369 | FRQV1 | f> Block OFF | 99E33
6370 | FRQV1 | f>> Block ON | 99E34
6371 | FRQV1 | f>> Block OFF | 99E35
6372 | FRQV1 | f>>> Block ON | 99E36
6373 | FRQV1 | f>>> Block OFF | 99E37
6374 | FRQV1 | f>>>> Block ON | 99E38
6375 | FRQV1 | f>>>> Block OFF | 99E39
6376 | FRQV1 | f< Block ON | 99E40
6377 | FRQV1 | f< Block OFF | 99E41
6378 | FRQV1 | f<< Block ON | 99E42
6379 | FRQV1 | f<< Block OFF | 99E43
6380 | FRQV1 | f<<< Block ON | 99E44
6381 | FRQV1 | f<<< Block OFF | 99E45
6382 | FRQV1 | f<<<< Block ON | 99E46
6383 | FRQV1 | f<<<< Block OFF | 99E47
6400 | OPW1 | Start ON | 100E0
6401 | OPW1 | Start OFF | 100E1
6402 | OPW1 | Trip ON | 100E2
6403 | OPW1 | Trip OFF | 100E3
6404 | OPW1 | Block ON | 100E4
6405 | OPW1 | Block OFF | 100E5
6464 | UPW1 | Start ON | 101E0
6465 | UPW1 | Start OFF | 101E1
6466 | UPW1 | Trip ON | 101E2
6467 | UPW1 | Trip OFF | 101E3
6468 | UPW1 | Block ON | 101E4
6469 | UPW1 | Block OFF | 101E5
6528 | RPW1 | Start ON | 102E0
6529 | RPW1 | Start OFF | 102E1
6530 | RPW1 | Trip ON | 102E2
6531 | RPW1 | Trip OFF | 102E3
6532 | RPW1 | Block ON | 102E4
6533 | RPW1 | Block OFF | 102E5
6592 | DFT1 | df/dt </> (1) Start ON | 103E0
6593 | DFT1 | df/dt </> (1) Start OFF | 103E1
6594 | DFT1 | df/dt </> (1) Trip ON | 103E2
6595 | DFT1 | df/dt </> (1) Trip OFF | 103E3
6596 | DFT1 | df/dt </> (2) Start ON | 103E4
6597 | DFT1 | df/dt </> (2) Start OFF | 103E5
6598 | DFT1 | df/dt </> (2) Trip ON | 103E6
6599 | DFT1 | df/dt </> (2) Trip OFF | 103E7
6600 | DFT1 | df/dt </> (3) Start ON | 103E8
6601 | DFT1 | df/dt </> (3) Start OFF | 103E9
6602 | DFT1 | df/dt </> (3) Trip ON | 103E10
6603 | DFT1 | df/dt </> (3) Trip OFF | 103E11
6604 | DFT1 | df/dt </> (4) Start ON | 103E12
6605 | DFT1 | df/dt </> (4) Start OFF | 103E13
6606 | DFT1 | df/dt </> (4) Trip ON | 103E14
6607 | DFT1 | df/dt </> (4) Trip OFF | 103E15
6608 | DFT1 | df/dt </> (5) Start ON | 103E16
6609 | DFT1 | df/dt </> (5) Start OFF | 103E17
6610 | DFT1 | df/dt </> (5) Trip ON | 103E18
6611 | DFT1 | df/dt </> (5) Trip OFF | 103E19
6612 | DFT1 | df/dt </> (6) Start ON | 103E20
6613 | DFT1 | df/dt </> (6) Start OFF | 103E21
6614 | DFT1 | df/dt </> (6) Trip ON | 103E22
6615 | DFT1 | df/dt </> (6) Trip OFF | 103E23
6616 | DFT1 | df/dt </> (7) Start ON | 103E24
6617 | DFT1 | df/dt </> (7) Start OFF | 103E25
6618 | DFT1 | df/dt </> (7) Trip ON | 103E26
6619 | DFT1 | df/dt </> (7) Trip OFF | 103E27
6620 | DFT1 | df/dt </> (8) Start ON | 103E28
6621 | DFT1 | df/dt </> (8) Start OFF | 103E29
6622 | DFT1 | df/dt </> (8) Trip ON | 103E30
6623 | DFT1 | df/dt </> (8) Trip OFF | 103E31
6624 | DFT1 | df/dt </> (1) Block ON | 103E32
6625 | DFT1 | df/dt </> (1) Block OFF | 103E33
6626 | DFT1 | df/dt </> (2) Block ON | 103E34
6627 | DFT1 | df/dt </> (2) Block OFF | 103E35
6628 | DFT1 | df/dt </> (3) Block ON | 103E36
6629 | DFT1 | df/dt </> (3) Block OFF | 103E37
6630 | DFT1 | df/dt </> (4) Block ON | 103E38
6631 | DFT1 | df/dt </> (4) Block OFF | 103E39
6632 | DFT1 | df/dt </> (5) Block ON | 103E40
6633 | DFT1 | df/dt </> (5) Block OFF | 103E41
6634 | DFT1 | df/dt </> (6) Block ON | 103E42
6635 | DFT1 | df/dt </> (6) Block OFF | 103E43
6636 | DFT1 | df/dt </> (7) Block ON | 103E44
6637 | DFT1 | df/dt </> (7) Block OFF | 103E45
6638 | DFT1 | df/dt </> (8) Block ON | 103E46
6639 | DFT1 | df/dt </> (8) Block OFF | 103E47
6656 | CIN1 | Intermediate | 104E0
6657 | CIN1 | Open | 104E1
6658 | CIN1 | Close | 104E2
6659 | CIN1 | Bad | 104E3
6720 | CIN2 | Intermediate | 105E0
6721 | CIN2 | Open | 105E1
6722 | CIN2 | Close | 105E2
6723 | CIN2 | Bad | 105E3
6784 | CIN3 | Intermediate | 106E0
6785 | CIN3 | Open | 106E1
6786 | CIN3 | Close | 106E2
6787 | CIN3 | Bad | 106E3
6848 | CIN4 | Intermediate | 107E0
6849 | CIN4 | Open | 107E1
6850 | CIN4 | Close | 107E2
6851 | CIN4 | Bad | 107E3
6912 | CIN5 | Intermediate | 108E0
6913 | CIN5 | Open | 108E1
6914 | CIN5 | Close | 108E2
6915 | CIN5 | Bad | 108E3
6976 | UEX1 | Start ON | 109E0
6977 | UEX1 | Start OFF | 109E1
6978 | UEX1 | Trip ON | 109E2
6979 | UEX1 | Trip OFF | 109E3
6980 | UEX1 | Block ON | 109E4
6981 | UEX1 | Block OFF | 109E5
7040 | SEF1 | Start ON | 110E0
7041 | SEF1 | Start OFF | 110E1
7042 | SEF1 | Trip ON | 110E2
7043 | SEF1 | Trip OFF | 110E3
7044 | SEF1 | Block ON | 110E4
7045 | SEF1 | Block OFF | 110E5
7104 | UIM1 | Start ON | 111E0
7105 | UIM1 | Start OFF | 111E1
7106 | UIM1 | Trip ON | 111E2
7107 | UIM1 | Trip OFF | 111E3
7108 | UIM1 | Block ON | 111E4
7109 | UIM1 | Block OFF | 111E5
7168 | VOC1 | Start ON | 112E0
7169 | VOC1 | Start OFF | 112E1
7170 | VOC1 | Trip ON | 112E2
7171 | VOC1 | Trip OFF | 112E3
7172 | VOC1 | Block ON | 112E4
7173 | VOC1 | Block OFF | 112E5
7232 | GST1 | Light/No load On | 113E0
7233 | GST1 | Light/No load Off | 113E1
7234 | GST1 | HV side inrush On | 113E2
7235 | GST1 | HV side inrush Off | 113E3
7236 | GST1 | LV side inrush On | 113E4
7237 | GST1 | LV side inrush Off | 113E5
7238 | GST1 | Load normal On | 113E6
7239 | GST1 | Load normal Off | 113E7
7240 | GST1 | Overloading On | 113E8
7241 | GST1 | Overloading Off | 113E9
7242 | GST1 | High overload On | 113E10
7243 | GST1 | High overload Off | 113E11
7244 | GST1 | Setting changes, calculating new trafo data | 113E12
7245 | GST1 | Calculation finished, possible restart | 113E13
7296 | IEF1 | Start FWD ON | 114E0
7297 | IEF1 | Start FWD OFF | 114E1
7298 | IEF1 | Start REV ON | 114E2
7299 | IEF1 | Start REV OFF | 114E3
7300 | IEF1 | Trip ON | 114E4
7301 | IEF1 | Trip OFF | 114E5
7302 | IEF1 | Block ON | 114E6
7303 | IEF1 | Block OFF | 114E7
7304 | IEF1 | Intermittent EF detected ON | 114E8
7305 | IEF1 | Intermittent EF detected OFF | 114E9
7306 | IEF1 | Normal earthfault detected | 114E10
7307 | IEF1 | Intermittent EF Locked | 114E11
7360 | VRG1 | Tap Raise command On | 115E0
7361 | VRG1 | Tap Raise command Off | 115E1
7362 | VRG1 | Tap Lower command On | 115E2
7363 | VRG1 | Tap Lower command Off | 115E3
7364 | VRG1 | Block operation On | 115E4
7365 | VRG1 | Block Operation Off | 115E5
7366 | VRG1 | Block Output commands On | 115E6
7367 | VRG1 | Block Output commands Off | 115E7
7368 | VRG1 | Low voltage blocking On | 115E8
7369 | VRG1 | Low voltage blocking Off | 115E9
7370 | VRG1 | Overcurrent blocking On | 115E10
7371 | VRG1 | Overcurrent blocking Off | 115E11
7372 | VRG1 | Tap on highlimit On | 115E12
7373 | VRG1 | Tap on highlimit Off | 115E13
7374 | VRG1 | Tap on lowlimit On | 115E14
7375 | VRG1 | Tap on lowlimit Off | 115E15
7376 | VRG1 | Operation blocked On | 115E16
7377 | VRG1 | Operation blocked Off | 115E17
7378 | VRG1 | U>/< Start On | 115E18
7379 | VRG1 | U>/< Start Off | 115E19
7380 | VRG1 | U>>/<< Start On | 115E20
7381 | VRG1 | U>>/<< Start Off | 115E21
7382 | VRG1 | Control wait time On | 115E22
7383 | VRG1 | Control wait time Off | 115E23
7384 | VRG1 | Manual control On | 115E24
7385 | VRG1 | Automatic control On | 115E25
7386 | VRG1 | Tap raise requested On | 115E26
7387 | VRG1 | Tap raise requested Off | 115E27
7388 | VRG1 | Tap lower requested On | 115E28
7389 | VRG1 | Tap lower requested Off | 115E29
8192 | VHZ1 | (1)Start ON | 128E0
8193 | VHZ1 | (1)Start OFF | 128E1
8194 | VHZ1 | (1)Alarm ON | 128E2
8195 | VHZ1 | (1)Alarm OFF | 128E3
8196 | VHZ1 | (1)Trip ON | 128E4
8197 | VHZ1 | (1)Trip OFF | 128E5
8198 | VHZ1 | (1)Block ON | 128E6
8199 | VHZ1 | (1)Block OFF | 128E7
8200 | VHZ1 | (2)Start ON | 128E8
8201 | VHZ1 | (2)Start OFF | 128E9
8202 | VHZ1 | (2)Alarm ON | 128E10
8203 | VHZ1 | (2)AlarmOFF | 128E11
8204 | VHZ1 | (2)Trip ON | 128E12
8205 | VHZ1 | (2)Trip OFF | 128E13
8206 | VHZ1 | (2)Block ON | 128E14
8207 | VHZ1 | (2)Block OFF | 128E15
8256 | UPF1 | Block On | 129E0
8257 | UPF1 | Block Off | 129E1
8258 | UPF1 | Start On | 129E2
8259 | UPF1 | Start Off | 129E3
8260 | UPF1 | Trip On | 129E4
8261 | UPF1 | Trip Off | 129E5
8262 | UPF1 | Alarm Start On | 129E6
8263 | UPF1 | Alarm Start Off | 129E7
8264 | UPF1 | Alarm On | 129E8
8265 | UPF1 | Alarm Off | 129E9
8320 | VUB1 | Start ON | 130E0
8321 | VUB1 | Start OFF | 130E1
8322 | VUB1 | Trip ON | 130E2
8323 | VUB1 | Trip OFF | 130E3
8324 | VUB1 | Block ON | 130E4
8325 | VUB1 | Block OFF | 130E5
8384 | VUB2 | Start ON | 131E0
8385 | VUB2 | Start OFF | 131E1
8386 | VUB2 | Trip ON | 131E2
8387 | VUB2 | Trip OFF | 131E3
8388 | VUB2 | Block ON | 131E4
8389 | VUB2 | Block OFF | 131E5
8448 | VUB3 | Start ON | 132E0
8449 | VUB3 | Start OFF | 132E1
8450 | VUB3 | Trip ON | 132E2
8451 | VUB3 | Trip OFF | 132E3
8452 | VUB3 | Block ON | 132E4
8453 | VUB3 | Block OFF | 132E5
8512 | VUB4 | Start ON | 133E0
8513 | VUB4 | Start OFF | 133E1
8514 | VUB4 | Trip ON | 133E2
8515 | VUB4 | Trip OFF | 133E3
8516 | VUB4 | Block ON | 133E4
8517 | VUB4 | Block OFF | 133E5
8576 | PGS1 | PS1 >/< Start ON | 134E0
8577 | PGS1 | PS1 >/< Start OFF | 134E1
8578 | PGS1 | PS1 >/< Trip ON | 134E2
8579 | PGS1 | PS1 >/< Trip OFF | 134E3
8580 | PGS1 | PS1 >/< Block ON | 134E4
8581 | PGS1 | PS1 >/< Block OFF | 134E5
8582 | PGS1 | PS2 >/< Start ON | 134E6
8583 | PGS1 | PS2 >/< Start OFF | 134E7
8584 | PGS1 | PS2 >/< Trip ON | 134E8
8585 | PGS1 | PS2 >/< Trip OFF | 134E9
8586 | PGS1 | PS2 >/< Block ON | 134E10
8587 | PGS1 | PS2 >/< Block OFF | 134E11
8588 | PGS1 | PS3 >/< Start ON | 134E12
8589 | PGS1 | PS3 >/< Start OFF | 134E13
8590 | PGS1 | PS3 >/< Trip ON | 134E14
8591 | PGS1 | PS3 >/< Trip OFF | 134E15
8592 | PGS1 | PS3 >/< Block ON | 134E16
8593 | PGS1 | PS3 >/< Block OFF | 134E17
8594 | PGS1 | PS4 >/< Start ON | 134E18
8595 | PGS1 | PS4 >/< Start OFF | 134E19
8596 | PGS1 | PS4 >/< Trip ON | 134E20
8597 | PGS1 | PS4 >/< Trip OFF | 134E21
8598 | PGS1 | PS4 >/< Block ON | 134E22
8599 | PGS1 | PS4 >/< Block OFF | 134E23
8600 | PGS1 | PS5 >/< Start ON | 134E24
8601 | PGS1 | PS5 >/< Start OFF | 134E25
8602 | PGS1 | PS5 >/< Trip ON | 134E26
8603 | PGS1 | PS5 >/< Trip OFF | 134E27
8604 | PGS1 | PS5 >/< Block ON | 134E28
8605 | PGS1 | PS5 >/< Block OFF | 134E29
8606 | PGS1 | reserved | 134E30
8607 | PGS1 | reserved | 134E31
8608 | PGS1 | PS6 >/< Start ON | 134E32
8609 | PGS1 | PS6 >/< Start OFF | 134E33
8610 | PGS1 | PS6 >/< Trip ON | 134E34
8611 | PGS1 | PS6 >/< Trip OFF | 134E35
8612 | PGS1 | PS6 >/< Block ON | 134E36
8613 | PGS1 | PS6 >/< Block OFF | 134E37
8614 | PGS1 | PS7 >/< Start ON | 134E38
8615 | PGS1 | PS7 >/< Start OFF | 134E39
8616 | PGS1 | PS7 >/< Trip ON | 134E40
8617 | PGS1 | PS7 >/< Trip OFF | 134E41
8618 | PGS1 | PS7 >/< Block ON | 134E42
8619 | PGS1 | PS7 >/< Block OFF | 134E43
8620 | PGS1 | PS8 >/< Start ON | 134E44
8621 | PGS1 | PS8 >/< Start OFF | 134E45
8622 | PGS1 | PS8 >/< Trip ON | 134E46
8623 | PGS1 | PS8 >/< Trip OFF | 134E47
8624 | PGS1 | PS8 >/< Block ON | 134E48
8625 | PGS1 | PS8 >/< Block OFF | 134E49
8626 | PGS1 | PS9 >/< Start ON | 134E50
8627 | PGS1 | PS9 >/< Start OFF | 134E51
8628 | PGS1 | PS9 >/< Trip ON | 134E52
8629 | PGS1 | PS9 >/< Trip OFF | 134E53
8630 | PGS1 | PS9 >/< Block ON | 134E54
8631 | PGS1 | PS9 >/< Block OFF | 134E55
8632 | PGS1 | PS10 >/< Start ON | 134E56
8633 | PGS1 | PS10 >/< Start OFF | 134E57
8634 | PGS1 | PS10 >/< Trip ON | 134E58
8635 | PGS1 | PS10 >/< Trip OFF | 134E59
8636 | PGS1 | PS10 >/< Block ON | 134E60
8637 | PGS1 | PS10 >/< Block OFF | 134E61
8640 | EMON1 | I> (50) Detect On | 135E0
8641 | EMON1 | I> (50) Detect Off | 135E1
8642 | EMON1 | I0> (50N) Detect On | 135E2
8643 | EMON1 | I0> (50N) Detect Off | 135E3
8644 | EMON1 | Idir> (67) Detect On | 135E4
8645 | EMON1 | Idir> (67) Detect Off | 135E5
8646 | EMON1 | I0dir> (67N) Detect On | 135E6
8647 | EMON1 | I0dir> (67N) Detect Off | 135E7
8648 | EMON1 | I0Int> (67NT) Detect FWD On | 135E8
8649 | EMON1 | I0Int> (67NT) Detect FWD Off | 135E9
8650 | EMON1 | I0Int> (67NT) Detect REV On | 135E10
8651 | EMON1 | I0Int> (67NT) Detect REV Off | 135E11
8652 | EMON1 | U< (27) Undervoltage detected On | 135E12
8653 | EMON1 | U< (27) Undervoltage detected Off | 135E13
8654 | EMON1 | U< (27) No voltage detected On | 135E14
8655 | EMON1 | U< (27) No voltage detected Off | 135E15
8656 | EMON1 | U0> (59N) Overvoltage detected On | 135E16
8657 | EMON1 | U0> (59N) Overvoltage detected Off | 135E17
8658 | EMON1 | FL (21FL) Triggered On | 135E18
8659 | EMON1 | FL (21FL) Triggered On | 135E19
8832 | MBIO | ModuleA Ch1 Invalid ON | 138E0
8833 | MBIO | ModuleA Ch1 Invalid OFF | 138E1
8834 | MBIO | ModuleA Ch2 Invalid ON | 138E2
8835 | MBIO | ModuleA Ch2 Invalid OFF | 138E3
8836 | MBIO | ModuleA Ch3 Invalid ON | 138E4
8837 | MBIO | ModuleA Ch3 Invalid OFF | 138E5
8838 | MBIO | ModuleA Ch4 Invalid ON | 138E6
8839 | MBIO | ModuleA Ch4 Invalid OFF | 138E7
8840 | MBIO | ModuleA Ch5 Invalid ON | 138E8
8841 | MBIO | ModuleA Ch5 Invalid OFF | 138E9
8842 | MBIO | ModuleA Ch6 Invalid ON | 138E10
8843 | MBIO | ModuleA Ch6 Invalid OFF | 138E11
8844 | MBIO | ModuleA Ch7 Invalid ON | 138E12
8845 | MBIO | ModuleA Ch7 Invalid OFF | 138E13
8846 | MBIO | ModuleA Ch8 Invalid ON | 138E14
8847 | MBIO | ModuleA Ch8 Invalid OFF | 138E15
8848 | MBIO | ModuleB Ch1 Invalid ON | 138E16
8849 | MBIO | ModuleB Ch1 Invalid OFF | 138E17
8850 | MBIO | ModuleB Ch2 Invalid ON | 138E18
8851 | MBIO | ModuleB Ch2 Invalid OFF | 138E19
8852 | MBIO | ModuleB Ch3 Invalid ON | 138E20
8853 | MBIO | ModuleB Ch3 Invalid OFF | 138E21
8854 | MBIO | ModuleB Ch4 Invalid ON | 138E22
8855 | MBIO | ModuleB Ch4 Invalid OFF | 138E23
8856 | MBIO | ModuleB Ch5 Invalid ON | 138E24
8857 | MBIO | ModuleB Ch5 Invalid OFF | 138E25
8858 | MBIO | ModuleB Ch6 Invalid ON | 138E26
8859 | MBIO | ModuleB Ch6 Invalid OFF | 138E27
8860 | MBIO | ModuleB Ch7 Invalid ON | 138E28
8861 | MBIO | ModuleB Ch7 Invalid OFF | 138E29
8862 | MBIO | ModuleB Ch8 Invalid ON | 138E30
8863 | MBIO | ModuleB Ch8 Invalid OFF | 138E31
8864 | MBIO | ModuleC Ch1 Invalid ON | 138E32
8865 | MBIO | ModuleC Ch1 Invalid OFF | 138E33
8866 | MBIO | ModuleC Ch2 Invalid ON | 138E34
8867 | MBIO | ModuleC Ch2 Invalid OFF | 138E35
8868 | MBIO | ModuleC Ch3 Invalid ON | 138E36
8869 | MBIO | ModuleC Ch3 Invalid OFF | 138E37
8870 | MBIO | ModuleC Ch4 Invalid ON | 138E38
8871 | MBIO | ModuleC Ch4 Invalid OFF | 138E39
8872 | MBIO | ModuleC Ch5 Invalid ON | 138E40
8873 | MBIO | ModuleC Ch5 Invalid OFF | 138E41
8874 | MBIO | ModuleC Ch6 Invalid ON | 138E42
8875 | MBIO | ModuleC Ch6 Invalid OFF | 138E43
8876 | MBIO | ModuleC Ch7 Invalid ON | 138E44
8877 | MBIO | ModuleC Ch7 Invalid OFF | 138E45
8878 | MBIO | ModuleC Ch8 Invalid ON | 138E46
8879 | MBIO | ModuleC Ch8 Invalid OFF | 138E47
9536 | UIM2 | Start ON | 149E0
9537 | UIM2 | Start OFF | 149E1
9538 | UIM2 | Trip ON | 149E2
9539 | UIM2 | Trip OFF | 149E3
9540 | UIM2 | Block ON | 149E4
9541 | UIM2 | Block OFF | 149E5
9600 | OBJ6 | Object Intermediate | 150E0
9601 | OBJ6 | Object Open | 150E1
9602 | OBJ6 | Object Close | 150E2
9603 | OBJ6 | Object Bad | 150E3
9604 | OBJ6 | WD Intermediate | 150E4
9605 | OBJ6 | WD Out | 150E5
9606 | OBJ6 | WD in | 150E6
9607 | OBJ6 | WD Bad | 150E7
9608 | OBJ6 | Open Request On | 150E8
9609 | OBJ6 | Open Request Off | 150E9
9610 | OBJ6 | Open Command On | 150E10
9611 | OBJ6 | Open Command Off | 150E11
9612 | OBJ6 | Close Request On | 150E12
9613 | OBJ6 | Close Request Off | 150E13
9614 | OBJ6 | Close Command On | 150E14
9615 | OBJ6 | Close Command Off | 150E15
9616 | OBJ6 | Open Blocked On | 150E16
9617 | OBJ6 | Open Blocked Off | 150E17
9618 | OBJ6 | Close Blocked On | 150E18
9619 | OBJ6 | Close Blocked Off | 150E19
9620 | OBJ6 | Object Ready | 150E20
9621 | OBJ6 | Object Not Ready | 150E21
9622 | OBJ6 | Sync Ok | 150E22
9623 | OBJ6 | Sync Not Ok | 150E23
9624 | OBJ6 | Open Command Fail | 150E24
9625 | OBJ6 | Close Command Fail | 150E25
9626 | OBJ6 | Final trip On | 150E26
9627 | OBJ6 | Final trip Off | 150E27
9664 | OBJ7 | Object Intermediate | 151E0
9665 | OBJ7 | Object Open | 151E1
9666 | OBJ7 | Object Close | 151E2
9667 | OBJ7 | Object Bad | 151E3
9668 | OBJ7 | WD Intermediate | 151E4
9669 | OBJ7 | WD Out | 151E5
9670 | OBJ7 | WD in | 151E6
9671 | OBJ7 | WD Bad | 151E7
9672 | OBJ7 | Open Request On | 151E8
9673 | OBJ7 | Open Request Off | 151E9
9674 | OBJ7 | Open Command On | 151E10
9675 | OBJ7 | Open Command Off | 151E11
9676 | OBJ7 | Close Request On | 151E12
9677 | OBJ7 | Close Request Off | 151E13
9678 | OBJ7 | Close Command On | 151E14
9679 | OBJ7 | Close Command Off | 151E15
9680 | OBJ7 | Open Blocked On | 151E16
9681 | OBJ7 | Open Blocked Off | 151E17
9682 | OBJ7 | Close Blocked On | 151E18
9683 | OBJ7 | Close Blocked Off | 151E19
9684 | OBJ7 | Object Ready | 151E20
9685 | OBJ7 | Object Not Ready | 151E21
9686 | OBJ7 | Sync Ok | 151E22
9687 | OBJ7 | Sync Not Ok | 151E23
9688 | OBJ7 | Open Command Fail | 151E24
9689 | OBJ7 | Close Command Fail | 151E25
9690 | OBJ7 | Final trip On | 151E26
9691 | OBJ7 | Final trip Off | 151E27
9728 | OBJ8 | Object Intermediate | 152E0
9729 | OBJ8 | Object Open | 152E1
9730 | OBJ8 | Object Close | 152E2
9731 | OBJ8 | Object Bad | 152E3
9732 | OBJ8 | WD Intermediate | 152E4
9733 | OBJ8 | WD Out | 152E5
9734 | OBJ8 | WD in | 152E6
9735 | OBJ8 | WD Bad | 152E7
9736 | OBJ8 | Open Request On | 152E8
9737 | OBJ8 | Open Request Off | 152E9
9738 | OBJ8 | Open Command On | 152E10
9739 | OBJ8 | Open Command Off | 152E11
9740 | OBJ8 | Close Request On | 152E12
9741 | OBJ8 | Close Request Off | 152E13
9742 | OBJ8 | Close Command On | 152E14
9743 | OBJ8 | Close Command Off | 152E15
9744 | OBJ8 | Open Blocked On | 152E16
9745 | OBJ8 | Open Blocked Off | 152E17
9746 | OBJ8 | Close Blocked On | 152E18
9747 | OBJ8 | Close Blocked Off | 152E19
9748 | OBJ8 | Object Ready | 152E20
9749 | OBJ8 | Object Not Ready | 152E21
9750 | OBJ8 | Sync Ok | 152E22
9751 | OBJ8 | Sync Not Ok | 152E23
9752 | OBJ8 | Open Command Fail | 152E24
9753 | OBJ8 | Close Command Fail | 152E25
9754 | OBJ8 | Final trip On | 152E26
9755 | OBJ8 | Final trip Off | 152E27
9792 | OBJ9 | Object Intermediate | 153E0
9793 | OBJ9 | Object Open | 153E1
9794 | OBJ9 | Object Close | 153E2
9795 | OBJ9 | Object Bad | 153E3
9796 | OBJ9 | WD Intermediate | 153E4
9797 | OBJ9 | WD Out | 153E5
9798 | OBJ9 | WD in | 153E6
9799 | OBJ9 | WD Bad | 153E7
9800 | OBJ9 | Open Request On | 153E8
9801 | OBJ9 | Open Request Off | 153E9
9802 | OBJ9 | Open Command On | 153E10
9803 | OBJ9 | Open Command Off | 153E11
9804 | OBJ9 | Close Request On | 153E12
9805 | OBJ9 | Close Request Off | 153E13
9806 | OBJ9 | Close Command On | 153E14
9807 | OBJ9 | Close Command Off | 153E15
9808 | OBJ9 | Open Blocked On | 153E16
9809 | OBJ9 | Open Blocked Off | 153E17
9810 | OBJ9 | Close Blocked On | 153E18
9811 | OBJ9 | Close Blocked Off | 153E19
9812 | OBJ9 | Object Ready | 153E20
9813 | OBJ9 | Object Not Ready | 153E21
9814 | OBJ9 | Sync Ok | 153E22
9815 | OBJ9 | Sync Not Ok | 153E23
9816 | OBJ9 | Open Command Fail | 153E24
9817 | OBJ9 | Close Command Fail | 153E25
9818 | OBJ9 | Final trip On | 153E26
9819 | OBJ9 | Final trip Off | 153E27
9856 | OBJ10 | Object Intermediate | 154E0
9857 | OBJ10 | Object Open | 154E1
9858 | OBJ10 | Object Close | 154E2
9859 | OBJ10 | Object Bad | 154E3
9860 | OBJ10 | WD Intermediate | 154E4
9861 | OBJ10 | WD Out | 154E5
9862 | OBJ10 | WD in | 154E6
9863 | OBJ10 | WD Bad | 154E7
9864 | OBJ10 | Open Request On | 154E8
9865 | OBJ10 | Open Request Off | 154E9
9866 | OBJ10 | Open Command On | 154E10
9867 | OBJ10 | Open Command Off | 154E11
9868 | OBJ10 | Close Request On | 154E12
9869 | OBJ10 | Close Request Off | 154E13
9870 | OBJ10 | Close Command On | 154E14
9871 | OBJ10 | Close Command Off | 154E15
9872 | OBJ10 | Open Blocked On | 154E16
9873 | OBJ10 | Open Blocked Off | 154E17
9874 | OBJ10 | Close Blocked On | 154E18
9875 | OBJ10 | Close Blocked Off | 154E19
9876 | OBJ10 | Object Ready | 154E20
9877 | OBJ10 | Object Not Ready | 154E21
9878 | OBJ10 | Sync Ok | 154E22
9879 | OBJ10 | Sync Not Ok | 154E23
9880 | OBJ10 | Open Command Fail | 154E24
9881 | OBJ10 | Close Command Fail | 154E25
9882 | OBJ10 | Final trip On | 154E26
9883 | OBJ10 | Final trip Off | 154E27
9920 | VJP1 | Block On | 155E0
9921 | VJP1 | Block Off | 155E1
9922 | VJP1 | Trip On | 155E2
9923 | VJP1 | Trip Off | 155E3
9924 | VJP1 | Alarm On | 155E4
9925 | VJP1 | Alarm Off | 155E5
9984 | GMAG | FCL on limit On | 156E0
9985 | GMAG | FCL on limit Off | 156E1
9986 | GMAG | UEL in operation On | 156E2
9987 | GMAG | UEL in operation Off | 156E3
9988 | GMAG | SCL Overexcitation On | 156E4
9989 | GMAG | SCL Overexcitation Off | 156E5
9990 | GMAG | SCL Underexcitation On | 156E6
9991 | GMAG | SCL Underexcitation Off | 156E7
9992 | GMAG | High IP On | 156E8
9993 | GMAG | High IP Off | 156E9
9994 | GMAG | Inst FCL On | 156E10
9995 | GMAG | Inst FCL Off | 156E11
9996 | GMAG | Low supply voltage On | 156E12
9997 | GMAG | Low supply voltage Off | 156E13
9998 | GMAG | FCR Mode On | 156E14
9999 | GMAG | FCR Mode Off | 156E15
10000 | GMAG | AVR Mode On | 156E16
10001 | GMAG | AVR Mode Off | 156E17
10002 | GMAG | Low meas volt On | 156E18
10003 | GMAG | Low meas volt Off | 156E19
10004 | GMAG | IGBT Shorted On | 156E20
10005 | GMAG | IGBT Shorted Off | 156E21
10006 | GMAG | PWM Enable On | 156E22
10007 | GMAG | PWM Enable Off | 156E23
10008 | GMAG | PWM DO1 On | 156E24
10009 | GMAG | PWM DO1 Off | 156E25
10010 | GMAG | PWM DO2 On | 156E26
10011 | GMAG | PWM DO2 Off | 156E27
10012 | GMAG | Rectifier trip On | 156E28
10013 | GMAG | Rectifier trip Off | 156E29
10014 | GMAG | Temp high breaker 1 On | 156E30
10015 | GMAG | Temp high breaker 1 Off | 156E31
10016 | GMAG | Temp high breaker 2 On | 156E32
10017 | GMAG | Temp high breaker 2 Off | 156E33
10018 | GMAG | Excitation On | 156E34
10019 | GMAG | Exc On Cmd Off | 156E35
10020 | GMAG | Excitation Off | 156E36
10021 | GMAG | Exc Off Cmd Off | 156E37
10022 | GMAG | Diode fault On | 156E38
10023 | GMAG | Diode fault Off | 156E39
10024 | GMAG | Overcurrent On | 156E40
10025 | GMAG | Overcurrent Off | 156E41
10026 | GMAG | PWM DI1 On | 156E42
10027 | GMAG | PWM DI1 Off | 156E43
10028 | GMAG | PWM DI2 On | 156E44
10029 | GMAG | PWM DI2 Off | 156E45
10030 | GMAG | PWM DI3 On | 156E46
10031 | GMAG | PWM DI3 Off | 156E47
10032 | GMAG | PWM DI4 On | 156E48
10033 | GMAG | PWM DI4 Off | 156E49
10034 | GMAG | PWM DI5 On | 156E50
10035 | GMAG | PWM DI5 Off | 156E51
10036 | GMAG | PWM DI6 On | 156E52
10037 | GMAG | PWM DI6 Off | 156E53
10038 | GMAG | PWM DI7 On | 156E54
10039 | GMAG | PWM DI7 Off | 156E55
10040 | GMAG | PWM DI8 On | 156E56
10041 | GMAG | PWM DI8 Off | 156E57
10048 | GMAG1 | Synchronised On | 157E0
10049 | GMAG1 | Synchronised Off | 157E1
10050 | GMAG1 | Islandmode On | 157E2
10051 | GMAG1 | Islandmode Off | 157E3
10052 | GMAG1 | FB is Open On | 157E4
10053 | GMAG1 | FB is Open Off | 157E5
10054 | GMAG1 | FB is Closed On | 157E6
10055 | GMAG1 | FB is Closed Off | 157E7
10056 | GMAG1 | Field flashing On | 157E8
10057 | GMAG1 | Field flashing Off | 157E9
10058 | GMAG1 | Long field flashing On | 157E10
10059 | GMAG1 | Long field flashing Off | 157E11
10060 | GMAG1 | Test mode On | 157E12
10061 | GMAG1 | Test mode Off | 157E13
10062 | GMAG1 | Phase retard On | 157E14
10063 | GMAG1 | Phase retard Off | 157E15
10064 | GMAG1 | Reset On | 157E16
10065 | GMAG1 | Reset Off | 157E17
10066 | GMAG1 | Command AVR On | 157E18
10067 | GMAG1 | Command AVR Off | 157E19
10068 | GMAG1 | Command FCR On | 157E20
10069 | GMAG1 | Command FCR Off | 157E21
10070 | GMAG1 | Command MVar On | 157E22
10071 | GMAG1 | Command MVar Off | 157E23
10072 | GMAG1 | Command PF On | 157E24
10073 | GMAG1 | Command PF Off | 157E25
10074 | GMAG1 | Excitation run order On | 157E26
10075 | GMAG1 | Excitation run order Off | 157E27
10076 | GMAG1 | Increase On | 157E28
10077 | GMAG1 | Increase Off | 157E29
10078 | GMAG1 | Decrease On | 157E30
10079 | GMAG1 | Decrease Off | 157E31
10080 | GMAG1 | AVR Bus On | 157E32
10081 | GMAG1 | AVR Bus Off | 157E33
10082 | GMAG1 | FCR Bus On | 157E34
10083 | GMAG1 | FCR Bus Off | 157E35
10084 | GMAG1 | MVar Bus On | 157E36
10085 | GMAG1 | MVar Bus Off | 157E37
10086 | GMAG1 | PF Bus On | 157E38
10087 | GMAG1 | PF Bus Off | 157E39
10088 | GMAG1 | Overriding control On | 157E40
10089 | GMAG1 | Overriding control Off | 157E41
10090 | GMAG1 | Increase MVAR/PF On | 157E42
10091 | GMAG1 | Increase MVAR/PF Off | 157E43
10092 | GMAG1 | Decrease MVAR/PF On | 157E44
10093 | GMAG1 | Decrease MVAR/PF Off | 157E45
10094 | GMAG1 | Low Q error On | 157E46
10095 | GMAG1 | Low Q error Off | 157E47
10096 | GMAG1 | AVR ref on lowlim On | 157E48
10097 | GMAG1 | AVR ref on lowlim Off | 157E49
10098 | GMAG1 | AVR ref on highlim On | 157E50
10099 | GMAG1 | AVR ref on highlim Off | 157E51
10100 | GMAG1 | FCR ref on lowlim On | 157E52
10101 | GMAG1 | FCR ref on lowlim Off | 157E53
10102 | GMAG1 | FCR ref on highlim On | 157E54
10103 | GMAG1 | FCR ref on highlim Off | 157E55
10104 | GMAG1 | VHZ limit active On | 157E56
10105 | GMAG1 | VHZ limit active Off | 157E57
10106 | GMAG1 | Process panel activated On | 157E58
10107 | GMAG1 | Process panel activated Off | 157E59
10108 | GMAG1 | Parameters active On | 157E60
10109 | GMAG1 | Parameters active Off | 157E61
10110 | GMAG1 | Bus activated On | 157E62
10111 | GMAG1 | Bus activated Off | 157E63
10112 | GMAG2 | Reset and excitation off On | 158E0
10113 | GMAG2 | Reset and excitation off Off | 158E1
10114 | GMAG2 | Field breaker does not open On | 158E2
10115 | GMAG2 | Field breaker does not open Off | 158E3
10116 | GMAG2 | New reference start On | 158E4
10117 | GMAG2 | New reference start Off | 158E5
10118 | GMAG2 | GB is closed On | 158E6
10119 | GMAG2 | GB is closed Off | 158E7
10120 | GMAG2 | FB off GB on On | 158E8
10121 | GMAG2 | FB off GB on Off | 158E9
10122 | GMAG2 | Disturbed mode On | 158E10
10123 | GMAG2 | Disturbed mode Off | 158E11
10124 | GMAG2 | Disturbed mode pulse On | 158E12
10125 | GMAG2 | Disturbed mode pulse Off | 158E13
10126 | GMAG2 | Following line voltage On | 158E14
10127 | GMAG2 | Following line voltage Off | 158E15
10128 | GMAG2 | Test Square enable On | 158E16
10129 | GMAG2 | Test Square enable Off | 158E17
10130 | GMAG2 | Order open FB On | 158E18
10131 | GMAG2 | Order open FB Off | 158E19
10132 | GMAG2 | Order close FB On | 158E20
10133 | GMAG2 | Order close FB Off | 158E21
10134 | GMAG2 | Q unloaded On | 158E22
10135 | GMAG2 | Q unloaded Off | 158E23
10136 | GMAG2 | MVAR ref on high On | 158E24
10137 | GMAG2 | MVAR ref on high Off | 158E25
10138 | GMAG2 | MVAR ref on low On | 158E26
10139 | GMAG2 | MVAR ref on low Off | 158E27
10140 | GMAG2 | PF ref on high On | 158E28
10141 | GMAG2 | PF ref on high Off | 158E29
10142 | GMAG2 | PF ref on low On | 158E30
10143 | GMAG2 | PF ref on low Off | 158E31
10144 | GMAG2 | AVR start Ref On | 158E32
10145 | GMAG2 | AVR start Ref Off | 158E33
10146 | GMAG2 | FCR start Ref On | 158E34
10147 | GMAG2 | FCR start Ref Off | 158E35
10148 | GMAG2 | Unload MVAR On | 158E36
10149 | GMAG2 | Unload MVAR Off | 158E37
10150 | GMAG2 | PWM DO3 On | 158E38
10151 | GMAG2 | PWM DO3 Off | 158E39
10152 | GMAG2 | PWM DO4 On | 158E40
10153 | GMAG2 | PWM DO4 Off | 158E41
10154 | GMAG2 | MVAR Mode On | 158E42
10155 | GMAG2 | MVAR Mode Off | 158E43
10156 | GMAG2 | PF Mode On | 158E44
10157 | GMAG2 | PF Mode Off | 158E45
10158 | GMAG2 | PSS Enabled On | 158E46
10159 | GMAG2 | PSS Enabled Off | 158E47
10160 | GMAG2 | PSS Blocked On | 158E48
10161 | GMAG2 | PSS Blocked Off | 158E49
10176 | ALARM1 | Alarm 1 On (Alarm 1) | 159E0
10177 | ALARM1 | Alarm 1 Off (Alarm 1) | 159E1
10178 | ALARM1 | Alarm 2 On (Alarm 2) | 159E2
10179 | ALARM1 | Alarm 2 Off (Alarm 2) | 159E3
10180 | ALARM1 | Alarm 3 On (Alarm 3) | 159E4
10181 | ALARM1 | Alarm 3 Off (Alarm 3) | 159E5
10182 | ALARM1 | Alarm 4 On (Alarm 4) | 159E6
10183 | ALARM1 | Alarm 4 Off (Alarm 4) | 159E7
10184 | ALARM1 | Alarm 5 On (Alarm 5) | 159E8
10185 | ALARM1 | Alarm 5 Off (Alarm 5) | 159E9
10186 | ALARM1 | Alarm 6 On (Alarm 6) | 159E10
10187 | ALARM1 | Alarm 6 Off (Alarm 6) | 159E11
10188 | ALARM1 | Alarm 7 On (Alarm 7) | 159E12
10189 | ALARM1 | Alarm 7 Off (Alarm 7) | 159E13
10190 | ALARM1 | Alarm 8 On (Alarm 8) | 159E14
10191 | ALARM1 | Alarm 8 Off (Alarm 8) | 159E15
10192 | ALARM1 | Alarm 9 On (Alarm 9) | 159E16
10193 | ALARM1 | Alarm 9 Off (Alarm 9) | 159E17
10194 | ALARM1 | Alarm 10 On (Alarm 10) | 159E18
10195 | ALARM1 | Alarm 10 Off (Alarm 10) | 159E19
10196 | ALARM1 | Alarm 11 On (Alarm 11) | 159E20
10197 | ALARM1 | Alarm 11 Off (Alarm 11) | 159E21
10198 | ALARM1 | Alarm 12 On (Alarm 12) | 159E22
10199 | ALARM1 | Alarm 12 Off (Alarm 12) | 159E23
10200 | ALARM1 | Alarm 13 On (Alarm 13) | 159E24
10201 | ALARM1 | Alarm 13 Off (Alarm 13) | 159E25
10202 | ALARM1 | Alarm 14 On (Alarm 14) | 159E26
10203 | ALARM1 | Alarm 14 Off (Alarm 14) | 159E27
10204 | ALARM1 | Alarm 15 On (Alarm 15) | 159E28
10205 | ALARM1 | Alarm 15 Off (Alarm 15) | 159E29
10206 | ALARM1 | Alarm 16 On (Alarm 16) | 159E30
10207 | ALARM1 | Alarm 16 Off (Alarm 16) | 159E31
10208 | ALARM1 | Alarm 17 On (Alarm 17) | 159E32
10209 | ALARM1 | Alarm 17 Off (Alarm 17) | 159E33
10210 | ALARM1 | Alarm 18 On (Alarm 18) | 159E34
10211 | ALARM1 | Alarm 18 Off (Alarm 18) | 159E35
10212 | ALARM1 | Alarm 19 On (Alarm 19) | 159E36
10213 | ALARM1 | Alarm 19 Off (Alarm 19) | 159E37
10214 | ALARM1 | Alarm 20 On (Alarm 20) | 159E38
10215 | ALARM1 | Alarm 20 Off (Alarm 20) | 159E39
10216 | ALARM1 | Alarm 21 On (Alarm 21) | 159E40
10217 | ALARM1 | Alarm 21 Off (Alarm 21) | 159E41
10218 | ALARM1 | Alarm 22 On (Alarm 22) | 159E42
10219 | ALARM1 | Alarm 22 Off (Alarm 22) | 159E43
10220 | ALARM1 | Alarm 23 On (Alarm 23) | 159E44
10221 | ALARM1 | Alarm 23 Off (Alarm 23) | 159E45
10222 | ALARM1 | Alarm 24 On (Alarm 24) | 159E46
10223 | ALARM1 | Alarm 24 Off (Alarm 24) | 159E47
10224 | ALARM1 | Alarm 25 On (Alarm 25) | 159E48
10225 | ALARM1 | Alarm 25 Off (Alarm 25) | 159E49
10226 | ALARM1 | Alarm 26 On (Alarm 26) | 159E50
10227 | ALARM1 | Alarm 26 Off (Alarm 26) | 159E51
10228 | ALARM1 | Alarm 27 On (Alarm 27) | 159E52
10229 | ALARM1 | Alarm 27 Off (Alarm 27) | 159E53
10230 | ALARM1 | Alarm 28 On (Alarm 28) | 159E54
10231 | ALARM1 | Alarm 28 Off (Alarm 28) | 159E55
10232 | ALARM1 | Alarm 29 On (Alarm 29) | 159E56
10233 | ALARM1 | Alarm 29 Off (Alarm 29) | 159E57
10234 | ALARM1 | Alarm 30 On (Alarm 30) | 159E58
10235 | ALARM1 | Alarm 30 Off (Alarm 30) | 159E59
10236 | ALARM1 | Alarm 31 On (Alarm 31) | 159E60
10237 | ALARM1 | Alarm 31 Off (Alarm 31) | 159E61
10238 | ALARM1 | Alarm 32 On (Alarm 32) | 159E62
10239 | ALARM1 | Alarm 32 Off (Alarm 32) | 159E63
10240 | ALARM2 | Alarm 33 On (Alarm 33) | 160E0
10241 | ALARM2 | Alarm 33 Off (Alarm 33) | 160E1
10242 | ALARM2 | Alarm 34 On (Alarm 34) | 160E2
10243 | ALARM2 | Alarm 34 Off (Alarm 34) | 160E3
10244 | ALARM2 | Alarm 35 On (Alarm 35) | 160E4
10245 | ALARM2 | Alarm 35 Off (Alarm 35) | 160E5
10246 | ALARM2 | Alarm 36 On (Alarm 36) | 160E6
10247 | ALARM2 | Alarm 36 Off (Alarm 36) | 160E7
10248 | ALARM2 | Alarm 37 On (Alarm 37) | 160E8
10249 | ALARM2 | Alarm 37 Off (Alarm 37) | 160E9
10250 | ALARM2 | Alarm 38 On (Alarm 38) | 160E10
10251 | ALARM2 | Alarm 38 Off (Alarm 38) | 160E11
10252 | ALARM2 | Alarm 39 On (Alarm 39) | 160E12
10253 | ALARM2 | Alarm 39 Off (Alarm 39) | 160E13
10254 | ALARM2 | Alarm 40 On (Alarm 40) | 160E14
10255 | ALARM2 | Alarm 40 Off (Alarm 40) | 160E15
10256 | ALARM2 | Alarm 41 On (Alarm 41) | 160E16
10257 | ALARM2 | Alarm 41 Off (Alarm 41) | 160E17
10258 | ALARM2 | Alarm 42 On (Alarm 42) | 160E18
10259 | ALARM2 | Alarm 42 Off (Alarm 42) | 160E19
10260 | ALARM2 | Alarm 43 On (Alarm 43) | 160E20
10261 | ALARM2 | Alarm 43 Off (Alarm 43) | 160E21
10262 | ALARM2 | Alarm 44 On (Alarm 44) | 160E22
10263 | ALARM2 | Alarm 44 Off (Alarm 44) | 160E23
10264 | ALARM2 | Alarm 45 On (Alarm 45) | 160E24
10265 | ALARM2 | Alarm 45 Off (Alarm 45) | 160E25
10266 | ALARM2 | Alarm 46 On (Alarm 46) | 160E26
10267 | ALARM2 | Alarm 46 Off (Alarm 46) | 160E27
10268 | ALARM2 | Alarm 47 On (Alarm 47) | 160E28
10269 | ALARM2 | Alarm 47 Off (Alarm 47) | 160E29
10270 | ALARM2 | Alarm 48 On (Alarm 48) | 160E30
10271 | ALARM2 | Alarm 48 Off (Alarm 48) | 160E31
10272 | ALARM2 | Alarm 49 On (Alarm 49) | 160E32
10273 | ALARM2 | Alarm 49 Off (Alarm 49) | 160E33
10274 | ALARM2 | Alarm 50 On (Alarm 50) | 160E34
10275 | ALARM2 | Alarm 50 Off (Alarm 50) | 160E35
10276 | ALARM2 | Alarm 51 On (Alarm 51) | 160E36
10277 | ALARM2 | Alarm 51 Off (Alarm 51) | 160E37
10278 | ALARM2 | Alarm 52 On (Alarm 52) | 160E38
10279 | ALARM2 | Alarm 52 Off (Alarm 52) | 160E39
10280 | ALARM2 | Alarm 53 On (Alarm 53) | 160E40
10281 | ALARM2 | Alarm 53 Off (Alarm 53) | 160E41
10282 | ALARM2 | Alarm 54 On (Alarm 54) | 160E42
10283 | ALARM2 | Alarm 54 Off (Alarm 54) | 160E43
10284 | ALARM2 | Alarm 55 On (Alarm 55) | 160E44
10285 | ALARM2 | Alarm 55 Off (Alarm 55) | 160E45
10286 | ALARM2 | Alarm 56 On (Alarm 56) | 160E46
10287 | ALARM2 | Alarm 56 Off (Alarm 56) | 160E47
10288 | ALARM2 | Alarm 57 On (Alarm 57) | 160E48
10289 | ALARM2 | Alarm 57 Off (Alarm 57) | 160E49
10290 | ALARM2 | Alarm 58 On (Alarm 58) | 160E50
10291 | ALARM2 | Alarm 58 Off (Alarm 58) | 160E51
10292 | ALARM2 | Alarm 59 On (Alarm 59) | 160E52
10293 | ALARM2 | Alarm 59 Off (Alarm 59) | 160E53
10294 | ALARM2 | Alarm 60 On (Alarm 60) | 160E54
10295 | ALARM2 | Alarm 60 Off (Alarm 60) | 160E55
10296 | ALARM2 | Alarm 61 On (Alarm 61) | 160E56
10297 | ALARM2 | Alarm 61 Off (Alarm 61) | 160E57
10298 | ALARM2 | Alarm 62 On (Alarm 62) | 160E58
10299 | ALARM2 | Alarm 62 Off (Alarm 62) | 160E59
10300 | ALARM2 | Alarm 63 On (Alarm 63) | 160E60
10301 | ALARM2 | Alarm 63 Off (Alarm 63) | 160E61
10302 | ALARM2 | Alarm 64 On (Alarm 64) | 160E62
10303 | ALARM2 | Alarm 64 Off (Alarm 64) | 160E63
10304 | IAE1 | Start ON | 161E0
10305 | IAE1 | Start OFF | 161E1
10306 | IAE1 | Trip ON | 161E2
10307 | IAE1 | Trip OFF | 161E3
10308 | IAE1 | Block ON | 161E4
10309 | IAE1 | Block OFF | 161E5
10310 | IAE1 | Low Current On | 161E6
10311 | IAE1 | Low Current Off | 161E7
10312 | IAE1 | Low Voltage On | 161E8
10313 | IAE1 | Low Voltage On | 161E9
10368 | GSYN | Synchronizing Blocked On | 162E0
10369 | GSYN | Synchronizing Blocked Off | 162E1
10370 | GSYN | Synchronizing Running On | 162E2
10371 | GSYN | Synchronizing Running Off | 162E3
10372 | GSYN | Synchr. Increase Voltage On | 162E4
10373 | GSYN | Synchr. Increase Voltage Off | 162E5
10374 | GSYN | Synchr. Decrease Voltage On | 162E6
10375 | GSYN | Synchr. Decrease Voltage Off | 162E7
10376 | GSYN | Synchr. Increase Frequency On | 162E8
10377 | GSYN | Synchr. Increase Frequency Off | 162E9
10378 | GSYN | Synchr. Decrease Frequency On | 162E10
10379 | GSYN | Synchr. Decrease Frequency Off | 162E11
10380 | GSYN | Synchronizer BRK Close On | 162E12
10381 | GSYN | Synchronizer BRK Close Off | 162E13
10382 | GSYN | Synchronizer Long Sync. Time On | 162E14
10383 | GSYN | Synchronizer Long Sync. Time Off | 162E15
10384 | GSYN | Synchroswitch Close fail Re-init On | 162E16
10385 | GSYN | Synchroswitch Close fail Re-init Off | 162E17
10386 | GSYN | Synchroswitching requested On | 162E18
10387 | GSYN | Synchroswitching requested Off | 162E19
10432 | VREC | Trigger On | 163E0
10433 | VREC | Trigger Off | 163E1
10496 | PWR1 | Start ON | 164E0
10497 | PWR1 | Start OFF | 164E1
10498 | PWR1 | Trip ON | 164E2
10499 | PWR1 | Trip OFF | 164E3
10500 | PWR1 | Block ON | 164E4
10501 | PWR1 | Block OFF | 164E5
10560 | PWR2 | Start ON | 165E0
10561 | PWR2 | Start OFF | 165E1
10562 | PWR2 | Trip ON | 165E2
10563 | PWR2 | Trip OFF | 165E3
10564 | PWR2 | Block ON | 165E4
10565 | PWR2 | Block OFF | 165E5
10624 | PWR3 | Start ON | 166E0
10625 | PWR3 | Start OFF | 166E1
10626 | PWR3 | Trip ON | 166E2
10627 | PWR3 | Trip OFF | 166E3
10628 | PWR3 | Block ON | 166E4
10629 | PWR3 | Block OFF | 166E5
10688 | PWR4 | Start ON | 167E0
10689 | PWR4 | Start OFF | 167E1
10690 | PWR4 | Trip ON | 167E2
10691 | PWR4 | Trip OFF | 167E3
10692 | PWR4 | Block ON | 167E4
10693 | PWR4 | Block OFF | 167E5
10752 | CIN6 | Intermediate | 168E0
10753 | CIN6 | Open | 168E1
10754 | CIN6 | Close | 168E2
10755 | CIN6 | Bad | 168E3
10816 | CIN7 | Intermediate | 169E0
10817 | CIN7 | Open | 169E1
10818 | CIN7 | Close | 169E2
10819 | CIN7 | Bad | 169E3
10880 | CIN8 | Intermediate | 170E0
10881 | CIN8 | Open | 170E1
10882 | CIN8 | Close | 170E2
10883 | CIN8 | Bad | 170E3
10944 | CIN9 | Intermediate | 171E0
10945 | CIN9 | Open | 171E1
10946 | CIN9 | Close | 171E2
10947 | CIN9 | Bad | 171E3
11008 | CIN10 | Intermediate | 172E0
11009 | CIN10 | Open | 172E1
11010 | CIN10 | Close | 172E2
11011 | CIN10 | Bad | 172E3
11072 | CIN11 | Intermediate | 173E0
11073 | CIN11 | Open | 173E1
11074 | CIN11 | Close | 173E2
11075 | CIN11 | Bad | 173E3
11136 | CIN12 | Intermediate | 174E0
11137 | CIN12 | Open | 174E1
11138 | CIN12 | Close | 174E2
11139 | CIN12 | Bad | 174E3
11200 | CIN13 | Intermediate | 175E0
11201 | CIN13 | Open | 175E1
11202 | CIN13 | Close | 175E2
11203 | CIN13 | Bad | 175E3
11264 | CIN14 | Intermediate | 176E0
11265 | CIN14 | Open | 176E1
11266 | CIN14 | Close | 176E2
11267 | CIN14 | Bad | 176E3
11328 | CIN15 | Intermediate | 177E0
11329 | CIN15 | Open | 177E1
11330 | CIN15 | Close | 177E2
11331 | CIN15 | Bad | 177E3
11392 | CIN16 | Intermediate | 178E0
11393 | CIN16 | Open | 178E1
11394 | CIN16 | Close | 178E2
11395 | CIN16 | Bad | 178E3
11456 | CIN17 | Intermediate | 179E0
11457 | CIN17 | Open | 179E1
11458 | CIN17 | Close | 179E2
11459 | CIN17 | Bad | 179E3
11520 | CIN18 | Intermediate | 180E0
11521 | CIN18 | Open | 180E1
11522 | CIN18 | Close | 180E2
11523 | CIN18 | Bad | 180E3
11584 | CIN19 | Intermediate | 181E0
11585 | CIN19 | Open | 181E1
11586 | CIN19 | Close | 181E2
11587 | CIN19 | Bad | 181E3
11648 | CIN20 | Intermediate | 182E0
11649 | CIN20 | Open | 182E1
11650 | CIN20 | Close | 182E2
11651 | CIN20 | Bad | 182E3
11712 | RHC1 | Running hour counter On | 183E0
11713 | RHC1 | Running hour counter Off | 183E1
11714 | RHC1 | Running hour counter cleared On | 183E2
11715 | RHC1 | Running hour counter cleared Off | 183E3
11776 | ALARM3 | Alarm 65 On | 184E0
11777 | ALARM3 | Alarm 65 Off | 184E1
11778 | ALARM3 | Alarm 66 On | 184E2
11779 | ALARM3 | Alarm 66 Off | 184E3
11780 | ALARM3 | Alarm 67 On | 184E4
11781 | ALARM3 | Alarm 67 Off | 184E5
11782 | ALARM3 | Alarm 68 On | 184E6
11783 | ALARM3 | Alarm 68 Off | 184E7
11784 | ALARM3 | Alarm 69 On | 184E8
11785 | ALARM3 | Alarm 69 Off | 184E9
11786 | ALARM3 | Alarm 70 On | 184E10
11787 | ALARM3 | Alarm 70 Off | 184E11
11788 | ALARM3 | Alarm 71 On | 184E12
11789 | ALARM3 | Alarm 71 Off | 184E13
11790 | ALARM3 | Alarm 72 On | 184E14
11791 | ALARM3 | Alarm 72 Off | 184E15
11792 | ALARM3 | Alarm 73 On | 184E16
11793 | ALARM3 | Alarm 73 Off | 184E17
11794 | ALARM3 | Alarm 74 On | 184E18
11795 | ALARM3 | Alarm 74 Off | 184E19
11796 | ALARM3 | Alarm 75 On | 184E20
11797 | ALARM3 | Alarm 75 Off | 184E21
11798 | ALARM3 | Alarm 76 On | 184E22
11799 | ALARM3 | Alarm 76 Off | 184E23
11800 | ALARM3 | Alarm 77 On | 184E24
11801 | ALARM3 | Alarm 77 Off | 184E25
11802 | ALARM3 | Alarm 78 On | 184E26
11803 | ALARM3 | Alarm 78 Off | 184E27
11804 | ALARM3 | Alarm 79 On | 184E28
11805 | ALARM3 | Alarm 79 Off | 184E29
11806 | ALARM3 | Alarm 80 On | 184E30
11807 | ALARM3 | Alarm 80 Off | 184E31
11808 | ALARM3 | Alarm 81 On | 184E32
11809 | ALARM3 | Alarm 81 Off | 184E33
11810 | ALARM3 | Alarm 82 On | 184E34
11811 | ALARM3 | Alarm 82 Off | 184E35
11812 | ALARM3 | Alarm 83 On | 184E36
11813 | ALARM3 | Alarm 83 Off | 184E37
11814 | ALARM3 | Alarm 84 On | 184E38
11815 | ALARM3 | Alarm 84 Off | 184E39
11816 | ALARM3 | Alarm 85 On | 184E40
11817 | ALARM3 | Alarm 85 Off | 184E41
11818 | ALARM3 | Alarm 86 On | 184E42
11819 | ALARM3 | Alarm 86 Off | 184E43
11820 | ALARM3 | Alarm 87 On | 184E44
11821 | ALARM3 | Alarm 87 Off | 184E45
11822 | ALARM3 | Alarm 88 On | 184E46
11823 | ALARM3 | Alarm 88 Off | 184E47
11824 | ALARM3 | Alarm 89 On | 184E48
11825 | ALARM3 | Alarm 89 Off | 184E49
11826 | ALARM3 | Alarm 90 On | 184E50
11827 | ALARM3 | Alarm 90 Off | 184E51
11828 | ALARM3 | Alarm 91 On | 184E52
11829 | ALARM3 | Alarm 91 Off | 184E53
11830 | ALARM3 | Alarm 92 On | 184E54
11831 | ALARM3 | Alarm 92 Off | 184E55
11832 | ALARM3 | Alarm 93 On | 184E56
11833 | ALARM3 | Alarm 93 Off | 184E57
11834 | ALARM3 | Alarm 94 On | 184E58
11835 | ALARM3 | Alarm 94 Off | 184E59
11836 | ALARM3 | Alarm 95 On | 184E60
11837 | ALARM3 | Alarm 95 Off | 184E61
11838 | ALARM3 | Alarm 96 On | 184E62
11839 | ALARM3 | Alarm 96 Off | 184E63
11840 | ALARM4 | Alarm 97 On | 185E0
11841 | ALARM4 | Alarm 97 Off | 185E1
11842 | ALARM4 | Alarm 98 On | 185E2
11843 | ALARM4 | Alarm 98 Off | 185E3
11844 | ALARM4 | Alarm 99 On | 185E4
11845 | ALARM4 | Alarm 99 Off | 185E5
11846 | ALARM4 | Alarm 100 On | 185E6
11847 | ALARM4 | Alarm 100 Off | 185E7
11848 | ALARM4 | Alarm 101 On | 185E8
11849 | ALARM4 | Alarm 101 Off | 185E9
11850 | ALARM4 | Alarm 102 On | 185E10
11851 | ALARM4 | Alarm 102 Off | 185E11
11852 | ALARM4 | Alarm 103 On | 185E12
11853 | ALARM4 | Alarm 103 Off | 185E13
11854 | ALARM4 | Alarm 104 On | 185E14
11855 | ALARM4 | Alarm 104 Off | 185E15
11856 | ALARM4 | Alarm 105 On | 185E16
11857 | ALARM4 | Alarm 105 Off | 185E17
11858 | ALARM4 | Alarm 106 On | 185E18
11859 | ALARM4 | Alarm 106 Off | 185E19
11860 | ALARM4 | Alarm 107 On | 185E20
11861 | ALARM4 | Alarm 107 Off | 185E21
11862 | ALARM4 | Alarm 108 On | 185E22
11863 | ALARM4 | Alarm 108 Off | 185E23
11864 | ALARM4 | Alarm 109 On | 185E24
11865 | ALARM4 | Alarm 109 Off | 185E25
11866 | ALARM4 | Alarm 110 On | 185E26
11867 | ALARM4 | Alarm 110 Off | 185E27
11868 | ALARM4 | Alarm 111 On | 185E28
11869 | ALARM4 | Alarm 111 Off | 185E29
11870 | ALARM4 | Alarm 112 On | 185E30
11871 | ALARM4 | Alarm 112 Off | 185E31
11872 | ALARM4 | Alarm 113 On | 185E32
11873 | ALARM4 | Alarm 113 Off | 185E33
11874 | ALARM4 | Alarm 114 On | 185E34
11875 | ALARM4 | Alarm 114 Off | 185E35
11876 | ALARM4 | Alarm 115 On | 185E36
11877 | ALARM4 | Alarm 115 Off | 185E37
11878 | ALARM4 | Alarm 116 On | 185E38
11879 | ALARM4 | Alarm 116 Off | 185E39
11880 | ALARM4 | Alarm 117 On | 185E40
11881 | ALARM4 | Alarm 117 Off | 185E41
11882 | ALARM4 | Alarm 118 On | 185E42
11883 | ALARM4 | Alarm 118 Off | 185E43
11884 | ALARM4 | Alarm 119 On | 185E44
11885 | ALARM4 | Alarm 119 Off | 185E45
11886 | ALARM4 | Alarm 120 On | 185E46
11887 | ALARM4 | Alarm 120 Off | 185E47
11888 | ALARM4 | Alarm 121 On | 185E48
11889 | ALARM4 | Alarm 121 Off | 185E49
11890 | ALARM4 | Alarm 122 On | 185E50
11891 | ALARM4 | Alarm 122 Off | 185E51
11892 | ALARM4 | Alarm 123 On | 185E52
11893 | ALARM4 | Alarm 123 Off | 185E53
11894 | ALARM4 | Alarm 124 On | 185E54
11895 | ALARM4 | Alarm 124 Off | 185E55
11896 | ALARM4 | Alarm 125 On | 185E56
11897 | ALARM4 | Alarm 125 Off | 185E57
11898 | ALARM4 | Alarm 126 On | 185E58
11899 | ALARM4 | Alarm 126 Off | 185E59
11900 | ALARM4 | Alarm 127 On | 185E60
11901 | ALARM4 | Alarm 127 Off | 185E61
11902 | ALARM4 | Alarm 128 On | 185E62
11903 | ALARM4 | Alarm 128 Off | 185E63
12096 | LDIF1 | Idb> Trip On | 189E0
12097 | LDIF1 | Idb> Trip Off | 189E1
12098 | LDIF1 | Idb> Blocked (ext) On | 189E2
12099 | LDIF1 | Idb> Blocked (ext) Off | 189E3
12100 | LDIF1 | Idi> Trip On | 189E4
12101 | LDIF1 | Idi> Trip Off | 189E5
12102 | LDIF1 | Idi> Blocked (ext) On | 189E6
12103 | LDIF1 | Idi> Blocked (ext) Off | 189E7
12104 | LDIF1 | 2.nd Harmonic Block On | 189E8
12105 | LDIF1 | 2.nd Harmonic Block Off | 189E9
12106 | LDIF1 | 5.th Harmonic Block On | 189E10
12107 | LDIF1 | 5.th Harmonic Block Off | 189E11
12108 | LDIF1 | L1 2.nd harm On | 189E12
12109 | LDIF1 | L1 2.nd harm Off | 189E13
12110 | LDIF1 | L2 2.nd harm On | 189E14
12111 | LDIF1 | L2 2.nd harm Off | 189E15
12112 | LDIF1 | L3 2.nd harm On | 189E16
12113 | LDIF1 | L3 2.nd harm Off | 189E17
12114 | LDIF1 | L1 5.th harm On | 189E18
12115 | LDIF1 | L1 5.th harm Off | 189E19
12116 | LDIF1 | L2 5.th harm On | 189E20
12117 | LDIF1 | L2 5.th harm Off | 189E21
12118 | LDIF1 | L3 5.th harm On | 189E22
12119 | LDIF1 | L3 5.th harm Off | 189E23
12160 | M1VT1 | Voltage memory enabled | 190E0
12161 | M1VT1 | Voltage memory disabled | 190E1
12162 | M1VT1 | Voltage low detected On | 190E2
12163 | M1VT1 | Voltage low detected Off | 190E3
12164 | M1VT1 | Current high detected On | 190E4
12165 | M1VT1 | Current high detected Off | 190E5
12166 | M1VT1 | Frequency tracked from CT On | 190E6
12167 | M1VT1 | Frequency tracked from CT Off | 190E7
12168 | M1VT1 | Using Voltage memory On | 190E8
12169 | M1VT1 | Using Voltage memory Off | 190E9
12170 | M1VT1 | Voltage memory blocked On | 190E10
12171 | M1VT1 | Voltage memory blocked Off | 190E11
12288 | NOCS1 | Start ON | 192E0
12289 | NOCS1 | Start OFF | 192E1
12290 | NOCS1 | Trip ON | 192E2
12291 | NOCS1 | Trip OFF | 192E3
12292 | NOCS1 | Block ON | 192E4
12293 | NOCS1 | Block OFF | 192E5
12294 | NOCS1 | L1 Start ON | 192E6
12295 | NOCS1 | L1 Start OFF | 192E7
12296 | NOCS1 | L2 Start ON | 192E8
12297 | NOCS1 | L2 Start OFF | 192E9
12298 | NOCS1 | L3 Start ON | 192E10
12299 | NOCS1 | L3 Start OFF | 192E11
12300 | NOCS1 | L1 Trip ON | 192E12
12301 | NOCS1 | L1 Trip OFF | 192E13
12302 | NOCS1 | L2 Trip ON | 192E14
12303 | NOCS1 | L2 Trip OFF | 192E15
12304 | NOCS1 | L3 Trip ON | 192E16
12305 | NOCS1 | L3 Trip OFF | 192E17
12352 | OBJS1 | Object A(L1) Intermediate | 193E0
12353 | OBJS1 | Object A(L1) Open | 193E1
12354 | OBJS1 | Object A(L1) Close | 193E2
12355 | OBJS1 | Object A(L1) Bad | 193E3
12356 | OBJS1 | Object B(L2) Open | 193E4
12357 | OBJS1 | Object B(L2) Close | 193E5
12358 | OBJS1 | Object B(L2) Bad | 193E6
12359 | OBJS1 | Object B(L2) Intermediate | 193E7
12360 | OBJS1 | Object C(L3) Open | 193E8
12361 | OBJS1 | Object C(L3) Close | 193E9
12362 | OBJS1 | Object C(L3) Bad | 193E10
12363 | OBJS1 | Object C(L3) Intermediate | 193E11
12364 | OBJS1 | WD Cart Intermediate | 193E12
12365 | OBJS1 | WD Cart Open | 193E13
12366 | OBJS1 | WD Cart Close | 193E14
12367 | OBJS1 | WD Cart Bad | 193E15
12368 | OBJS1 | Object A(L1) Open Command On | 193E16
12369 | OBJS1 | Object A(L1) Open Command Off | 193E17
12370 | OBJS1 | Object B(L2) Open Command On | 193E18
12371 | OBJS1 | Object B(L2) Open Command Off | 193E19
12372 | OBJS1 | Object C(L3) Open Command On | 193E20
12373 | OBJS1 | Object C(L3) Open Command Off | 193E21
12374 | OBJS1 | Close Command On | 193E22
12375 | OBJS1 | Close Command Off | 193E23
12376 | OBJS1 | Open Commands Blocked | 193E24
12377 | OBJS1 | Open Commands Allowed | 193E25
12378 | OBJS1 | Close Commands Blocked | 193E26
12379 | OBJS1 | Close Commands Allowed | 193E27
12380 | OBJS1 | Object Is Ready | 193E28
12381 | OBJS1 | Object Not Ready, Wait for Ready | 193E29
12382 | OBJS1 | Sync Is Ok | 193E30
12383 | OBJS1 | Sync Not Ok Wait for sync | 193E31
12384 | OBJS1 | Final Trip On | 193E32
12385 | OBJS1 | Final Trip Off | 193E33
12386 | OBJS1 | Open Command Fail On | 193E34
12387 | OBJS1 | Open Command Fail Off | 193E35
12388 | OBJS1 | Close Command Fail On | 193E36
12389 | OBJS1 | Close Command Fail Off | 193E37
12390 | OBJS1 | L1 Open Command Timeout On | 193E38
12391 | OBJS1 | L1 Open Command Timeout On | 193E39
12392 | OBJS1 | L2 Open Command Timeout On | 193E40
12393 | OBJS1 | L2 Open Command Timeout On | 193E41
12394 | OBJS1 | L3 Open Command Timeout On | 193E42
12395 | OBJS1 | L3 Open Command Timeout On | 193E43
12396 | OBJS1 | Close Command Timeout On | 193E44
12397 | OBJS1 | Close Command Timeout On | 193E45
12416 | NOCS2 | Start ON | 194E0
12417 | NOCS2 | Start OFF | 194E1
12418 | NOCS2 | Trip ON | 194E2
12419 | NOCS2 | Trip OFF | 194E3
12420 | NOCS2 | Block ON | 194E4
12421 | NOCS2 | Block OFF | 194E5
12422 | NOCS2 | L1 Start ON | 194E6
12423 | NOCS2 | L1 Start OFF | 194E7
12424 | NOCS2 | L2 Start ON | 194E8
12425 | NOCS2 | L2 Start OFF | 194E9
12426 | NOCS2 | L3 Start ON | 194E10
12427 | NOCS2 | L3 Start OFF | 194E11
12428 | NOCS2 | L1 Trip ON | 194E12
12429 | NOCS2 | L1 Trip OFF | 194E13
12430 | NOCS2 | L2 Trip ON | 194E14
12431 | NOCS2 | L2 Trip OFF | 194E15
12432 | NOCS2 | L3 Trip ON | 194E16
12433 | NOCS2 | L3 Trip OFF | 194E17
12480 | SGS2 | SG2 Enabled | 195E0
12481 | SGS2 | SG2 Disabled | 195E1
12482 | SGS2 | SG3 Enabled | 195E2
12483 | SGS2 | SG3 Disabled | 195E3
12484 | SGS2 | SG4 Enabled | 195E4
12485 | SGS2 | SG4 Disabled | 195E5
12486 | SGS2 | SG5 Enabled | 195E6
12487 | SGS2 | SG5 Disabled | 195E7
12488 | SGS2 | SG6 Enabled | 195E8
12489 | SGS2 | SG6 Disabled | 195E9
12490 | SGS2 | SG7 Enabled | 195E10
12491 | SGS2 | SG7 Disabled | 195E11
12492 | SGS2 | SG8 Enabled | 195E12
12493 | SGS2 | SG8 Disabled | 195E13
12494 | SGS2 | SG1 Request On | 195E14
12495 | SGS2 | SG1 Request Off | 195E15
12496 | SGS2 | SG2 Request On | 195E16
12497 | SGS2 | SG2 Request Off | 195E17
12498 | SGS2 | SG3 Request On | 195E18
12499 | SGS2 | SG3 Request Off | 195E19
12500 | SGS2 | SG4 Request On | 195E20
12501 | SGS2 | SG4 Request Off | 195E21
12502 | SGS2 | SG5 Request On | 195E22
12503 | SGS2 | SG5 Request Off | 195E23
12504 | SGS2 | SG6 Request On | 195E24
12505 | SGS2 | SG6 Request Off | 195E25
12506 | SGS2 | SG7 Request On | 195E26
12507 | SGS2 | SG7 Request Off | 195E27
12508 | SGS2 | SG8 Request On | 195E28
12509 | SGS2 | SG8 Request Off | 195E29
12510 | SGS2 | Remote Change SG Req On | 195E30
12511 | SGS2 | Remote Change SG Req Off | 195E31
12512 | SGS2 | Local Change SG Req On | 195E32
12513 | SGS2 | Local Change SG Req On | 195E33
12514 | SGS2 | Force Change SG On | 195E34
12515 | SGS2 | Force Change SG Off | 195E35
12516 | SGS2 | SG Req. Fail Not configured SG On | 195E36
12517 | SGS2 | SG Req. Fail Not configured SG On | 195E37
12518 | SGS2 | Force Req. Fail Force not On | 195E38
12519 | SGS2 | Force Req. Fail Off | 195E39
12520 | SGS2 | SG Req. Fail Lower priority Req. On | 195E40
12521 | SGS2 | SG Req. Fail Lower priority Req. Off | 195E41
12522 | SGS2 | SG1 Active On | 195E42
12523 | SGS2 | SG1 Active Off | 195E43
12524 | SGS2 | SG2 Active On | 195E44
12525 | SGS2 | SG2 Active Off | 195E45
12526 | SGS2 | SG3 Active On | 195E46
12527 | SGS2 | SG3 Active Off | 195E47
12528 | SGS2 | SG4 Active On | 195E48
12529 | SGS2 | SG4 Active Off | 195E49
12530 | SGS2 | SG5 Active On | 195E50
12531 | SGS2 | SG5 Active Off | 195E51
12532 | SGS2 | SG6 Active On | 195E52
12533 | SGS2 | SG6 Active Off | 195E53
12534 | SGS2 | SG7 Active On | 195E54
12535 | SGS2 | SG7 Active Off | 195E55
12536 | SGS2 | SG8 Active On | 195E56
12537 | SGS2 | SG8 Active Off | 195E57
12544 | URX1 | Start ON | 196E0
12545 | URX1 | Start OFF | 196E1
12546 | URX1 | Trip ON | 196E2
12547 | URX1 | Trip OFF | 196E3
12548 | URX1 | Block ON | 196E4
12549 | URX1 | Block OFF | 196E5
12608 | URX2 | Start ON | 197E0
12609 | URX2 | Start OFF | 197E1
12610 | URX2 | Trip ON | 197E2
12611 | URX2 | Trip OFF | 197E3
12612 | URX2 | Block ON | 197E4
12613 | URX2 | Block OFF | 197E5
12736 | MGWB1 | On Bit 1 | 199E0
12737 | MGWB1 | Off Bit 1 | 199E1
12738 | MGWB1 | On Bit 2 | 199E2
12739 | MGWB1 | Off Bit 2 | 199E3
12740 | MGWB1 | On Bit 3 | 199E4
12741 | MGWB1 | Off Bit 3 | 199E5
12742 | MGWB1 | On Bit 4 | 199E6
12743 | MGWB1 | Off Bit 4 | 199E7
12744 | MGWB1 | On Bit 5 | 199E8
12745 | MGWB1 | Off Bit 5 | 199E9
12746 | MGWB1 | On Bit 6 | 199E10
12747 | MGWB1 | Off Bit 6 | 199E11
12748 | MGWB1 | On Bit 7 | 199E12
12749 | MGWB1 | Off Bit 7 | 199E13
12750 | MGWB1 | On Bit 8 | 199E14
12751 | MGWB1 | Off Bit 8 | 199E15
12752 | MGWB1 | On Bit 9 | 199E16
12753 | MGWB1 | Off Bit 9 | 199E17
12754 | MGWB1 | On Bit 10 | 199E18
12755 | MGWB1 | Off Bit 10 | 199E19
12756 | MGWB1 | On Bit 11 | 199E20
12757 | MGWB1 | Off Bit 11 | 199E21
12758 | MGWB1 | On Bit 12 | 199E22
12759 | MGWB1 | Off Bit 12 | 199E23
12760 | MGWB1 | On Bit 13 | 199E24
12761 | MGWB1 | Off Bit 13 | 199E25
12762 | MGWB1 | On Bit 14 | 199E26
12763 | MGWB1 | Off Bit 14 | 199E27
12764 | MGWB1 | On Bit 15 | 199E28
12765 | MGWB1 | Off Bit 15 | 199E29
12766 | MGWB1 | On Bit 16 | 199E30
12767 | MGWB1 | Off Bit 16 | 199E31
12768 | MGWB1 | On Bit 17 | 199E32
12769 | MGWB1 | Off Bit 17 | 199E33
12770 | MGWB1 | On Bit 18 | 199E34
12771 | MGWB1 | Off Bit 18 | 199E35
12772 | MGWB1 | On Bit 19 | 199E36
12773 | MGWB1 | Off Bit 19 | 199E37
12774 | MGWB1 | On Bit 20 | 199E38
12775 | MGWB1 | Off Bit 20 | 199E39
12776 | MGWB1 | On Bit 21 | 199E40
12777 | MGWB1 | Off Bit 21 | 199E41
12778 | MGWB1 | On Bit 22 | 199E42
12779 | MGWB1 | Off Bit 22 | 199E43
12780 | MGWB1 | On Bit 23 | 199E44
12781 | MGWB1 | Off Bit 23 | 199E45
12782 | MGWB1 | On Bit 24 | 199E46
12783 | MGWB1 | Off Bit 24 | 199E47
12784 | MGWB1 | On Bit 25 | 199E48
12785 | MGWB1 | Off Bit 25 | 199E49
12786 | MGWB1 | On Bit 26 | 199E50
12787 | MGWB1 | Off Bit 26 | 199E51
12788 | MGWB1 | On Bit 27 | 199E52
12789 | MGWB1 | Off Bit 27 | 199E53
12790 | MGWB1 | On Bit 28 | 199E54
12791 | MGWB1 | Off Bit 28 | 199E55
12792 | MGWB1 | On Bit 29 | 199E56
12793 | MGWB1 | Off Bit 29 | 199E57
12794 | MGWB1 | On Bit 30 | 199E58
12795 | MGWB1 | Off Bit 30 | 199E59
12796 | MGWB1 | On Bit 31 | 199E60
12797 | MGWB1 | Off Bit 31 | 199E61
12798 | MGWB1 | On Bit 32 | 199E62
12799 | MGWB1 | Off Bit 32 | 199E63
12800 | MGWB2 | On Bit 33 | 200E0
12801 | MGWB2 | Off Bit 33 | 200E1
12802 | MGWB2 | On Bit 34 | 200E2
12803 | MGWB2 | Off Bit 34 | 200E3
12804 | MGWB2 | On Bit 35 | 200E4
12805 | MGWB2 | Off Bit 35 | 200E5
12806 | MGWB2 | On Bit 36 | 200E6
12807 | MGWB2 | Off Bit 36 | 200E7
12808 | MGWB2 | On Bit 37 | 200E8
12809 | MGWB2 | Off Bit 37 | 200E9
12810 | MGWB2 | On Bit 38 | 200E10
12811 | MGWB2 | Off Bit 38 | 200E11
12812 | MGWB2 | On Bit 39 | 200E12
12813 | MGWB2 | Off Bit 39 | 200E13
12814 | MGWB2 | On Bit 40 | 200E14
12815 | MGWB2 | Off Bit 40 | 200E15
12816 | MGWB2 | On Bit 41 | 200E16
12817 | MGWB2 | Off Bit 41 | 200E17
12818 | MGWB2 | On Bit 42 | 200E18
12819 | MGWB2 | Off Bit 42 | 200E19
12820 | MGWB2 | On Bit 43 | 200E20
12821 | MGWB2 | Off Bit 43 | 200E21
12822 | MGWB2 | On Bit 44 | 200E22
12823 | MGWB2 | Off Bit 44 | 200E23
12824 | MGWB2 | On Bit 45 | 200E24
12825 | MGWB2 | Off Bit 45 | 200E25
12826 | MGWB2 | On Bit 46 | 200E26
12827 | MGWB2 | Off Bit 46 | 200E27
12828 | MGWB2 | On Bit 47 | 200E28
12829 | MGWB2 | Off Bit 47 | 200E29
12830 | MGWB2 | On Bit 48 | 200E30
12831 | MGWB2 | Off Bit 48 | 200E31
12832 | MGWB2 | On Bit 49 | 200E32
12833 | MGWB2 | Off Bit 49 | 200E33
12834 | MGWB2 | On Bit 50 | 200E34
12835 | MGWB2 | Off Bit 50 | 200E35
12836 | MGWB2 | On Bit 51 | 200E36
12837 | MGWB2 | Off Bit 51 | 200E37
12838 | MGWB2 | On Bit 52 | 200E38
12839 | MGWB2 | Off Bit 52 | 200E39
12840 | MGWB2 | On Bit 53 | 200E40
12841 | MGWB2 | Off Bit 53 | 200E41
12842 | MGWB2 | On Bit 54 | 200E42
12843 | MGWB2 | Off Bit 54 | 200E43
12844 | MGWB2 | On Bit 55 | 200E44
12845 | MGWB2 | Off Bit 55 | 200E45
12846 | MGWB2 | On Bit 56 | 200E46
12847 | MGWB2 | Off Bit 56 | 200E47
12848 | MGWB2 | On Bit 57 | 200E48
12849 | MGWB2 | Off Bit 57 | 200E49
12850 | MGWB2 | On Bit 58 | 200E50
12851 | MGWB2 | Off Bit 58 | 200E51
12852 | MGWB2 | On Bit 59 | 200E52
12853 | MGWB2 | Off Bit 59 | 200E53
12854 | MGWB2 | On Bit 60 | 200E54
12855 | MGWB2 | Off Bit 60 | 200E55
12856 | MGWB2 | On Bit 61 | 200E56
12857 | MGWB2 | Off Bit 61 | 200E57
12858 | MGWB2 | On Bit 62 | 200E58
12859 | MGWB2 | Off Bit 62 | 200E59
12860 | MGWB2 | On Bit 63 | 200E60
12861 | MGWB2 | Off Bit 63 | 200E61
12862 | MGWB2 | On Bit 64 | 200E62
12863 | MGWB2 | Off Bit 64 | 200E63
12864 | MGWB3 | On Bit 65 | 201E0
12865 | MGWB3 | Off Bit 65 | 201E1
12866 | MGWB3 | On Bit 66 | 201E2
12867 | MGWB3 | Off Bit 66 | 201E3
12868 | MGWB3 | On Bit 67 | 201E4
12869 | MGWB3 | Off Bit 67 | 201E5
12870 | MGWB3 | On Bit 68 | 201E6
12871 | MGWB3 | Off Bit 68 | 201E7
12872 | MGWB3 | On Bit 69 | 201E8
12873 | MGWB3 | Off Bit 69 | 201E9
12874 | MGWB3 | On Bit 70 | 201E10
12875 | MGWB3 | Off Bit 70 | 201E11
12876 | MGWB3 | On Bit 71 | 201E12
12877 | MGWB3 | Off Bit 71 | 201E13
12878 | MGWB3 | On Bit 72 | 201E14
12879 | MGWB3 | Off Bit 72 | 201E15
12880 | MGWB3 | On Bit 73 | 201E16
12881 | MGWB3 | Off Bit 73 | 201E17
12882 | MGWB3 | On Bit 74 | 201E18
12883 | MGWB3 | Off Bit 74 | 201E19
12884 | MGWB3 | On Bit 75 | 201E20
12885 | MGWB3 | Off Bit 75 | 201E21
12886 | MGWB3 | On Bit 76 | 201E22
12887 | MGWB3 | Off Bit 76 | 201E23
12888 | MGWB3 | On Bit 77 | 201E24
12889 | MGWB3 | Off Bit 77 | 201E25
12890 | MGWB3 | On Bit 78 | 201E26
12891 | MGWB3 | Off Bit 78 | 201E27
12892 | MGWB3 | On Bit 79 | 201E28
12893 | MGWB3 | Off Bit 79 | 201E29
12894 | MGWB3 | On Bit 80 | 201E30
12895 | MGWB3 | Off Bit 80 | 201E31
12896 | MGWB3 | On Bit 81 | 201E32
12897 | MGWB3 | Off Bit 81 | 201E33
12898 | MGWB3 | On Bit 82 | 201E34
12899 | MGWB3 | Off Bit 82 | 201E35
12900 | MGWB3 | On Bit 83 | 201E36
12901 | MGWB3 | Off Bit 83 | 201E37
12902 | MGWB3 | On Bit 84 | 201E38
12903 | MGWB3 | Off Bit 84 | 201E39
12904 | MGWB3 | On Bit 85 | 201E40
12905 | MGWB3 | Off Bit 85 | 201E41
12906 | MGWB3 | On Bit 86 | 201E42
12907 | MGWB3 | Off Bit 86 | 201E43
12908 | MGWB3 | On Bit 87 | 201E44
12909 | MGWB3 | Off Bit 87 | 201E45
12910 | MGWB3 | On Bit 88 | 201E46
12911 | MGWB3 | Off Bit 88 | 201E47
12912 | MGWB3 | On Bit 89 | 201E48
12913 | MGWB3 | Off Bit 89 | 201E49
12914 | MGWB3 | On Bit 90 | 201E50
12915 | MGWB3 | Off Bit 90 | 201E51
12916 | MGWB3 | On Bit 91 | 201E52
12917 | MGWB3 | Off Bit 91 | 201E53
12918 | MGWB3 | On Bit 92 | 201E54
12919 | MGWB3 | Off Bit 92 | 201E55
12920 | MGWB3 | On Bit 93 | 201E56
12921 | MGWB3 | Off Bit 93 | 201E57
12922 | MGWB3 | On Bit 94 | 201E58
12923 | MGWB3 | Off Bit 94 | 201E59
12924 | MGWB3 | On Bit 95 | 201E60
12925 | MGWB3 | Off Bit 95 | 201E61
12926 | MGWB3 | On Bit 96 | 201E62
12927 | MGWB3 | Off Bit 96 | 201E63
12928 | MGWB4 | On Bit 97 | 202E0
12929 | MGWB4 | Off Bit 97 | 202E1
12930 | MGWB4 | On Bit 98 | 202E2
12931 | MGWB4 | Off Bit 98 | 202E3
12932 | MGWB4 | On Bit 99 | 202E4
12933 | MGWB4 | Off Bit 99 | 202E5
12934 | MGWB4 | On Bit 100 | 202E6
12935 | MGWB4 | Off Bit 100 | 202E7
12936 | MGWB4 | On Bit 101 | 202E8
12937 | MGWB4 | Off Bit 101 | 202E9
12938 | MGWB4 | On Bit 102 | 202E10
12939 | MGWB4 | Off Bit 102 | 202E11
12940 | MGWB4 | On Bit 103 | 202E12
12941 | MGWB4 | Off Bit 103 | 202E13
12942 | MGWB4 | On Bit 104 | 202E14
12943 | MGWB4 | Off Bit 104 | 202E15
12944 | MGWB4 | On Bit 105 | 202E16
12945 | MGWB4 | Off Bit 105 | 202E17
12946 | MGWB4 | On Bit 106 | 202E18
12947 | MGWB4 | Off Bit 106 | 202E19
12948 | MGWB4 | On Bit 107 | 202E20
12949 | MGWB4 | Off Bit 107 | 202E21
12950 | MGWB4 | On Bit 108 | 202E22
12951 | MGWB4 | Off Bit 108 | 202E23
12952 | MGWB4 | On Bit 109 | 202E24
12953 | MGWB4 | Off Bit 109 | 202E25
12954 | MGWB4 | On Bit 110 | 202E26
12955 | MGWB4 | Off Bit 110 | 202E27
12956 | MGWB4 | On Bit 111 | 202E28
12957 | MGWB4 | Off Bit 111 | 202E29
12958 | MGWB4 | On Bit 112 | 202E30
12959 | MGWB4 | Off Bit 112 | 202E31
12960 | MGWB4 | On Bit 113 | 202E32
12961 | MGWB4 | Off Bit 113 | 202E33
12962 | MGWB4 | On Bit 114 | 202E34
12963 | MGWB4 | Off Bit 114 | 202E35
12964 | MGWB4 | On Bit 115 | 202E36
12965 | MGWB4 | Off Bit 115 | 202E37
12966 | MGWB4 | On Bit 116 | 202E38
12967 | MGWB4 | Off Bit 116 | 202E39
12968 | MGWB4 | On Bit 117 | 202E40
12969 | MGWB4 | Off Bit 117 | 202E41
12970 | MGWB4 | On Bit 118 | 202E42
12971 | MGWB4 | Off Bit 118 | 202E43
12972 | MGWB4 | On Bit 119 | 202E44
12973 | MGWB4 | Off Bit 119 | 202E45
12974 | MGWB4 | On Bit 120 | 202E46
12975 | MGWB4 | Off Bit 120 | 202E47
12976 | MGWB4 | On Bit 121 | 202E48
12977 | MGWB4 | Off Bit 121 | 202E49
12978 | MGWB4 | On Bit 122 | 202E50
12979 | MGWB4 | Off Bit 122 | 202E51
12980 | MGWB4 | On Bit 123 | 202E52
12981 | MGWB4 | Off Bit 123 | 202E53
12982 | MGWB4 | On Bit 124 | 202E54
12983 | MGWB4 | Off Bit 124 | 202E55
12984 | MGWB4 | On Bit 125 | 202E56
12985 | MGWB4 | Off Bit 125 | 202E57
12986 | MGWB4 | On Bit 126 | 202E58
12987 | MGWB4 | Off Bit 126 | 202E59
12988 | MGWB4 | On Bit 127 | 202E60
12989 | MGWB4 | Off Bit 127 | 202E61
12990 | MGWB4 | On Bit 128 | 202E62
12991 | MGWB4 | Off Bit 128 | 202E63
12992 | MGWD1 | Off Off Double Bit 1 | 203E0
12993 | MGWD1 | On Off Double Bit 1 | 203E1
12994 | MGWD1 | Off On Double Bit 1 | 203E2
12995 | MGWD1 | On On Double Bit 1 | 203E3
12996 | MGWD1 | Off Off Double Bit 2 | 203E4
12997 | MGWD1 | On Off Double Bit 2 | 203E5
12998 | MGWD1 | Off On Double Bit 2 | 203E6
12999 | MGWD1 | On On Double Bit 2 | 203E7
13000 | MGWD1 | Off Off Double Bit 3 | 203E8
13001 | MGWD1 | On Off Double Bit 3 | 203E9
13002 | MGWD1 | Off On Double Bit 3 | 203E10
13003 | MGWD1 | On On Double Bit 3 | 203E11
13004 | MGWD1 | Off Off Double Bit 4 | 203E12
13005 | MGWD1 | On Off Double Bit 4 | 203E13
13006 | MGWD1 | Off On Double Bit 4 | 203E14
13007 | MGWD1 | On On Double Bit 4 | 203E15
13008 | MGWD1 | Off Off Double Bit 5 | 203E16
13009 | MGWD1 | On Off Double Bit 5 | 203E17
13010 | MGWD1 | Off On Double Bit 5 | 203E18
13011 | MGWD1 | On On Double Bit 5 | 203E19
13012 | MGWD1 | Off Off Double Bit 6 | 203E20
13013 | MGWD1 | On Off Double Bit 6 | 203E21
13014 | MGWD1 | Off On Double Bit 6 | 203E22
13015 | MGWD1 | On On Double Bit 6 | 203E23
13016 | MGWD1 | Off Off Double Bit 7 | 203E24
13017 | MGWD1 | On Off Double Bit 7 | 203E25
13018 | MGWD1 | Off On Double Bit 7 | 203E26
13019 | MGWD1 | On On Double Bit 7 | 203E27
13020 | MGWD1 | Off Off Double Bit 8 | 203E28
13021 | MGWD1 | On Off Double Bit 8 | 203E29
13022 | MGWD1 | Off On Double Bit 8 | 203E30
13023 | MGWD1 | On On Double Bit 8 | 203E31
13024 | MGWD1 | Off Off Double Bit 9 | 203E32
13025 | MGWD1 | On Off Double Bit 9 | 203E33
13026 | MGWD1 | Off On Double Bit 9 | 203E34
13027 | MGWD1 | On On Double Bit 9 | 203E35
13028 | MGWD1 | Off Off Double Bit 10 | 203E36
13029 | MGWD1 | On Off Double Bit 10 | 203E37
13030 | MGWD1 | Off On Double Bit 10 | 203E38
13031 | MGWD1 | On On Double Bit 10 | 203E39
13032 | MGWD1 | Off Off Double Bit 11 | 203E40
13033 | MGWD1 | On Off Double Bit 11 | 203E41
13034 | MGWD1 | Off On Double Bit 11 | 203E42
13035 | MGWD1 | On On Double Bit 11 | 203E43
13036 | MGWD1 | Off Off Double Bit 12 | 203E44
13037 | MGWD1 | On Off Double Bit 12 | 203E45
13038 | MGWD1 | Off On Double Bit 12 | 203E46
13039 | MGWD1 | On On Double Bit 12 | 203E47
13040 | MGWD1 | Off Off Double Bit 13 | 203E48
13041 | MGWD1 | On Off Double Bit 13 | 203E49
13042 | MGWD1 | Off On Double Bit 13 | 203E50
13043 | MGWD1 | On On Double Bit 13 | 203E51
13044 | MGWD1 | Off Off Double Bit 14 | 203E52
13045 | MGWD1 | On Off Double Bit 14 | 203E53
13046 | MGWD1 | Off On Double Bit 14 | 203E54
13047 | MGWD1 | On On Double Bit 14 | 203E55
13048 | MGWD1 | Off Off Double Bit 15 | 203E56
13049 | MGWD1 | On Off Double Bit 15 | 203E57
13050 | MGWD1 | Off On Double Bit 15 | 203E58
13051 | MGWD1 | On On Double Bit 15 | 203E59
13052 | MGWD1 | Off Off Double Bit 16 | 203E60
13053 | MGWD1 | On Off Double Bit 16 | 203E61
13054 | MGWD1 | Off On Double Bit 16 | 203E62
13055 | MGWD1 | On On Double Bit 16 | 203E63
13056 | MGWD2 | Off Off Double Bit 17 | 204E0
13057 | MGWD2 | On Off Double Bit 17 | 204E1
13058 | MGWD2 | Off On Double Bit 17 | 204E2
13059 | MGWD2 | On On Double Bit 17 | 204E3
13060 | MGWD2 | Off Off Double Bit 18 | 204E4
13061 | MGWD2 | On Off Double Bit 18 | 204E5
13062 | MGWD2 | Off On Double Bit 18 | 204E6
13063 | MGWD2 | On On Double Bit 18 | 204E7
13064 | MGWD2 | Off Off Double Bit 19 | 204E8
13065 | MGWD2 | On Off Double Bit 19 | 204E9
13066 | MGWD2 | Off On Double Bit 19 | 204E10
13067 | MGWD2 | On On Double Bit 19 | 204E11
13068 | MGWD2 | Off Off Double Bit 20 | 204E12
13069 | MGWD2 | On Off Double Bit 20 | 204E13
13070 | MGWD2 | Off On Double Bit 20 | 204E14
13071 | MGWD2 | On On Double Bit 20 | 204E15
13072 | MGWD2 | Off Off Double Bit 21 | 204E16
13073 | MGWD2 | On Off Double Bit 21 | 204E17
13074 | MGWD2 | Off On Double Bit 21 | 204E18
13075 | MGWD2 | On On Double Bit 21 | 204E19
13076 | MGWD2 | Off Off Double Bit 22 | 204E20
13077 | MGWD2 | On Off Double Bit 22 | 204E21
13078 | MGWD2 | Off On Double Bit 22 | 204E22
13079 | MGWD2 | On On Double Bit 22 | 204E23
13080 | MGWD2 | Off Off Double Bit 23 | 204E24
13081 | MGWD2 | On Off Double Bit 23 | 204E25
13082 | MGWD2 | Off On Double Bit 23 | 204E26
13083 | MGWD2 | On On Double Bit 23 | 204E27
13084 | MGWD2 | Off Off Double Bit 24 | 204E28
13085 | MGWD2 | On Off Double Bit 24 | 204E29
13086 | MGWD2 | Off On Double Bit 24 | 204E30
13087 | MGWD2 | On On Double Bit 24 | 204E31
13088 | MGWD2 | Off Off Double Bit 25 | 204E32
13089 | MGWD2 | On Off Double Bit 25 | 204E33
13090 | MGWD2 | Off On Double Bit 25 | 204E34
13091 | MGWD2 | On On Double Bit 25 | 204E35
13092 | MGWD2 | Off Off Double Bit 26 | 204E36
13093 | MGWD2 | On Off Double Bit 26 | 204E37
13094 | MGWD2 | Off On Double Bit 26 | 204E38
13095 | MGWD2 | On On Double Bit 26 | 204E39
13096 | MGWD2 | Off Off Double Bit 27 | 204E40
13097 | MGWD2 | On Off Double Bit 27 | 204E41
13098 | MGWD2 | Off On Double Bit 27 | 204E42
13099 | MGWD2 | On On Double Bit 27 | 204E43
13100 | MGWD2 | Off Off Double Bit 28 | 204E44
13101 | MGWD2 | On Off Double Bit 28 | 204E45
13102 | MGWD2 | Off On Double Bit 28 | 204E46
13103 | MGWD2 | On On Double Bit 28 | 204E47
13104 | MGWD2 | Off Off Double Bit 29 | 204E48
13105 | MGWD2 | On Off Double Bit 29 | 204E49
13106 | MGWD2 | Off On Double Bit 29 | 204E50
13107 | MGWD2 | On On Double Bit 29 | 204E51
13108 | MGWD2 | Off Off Double Bit 30 | 204E52
13109 | MGWD2 | On Off Double Bit 30 | 204E53
13110 | MGWD2 | Off On Double Bit 30 | 204E54
13111 | MGWD2 | On On Double Bit 30 | 204E55
13112 | MGWD2 | Off Off Double Bit 31 | 204E56
13113 | MGWD2 | On Off Double Bit 31 | 204E57
13114 | MGWD2 | Off On Double Bit 31 | 204E58
13115 | MGWD2 | On On Double Bit 31 | 204E59
13116 | MGWD2 | Off Off Double Bit 32 | 204E60
13117 | MGWD2 | On Off Double Bit 32 | 204E61
13118 | MGWD2 | Off On Double Bit 32 | 204E62
13119 | MGWD2 | On On Double Bit 32 | 204E63
13120 | ROC1 | Start ON | 205E0
13121 | ROC1 | Start OFF | 205E1
13122 | ROC1 | Trip ON | 205E2
13123 | ROC1 | Trip OFF | 205E3
13124 | ROC1 | Block ON | 205E4
13125 | ROC1 | Block OFF | 205E5
13184 | ROC2 | Start ON | 206E0
13185 | ROC2 | Start OFF | 206E1
13186 | ROC2 | Trip ON | 206E2
13187 | ROC2 | Trip OFF | 206E3
13188 | ROC2 | Block ON | 206E4
13189 | ROC2 | Block OFF | 206E5
13248 | ROC3 | Start ON | 207E0
13249 | ROC3 | Start OFF | 207E1
13250 | ROC3 | Trip ON | 207E2
13251 | ROC3 | Trip OFF | 207E3
13252 | ROC3 | Block ON | 207E4
13253 | ROC3 | Block OFF | 207E5
13312 | ROC4 | Start ON | 208E0
13313 | ROC4 | Start OFF | 208E1
13314 | ROC4 | Trip ON | 208E2
13315 | ROC4 | Trip OFF | 208E3
13316 | ROC4 | Block ON | 208E4
13317 | ROC4 | Block OFF | 208E5
13376 | ROC5 | Start ON | 209E0
13377 | ROC5 | Start OFF | 209E1
13378 | ROC5 | Trip ON | 209E2
13379 | ROC5 | Trip OFF | 209E3
13380 | ROC5 | Block ON | 209E4
13381 | ROC5 | Block OFF | 209E5
13440 | ROC6 | Start ON | 210E0
13441 | ROC6 | Start OFF | 210E1
13442 | ROC6 | Trip ON | 210E2
13443 | ROC6 | Trip OFF | 210E3
13444 | ROC6 | Block ON | 210E4
13445 | ROC6 | Block OFF | 210E5
13504 | ROC7 | Start ON | 211E0
13505 | ROC7 | Start OFF | 211E1
13506 | ROC7 | Trip ON | 211E2
13507 | ROC7 | Trip OFF | 211E3
13508 | ROC7 | Block ON | 211E4
13509 | ROC7 | Block OFF | 211E5
13568 | ROC8 | Start ON | 212E0
13569 | ROC8 | Start OFF | 212E1
13570 | ROC8 | Trip ON | 212E2
13571 | ROC8 | Trip OFF | 212E3
13572 | ROC8 | Block ON | 212E4
13573 | ROC8 | Block OFF | 212E5
13632 | ROV1 | Start ON | 213E0
13633 | ROV1 | Start OFF | 213E1
13634 | ROV1 | Trip ON | 213E2
13635 | ROV1 | Trip OFF | 213E3
13636 | ROV1 | Block ON | 213E4
13637 | ROV1 | Block OFF | 213E5
13696 | ROV2 | Start ON | 214E0
13697 | ROV2 | Start OFF | 214E1
13698 | ROV2 | Trip ON | 214E2
13699 | ROV2 | Trip OFF | 214E3
13700 | ROV2 | Block ON | 214E4
13701 | ROV2 | Block OFF | 214E5
13760 | ROV3 | Start ON | 215E0
13761 | ROV3 | Start OFF | 215E1
13762 | ROV3 | Trip ON | 215E2
13763 | ROV3 | Trip OFF | 215E3
13764 | ROV3 | Block ON | 215E4
13765 | ROV3 | Block OFF | 215E5
13824 | ROV4 | Start ON | 216E0
13825 | ROV4 | Start OFF | 216E1
13826 | ROV4 | Trip ON | 216E2
13827 | ROV4 | Trip OFF | 216E3
13828 | ROV4 | Block ON | 216E4
13829 | ROV4 | Block OFF | 216E5
13888 | UCP1 | Alarm Start ON | 217E0
13889 | UCP1 | Alarm Start OFF | 217E1
13890 | UCP1 | Alarm ON | 217E2
13891 | UCP1 | Alarm OFF | 217E3
13892 | UCP1 | Start ON | 217E4
13893 | UCP1 | Start OFF | 217E5
13894 | UCP1 | Trip ON | 217E6
13895 | UCP1 | Trip OFF | 217E7
13896 | UCP1 | Block ON | 217E8
13897 | UCP1 | Block OFF | 217E9
13898 | UCP1 | Harmonic block ON | 217E10
13899 | UCP1 | Harmonic block OFF | 217E11
13952 | PGS1B | PS6 >/< Start ON | 218E0
13953 | PGS1B | PS6 >/< Start OFF | 218E1
13954 | PGS1B | PS6 >/< Trip ON | 218E2
13955 | PGS1B | PS6 >/< Trip OFF | 218E3
13956 | PGS1B | PS6 >/< Block ON | 218E4
13957 | PGS1B | PS6 >/< Block OFF | 218E5
13958 | PGS1B | PS7 >/< Start ON | 218E6
13959 | PGS1B | PS7 >/< Start OFF | 218E7
13960 | PGS1B | PS7 >/< Trip ON | 218E8
13961 | PGS1B | PS7 >/< Trip OFF | 218E9
13962 | PGS1B | PS7 >/< Block ON | 218E10
13963 | PGS1B | PS7 >/< Block OFF | 218E11
13964 | PGS1B | PS8 >/< Start ON | 218E12
13965 | PGS1B | PS8 >/< Start OFF | 218E13
13966 | PGS1B | PS8 >/< Trip ON | 218E14
13967 | PGS1B | PS8 >/< Trip OFF | 218E15
13968 | PGS1B | PS8 >/< Block ON | 218E16
13969 | PGS1B | PS8 >/< Block OFF | 218E17
13970 | PGS1B | PS9 >/< Start ON | 218E18
13971 | PGS1B | PS9 >/< Start OFF | 218E19
13972 | PGS1B | PS9 >/< Trip ON | 218E20
13973 | PGS1B | PS9 >/< Trip OFF | 218E21
13974 | PGS1B | PS9 >/< Block ON | 218E22
13975 | PGS1B | PS9 >/< Block OFF | 218E23
13976 | PGS1B | PS10 >/< Start ON | 218E24
13977 | PGS1B | PS10 >/< Start OFF | 218E25
13978 | PGS1B | PS10 >/< Trip ON | 218E26
13979 | PGS1B | PS10 >/< Trip OFF | 218E27
13980 | PGS1B | PS10 >/< Block ON | 218E28
13981 | PGS1B | PS10 >/< Block OFF | 218E29
14016 | SYNX1 | SYN1 Voltage difference Ok On | 219E0
14017 | SYNX1 | SYN1 Voltage difference Ok Off | 219E1
14018 | SYNX1 | SYN1 Angle difference Ok On | 219E2
14019 | SYNX1 | SYN1 Angle difference Ok Off | 219E3
14020 | SYNX1 | SYN1 Frequency difference Ok On | 219E4
14021 | SYNX1 | SYN1 Frequency difference Ok On | 219E5
14022 | SYNX1 | SYN1 Live Live Condition On | 219E6
14023 | SYNX1 | SYN1 Live Live Condition Off | 219E7
14024 | SYNX1 | SYN1 Live Dead Condition On | 219E8
14025 | SYNX1 | SYN1 Live Dead Condition Off | 219E9
14026 | SYNX1 | SYN1 Dead Live Condition On | 219E10
14027 | SYNX1 | SYN1 Dead Live Condition Off | 219E11
14028 | SYNX1 | SYN1 Dead Dead Condition On | 219E12
14029 | SYNX1 | SYN1 Dead Dead Condition On | 219E13
14030 | SYNX1 | SYN1 Voltage Difference too high Vbus > Vline On | 219E14
14031 | SYNX1 | SYN1 Voltage Difference too high Vbus > Vline Off | 219E15
14032 | SYNX1 | SYN1 Voltage Difference too high Vline > Vbus On | 219E16
14033 | SYNX1 | SYN1 Voltage Difference too high Vline > Vbus Off | 219E17
14034 | SYNX1 | SYN1 Frequency Difference too high fbus > fline On | 219E18
14035 | SYNX1 | SYN1 Frequency Difference too high fbus > fline Off | 219E19
14036 | SYNX1 | SYN1 Frequency Difference too high fline > fbus On | 219E20
14037 | SYNX1 | SYN1 Frequency Difference too high fline > fbus Off | 219E21
14038 | SYNX1 | SYN1 Angle Difference too high a bus leads a line On | 219E22
14039 | SYNX1 | SYN1 Angle Difference too high a bus leads a line Off | 219E23
14040 | SYNX1 | SYN1 Angle Difference too high a line leads a bus On | 219E24
14041 | SYNX1 | SYN1 Angle Difference too high a line leads a bus Off | 219E25
14042 | SYNX1 | SYN1 Bus voltage Live On | 219E26
14043 | SYNX1 | SYN1 Bus voltage Live Off | 219E27
14044 | SYNX1 | SYN1 Bus voltage Dead On | 219E28
14045 | SYNX1 | SYN1 Bus voltage Dead Off | 219E29
14046 | SYNX1 | SYN1 Line voltage Live On | 219E30
14047 | SYNX1 | SYN1 Line voltage Live Off | 219E31
14048 | SYNX1 | SYN1 Line voltage Dead On | 219E32
14049 | SYNX1 | SYN1 Line voltage Dead Off | 219E33
14080 | SYNX2 | SYN2 Voltage difference Ok On | 220E0
14081 | SYNX2 | SYN2 Voltage difference Ok Off | 220E1
14082 | SYNX2 | SYN2 Angle difference Ok On | 220E2
14083 | SYNX2 | SYN2 Angle difference Ok Off | 220E3
14084 | SYNX2 | SYN2 Frequency difference Ok On | 220E4
14085 | SYNX2 | SYN2 Frequency difference Ok On | 220E5
14086 | SYNX2 | SYN2 Live Live Condition On | 220E6
14087 | SYNX2 | SYN2 Live Live Condition Off | 220E7
14088 | SYNX2 | SYN2 Live Dead Condition On | 220E8
14089 | SYNX2 | SYN2 Live Dead Condition Off | 220E9
14090 | SYNX2 | SYN2 Dead Live Condition On | 220E10
14091 | SYNX2 | SYN2 Dead Live Condition Off | 220E11
14092 | SYNX2 | SYN2 Dead Dead Condition On | 220E12
14093 | SYNX2 | SYN2 Dead Dead Condition On | 220E13
14094 | SYNX2 | SYN2 Voltage Difference too high Vbus > Vline On | 220E14
14095 | SYNX2 | SYN2 Voltage Difference too high Vbus > Vline Off | 220E15
14096 | SYNX2 | SYN2 Voltage Difference too high Vline > Vbus On | 220E16
14097 | SYNX2 | SYN2 Voltage Difference too high Vline > Vbus Off | 220E17
14098 | SYNX2 | SYN2 Frequency Difference too high fbus > fline On | 220E18
14099 | SYNX2 | SYN2 Frequency Difference too high fbus > fline Off | 220E19
14100 | SYNX2 | SYN2 Frequency Difference too high fline > fbus On | 220E20
14101 | SYNX2 | SYN2 Frequency Difference too high fline > fbus Off | 220E21
14102 | SYNX2 | SYN2 Angle Difference too high a bus leads a line On | 220E22
14103 | SYNX2 | SYN2 Angle Difference too high a bus leads a line Off | 220E23
14104 | SYNX2 | SYN2 Angle Difference too high a line leads a bus On | 220E24
14105 | SYNX2 | SYN2 Angle Difference too high a line leads a bus Off | 220E25
14106 | SYNX2 | SYN2 Bus voltage Live On | 220E26
14107 | SYNX2 | SYN2 Bus voltage Live Off | 220E27
14108 | SYNX2 | SYN2 Bus voltage Dead On | 220E28
14109 | SYNX2 | SYN2 Bus voltage Dead Off | 220E29
14110 | SYNX2 | SYN2 Line voltage Live On | 220E30
14111 | SYNX2 | SYN2 Line voltage Live Off | 220E31
14112 | SYNX2 | SYN2 Line voltage Dead On | 220E32
14113 | SYNX2 | SYN2 Line voltage Dead Off | 220E33
14144 | SYNX3 | SYN3 Voltage difference Ok On | 221E0
14145 | SYNX3 | SYN3 Voltage difference Ok Off | 221E1
14146 | SYNX3 | SYN3 Angle difference Ok On | 221E2
14147 | SYNX3 | SYN3 Angle difference Ok Off | 221E3
14148 | SYNX3 | SYN3 Frequency difference Ok On | 221E4
14149 | SYNX3 | SYN3 Frequency difference Ok On | 221E5
14150 | SYNX3 | SYN3 Live Live Condition On | 221E6
14151 | SYNX3 | SYN3 Live Live Condition Off | 221E7
14152 | SYNX3 | SYN3 Live Dead Condition On | 221E8
14153 | SYNX3 | SYN3 Live Dead Condition Off | 221E9
14154 | SYNX3 | SYN3 Dead Live Condition On | 221E10
14155 | SYNX3 | SYN3 Dead Live Condition Off | 221E11
14156 | SYNX3 | SYN3 Dead Dead Condition On | 221E12
14157 | SYNX3 | SYN3 Dead Dead Condition On | 221E13
14158 | SYNX3 | SYN3 Voltage Difference too high Vbus > Vline On | 221E14
14159 | SYNX3 | SYN3 Voltage Difference too high Vbus > Vline Off | 221E15
14160 | SYNX3 | SYN3 Voltage Difference too high Vline > Vbus On | 221E16
14161 | SYNX3 | SYN3 Voltage Difference too high Vline > Vbus Off | 221E17
14162 | SYNX3 | SYN3 Frequency Difference too high fbus > fline On | 221E18
14163 | SYNX3 | SYN3 Frequency Difference too high fbus > fline Off | 221E19
14164 | SYNX3 | SYN3 Frequency Difference too high fline > fbus On | 221E20
14165 | SYNX3 | SYN3 Frequency Difference too high fline > fbus Off | 221E21
14166 | SYNX3 | SYN3 Angle Difference too high a bus leads a line On | 221E22
14167 | SYNX3 | SYN3 Angle Difference too high a bus leads a line Off | 221E23
14168 | SYNX3 | SYN3 Angle Difference too high a line leads a bus On | 221E24
14169 | SYNX3 | SYN3 Angle Difference too high a line leads a bus Off | 221E25
14170 | SYNX3 | SYN3 Bus voltage Live On | 221E26
14171 | SYNX3 | SYN3 Bus voltage Live Off | 221E27
14172 | SYNX3 | SYN3 Bus voltage Dead On | 221E28
14173 | SYNX3 | SYN3 Bus voltage Dead Off | 221E29
14174 | SYNX3 | SYN3 Line voltage Live On | 221E30
14175 | SYNX3 | SYN3 Line voltage Live Off | 221E31
14176 | SYNX3 | SYN3 Line voltage Dead On | 221E32
14177 | SYNX3 | SYN3 Line voltage Dead Off | 221E33
14208 | COL1 | Start ON | 222E0
14209 | COL1 | Start OFF | 222E1
14210 | COL1 | Trip ON | 222E2
14211 | COL1 | Trip OFF | 222E3
14212 | COL1 | Block ON | 222E4
14213 | COL1 | Block OFF | 222E5
14272 | COL2 | Start ON | 223E0
14273 | COL2 | Start OFF | 223E1
14274 | COL2 | Trip ON | 223E2
14275 | COL2 | Trip OFF | 223E3
14276 | COL2 | Block ON | 223E4
14277 | COL2 | Block OFF | 223E5
14336 | CNU1 | Alarm Start On | 224E0
14337 | CNU1 | Alarm Start Off | 224E1
14338 | CNU1 | Alarm On | 224E2
14339 | CNU1 | Alarm Off | 224E3
14340 | CNU1 | Trip Start On | 224E4
14341 | CNU1 | Trip Start Off | 224E5
14342 | CNU1 | Trip On | 224E6
14343 | CNU1 | Trip Off | 224E7
14344 | CNU1 | Blocked On | 224E8
14345 | CNU1 | Blocked Off | 224E9
14346 | CNU1 | Unbalance detected On | 224E10
14347 | CNU1 | Unbalance detected Off | 224E11
14348 | CNU1 | Compensating natural unbalance On | 224E12
14349 | CNU1 | Compensating natural unbalance Off | 224E13

## FVSPE SPA map v2.1.1.3-233
SPA Ch | SPA Data | Ch Name | Description | Type | Access | Range
46 | V1 | OBJ1 | Open Select | UINT32 | W | 1=Select
46 | V2 | OBJ1 | Close Select | UINT32 | W | 1=Select
46 | V3 | OBJ1 | Execute | UINT32 | W | 1=Execute
46 | V4 | OBJ1 | Cancel | UINT32 | W | 1=Cancel
46 | V5 | OBJ1 | Direct Open | UINT32 | W | 1=Open
46 | V6 | OBJ1 | Direct Close | UINT32 | W | 1=Close
47 | V1 | OBJ2 | Open Select | UINT32 | W | 1=Select
47 | V2 | OBJ2 | Close Select | UINT32 | W | 1=Select
47 | V3 | OBJ2 | Execute | UINT32 | W | 1=Execute
47 | V4 | OBJ2 | Cancel | UINT32 | W | 1=Cancel
47 | V5 | OBJ2 | Direct Open | UINT32 | W | 1=Open
47 | V6 | OBJ2 | Direct Close | UINT32 | W | 1=Close
48 | V1 | OBJ3 | Open Select | UINT32 | W | 1=Select
48 | V2 | OBJ3 | Close Select | UINT32 | W | 1=Select
48 | V3 | OBJ3 | Execute | UINT32 | W | 1=Execute
48 | V4 | OBJ3 | Cancel | UINT32 | W | 1=Cancel
48 | V5 | OBJ3 | Direct Open | UINT32 | W | 1=Open
48 | V6 | OBJ3 | Direct Close | UINT32 | W | 1=Close
49 | V1 | OBJ4 | Open Select | UINT32 | W | 1=Select
49 | V2 | OBJ4 | Close Select | UINT32 | W | 1=Select
49 | V3 | OBJ4 | Execute | UINT32 | W | 1=Execute
49 | V4 | OBJ4 | Cancel | UINT32 | W | 1=Cancel
49 | V5 | OBJ4 | Direct Open | UINT32 | W | 1=Open
49 | V6 | OBJ4 | Direct Close | UINT32 | W | 1=Close
50 | V1 | OBJ5 | Open Select | UINT32 | W | 1=Select
50 | V2 | OBJ5 | Close Select | UINT32 | W | 1=Select
50 | V3 | OBJ5 | Execute | UINT32 | W | 1=Execute
50 | V4 | OBJ5 | Cancel | UINT32 | W | 1=Cancel
50 | V5 | OBJ5 | Direct Open | UINT32 | W | 1=Open
50 | V6 | OBJ5 | Direct Close | UINT32 | W | 1=Close
150 | V1 | OBJ6 | Open Select | UINT32 | W | 1=Select
150 | V2 | OBJ6 | Close Select | UINT32 | W | 1=Select
150 | V3 | OBJ6 | Execute | UINT32 | W | 1=Execute
150 | V4 | OBJ6 | Cancel | UINT32 | W | 1=Cancel
150 | V5 | OBJ6 | Direct Open | UINT32 | W | 1=Open
150 | V6 | OBJ6 | Direct Close | UINT32 | W | 1=Close
151 | V1 | OBJ7 | Open Select | UINT32 | W | 1=Select
151 | V2 | OBJ7 | Close Select | UINT32 | W | 1=Select
151 | V3 | OBJ7 | Execute | UINT32 | W | 1=Execute
151 | V4 | OBJ7 | Cancel | UINT32 | W | 1=Cancel
151 | V5 | OBJ7 | Direct Open | UINT32 | W | 1=Open
151 | V6 | OBJ7 | Direct Close | UINT32 | W | 1=Close
152 | V1 | OBJ8 | Open Select | UINT32 | W | 1=Select
152 | V2 | OBJ8 | Close Select | UINT32 | W | 1=Select
152 | V3 | OBJ8 | Execute | UINT32 | W | 1=Execute
152 | V4 | OBJ8 | Cancel | UINT32 | W | 1=Cancel
152 | V5 | OBJ8 | Direct Open | UINT32 | W | 1=Open
152 | V6 | OBJ8 | Direct Close | UINT32 | W | 1=Close
153 | V1 | OBJ9 | Open Select | UINT32 | W | 1=Select
153 | V2 | OBJ9 | Close Select | UINT32 | W | 1=Select
153 | V3 | OBJ9 | Execute | UINT32 | W | 1=Execute
153 | V4 | OBJ9 | Cancel | UINT32 | W | 1=Cancel
153 | V5 | OBJ9 | Direct Open | UINT32 | W | 1=Open
153 | V6 | OBJ9 | Direct Close | UINT32 | W | 1=Close
154 | V1 | OBJ10 | Open Select | UINT32 | W | 1=Select
154 | V2 | OBJ10 | Close Select | UINT32 | W | 1=Select
154 | V3 | OBJ10 | Execute | UINT32 | W | 1=Execute
154 | V4 | OBJ10 | Cancel | UINT32 | W | 1=Cancel
154 | V5 | OBJ10 | Direct Open | UINT32 | W | 1=Open
154 | V6 | OBJ10 | Direct Close | UINT32 | W | 1=Close
116 | S1 | MEAS1 | Side 1 Current meas update interval | UINT32 | RW | 5...10000
116 | I1 | MEAS1 | Pri.Pha.curr.IL1 | FLOAT | R | 0...100000
116 | I2 | MEAS1 | Pri.Pha.curr.IL2 | FLOAT | R | 0...100000
116 | I3 | MEAS1 | Pri.Pha.curr.IL3 | FLOAT | R | 0...100000
116 | I4 | MEAS1 | Pri.Res.curr.I01 | FLOAT | R | 0...100000
116 | I5 | MEAS1 | Pri.Res.curr.I02 | FLOAT | R | 0...100000
116 | I6 | MEAS1 | Pha.angle IL1 | FLOAT | R | -360...360
116 | I7 | MEAS1 | Pha.angle IL2 | FLOAT | R | -360...360
116 | I8 | MEAS1 | Pha.angle IL3 | FLOAT | R | -360...360
116 | I9 | MEAS1 | Res.curr.angle I01 | FLOAT | R | -360...360
116 | I10 | MEAS1 | Res.curr.angle I02 | FLOAT | R | -360...360
116 | I11 | MEAS1 | Pri.calc.I0 | FLOAT | R | 0...100000
116 | I12 | MEAS1 | calc.I0 Pha.angle | FLOAT | R | -360...360
116 | I13 | MEAS1 | Pha.curr.IL1 TRMS Pri | FLOAT | R | 0...100000
116 | I14 | MEAS1 | Pha.curr.IL2 TRMS Pri | FLOAT | R | 0...100000
116 | I15 | MEAS1 | Pha.curr.IL3 TRMS Pri | FLOAT | R | 0...100000
116 | I16 | MEAS1 | Pri.Pos.seq.curr. | FLOAT | R | 0...100000
116 | I17 | MEAS1 | Pri.Neg.seq.curr. | FLOAT | R | 0...100000
116 | I18 | MEAS1 | Pri.Zero seq.curr. | FLOAT | R | 0...100000
116 | I19 | MEAS1 | Pos.seq.curr.angle | FLOAT | R | -360...360
116 | I20 | MEAS1 | Neg.seq.curr.angle | FLOAT | R | -360...360
116 | I21 | MEAS1 | Zero seq.curr.angle | FLOAT | R | -360...360
116 | I22 | MEAS1 | Res.curr.I01 TRMS Pri | FLOAT | R | 0...100000
116 | I23 | MEAS1 | Res.curr.I02 TRMS Pri | FLOAT | R | 0...100000
116 | I24 | MEAS1 | Pha.L1 ampl. THD | FLOAT | R | 0...100
116 | I25 | MEAS1 | Pha.L1 pow. THD | FLOAT | R | 0...100
116 | I26 | MEAS1 | Pha.L2 ampl. THD | FLOAT | R | 0...100
116 | I27 | MEAS1 | Pha.L2 pow. THD | FLOAT | R | 0...100
116 | I28 | MEAS1 | Pha.L3 ampl. THD | FLOAT | R | 0...100
116 | I29 | MEAS1 | Pha.L3 pow. THD | FLOAT | R | 0...100
116 | I30 | MEAS1 | Res.I01 ampl. THD | FLOAT | R | 0...100
116 | I31 | MEAS1 | Res.I01 pow. THD | FLOAT | R | 0...100
116 | I32 | MEAS1 | Res.I02 ampl. THD | FLOAT | R | 0...100
116 | I33 | MEAS1 | Res.I02 pow. THD | FLOAT | R | 0...100
116 | I34 | MEAS1 | Meas1 IL ang. Ref | FLOAT | R | -360...360
117 | S1 | MEAS2 | Side 2 Current meas update interval | UINT32 | RW | 5...10000
117 | I1 | MEAS2 | Pri.Pha.curr.I''L1 | FLOAT | R | 0...100000
117 | I2 | MEAS2 | Pri.Pha.curr.I''L2 | FLOAT | R | 0...100000
117 | I3 | MEAS2 | Pri.Pha.curr.I''L3 | FLOAT | R | 0...100000
117 | I4 | MEAS2 | Pha.angle I''L1 | FLOAT | R | -360...360
117 | I5 | MEAS2 | Pha.angle I''L2 | FLOAT | R | -360...360
117 | I6 | MEAS2 | Pha.angle I''L3 | FLOAT | R | -360...360
117 | I7 | MEAS2 | Pri.Res.curr.I''01 | FLOAT | R | 0...100000
117 | I8 | MEAS2 | Res.curr.angle I''01 | FLOAT | R | -360...360
117 | I9 | MEAS2 | Pri.Res.curr.I''02 | FLOAT | R | 0...100000
117 | I10 | MEAS2 | Res.curr.angle I''02 | FLOAT | R | -360...360
117 | I11 | MEAS2 | Pri.calc.I''0 | FLOAT | R | 0...100000
117 | I12 | MEAS2 | calc.I''0 Pha.angle | FLOAT | R | -360...360
117 | I13 | MEAS2 | Pha.curr.I''L1 TRMS Pri | FLOAT | R | 0...100000
117 | I14 | MEAS2 | Pha.curr.I''L2 TRMS Pri | FLOAT | R | 0...100000
117 | I15 | MEAS2 | Pha.curr.I''L3 TRMS Pri | FLOAT | R | 0...100000
117 | I16 | MEAS2 | I'' Pri.Pos.seq.curr. | FLOAT | R | 0...100000
117 | I17 | MEAS2 | I'' Pri.Neg.seq.curr. | FLOAT | R | 0...100000
117 | I18 | MEAS2 | I'' Pri.Zero seq.curr. | FLOAT | R | 0...100000
117 | I19 | MEAS2 | I'' Pos.seq.curr.angle | FLOAT | R | -360...360
117 | I20 | MEAS2 | I'' Neg.seq.curr.angle | FLOAT | R | -360...360
117 | I21 | MEAS2 | I'' Zero seq.curr.angle | FLOAT | R | -360...360
117 | I22 | MEAS2 | Res.curr.I''01 TRMS Pri | FLOAT | R | 0...100000
117 | I23 | MEAS2 | Res.curr.I''02 TRMS Pri | FLOAT | R | 0...100000
117 | I24 | MEAS2 | Pha.I''L1 ampl. THD | FLOAT | R | 0...100
117 | I25 | MEAS2 | Pha.I''L1 pow. THD | FLOAT | R | 0...100
117 | I26 | MEAS2 | Pha.I''L2 ampl. THD | FLOAT | R | 0...100
117 | I27 | MEAS2 | Pha.I''L2 pow. THD | FLOAT | R | 0...100
117 | I28 | MEAS2 | Pha.I''L3 ampl. THD | FLOAT | R | 0...100
117 | I29 | MEAS2 | Pha.I''L3 pow. THD | FLOAT | R | 0...100
117 | I30 | MEAS2 | Res.I''01 ampl. THD | FLOAT | R | 0...100
117 | I31 | MEAS2 | Res.I''01 pow. THD | FLOAT | R | 0...100
117 | I32 | MEAS2 | Res.I''02 ampl. THD | FLOAT | R | 0...100
117 | I33 | MEAS2 | Res.I''02 pow. THD | FLOAT | R | 0...100
117 | I34 | MEAS2 | MEAS2 IL ang. Ref | FLOAT | R | -360...360
118 | S1 | MEAS3 | Voltage meas update interval | UINT32 | RW | 5...10000
118 | I1 | MEAS3 | Pos.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I2 | MEAS3 | Neg.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I3 | MEAS3 | Zero.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I4 | MEAS3 | Pos.Seq volt.Angle | FLOAT | R | -360...360
118 | I5 | MEAS3 | Neg.Seq.volt.Angle | FLOAT | R | -360...360
118 | I6 | MEAS3 | Zero.Seq.volt.Angle | FLOAT | R | -360...360
118 | I7 | MEAS3 | System volt UL12 mag | FLOAT | R | 0...1000000
118 | I8 | MEAS3 | System volt UL12 mag(kV) | FLOAT | R | 0...1000
118 | I9 | MEAS3 | System volt UL12 ang | FLOAT | R | -360...360
118 | I10 | MEAS3 | System volt UL23 mag | FLOAT | R | 0...1000000
118 | I11 | MEAS3 | System volt UL23 mag(kV) | FLOAT | R | 0...1000
118 | I12 | MEAS3 | System volt UL23 ang | FLOAT | R | -360...360
118 | I13 | MEAS3 | System volt UL31 mag | FLOAT | R | 0...1000000
118 | I14 | MEAS3 | System volt UL31 mag(kV) | FLOAT | R | 0...1000
118 | I15 | MEAS3 | System volt UL31 ang | FLOAT | R | -360...360
118 | I16 | MEAS3 | System volt UL1 mag | FLOAT | R | 0...1000000
118 | I17 | MEAS3 | System volt UL1 mag(kV) | FLOAT | R | 0...1000
118 | I18 | MEAS3 | System volt UL1 ang | FLOAT | R | -360...360
118 | I19 | MEAS3 | System volt UL2 mag | FLOAT | R | 0...1000000
118 | I20 | MEAS3 | System volt UL2 mag(kV) | FLOAT | R | 0...1000
118 | I21 | MEAS3 | System volt UL2 ang | FLOAT | R | -360...360
118 | I22 | MEAS3 | System volt UL3 mag | FLOAT | R | 0...1000000
118 | I23 | MEAS3 | System volt UL3 mag(kV) | FLOAT | R | 0...1000
118 | I24 | MEAS3 | System volt UL3 ang | FLOAT | R | -360...360
118 | I25 | MEAS3 | System volt U0 mag | FLOAT | R | 0...1000000
118 | I26 | MEAS3 | System volt U0 mag(kV) | FLOAT | R | 0...1000
118 | I27 | MEAS3 | System volt U0 mag(%) | FLOAT | R | 0...120
118 | I28 | MEAS3 | System volt U0 ang | FLOAT | R | -360...360
118 | I29 | MEAS3 | System volt U3 mag | FLOAT | R | 0...1000000
118 | I30 | MEAS3 | System volt U3 mag(kV) | FLOAT | R | 0...1000
118 | I31 | MEAS3 | System volt U3 ang | FLOAT | R | -360...360
118 | I32 | MEAS3 | System volt U4 mag | FLOAT | R | 0...1000000
118 | I33 | MEAS3 | System volt U4 mag(kV) | FLOAT | R | 0...1000
118 | I34 | MEAS3 | System volt U4 ang | FLOAT | R | -360...360
188 | I1 | IMERX | IL1 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I2 | IMERX | IL1 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I3 | IMERX | IL2 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I4 | IMERX | IL2 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I5 | IMERX | IL3 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I6 | IMERX | IL3 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I7 | IMERX | Pos.seq. Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I8 | IMERX | Pos.Seq. Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I9 | IMERX | I01 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I10 | IMERX | I01 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I11 | IMERX | I02 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I12 | IMERX | I02 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I13 | IMERX | I01 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I14 | IMERX | I01 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
188 | I15 | IMERX | I02 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I16 | IMERX | I02 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
119 | S1 | POW1 | Power meas update interval | UINT32 | RW | 5...10000
119 | S2 | POW1 | Nominal Power kVA | FLOAT | RW | 0.1...500000
119 | I1 | POW1 | PQ Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Ind;2=Q2 Rev Cap;3=Q3 Rev Ind;4=Q4 Fwd Cap
119 | I2 | POW1 | VA Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Cap, AV;2=Q2 Rev Ind AV;3=Q3 Rev Cap VA;4=Q4 Fwd Ind VA
119 | I3 | POW1 | Export Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I4 | POW1 | Export Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I5 | POW1 | Import Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I6 | POW1 | Import Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I7 | POW1 | Active Energy (P) Export/Import balance MWh | INT32 | R | -2147483647...2147483647
119 | I8 | POW1 | Active Energy (P) Export/Import balance kWh | INT32 | R | -2147483647...2147483647
119 | I9 | POW1 | Exported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I10 | POW1 | Exported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I11 | POW1 | Imported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I12 | POW1 | Imported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I13 | POW1 | Reactive Energy (Q) balance while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I14 | POW1 | Reactive Energy (Q) balance while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I15 | POW1 | Exported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I16 | POW1 | Exported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I17 | POW1 | Imported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I18 | POW1 | Imported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I19 | POW1 | Reactive Energy (Q) balance while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I20 | POW1 | Reactive Energy (Q) balance while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I21 | POW1 | Apparent Energy (S) while Export (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I22 | POW1 | Apparent Energy (S) while Export (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I23 | POW1 | Apparent Energy (S) while Import (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I24 | POW1 | Apparent Energy (S) while Import (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I25 | POW1 | Apparent Energy (S) Net | INT32 | R | -2147483647...2147483647
119 | I26 | POW1 | Real Energy (P) Net | INT32 | RW | -2147483647...2147483647
119 | I27 | POW1 | Reactive Energy (Q) Net | INT32 | RW | -2147483647...2147483647
119 | I28 | POW1 | Real Energy (P) Supply (Default supply direction towards busbar) | INT32 | RW | -2147483647...2147483647
119 | I29 | POW1 | Reactive Energy (Q) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
119 | I30 | POW1 | Real Energy (P) Demand (Default demand direction from busbar) | INT32 | RW | -2147483647...2147483647
119 | I31 | POW1 | Reactive Energy (Q) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
119 | S3 | POW1 | Reset 3ph Energies | UINT32 | RW | 0=-;1=Reset
119 | I32 | POW1 | POW1 L1 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I33 | POW1 | POW1 L1 Active power (P) | FLOAT | R | -1000000...1000000
119 | I34 | POW1 | POW1 L1 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I35 | POW1 | POW1 L1 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I36 | POW1 | POW1 L1 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I37 | POW1 | L1 PF | FLOAT | R | -1000000...1000000
119 | I38 | POW1 | POW1 L2 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I39 | POW1 | POW1 L2 Active power (P) | FLOAT | R | -1000000...1000000
119 | I40 | POW1 | POW1 L2 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I41 | POW1 | POW1 L2 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I42 | POW1 | POW1 L2 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I43 | POW1 | L2 PF | FLOAT | R | -1000000...1000000
119 | I44 | POW1 | POW1 L3 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I45 | POW1 | POW1 L3 Active power (P) | FLOAT | R | -1000000...1000000
119 | I46 | POW1 | POW1 L3 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I47 | POW1 | POW1 L3 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I48 | POW1 | POW1 L3 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I49 | POW1 | L3 PF | FLOAT | R | -1000000...1000000
119 | I50 | POW1 | POW1 3PH Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I51 | POW1 | POW1 3PH Apparent power (S MVA) | FLOAT | R | -1000000...1000000
119 | I52 | POW1 | POW1 3PH Active power (P) | FLOAT | R | -1000000...1000000
119 | I53 | POW1 | POW1 3PH Active power (P MW) | FLOAT | R | -1000000...1000000
119 | I54 | POW1 | POW1 3PH Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I55 | POW1 | POW1 3PH Reactive power (QMVar) | FLOAT | R | -1000000...1000000
119 | I56 | POW1 | POW1 3PH Tan(phi) | FLOAT | R | -1000000...1000000
119 | I57 | POW1 | POW1 3PH Cos(phi) | FLOAT | R | -1000000...1000000
119 | I58 | POW1 | 3PH PF | FLOAT | R | -1000000...1000000
136 | S1 | IMP1 | Impedance meas. update interval | UINT32 | RW | 500...10000
136 | I1 | IMP1 | Primary L12 R | FLOAT | R | -1000000...1000000
136 | I2 | IMP1 | Primary L12 X | FLOAT | R | -1000000...1000000
136 | I3 | IMP1 | Primary L23 R | FLOAT | R | -1000000...1000000
136 | I4 | IMP1 | Primary L23 X | FLOAT | R | -1000000...1000000
136 | I5 | IMP1 | Primary L31 R | FLOAT | R | -1000000...1000000
136 | I6 | IMP1 | Primary L31 X | FLOAT | R | -1000000...1000000
136 | I7 | IMP1 | Primary Z12 | FLOAT | R | -1000000...1000000
136 | I8 | IMP1 | Primary Z23 | FLOAT | R | -1000000...1000000
136 | I9 | IMP1 | Primary Z31 | FLOAT | R | -1000000...1000000
136 | I10 | IMP1 | Angle Z12 | FLOAT | R | -360...360
136 | I11 | IMP1 | Angle Z23 | FLOAT | R | -360...360
136 | I12 | IMP1 | Angle Z31 | FLOAT | R | -360...360
136 | I13 | IMP1 | Primary L1 R | FLOAT | R | -1000000...1000000
136 | I14 | IMP1 | Primary L1 X | FLOAT | R | -1000000...1000000
136 | I15 | IMP1 | Primary L2 R | FLOAT | R | -1000000...1000000
136 | I16 | IMP1 | Primary L2 X | FLOAT | R | -1000000...1000000
136 | I17 | IMP1 | Primary L3 R | FLOAT | R | -1000000...1000000
136 | I18 | IMP1 | Primary L3 X | FLOAT | R | -1000000...1000000
136 | I19 | IMP1 | Primary Z1 | FLOAT | R | -1000000...1000000
136 | I20 | IMP1 | Primary Z2 | FLOAT | R | -1000000...1000000
136 | I21 | IMP1 | Primary Z3 | FLOAT | R | -1000000...1000000
136 | I22 | IMP1 | Angle Z1 | FLOAT | R | -360...360
136 | I23 | IMP1 | Angle Z2 | FLOAT | R | -360...360
136 | I24 | IMP1 | Angle Z3 | FLOAT | R | -360...360
137 | I1 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I2 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I3 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I4 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I5 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I6 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I7 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I8 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I9 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I10 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I11 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I12 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
120 | S1 | FREQS | Smpl mode | UINT32 | RW | 0=Fixed;1=Tracking
120 | S2 | FREQS | Max. Tracking freq. allowed (+Nom f) | FLOAT | RW | 0.001...75
120 | S3 | FREQS | Sys.nom.f | FLOAT | RW | 7...75
120 | S4 | FREQS | Min. Tracking freq. allowed (- Nom f) | FLOAT | RW | 0.001...75
120 | I1 | FREQS | Track.sys.f | FLOAT | R | 0...75
120 | I2 | FREQS | f atm. Protections (when not measurable returns to nominal) | FLOAT | R | 0...75
120 | I3 | FREQS | f atm. Display (when not measurable is 0Hz) | FLOAT | R | 0...75
10 | I1 | DIGI | Dis 1-32 | UINT32 | R | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32
10 | I2 | DIGI | Dis 33-64 | UINT32 | R | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51
10 | I3 | DIGI | DI1 | SIGNAL_OUT | R | 0...4294967295
10 | V1 | DIGI | DI1 Counter | UINT32 | R | 0...4294967295
10 | V2 | DIGI | DI1 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I4 | DIGI | DI2 | SIGNAL_OUT | R | 0...4294967295
10 | V3 | DIGI | DI2 Counter | UINT32 | R | 0...4294967295
10 | V4 | DIGI | DI2 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I5 | DIGI | DI3 | SIGNAL_OUT | R | 0...4294967295
10 | V5 | DIGI | DI3 Counter | UINT32 | R | 0...4294967295
10 | V6 | DIGI | DI3 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I6 | DIGI | DI4 | SIGNAL_OUT | R | 0...4294967295
10 | V7 | DIGI | DI4 Counter | UINT32 | R | 0...4294967295
10 | V8 | DIGI | DI4 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I7 | DIGI | DI5 | SIGNAL_OUT | R | 0...4294967295
10 | V9 | DIGI | DI5 Counter | UINT32 | R | 0...4294967295
10 | V10 | DIGI | DI5 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I8 | DIGI | DI6 | SIGNAL_OUT | R | 0...4294967295
10 | V11 | DIGI | DI6 Counter | UINT32 | R | 0...4294967295
10 | V12 | DIGI | DI6 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I9 | DIGI | DI7 | SIGNAL_OUT | R | 0...4294967295
10 | V13 | DIGI | DI7 Counter | UINT32 | R | 0...4294967295
10 | V14 | DIGI | DI7 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I10 | DIGI | DI8 | SIGNAL_OUT | R | 0...4294967295
10 | V15 | DIGI | DI8 Counter | UINT32 | R | 0...4294967295
10 | V16 | DIGI | DI8 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I11 | DIGI | DI9 | SIGNAL_OUT | R | 0...4294967295
10 | V17 | DIGI | DI9 Counter | UINT32 | R | 0...4294967295
10 | V18 | DIGI | DI9 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I12 | DIGI | DI10 | SIGNAL_OUT | R | 0...4294967295
10 | V19 | DIGI | DI10 Counter | UINT32 | R | 0...4294967295
10 | V20 | DIGI | DI10 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I13 | DIGI | DI11 | SIGNAL_OUT | R | 0...4294967295
10 | V21 | DIGI | DI11 Counter | UINT32 | R | 0...4294967295
10 | V22 | DIGI | DI11 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I14 | DIGI | DI12 | SIGNAL_OUT | R | 0...4294967295
10 | V23 | DIGI | DI12 Counter | UINT32 | R | 0...4294967295
10 | V24 | DIGI | DI12 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I15 | DIGI | DI13 | SIGNAL_OUT | R | 0...4294967295
10 | V25 | DIGI | DI13 Counter | UINT32 | R | 0...4294967295
10 | V26 | DIGI | DI13 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I16 | DIGI | DI14 | SIGNAL_OUT | R | 0...4294967295
10 | V27 | DIGI | DI14 Counter | UINT32 | R | 0...4294967295
10 | V28 | DIGI | DI14 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I17 | DIGI | DI15 | SIGNAL_OUT | R | 0...4294967295
10 | V29 | DIGI | DI15 Counter | UINT32 | R | 0...4294967295
10 | V30 | DIGI | DI15 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I18 | DIGI | DI16 | SIGNAL_OUT | R | 0...4294967295
10 | V31 | DIGI | DI16 Counter | UINT32 | R | 0...4294967295
10 | V32 | DIGI | DI16 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I19 | DIGI | DI17 | SIGNAL_OUT | R | 0...4294967295
10 | V33 | DIGI | DI17 Counter | UINT32 | R | 0...4294967295
10 | V34 | DIGI | DI17 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I20 | DIGI | DI18 | SIGNAL_OUT | R | 0...4294967295
10 | V35 | DIGI | DI18 Counter | UINT32 | R | 0...4294967295
10 | V36 | DIGI | DI18 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I21 | DIGI | DI19 | SIGNAL_OUT | R | 0...4294967295
10 | V37 | DIGI | DI19 Counter | UINT32 | R | 0...4294967295
10 | V38 | DIGI | DI19 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I22 | DIGI | DI20 | SIGNAL_OUT | R | 0...4294967295
10 | V39 | DIGI | DI20 Counter | UINT32 | R | 0...4294967295
10 | V40 | DIGI | DI20 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I23 | DIGI | DI21 | SIGNAL_OUT | R | 0...4294967295
10 | V41 | DIGI | DI21 Counter | UINT32 | R | 0...4294967295
10 | V42 | DIGI | DI21 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I24 | DIGI | DI22 | SIGNAL_OUT | R | 0...4294967295
10 | V43 | DIGI | DI22 Counter | UINT32 | R | 0...4294967295
10 | V44 | DIGI | DI22 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I25 | DIGI | DI23 | SIGNAL_OUT | R | 0...4294967295
10 | V45 | DIGI | DI23 Counter | UINT32 | R | 0...4294967295
10 | V46 | DIGI | DI23 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I26 | DIGI | DI24 | SIGNAL_OUT | R | 0...4294967295
10 | V47 | DIGI | DI24 Counter | UINT32 | R | 0...4294967295
10 | V48 | DIGI | DI24 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I27 | DIGI | DI25 | SIGNAL_OUT | R | 0...4294967295
10 | V49 | DIGI | DI25 Counter | UINT32 | R | 0...4294967295
10 | V50 | DIGI | DI25 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I28 | DIGI | DI26 | SIGNAL_OUT | R | 0...4294967295
10 | V51 | DIGI | DI26 Counter | UINT32 | R | 0...4294967295
10 | V52 | DIGI | DI26 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I29 | DIGI | DI27 | SIGNAL_OUT | R | 0...4294967295
10 | V53 | DIGI | DI27 Counter | UINT32 | R | 0...4294967295
10 | V54 | DIGI | DI27 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I30 | DIGI | DI28 | SIGNAL_OUT | R | 0...4294967295
10 | V55 | DIGI | DI28 Counter | UINT32 | R | 0...4294967295
10 | V56 | DIGI | DI28 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I31 | DIGI | DI29 | SIGNAL_OUT | R | 0...4294967295
10 | V57 | DIGI | DI29 Counter | UINT32 | R | 0...4294967295
10 | V58 | DIGI | DI29 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I32 | DIGI | DI30 | SIGNAL_OUT | R | 0...4294967295
10 | V59 | DIGI | DI30 Counter | UINT32 | R | 0...4294967295
10 | V60 | DIGI | DI30 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I33 | DIGI | DI31 | SIGNAL_OUT | R | 0...4294967295
10 | V61 | DIGI | DI31 Counter | UINT32 | R | 0...4294967295
10 | V62 | DIGI | DI31 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I34 | DIGI | DI32 | SIGNAL_OUT | R | 0...4294967295
10 | V63 | DIGI | DI32 Counter | UINT32 | R | 0...4294967295
10 | V64 | DIGI | DI32 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I35 | DIGI | DI33 | SIGNAL_OUT | R | 0...4294967295
10 | V65 | DIGI | DI33 Counter | UINT32 | R | 0...4294967295
10 | V66 | DIGI | DI33 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I36 | DIGI | DI34 | SIGNAL_OUT | R | 0...4294967295
10 | V67 | DIGI | DI34 Counter | UINT32 | R | 0...4294967295
10 | V68 | DIGI | DI34 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I37 | DIGI | DI35 | SIGNAL_OUT | R | 0...4294967295
10 | V69 | DIGI | DI35 Counter | UINT32 | R | 0...4294967295
10 | V70 | DIGI | DI35 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I38 | DIGI | DI36 | SIGNAL_OUT | R | 0...4294967295
10 | V71 | DIGI | DI36 Counter | UINT32 | R | 0...4294967295
10 | V72 | DIGI | DI36 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I39 | DIGI | DI37 | SIGNAL_OUT | R | 0...4294967295
10 | V73 | DIGI | DI37 Counter | UINT32 | R | 0...4294967295
10 | V74 | DIGI | DI37 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I40 | DIGI | DI38 | SIGNAL_OUT | R | 0...4294967295
10 | V75 | DIGI | DI38 Counter | UINT32 | R | 0...4294967295
10 | V76 | DIGI | DI38 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I41 | DIGI | DI39 | SIGNAL_OUT | R | 0...4294967295
10 | V77 | DIGI | DI39 Counter | UINT32 | R | 0...4294967295
10 | V78 | DIGI | DI39 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I42 | DIGI | DI40 | SIGNAL_OUT | R | 0...4294967295
10 | V79 | DIGI | DI40 Counter | UINT32 | R | 0...4294967295
10 | V80 | DIGI | DI40 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I43 | DIGI | DI41 | SIGNAL_OUT | R | 0...4294967295
10 | V81 | DIGI | DI41 Counter | UINT32 | R | 0...4294967295
10 | V82 | DIGI | DI41 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I44 | DIGI | DI42 | SIGNAL_OUT | R | 0...4294967295
10 | V83 | DIGI | DI42 Counter | UINT32 | R | 0...4294967295
10 | V84 | DIGI | DI42 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I45 | DIGI | DI43 | SIGNAL_OUT | R | 0...4294967295
10 | V85 | DIGI | DI43 Counter | UINT32 | R | 0...4294967295
10 | V86 | DIGI | DI43 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I46 | DIGI | DI44 | SIGNAL_OUT | R | 0...4294967295
10 | V87 | DIGI | DI44 Counter | UINT32 | R | 0...4294967295
10 | V88 | DIGI | DI44 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I47 | DIGI | DI45 | SIGNAL_OUT | R | 0...4294967295
10 | V89 | DIGI | DI45 Counter | UINT32 | R | 0...4294967295
10 | V90 | DIGI | DI45 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I48 | DIGI | DI46 | SIGNAL_OUT | R | 0...4294967295
10 | V91 | DIGI | DI46 Counter | UINT32 | R | 0...4294967295
10 | V92 | DIGI | DI46 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I49 | DIGI | DI47 | SIGNAL_OUT | R | 0...4294967295
10 | V93 | DIGI | DI47 Counter | UINT32 | R | 0...4294967295
10 | V94 | DIGI | DI47 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I50 | DIGI | DI48 | SIGNAL_OUT | R | 0...4294967295
10 | V95 | DIGI | DI48 Counter | UINT32 | R | 0...4294967295
10 | V96 | DIGI | DI48 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I51 | DIGI | DI49 | SIGNAL_OUT | R | 0...4294967295
10 | V97 | DIGI | DI49 Counter | UINT32 | R | 0...4294967295
10 | V98 | DIGI | DI49 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I52 | DIGI | DI50 | SIGNAL_OUT | R | 0...4294967295
10 | V99 | DIGI | DI50 Counter | UINT32 | R | 0...4294967295
10 | V100 | DIGI | DI50 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I53 | DIGI | DI51 | SIGNAL_OUT | R | 0...4294967295
10 | V101 | DIGI | DI51 Counter | UINT32 | R | 0...4294967295
10 | V102 | DIGI | DI51 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | S1 | DIGI | EventMaskLo | UINT32 | RW | 0...4294967295
10 | S2 | DIGI | EventMaskHi | UINT32 | RW | 0...4294967295
11 | S1 | DIGI2 | EventMaskLo | UINT32 | RW | 0...4294967295
11 | S2 | DIGI2 | EventMaskHi | UINT32 | RW | 0...4294967295
15 | O1 | RELE | Outputs status | UINT32 | R | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15
15 | O2 | RELE | OUT1 | SIGNAL_IN | RW | 0...4294967295
15 | O3 | RELE | OUT2 | SIGNAL_IN | RW | 0...4294967295
15 | O4 | RELE | OUT3 | SIGNAL_IN | RW | 0...4294967295
15 | O5 | RELE | OUT4 | SIGNAL_IN | RW | 0...4294967295
15 | O6 | RELE | OUT5 | SIGNAL_IN | RW | 0...4294967295
15 | O7 | RELE | OUT6 | SIGNAL_IN | RW | 0...4294967295
15 | O8 | RELE | OUT7 | SIGNAL_IN | RW | 0...4294967295
15 | O9 | RELE | OUT8 | SIGNAL_IN | RW | 0...4294967295
15 | O10 | RELE | OUT9 | SIGNAL_IN | RW | 0...4294967295
15 | O11 | RELE | OUT10 | SIGNAL_IN | RW | 0...4294967295
15 | O12 | RELE | OUT11 | SIGNAL_IN | RW | 0...4294967295
15 | O13 | RELE | OUT12 | SIGNAL_IN | RW | 0...4294967295
15 | O14 | RELE | OUT13 | SIGNAL_IN | RW | 0...4294967295
15 | O15 | RELE | OUT14 | SIGNAL_IN | RW | 0...4294967295
15 | O16 | RELE | OUT15 | SIGNAL_IN | RW | 0...4294967295
121 | O1 | LED | LED START | SIGNAL_IN | RW | 0...4294967295
121 | O2 | LED | LED TRIP | SIGNAL_IN | RW | 0...4294967295
121 | O3 | LED | User LED 1 | SIGNAL_IN | RW | 0...4294967295
121 | O4 | LED | User LED 2 | SIGNAL_IN | RW | 0...4294967295
121 | O5 | LED | User LED 3 | SIGNAL_IN | RW | 0...4294967295
121 | O6 | LED | User LED 4 | SIGNAL_IN | RW | 0...4294967295
121 | O7 | LED | User LED 5 | SIGNAL_IN | RW | 0...4294967295
121 | O8 | LED | User LED 6 | SIGNAL_IN | RW | 0...4294967295
121 | O9 | LED | User LED 7 | SIGNAL_IN | RW | 0...4294967295
121 | O10 | LED | User LED 8 | SIGNAL_IN | RW | 0...4294967295
121 | O11 | LED | User LED 9 | SIGNAL_IN | RW | 0...4294967295
121 | O12 | LED | User LED 10 | SIGNAL_IN | RW | 0...4294967295
121 | O13 | LED | User LED 11 | SIGNAL_IN | RW | 0...4294967295
121 | O14 | LED | User LED 12 | SIGNAL_IN | RW | 0...4294967295
121 | O15 | LED | User LED 13 | SIGNAL_IN | RW | 0...4294967295
121 | O16 | LED | User LED 14 | SIGNAL_IN | RW | 0...4294967295
121 | O17 | LED | User LED 15 | SIGNAL_IN | RW | 0...4294967295
121 | O18 | LED | User LED 16 | SIGNAL_IN | RW | 0...4294967295
122 | O1 | LEDX | User LED 17 | SIGNAL_IN | RW | 0...4294967295
122 | O2 | LEDX | User LED 18 | SIGNAL_IN | RW | 0...4294967295
122 | O3 | LEDX | User LED 19 | SIGNAL_IN | RW | 0...4294967295
122 | O4 | LEDX | User LED 20 | SIGNAL_IN | RW | 0...4294967295
122 | O5 | LEDX | User LED 21 | SIGNAL_IN | RW | 0...4294967295
122 | O6 | LEDX | User LED 22 | SIGNAL_IN | RW | 0...4294967295
122 | O7 | LEDX | User LED 23 | SIGNAL_IN | RW | 0...4294967295
122 | O8 | LEDX | User LED 24 | SIGNAL_IN | RW | 0...4294967295
122 | O9 | LEDX | User LED 25 | SIGNAL_IN | RW | 0...4294967295
122 | O10 | LEDX | User LED 26 | SIGNAL_IN | RW | 0...4294967295
122 | O11 | LEDX | User LED 27 | SIGNAL_IN | RW | 0...4294967295
122 | O12 | LEDX | User LED 28 | SIGNAL_IN | RW | 0...4294967295
122 | O13 | LEDX | User LED 29 | SIGNAL_IN | RW | 0...4294967295
122 | O14 | LEDX | User LED 30 | SIGNAL_IN | RW | 0...4294967295
122 | O15 | LEDX | User LED 31 | SIGNAL_IN | RW | 0...4294967295
122 | O16 | LEDX | User LED 32 | SIGNAL_IN | RW | 0...4294967295
122 | O17 | LEDX | User LED 33 | SIGNAL_IN | RW | 0...4294967295
122 | O18 | LEDX | User LED 34 | SIGNAL_IN | RW | 0...4294967295
122 | O19 | LEDX | User LED 35 | SIGNAL_IN | RW | 0...4294967295
122 | O20 | LEDX | User LED 36 | SIGNAL_IN | RW | 0...4294967295
122 | O21 | LEDX | User LED 37 | SIGNAL_IN | RW | 0...4294967295
122 | O22 | LEDX | User LED 38 | SIGNAL_IN | RW | 0...4294967295
122 | O23 | LEDX | User LED 39 | SIGNAL_IN | RW | 0...4294967295
122 | O24 | LEDX | User LED 40 | SIGNAL_IN | RW | 0...4294967295
122 | O25 | LEDX | User LED 41 | SIGNAL_IN | RW | 0...4294967295
122 | O26 | LEDX | User LED 42 | SIGNAL_IN | RW | 0...4294967295
122 | O27 | LEDX | User LED 43 | SIGNAL_IN | RW | 0...4294967295
122 | O28 | LEDX | User LED 44 | SIGNAL_IN | RW | 0...4294967295
122 | O29 | LEDX | User LED 45 | SIGNAL_IN | RW | 0...4294967295
122 | O30 | LEDX | User LED 46 | SIGNAL_IN | RW | 0...4294967295
122 | O31 | LEDX | User LED 47 | SIGNAL_IN | RW | 0...4294967295
122 | O32 | LEDX | User LED 48 | SIGNAL_IN | RW | 0...4294967295
65 | V1 | SGS | Active setting group | UINT32 | R | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
65 | S1 | SGS | Force SG | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | S2 | SGS | Force SG change | UINT32 | RW | 0=Disabled;1=Enabled
65 | S3 | SGS | Used setting groups | UINT32 | RW | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
65 | S4 | SGS | Remote SG change | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | O1 | SGS | Forced SG in use | SIGNAL_OUT | RW | 0...4294967295
65 | O2 | SGS | SG1 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O3 | SGS | SG2 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O4 | SGS | SG3 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O5 | SGS | SG4 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O6 | SGS | SG5 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O7 | SGS | SG6 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O8 | SGS | SG7 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O9 | SGS | SG8 Active | SIGNAL_OUT | RW | 0...4294967295
7 | I1 | CTRL | Local/Remote status | UINT32 | R | 0=Remote;1=Local
123 | V1 | DEV | Serial number | UINT32 | R | 0...4294967295
123 | V2 | DEV | SW version | STRING | R | ...32
124 | S1 | EVENT | Clear Events | UINT32 | RW | 0=-;1=Clear
125 | I1 | DIAG | Diagnostic alarm status | UINT32 | R | 0b=Temp. out of range;1b=Voltage out of range;2b=HW configuration invalid;3b=Relay output failure;4b=Option card A alarm;5b=Option card B alarm;6b=Option card C alarm;7b=Option card D alarm;8b=Option card E alarm;9b=Option card F alarm;10b=GOOSE invalid;
125 | S1 | DIAG | Clear diagnostic alarm | UINT32 | W | 0=-;1=Clear
125 | I2 | DIAG | Internal temperature | FLOAT | R | 0...200
125 | I3 | DIAG | Internal voltage 24V | FLOAT | R | 0...50
125 | I4 | DIAG | Internal voltage 24V max | FLOAT | R | 0...50
125 | I5 | DIAG | Internal voltage 24V min | FLOAT | R | 0...50
125 | I6 | DIAG | Internal voltage 24V deviation | FLOAT | R | 0...50
138 | I1 | MBIO | Input value | FLOAT | R | -101...2000
138 | I2 | MBIO | Input value | FLOAT | R | -101...2000
138 | I3 | MBIO | Input value | FLOAT | R | -101...2000
138 | I4 | MBIO | Input value | FLOAT | R | -101...2000
138 | I5 | MBIO | Input value | FLOAT | R | -101...2000
138 | I6 | MBIO | Input value | FLOAT | R | -101...2000
138 | I7 | MBIO | Input value | FLOAT | R | -101...2000
138 | I8 | MBIO | Input value | FLOAT | R | -101...2000
138 | I9 | MBIO | Input value | FLOAT | R | -101...2000
138 | I10 | MBIO | Input value | FLOAT | R | -101...2000
138 | I11 | MBIO | Input value | FLOAT | R | -101...2000
138 | I12 | MBIO | Input value | FLOAT | R | -101...2000
138 | I13 | MBIO | Input value | FLOAT | R | -101...2000
138 | I14 | MBIO | Input value | FLOAT | R | -101...2000
138 | I15 | MBIO | Input value | FLOAT | R | -101...2000
138 | I16 | MBIO | Input value | FLOAT | R | -101...2000
138 | I17 | MBIO | Input value | FLOAT | R | -101...2000
138 | I18 | MBIO | Input value | FLOAT | R | -101...2000
138 | I19 | MBIO | Input value | FLOAT | R | -101...2000
138 | I20 | MBIO | Input value | FLOAT | R | -101...2000
138 | I21 | MBIO | Input value | FLOAT | R | -101...2000
138 | I22 | MBIO | Input value | FLOAT | R | -101...2000
138 | I23 | MBIO | Input value | FLOAT | R | -101...2000
138 | I24 | MBIO | Input value | FLOAT | R | -101...2000
138 | I25 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I26 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I27 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I28 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I29 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I30 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I31 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I32 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I33 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I34 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I35 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I36 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I37 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I38 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I39 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I40 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I41 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I42 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I43 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I44 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I45 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I46 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I47 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I48 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | O1 | MBIO | MBIO ModA Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O2 | MBIO | MBIO ModA Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O3 | MBIO | MBIO ModA Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O4 | MBIO | MBIO ModA Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O5 | MBIO | MBIO ModA Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O6 | MBIO | MBIO ModA Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O7 | MBIO | MBIO ModA Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O8 | MBIO | MBIO ModA Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O9 | MBIO | MBIO ModB Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O10 | MBIO | MBIO ModB Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O11 | MBIO | MBIO ModB Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O12 | MBIO | MBIO ModB Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O13 | MBIO | MBIO ModB Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O14 | MBIO | MBIO ModB Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O15 | MBIO | MBIO ModB Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O16 | MBIO | MBIO ModB Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O17 | MBIO | MBIO ModC Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O18 | MBIO | MBIO ModC Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O19 | MBIO | MBIO ModC Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O20 | MBIO | MBIO ModC Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O21 | MBIO | MBIO ModC Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O22 | MBIO | MBIO ModC Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O23 | MBIO | MBIO ModC Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O24 | MBIO | MBIO ModC Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
139 | V1 | LOGIC | Reset Latches | UINT32 | RW | 0=-;1=Reset
8 | O1 | LOGIC1 | Logic out 1-32 | UINT32 | RW | 0...4294967295
139 | O1 | LOGIC | Logical Output 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O2 | LOGIC | Logical Output 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O3 | LOGIC | Logical Output 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O4 | LOGIC | Logical Output 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O5 | LOGIC | Logical Output 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O6 | LOGIC | Logical Output 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O7 | LOGIC | Logical Output 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O8 | LOGIC | Logical Output 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O9 | LOGIC | Logical Output 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O10 | LOGIC | Logical Output 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O11 | LOGIC | Logical Output 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O12 | LOGIC | Logical Output 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O13 | LOGIC | Logical Output 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O14 | LOGIC | Logical Output 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O15 | LOGIC | Logical Output 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O16 | LOGIC | Logical Output 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O17 | LOGIC | Logical Output 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O18 | LOGIC | Logical Output 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O19 | LOGIC | Logical Output 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O20 | LOGIC | Logical Output 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O21 | LOGIC | Logical Output 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O22 | LOGIC | Logical Output 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O23 | LOGIC | Logical Output 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O24 | LOGIC | Logical Output 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O25 | LOGIC | Logical Output 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O26 | LOGIC | Logical Output 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O27 | LOGIC | Logical Output 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O28 | LOGIC | Logical Output 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O29 | LOGIC | Logical Output 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O30 | LOGIC | Logical Output 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O31 | LOGIC | Logical Output 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O32 | LOGIC | Logical Output 32 | SIGNAL_OUT | RW | 0...4294967295
139 | O33 | LOGIC | Logical Input 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O34 | LOGIC | Logical Input 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O35 | LOGIC | Logical Input 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O36 | LOGIC | Logical Input 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O37 | LOGIC | Logical Input 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O38 | LOGIC | Logical Input 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O39 | LOGIC | Logical Input 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O40 | LOGIC | Logical Input 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O41 | LOGIC | Logical Input 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O42 | LOGIC | Logical Input 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O43 | LOGIC | Logical Input 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O44 | LOGIC | Logical Input 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O45 | LOGIC | Logical Input 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O46 | LOGIC | Logical Input 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O47 | LOGIC | Logical Input 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O48 | LOGIC | Logical Input 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O49 | LOGIC | Logical Input 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O50 | LOGIC | Logical Input 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O51 | LOGIC | Logical Input 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O52 | LOGIC | Logical Input 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O53 | LOGIC | Logical Input 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O54 | LOGIC | Logical Input 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O55 | LOGIC | Logical Input 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O56 | LOGIC | Logical Input 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O57 | LOGIC | Logical Input 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O58 | LOGIC | Logical Input 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O59 | LOGIC | Logical Input 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O60 | LOGIC | Logical Input 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O61 | LOGIC | Logical Input 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O62 | LOGIC | Logical Input 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O63 | LOGIC | Logical Input 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O64 | LOGIC | Logical Input 32 | SIGNAL_OUT | RW | 0...4294967295
8 | S1 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
8 | S2 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
9 | S1 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
9 | S2 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
140 | O1 | TIMER | Timer1 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O2 | TIMER | Timer2 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O3 | TIMER | Timer3 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O4 | TIMER | Timer4 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O5 | TIMER | Timer5 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O6 | TIMER | Timer6 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O7 | TIMER | Timer7 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O8 | TIMER | Timer8 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O9 | TIMER | Timer9 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O10 | TIMER | Timer10 Output | SIGNAL_OUT | RW | 0...4294967295
2 | I1 | IRF | Internal Relay Fault status | UINT32 | R | 0b=Storage error;1b=Logic file missing;2b=Aquisition unit error;3b=Measurement config error;4b=Relay hardware setup error;5b=System overload error;6b=Not configured yet;7b=Firmware upgrade done;8b=Slot supervision error;9b=Software inconsistency error;10b=Safe setting mode active;
2 | S1 | IRF | Clear Fault status | UINT32 | W | 0=-;1=Clear
2 | I2 | IRF | Option card health status | UINT32 | R | 0b=Baseboard fault;1b=Card slot A fault;2b=Card slot B fault;3b=Card slot C fault;4b=Card slot D fault;5b=Card slot E fault;6b=Card slot F fault;
20 | S1 | NOC1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
20 | V1 | NOC1 | I> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
20 | V2 | NOC1 | I> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
20 | I1 | NOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
20 | I2 | NOC1 | I> starts | UINT32 | R | 0...4294967295
20 | I3 | NOC1 | I> trips | UINT32 | R | 0...4294967295
20 | I4 | NOC1 | I> blocks | UINT32 | R | 0...4294967295
20 | S2 | NOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
20 | S3 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S4 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S5 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S6 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S7 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S8 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S9 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S10 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S11 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S12 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S13 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S14 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S15 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S16 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S17 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S18 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S19 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S20 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S21 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S22 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S23 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S24 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S25 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S26 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S27 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S28 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S29 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S30 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S31 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S32 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S33 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S34 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | O1 | NOC1 | I> START (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O2 | NOC1 | I> START(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O3 | NOC1 | I> START(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O4 | NOC1 | I> START(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O5 | NOC1 | I> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O6 | NOC1 | I> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O7 | NOC1 | I> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O8 | NOC1 | I> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O9 | NOC1 | I> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
20 | V3 | NOC1 | Newest Register | UINT32 | R | 0...12
20 | V4 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V5 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V6 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V7 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V8 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V9 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V10 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V11 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V12 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V13 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V14 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V15 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V16 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V17 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V18 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V19 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V20 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V21 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V22 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V23 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V24 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V25 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V26 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V27 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V28 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V29 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V30 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V31 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V32 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V33 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V34 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V35 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V36 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V37 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V38 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V39 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | S35 | NOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
21 | S1 | NOC2 | I>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
21 | S2 | NOC2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
21 | V1 | NOC2 | I>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
21 | V2 | NOC2 | I>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
21 | I1 | NOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
21 | I2 | NOC2 | I>> starts | UINT32 | R | 0...4294967295
21 | I3 | NOC2 | I>> trips | UINT32 | R | 0...4294967295
21 | I4 | NOC2 | I>> blocks | UINT32 | R | 0...4294967295
21 | S3 | NOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
21 | S4 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S5 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S6 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S7 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S8 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S9 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S10 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S11 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S12 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S13 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S14 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S15 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S16 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S17 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S18 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S19 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S20 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S21 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S22 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S23 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S24 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S25 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S26 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S27 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S28 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S29 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S30 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S31 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S32 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S33 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S34 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S35 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | O1 | NOC2 | I>> START (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O2 | NOC2 | I>> START(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O3 | NOC2 | I>> START(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O4 | NOC2 | I>> START(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O5 | NOC2 | I>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O6 | NOC2 | I>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O7 | NOC2 | I>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O8 | NOC2 | I>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O9 | NOC2 | I>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
21 | V3 | NOC2 | Newest Register | UINT32 | R | 0...12
21 | V4 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V5 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V6 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V7 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V8 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V9 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V10 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V11 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V12 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V13 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V14 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V15 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V16 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V17 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V18 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V19 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V20 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V21 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V22 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V23 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V24 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V25 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V26 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V27 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V28 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V29 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V30 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V31 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V32 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V33 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V34 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V35 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V36 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V37 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V38 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V39 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | S36 | NOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
22 | S1 | NOC3 | I>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
22 | S2 | NOC3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
22 | V1 | NOC3 | I>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
22 | V2 | NOC3 | I>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
22 | I1 | NOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
22 | I2 | NOC3 | I>>> starts | UINT32 | R | 0...4294967295
22 | I3 | NOC3 | I>>> trips | UINT32 | R | 0...4294967295
22 | I4 | NOC3 | I>>> blocks | UINT32 | R | 0...4294967295
22 | S3 | NOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
22 | S4 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S5 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S6 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S7 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S8 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S9 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S10 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S11 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S12 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S13 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S14 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S15 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S16 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S17 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S18 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S19 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S20 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S21 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S22 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S23 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S24 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S25 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S26 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S27 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S28 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S29 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S30 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S31 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S32 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S33 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S34 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S35 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | O1 | NOC3 | I>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O2 | NOC3 | I>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O3 | NOC3 | I>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O4 | NOC3 | I>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O5 | NOC3 | I>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O6 | NOC3 | I>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O7 | NOC3 | I>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O8 | NOC3 | I>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O9 | NOC3 | I>>>BLOCKED | SIGNAL_OUT | RW | 0...4294967295
22 | V3 | NOC3 | Newest Register | UINT32 | R | 0...12
22 | V4 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V5 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V6 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V7 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V8 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V9 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V10 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V11 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V12 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V13 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V14 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V15 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V16 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V17 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V18 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V19 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V20 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V21 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V22 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V23 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V24 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V25 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V26 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V27 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V28 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V29 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V30 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V31 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V32 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V33 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V34 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V35 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V36 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V37 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V38 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V39 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | S36 | NOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
23 | S1 | NOC4 | I>>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
23 | S2 | NOC4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
23 | V1 | NOC4 | I>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
23 | V2 | NOC4 | I>>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
23 | I1 | NOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
23 | I2 | NOC4 | I>>>> starts | UINT32 | R | 0...4294967295
23 | I3 | NOC4 | I>>>> trips | UINT32 | R | 0...4294967295
23 | I4 | NOC4 | I>>>> blocks | UINT32 | R | 0...4294967295
23 | S3 | NOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
23 | S4 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S5 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S6 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S7 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S8 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S9 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S10 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S11 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S12 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S13 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S14 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S15 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S16 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S17 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S18 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S19 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S20 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S21 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S22 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S23 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S24 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S25 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S26 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S27 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S28 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S29 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S30 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S31 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S32 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S33 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S34 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S35 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | O1 | NOC4 | I>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O2 | NOC4 | I>>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O3 | NOC4 | I>>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O4 | NOC4 | I>>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O5 | NOC4 | I>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O6 | NOC4 | I>>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O7 | NOC4 | I>>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O8 | NOC4 | I>>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O9 | NOC4 | I>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
23 | V3 | NOC4 | Newest Register | UINT32 | R | 0...12
23 | V4 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V5 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V6 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V7 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V8 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V9 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V10 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V11 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V12 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V13 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V14 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V15 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V16 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V17 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V18 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V19 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V20 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V21 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V22 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V23 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V24 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V25 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V26 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V27 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V28 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V29 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V30 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V31 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V32 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V33 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V34 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V35 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V36 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V37 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V38 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V39 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | S36 | NOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
205 | V1 | ROC1 | Idrw> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
205 | I1 | ROC1 | Idrw> Imeas/Iset at the moment | FLOAT | R | -1250...1250
205 | I2 | ROC1 | Idrw> I/U Angle atm. | FLOAT | R | -360...360
205 | I3 | ROC1 | Idrw> I measured p.u. | FLOAT | R | 0...1250
205 | I4 | ROC1 | Idrw> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
205 | I5 | ROC1 | Idrw> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
205 | I6 | ROC1 | Idrw> U measured p.u. | FLOAT | R | 0...1250
205 | I7 | ROC1 | Idrw> starts | UINT32 | R | 0...4294967295
205 | I8 | ROC1 | Idrw> trips | UINT32 | R | 0...4294967295
205 | I9 | ROC1 | Idrw> blocks | UINT32 | R | 0...4294967295
205 | S1 | ROC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
205 | S2 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S3 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S4 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S5 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S6 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S7 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S8 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S9 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S10 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S11 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S12 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S13 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S14 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S15 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S16 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S17 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S18 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S19 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S20 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S21 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S22 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S23 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S24 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S25 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S26 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S27 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S28 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S29 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S30 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S31 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S32 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S33 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S34 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S35 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S36 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S37 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S38 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S39 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S40 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S41 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S42 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S43 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S44 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S45 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S46 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S47 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S48 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S49 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S50 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S51 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S52 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S53 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S54 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S55 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S56 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S57 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S58 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S59 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S60 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S61 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S62 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S63 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S64 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S65 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | O1 | ROC1 | Idrw> START | SIGNAL_OUT | RW | 0...4294967295
205 | O2 | ROC1 | Idrw> TRIP | SIGNAL_OUT | RW | 0...4294967295
205 | O3 | ROC1 | Idrw> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
205 | V2 | ROC1 | Newest Register | UINT32 | R | 0...12
205 | V3 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V4 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V5 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V6 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V7 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V8 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V9 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V10 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V11 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V12 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V13 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V14 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V15 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V16 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V17 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V18 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V19 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V20 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V21 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V22 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V23 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V24 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V25 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V26 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | S66 | ROC1 | EventMaskLo | UINT32 | RW | 0...4294967295
206 | V1 | ROC2 | Idrw>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
206 | I1 | ROC2 | Idrw>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
206 | I2 | ROC2 | Idrw>> I/U Angle atm. | FLOAT | R | -360...360
206 | I3 | ROC2 | Idrw>> I measured p.u. | FLOAT | R | 0...1250
206 | I4 | ROC2 | Idrw>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
206 | I5 | ROC2 | Idrw>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
206 | I6 | ROC2 | Idrw>> U measured p.u. | FLOAT | R | 0...1250
206 | I7 | ROC2 | Idrw>> starts | UINT32 | R | 0...4294967295
206 | I8 | ROC2 | Idrw>> trips | UINT32 | R | 0...4294967295
206 | I9 | ROC2 | Idrw>> blocks | UINT32 | R | 0...4294967295
206 | S1 | ROC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
206 | S2 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S3 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S4 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S5 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S6 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S7 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S8 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S9 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S10 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S11 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S12 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S13 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S14 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S15 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S16 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S17 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S18 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S19 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S20 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S21 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S22 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S23 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S24 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S25 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S26 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S27 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S28 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S29 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S30 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S31 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S32 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S33 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S34 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S35 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S36 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S37 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S38 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S39 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S40 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S41 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S42 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S43 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S44 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S45 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S46 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S47 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S48 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S49 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S50 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S51 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S52 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S53 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S54 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S55 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S56 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S57 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S58 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S59 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S60 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S61 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S62 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S63 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S64 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S65 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | O1 | ROC2 | Idrw>> START | SIGNAL_OUT | RW | 0...4294967295
206 | O2 | ROC2 | Idrw>> TRIP | SIGNAL_OUT | RW | 0...4294967295
206 | O3 | ROC2 | Idrw>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
206 | V2 | ROC2 | Newest Register | UINT32 | R | 0...12
206 | V3 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V4 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V5 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V6 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V7 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V8 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V9 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V10 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V11 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V12 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V13 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V14 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V15 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V16 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V17 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V18 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V19 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V20 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V21 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V22 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V23 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V24 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V25 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V26 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | S66 | ROC2 | EventMaskLo | UINT32 | RW | 0...4294967295
207 | V1 | ROC3 | Idrw>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
207 | I1 | ROC3 | Idrw>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
207 | I2 | ROC3 | Idrw>>> I/U Angle atm. | FLOAT | R | -360...360
207 | I3 | ROC3 | Idrw>>> I measured p.u. | FLOAT | R | 0...1250
207 | I4 | ROC3 | Idrw>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
207 | I5 | ROC3 | Idrw>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
207 | I6 | ROC3 | Idrw>>> U measured p.u. | FLOAT | R | 0...1250
207 | I7 | ROC3 | Idrw>>> starts | UINT32 | R | 0...4294967295
207 | I8 | ROC3 | Idrw>>> trips | UINT32 | R | 0...4294967295
207 | I9 | ROC3 | Idrw>>> blocks | UINT32 | R | 0...4294967295
207 | S1 | ROC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
207 | S2 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S3 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S4 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S5 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S6 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S7 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S8 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S9 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S10 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S11 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S12 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S13 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S14 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S15 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S16 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S17 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S18 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S19 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S20 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S21 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S22 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S23 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S24 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S25 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S26 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S27 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S28 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S29 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S30 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S31 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S32 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S33 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S34 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S35 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S36 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S37 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S38 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S39 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S40 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S41 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S42 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S43 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S44 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S45 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S46 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S47 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S48 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S49 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S50 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S51 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S52 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S53 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S54 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S55 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S56 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S57 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S58 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S59 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S60 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S61 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S62 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S63 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S64 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S65 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | O1 | ROC3 | Idrw>>> START | SIGNAL_OUT | RW | 0...4294967295
207 | O2 | ROC3 | Idrw>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
207 | O3 | ROC3 | Idrw>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
207 | V2 | ROC3 | Newest Register | UINT32 | R | 0...12
207 | V3 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V4 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V5 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V6 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V7 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V8 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V9 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V10 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V11 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V12 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V13 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V14 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V15 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V16 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V17 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V18 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V19 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V20 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V21 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V22 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V23 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V24 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V25 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V26 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | S66 | ROC3 | EventMaskLo | UINT32 | RW | 0...4294967295
208 | V1 | ROC4 | Idrw>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
208 | I1 | ROC4 | Idrw>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
208 | I2 | ROC4 | Idrw>>>> I/U Angle atm. | FLOAT | R | -360...360
208 | I3 | ROC4 | Idrw>>>> I measured p.u. | FLOAT | R | 0...1250
208 | I4 | ROC4 | Idrw>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
208 | I5 | ROC4 | Idrw>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
208 | I6 | ROC4 | Idrw>>>> U measured p.u. | FLOAT | R | 0...1250
208 | I7 | ROC4 | Idrw>>>> starts | UINT32 | R | 0...4294967295
208 | I8 | ROC4 | Idrw>>>> trips | UINT32 | R | 0...4294967295
208 | I9 | ROC4 | Idrw>>>> blocks | UINT32 | R | 0...4294967295
208 | S1 | ROC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
208 | S2 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S3 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S4 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S5 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S6 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S7 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S8 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S9 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S10 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S11 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S12 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S13 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S14 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S15 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S16 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S17 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S18 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S19 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S20 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S21 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S22 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S23 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S24 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S25 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S26 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S27 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S28 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S29 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S30 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S31 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S32 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S33 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S34 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S35 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S36 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S37 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S38 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S39 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S40 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S41 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S42 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S43 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S44 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S45 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S46 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S47 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S48 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S49 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S50 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S51 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S52 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S53 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S54 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S55 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S56 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S57 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S58 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S59 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S60 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S61 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S62 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S63 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S64 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S65 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | O1 | ROC4 | Idrw>>>> START | SIGNAL_OUT | RW | 0...4294967295
208 | O2 | ROC4 | Idrw>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
208 | O3 | ROC4 | Idrw>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
208 | V2 | ROC4 | Newest Register | UINT32 | R | 0...12
208 | V3 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V4 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V5 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V6 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V7 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V8 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V9 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V10 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V11 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V12 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V13 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V14 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V15 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V16 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V17 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V18 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V19 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V20 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V21 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V22 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V23 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V24 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V25 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V26 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | S66 | ROC4 | EventMaskLo | UINT32 | RW | 0...4294967295
209 | V1 | ROC5 | Idrw>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
209 | I1 | ROC5 | Idrw>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
209 | I2 | ROC5 | Idrw>>>>> I/U Angle atm. | FLOAT | R | -360...360
209 | I3 | ROC5 | Idrw>>>>> I measured p.u. | FLOAT | R | 0...1250
209 | I4 | ROC5 | Idrw>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
209 | I5 | ROC5 | Idrw>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
209 | I6 | ROC5 | Idrw>>>>> U measured p.u. | FLOAT | R | 0...1250
209 | I7 | ROC5 | Idrw>>>>> starts | UINT32 | R | 0...4294967295
209 | I8 | ROC5 | Idrw>>>>> trips | UINT32 | R | 0...4294967295
209 | I9 | ROC5 | Idrw>>>>> blocks | UINT32 | R | 0...4294967295
209 | S1 | ROC5 | Clear statistics | UINT32 | W | 0=-;1=Clear
209 | S2 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S3 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S4 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S5 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S6 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S7 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S8 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S9 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S10 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S11 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S12 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S13 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S14 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S15 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S16 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S17 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S18 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S19 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S20 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S21 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S22 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S23 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S24 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S25 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S26 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S27 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S28 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S29 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S30 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S31 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S32 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S33 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S34 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S35 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S36 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S37 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S38 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S39 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S40 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S41 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S42 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S43 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S44 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S45 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S46 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S47 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S48 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S49 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S50 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S51 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S52 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S53 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S54 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S55 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S56 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S57 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S58 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S59 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S60 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S61 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S62 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S63 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S64 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S65 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | O1 | ROC5 | Idrw>>>>> START | SIGNAL_OUT | RW | 0...4294967295
209 | O2 | ROC5 | Idrw>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
209 | O3 | ROC5 | Idrw>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
209 | V2 | ROC5 | Newest Register | UINT32 | R | 0...12
209 | V3 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V4 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V5 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V6 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V7 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V8 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V9 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V10 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V11 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V12 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V13 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V14 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V15 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V16 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V17 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V18 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V19 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V20 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V21 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V22 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V23 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V24 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V25 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V26 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | S66 | ROC5 | EventMaskLo | UINT32 | RW | 0...4294967295
210 | V1 | ROC6 | Idrw>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
210 | I1 | ROC6 | Idrw>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
210 | I2 | ROC6 | Idrw>>>>>> I/U Angle atm. | FLOAT | R | -360...360
210 | I3 | ROC6 | Idrw>>>>>> I measured p.u. | FLOAT | R | 0...1250
210 | I4 | ROC6 | Idrw>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
210 | I5 | ROC6 | Idrw>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
210 | I6 | ROC6 | Idrw>>>>>> U measured p.u. | FLOAT | R | 0...1250
210 | I7 | ROC6 | Idrw>>>>>> starts | UINT32 | R | 0...4294967295
210 | I8 | ROC6 | Idrw>>>>>> trips | UINT32 | R | 0...4294967295
210 | I9 | ROC6 | Idrw>>>>>> blocks | UINT32 | R | 0...4294967295
210 | S1 | ROC6 | Clear statistics | UINT32 | W | 0=-;1=Clear
210 | S2 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S3 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S4 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S5 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S6 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S7 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S8 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S9 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S10 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S11 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S12 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S13 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S14 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S15 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S16 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S17 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S18 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S19 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S20 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S21 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S22 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S23 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S24 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S25 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S26 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S27 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S28 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S29 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S30 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S31 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S32 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S33 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S34 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S35 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S36 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S37 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S38 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S39 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S40 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S41 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S42 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S43 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S44 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S45 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S46 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S47 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S48 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S49 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S50 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S51 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S52 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S53 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S54 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S55 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S56 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S57 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S58 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S59 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S60 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S61 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S62 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S63 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S64 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S65 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | O1 | ROC6 | Idrw>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
210 | O2 | ROC6 | Idrw>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
210 | O3 | ROC6 | Idrw>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
210 | V2 | ROC6 | Newest Register | UINT32 | R | 0...12
210 | V3 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V4 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V5 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V6 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V7 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V8 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V9 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V10 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V11 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V12 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V13 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V14 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V15 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V16 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V17 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V18 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V19 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V20 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V21 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V22 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V23 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V24 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V25 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V26 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | S66 | ROC6 | EventMaskLo | UINT32 | RW | 0...4294967295
211 | V1 | ROC7 | Idrw>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
211 | I1 | ROC7 | Idrw>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
211 | I2 | ROC7 | Idrw>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
211 | I3 | ROC7 | Idrw>>>>>>> I measured p.u. | FLOAT | R | 0...1250
211 | I4 | ROC7 | Idrw>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
211 | I5 | ROC7 | Idrw>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
211 | I6 | ROC7 | Idrw>>>>>>> U measured p.u. | FLOAT | R | 0...1250
211 | I7 | ROC7 | Idrw>>>>>>> starts | UINT32 | R | 0...4294967295
211 | I8 | ROC7 | Idrw>>>>>>> trips | UINT32 | R | 0...4294967295
211 | I9 | ROC7 | Idrw>>>>>>> blocks | UINT32 | R | 0...4294967295
211 | S1 | ROC7 | Clear statistics | UINT32 | W | 0=-;1=Clear
211 | S2 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S3 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S4 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S5 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S6 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S7 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S8 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S9 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S10 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S11 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S12 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S13 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S14 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S15 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S16 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S17 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S18 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S19 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S20 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S21 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S22 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S23 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S24 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S25 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S26 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S27 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S28 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S29 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S30 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S31 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S32 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S33 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S34 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S35 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S36 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S37 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S38 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S39 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S40 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S41 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S42 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S43 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S44 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S45 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S46 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S47 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S48 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S49 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S50 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S51 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S52 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S53 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S54 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S55 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S56 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S57 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S58 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S59 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S60 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S61 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S62 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S63 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S64 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S65 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | O1 | ROC7 | Idrw>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
211 | O2 | ROC7 | Idrw>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
211 | O3 | ROC7 | Idrw>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
211 | V2 | ROC7 | Newest Register | UINT32 | R | 0...12
211 | V3 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V4 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V5 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V6 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V7 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V8 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V9 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V10 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V11 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V12 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V13 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V14 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V15 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V16 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V17 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V18 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V19 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V20 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V21 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V22 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V23 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V24 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V25 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V26 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | S66 | ROC7 | EventMaskLo | UINT32 | RW | 0...4294967295
212 | V1 | ROC8 | Idrw>>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
212 | I1 | ROC8 | Idrw>>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
212 | I2 | ROC8 | Idrw>>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
212 | I3 | ROC8 | Idrw>>>>>>>> I measured p.u. | FLOAT | R | 0...1250
212 | I4 | ROC8 | Idrw>>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
212 | I5 | ROC8 | Idrw>>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
212 | I6 | ROC8 | Idrw>>>>>>>> U measured p.u. | FLOAT | R | 0...1250
212 | I7 | ROC8 | Idrw>>>>>>>> starts | UINT32 | R | 0...4294967295
212 | I8 | ROC8 | Idrw>>>>>>>> trips | UINT32 | R | 0...4294967295
212 | I9 | ROC8 | Idrw>>>>>>>> blocks | UINT32 | R | 0...4294967295
212 | S1 | ROC8 | Clear statistics | UINT32 | W | 0=-;1=Clear
212 | S2 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S3 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S4 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S5 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S6 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S7 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S8 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S9 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S10 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S11 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S12 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S13 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S14 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S15 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S16 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S17 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S18 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S19 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S20 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S21 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S22 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S23 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S24 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S25 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S26 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S27 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S28 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S29 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S30 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S31 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S32 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S33 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S34 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S35 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S36 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S37 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S38 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S39 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S40 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S41 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S42 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S43 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S44 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S45 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S46 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S47 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S48 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S49 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S50 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S51 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S52 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S53 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S54 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S55 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S56 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S57 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S58 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S59 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S60 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S61 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S62 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S63 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S64 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S65 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | O1 | ROC8 | Idrw>>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
212 | O2 | ROC8 | Idrw>>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
212 | O3 | ROC8 | Idrw>>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
212 | V2 | ROC8 | Newest Register | UINT32 | R | 0...12
212 | V3 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V4 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V5 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V6 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V7 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V8 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V9 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V10 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V11 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V12 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V13 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V14 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V15 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V16 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V17 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V18 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V19 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V20 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V21 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V22 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V23 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V24 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V25 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V26 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | S66 | ROC8 | EventMaskLo | UINT32 | RW | 0...4294967295
213 | V1 | ROV1 | Urw>/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
213 | I1 | ROV1 | Urw>/< Umeas/Uset at the moment | FLOAT | R | 0...1250
213 | I2 | ROV1 | Urw>/< U measured p.u. | FLOAT | R | 0...1250
213 | I3 | ROV1 | Urw>/< starts | UINT32 | R | 0...4294967295
213 | I4 | ROV1 | Urw>/< trips | UINT32 | R | 0...4294967295
213 | I5 | ROV1 | Urw>/< blocks | UINT32 | R | 0...4294967295
213 | S1 | ROV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
213 | S2 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S3 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S4 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S5 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S6 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S7 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S8 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S9 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S10 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S11 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S12 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S13 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S14 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S15 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S16 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S17 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S18 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S19 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S20 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S21 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S22 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S23 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S24 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S25 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S26 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S27 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S28 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S29 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S30 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S31 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S32 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S33 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S34 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S35 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S36 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S37 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S38 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S39 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S40 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S41 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S42 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S43 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S44 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S45 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S46 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S47 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S48 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S49 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | O1 | ROV1 | Urw>/< START | SIGNAL_OUT | RW | 0...4294967295
213 | O2 | ROV1 | Urw>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
213 | O3 | ROV1 | Urw>/< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
213 | O4 | ROV1 | Urw>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
213 | V2 | ROV1 | Newest Register | UINT32 | R | 0...12
213 | V3 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V4 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V5 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V6 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V7 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V8 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V9 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V10 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V11 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V12 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V13 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V14 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V15 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V16 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V17 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V18 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V19 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V20 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V21 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V22 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V23 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V24 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V25 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V26 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | S50 | ROV1 | EventMaskLo | UINT32 | RW | 0...4294967295
214 | V1 | ROV2 | Urw>>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
214 | I1 | ROV2 | Urw>>/<< Umeas/Uset at the moment | FLOAT | R | 0...1250
214 | I2 | ROV2 | Urw>>/<< U measured p.u. | FLOAT | R | 0...1250
214 | I3 | ROV2 | Urw>>/<< starts | UINT32 | R | 0...4294967295
214 | I4 | ROV2 | Urw>>/<< trips | UINT32 | R | 0...4294967295
214 | I5 | ROV2 | Urw>>/<< blocks | UINT32 | R | 0...4294967295
214 | S1 | ROV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
214 | S2 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S3 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S4 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S5 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S6 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S7 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S8 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S9 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S10 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S11 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S12 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S13 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S14 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S15 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S16 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S17 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S18 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S19 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S20 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S21 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S22 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S23 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S24 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S25 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S26 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S27 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S28 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S29 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S30 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S31 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S32 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S33 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S34 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S35 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S36 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S37 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S38 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S39 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S40 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S41 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S42 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S43 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S44 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S45 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S46 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S47 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S48 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S49 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | O1 | ROV2 | Urw>>/<< START | SIGNAL_OUT | RW | 0...4294967295
214 | O2 | ROV2 | Urw>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
214 | O3 | ROV2 | Urw>>/<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
214 | O4 | ROV2 | Urw>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
214 | V2 | ROV2 | Newest Register | UINT32 | R | 0...12
214 | V3 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V4 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V5 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V6 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V7 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V8 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V9 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V10 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V11 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V12 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V13 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V14 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V15 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V16 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V17 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V18 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V19 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V20 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V21 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V22 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V23 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V24 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V25 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V26 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | S50 | ROV2 | EventMaskLo | UINT32 | RW | 0...4294967295
215 | V1 | ROV3 | Urw>>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
215 | I1 | ROV3 | Urw>>>/<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
215 | I2 | ROV3 | Urw>>>/<<< U measured p.u. | FLOAT | R | 0...1250
215 | I3 | ROV3 | Urw>>>/<<< starts | UINT32 | R | 0...4294967295
215 | I4 | ROV3 | Urw>>>/<<< trips | UINT32 | R | 0...4294967295
215 | I5 | ROV3 | Urw>>>/<<< blocks | UINT32 | R | 0...4294967295
215 | S1 | ROV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
215 | S2 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S3 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S4 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S5 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S6 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S7 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S8 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S9 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S10 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S11 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S12 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S13 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S14 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S15 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S16 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S17 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S18 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S19 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S20 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S21 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S22 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S23 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S24 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S25 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S26 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S27 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S28 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S29 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S30 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S31 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S32 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S33 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S34 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S35 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S36 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S37 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S38 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S39 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S40 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S41 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S42 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S43 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S44 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S45 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S46 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S47 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S48 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S49 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | O1 | ROV3 | Urw>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
215 | O2 | ROV3 | Urw>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
215 | O3 | ROV3 | Urw>>>/<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
215 | O4 | ROV3 | Urw>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
215 | V2 | ROV3 | Newest Register | UINT32 | R | 0...12
215 | V3 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V4 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V5 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V6 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V7 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V8 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V9 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V10 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V11 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V12 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V13 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V14 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V15 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V16 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V17 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V18 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V19 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V20 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V21 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V22 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V23 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V24 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V25 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V26 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | S50 | ROV3 | EventMaskLo | UINT32 | RW | 0...4294967295
216 | V1 | ROV4 | Urw>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
216 | I1 | ROV4 | Urw>>>>/<<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
216 | I2 | ROV4 | Urw>>>>/<<<< U measured p.u. | FLOAT | R | 0...1250
216 | I3 | ROV4 | Urw>>>>/<<<< starts | UINT32 | R | 0...4294967295
216 | I4 | ROV4 | Urw>>>>/<<<< trips | UINT32 | R | 0...4294967295
216 | I5 | ROV4 | Urw>>>>/<<<< blocks | UINT32 | R | 0...4294967295
216 | S1 | ROV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
216 | S2 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S3 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S4 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S5 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S6 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S7 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S8 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S9 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S10 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S11 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S12 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S13 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S14 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S15 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S16 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S17 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S18 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S19 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S20 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S21 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S22 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S23 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S24 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S25 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S26 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S27 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S28 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S29 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S30 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S31 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S32 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S33 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S34 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S35 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S36 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S37 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S38 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S39 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S40 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S41 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S42 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S43 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S44 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S45 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S46 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S47 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S48 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S49 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | O1 | ROV4 | Urw>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
216 | O2 | ROV4 | Urw>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
216 | O3 | ROV4 | Urw>>>>/<<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
216 | O4 | ROV4 | Urw>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
216 | V2 | ROV4 | Newest Register | UINT32 | R | 0...12
216 | V3 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V4 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V5 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V6 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V7 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V8 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V9 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V10 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V11 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V12 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V13 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V14 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V15 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V16 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V17 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V18 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V19 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V20 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V21 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V22 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V23 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V24 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V25 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V26 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | S50 | ROV4 | EventMaskLo | UINT32 | RW | 0...4294967295
224 | I1 | CNU1 | Measured unbalance current | FLOAT | R | 0...50.00
224 | I2 | CNU1 | Unbalance current angle | FLOAT | R | -360.00...360.00
224 | S1 | CNU1 | Natural unbalance compensation | UINT32 | RW | 0=Not used;1=In use
224 | S2 | CNU1 | Compensate natural unbal. | UINT32 | RW | 0=-;1=Comp
224 | I3 | CNU1 | Natural unbalance | FLOAT | R | -50.00...50.00
224 | I4 | CNU1 | Natural unbalance ang | FLOAT | R | -360.00...360.00
224 | I5 | CNU1 | Compensated magnitude | FLOAT | R | -50.00...50.00
224 | I6 | CNU1 | Compensated angle | FLOAT | R | -360.00...360.00
217 | V1 | UCP1 | IUC> condition | UINT32 | R | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
217 | I1 | UCP1 | Unbalance current atm. | FLOAT | R | 0...1250
217 | I2 | UCP1 | Imeas/Iset (ALARM) atm. | FLOAT | R | 0...1250
217 | I3 | UCP1 | Imeas/Iset (TRIP) atm. | FLOAT | R | 0...1250
217 | I4 | UCP1 | IUC> Alarm Starts | UINT32 | R | 0...4294967295
217 | I5 | UCP1 | IUC> Alarms | UINT32 | R | 0...4294967295
217 | I6 | UCP1 | IUC> Starts | UINT32 | R | 0...4294967295
217 | I7 | UCP1 | IUC> Trips | UINT32 | R | 0...4294967295
217 | I8 | UCP1 | IUC> Blocks | UINT32 | R | 0...4294967295
217 | S1 | UCP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
217 | S2 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S3 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S4 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S5 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S6 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S7 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S8 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S9 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S10 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S11 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S12 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S13 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S14 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S15 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S16 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S17 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S18 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S19 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S20 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S21 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S22 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S23 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S24 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S25 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S26 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S27 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S28 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S29 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S30 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S31 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S32 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S33 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S34 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S35 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S36 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S37 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S38 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S39 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S40 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S41 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | O1 | UCP1 | IUC> ALARM START | SIGNAL_OUT | RW | 0...4294967295
217 | O2 | UCP1 | IUC> ALARM | SIGNAL_OUT | RW | 0...4294967295
217 | O3 | UCP1 | IUC> START | SIGNAL_OUT | RW | 0...4294967295
217 | O4 | UCP1 | IUC> TRIP | SIGNAL_OUT | RW | 0...4294967295
217 | O5 | UCP1 | IUC> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
217 | V2 | UCP1 | Newest Register | UINT32 | R | 0...12
217 | V3 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V4 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V5 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V6 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V7 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V8 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V9 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V10 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V11 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V12 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V13 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V14 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | S42 | UCP1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S1 | DOC1 | Idir> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
75 | V1 | DOC1 | Idir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
75 | I1 | DOC1 | Operating angle now | FLOAT | R | -360...360
75 | I2 | DOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
75 | I3 | DOC1 | Idir> starts | UINT32 | R | 0...4294967295
75 | I4 | DOC1 | Idir> trips | UINT32 | R | 0...4294967295
75 | I5 | DOC1 | Idir> blocks | UINT32 | R | 0...4294967295
75 | S2 | DOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
75 | S3 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S4 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S5 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S6 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S7 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S8 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S9 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S10 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S11 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S12 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S13 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S14 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S15 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S16 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S17 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S18 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S19 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S20 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S21 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S22 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S23 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S24 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S25 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S26 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S27 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S28 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S29 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S30 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S31 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S32 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S33 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S34 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S35 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S36 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S37 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S38 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S39 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S40 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S41 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S42 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S43 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S44 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S45 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S46 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S47 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S48 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S49 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S50 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S51 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S52 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S53 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S54 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S55 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S56 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S57 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S58 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | O1 | DOC1 | Idir> START | SIGNAL_OUT | RW | 0...4294967295
75 | O2 | DOC1 | Idir> TRIP | SIGNAL_OUT | RW | 0...4294967295
75 | O3 | DOC1 | Idir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
75 | S59 | DOC1 | Clear registers | UINT32 | W | 0=-;1=Clear
75 | I6 | DOC1 | Newest Register | UINT32 | R | 0...12
75 | I7 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I8 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I9 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I10 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I11 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I12 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I13 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I14 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I15 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I16 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I17 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I18 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I19 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I20 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I21 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I22 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I23 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I24 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I25 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I26 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I27 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I28 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I29 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I30 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I31 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I32 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I33 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I34 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I35 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I36 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I37 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I38 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I39 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I40 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I41 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I42 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I43 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I44 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I45 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I46 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I47 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I48 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I49 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I50 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I51 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I52 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I53 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I54 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | S60 | DOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S61 | DOC1 | EventMaskHi | UINT32 | RW | 0...4294967295
76 | S1 | DOC2 | Idir>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
76 | V1 | DOC2 | Idir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
76 | I1 | DOC2 | Operating angle now | FLOAT | R | -360.00...360.00
76 | I2 | DOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
76 | I3 | DOC2 | Idir>> starts | UINT32 | R | 0...4294967295
76 | I4 | DOC2 | Idir>> trips | UINT32 | R | 0...4294967295
76 | I5 | DOC2 | Idir>> blocks | UINT32 | R | 0...4294967295
76 | S2 | DOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
76 | S3 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S4 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S5 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S6 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S7 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S8 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S9 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S10 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S11 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S12 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S13 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S14 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S15 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S16 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S17 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S18 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S19 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S20 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S21 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S22 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S23 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S24 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S25 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S26 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S27 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S28 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S29 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S30 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S31 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S32 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S33 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S34 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S35 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S36 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S37 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S38 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S39 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S40 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S41 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S42 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S43 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S44 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S45 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S46 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S47 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S48 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S49 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S50 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S51 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S52 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S53 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S54 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S55 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S56 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S57 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S58 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | O1 | DOC2 | Idir>> START | SIGNAL_OUT | RW | 0...4294967295
76 | O2 | DOC2 | Idir>> TRIP | SIGNAL_OUT | RW | 0...4294967295
76 | O3 | DOC2 | Idir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
76 | S59 | DOC2 | Clear registers | UINT32 | W | 0=-;1=Clear
76 | I6 | DOC2 | Newest Register | UINT32 | R | 0...12
76 | I7 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I8 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I9 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I10 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I11 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I12 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I13 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I14 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I15 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I16 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I17 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I18 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I19 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I20 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I21 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I22 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I23 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I24 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I25 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I26 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I27 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I28 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I29 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I30 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I31 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I32 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I33 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I34 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I35 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I36 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I37 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I38 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I39 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I40 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I41 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I42 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I43 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I44 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I45 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I46 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I47 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I48 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I49 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I50 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I51 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I52 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I53 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I54 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | S60 | DOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
76 | S61 | DOC2 | EventMaskHi | UINT32 | RW | 0...4294967295
77 | S1 | DOC3 | Idir>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
77 | V1 | DOC3 | Idir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
77 | I1 | DOC3 | Operating angle now | FLOAT | R | -360...360
77 | I2 | DOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
77 | I3 | DOC3 | Idir>>> starts | UINT32 | R | 0...4294967295
77 | I4 | DOC3 | Idir>>> trips | UINT32 | R | 0...4294967295
77 | I5 | DOC3 | Idir>>> blocks | UINT32 | R | 0...4294967295
77 | S2 | DOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
77 | S3 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S4 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S5 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S6 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S7 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S8 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S9 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S10 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S11 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S12 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S13 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S14 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S15 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S16 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S17 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S18 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S19 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S20 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S21 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S22 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S23 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S24 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S25 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S26 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S27 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S28 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S29 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S30 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S31 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S32 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S33 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S34 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S35 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S36 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S37 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S38 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S39 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S40 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S41 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S42 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S43 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S44 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S45 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S46 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S47 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S48 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S49 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S50 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S51 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S52 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S53 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S54 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S55 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S56 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S57 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S58 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | O1 | DOC3 | Idir>>> START | SIGNAL_OUT | RW | 0...4294967295
77 | O2 | DOC3 | Idir>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
77 | O3 | DOC3 | Idir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
77 | S59 | DOC3 | Clear registers | UINT32 | W | 0=-;1=Clear
77 | I6 | DOC3 | Newest Register | UINT32 | R | 0...12
77 | I7 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I8 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I9 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I10 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I11 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I12 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I13 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I14 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I15 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I16 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I17 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I18 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I19 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I20 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I21 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I22 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I23 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I24 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I25 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I26 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I27 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I28 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I29 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I30 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I31 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I32 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I33 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I34 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I35 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I36 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I37 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I38 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I39 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I40 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I41 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I42 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I43 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I44 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I45 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I46 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I47 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I48 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I49 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I50 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I51 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I52 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I53 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I54 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | S60 | DOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
77 | S61 | DOC3 | EventMaskHi | UINT32 | RW | 0...4294967295
78 | S1 | DOC4 | Idir>>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
78 | V1 | DOC4 | Idir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
78 | I1 | DOC4 | Operating angle now | FLOAT | R | -360.00...360.00
78 | I2 | DOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
78 | I3 | DOC4 | Idir>>>> starts | UINT32 | R | 0...4294967295
78 | I4 | DOC4 | Idir>>>> trips | UINT32 | R | 0...4294967295
78 | I5 | DOC4 | Idir>>>> blocks | UINT32 | R | 0...4294967295
78 | S2 | DOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
78 | S3 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S4 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S5 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S6 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S7 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S8 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S9 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S10 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S11 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S12 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S13 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S14 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S15 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S16 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S17 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S18 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S19 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S20 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S21 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S22 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S23 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S24 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S25 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S26 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S27 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S28 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S29 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S30 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S31 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S32 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S33 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S34 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S35 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S36 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S37 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S38 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S39 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S40 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S41 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S42 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S43 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S44 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S45 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S46 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S47 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S48 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S49 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S50 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S51 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S52 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S53 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S54 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S55 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S56 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S57 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S58 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | O1 | DOC4 | Idir>>>> START | SIGNAL_OUT | RW | 0...4294967295
78 | O2 | DOC4 | Idir>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
78 | O3 | DOC4 | Idir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
78 | S59 | DOC4 | Clear registers | UINT32 | W | 0=-;1=Clear
78 | I6 | DOC4 | Newest Register | UINT32 | R | 0...12
78 | I7 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I8 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I9 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I10 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I11 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I12 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I13 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I14 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I15 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I16 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I17 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I18 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I19 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I20 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I21 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I22 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I23 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I24 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I25 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I26 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I27 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I28 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I29 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I30 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I31 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I32 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I33 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I34 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I35 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I36 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I37 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I38 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I39 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I40 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I41 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I42 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I43 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I44 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I45 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I46 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I47 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I48 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I49 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I50 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I51 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I52 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I53 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I54 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | S60 | DOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
78 | S61 | DOC4 | EventMaskHi | UINT32 | RW | 0...4294967295
26 | S1 | NEF1 | I0> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
26 | S2 | NEF1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
26 | V1 | NEF1 | I0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
26 | I1 | NEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
26 | I2 | NEF1 | I0> starts | UINT32 | R | 0...4294967295
26 | I3 | NEF1 | I0> trips | UINT32 | R | 0...4294967295
26 | I4 | NEF1 | I0> blocks | UINT32 | R | 0...4294967295
26 | S3 | NEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
26 | S4 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S5 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S6 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S7 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S8 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S9 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S10 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S11 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S12 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S13 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S14 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S15 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S16 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S17 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S18 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S19 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S20 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S21 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S22 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S23 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S24 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S25 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S26 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S27 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S28 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S29 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S30 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S31 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S32 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S33 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S34 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S35 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | O1 | NEF1 | I0> START | SIGNAL_OUT | RW | 0...4294967295
26 | O2 | NEF1 | I0> TRIP | SIGNAL_OUT | RW | 0...4294967295
26 | O3 | NEF1 | I0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
26 | I5 | NEF1 | Newest Register | UINT32 | R | 0...12
26 | I6 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I7 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I8 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I9 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I10 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I11 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I12 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I13 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I14 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I15 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I16 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I17 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | S36 | NEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
27 | S1 | NEF2 | I0>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
27 | S2 | NEF2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
27 | V1 | NEF2 | I0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
27 | I1 | NEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
27 | I2 | NEF2 | I0>> starts | UINT32 | R | 0...4294967295
27 | I3 | NEF2 | I0>> trips | UINT32 | R | 0...4294967295
27 | I4 | NEF2 | I0>> blocks | UINT32 | R | 0...4294967295
27 | S3 | NEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
27 | S4 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S5 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S6 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S7 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S8 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S9 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S10 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S11 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S12 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S13 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S14 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S15 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S16 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S17 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S18 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S19 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S20 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S21 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S22 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S23 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S24 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S25 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S26 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S27 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S28 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S29 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S30 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S31 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S32 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S33 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S34 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S35 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | O1 | NEF2 | I0>> START | SIGNAL_OUT | RW | 0...4294967295
27 | O2 | NEF2 | I0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
27 | O3 | NEF2 | I0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
27 | I5 | NEF2 | Newest Register | UINT32 | R | 0...12
27 | I6 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I7 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I8 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I9 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I10 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I11 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I12 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I13 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I14 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I15 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I16 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I17 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | S36 | NEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
28 | S1 | NEF3 | I0>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
28 | S2 | NEF3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
28 | V1 | NEF3 | I0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
28 | I1 | NEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
28 | I2 | NEF3 | I0>>> starts | UINT32 | R | 0...4294967295
28 | I3 | NEF3 | I0>>> trips | UINT32 | R | 0...4294967295
28 | I4 | NEF3 | I0>>> blocks | UINT32 | R | 0...4294967295
28 | S3 | NEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
28 | S4 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S5 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S6 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S7 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S8 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S9 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S10 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S11 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S12 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S13 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S14 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S15 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S16 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S17 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S18 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S19 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S20 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S21 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S22 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S23 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S24 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S25 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S26 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S27 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S28 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S29 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S30 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S31 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S32 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S33 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S34 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S35 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | O1 | NEF3 | I0>>> START | SIGNAL_OUT | RW | 0...4294967295
28 | O2 | NEF3 | I0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
28 | O3 | NEF3 | I0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
28 | I5 | NEF3 | Newest Register | UINT32 | R | 0...12
28 | I6 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I7 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I8 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I9 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I10 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I11 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I12 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I13 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I14 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I15 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I16 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I17 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | S36 | NEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
29 | S1 | NEF4 | I0>>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
29 | S2 | NEF4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
29 | V1 | NEF4 | I0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
29 | I1 | NEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
29 | I2 | NEF4 | I0>>>> starts | UINT32 | R | 0...4294967295
29 | I3 | NEF4 | I0>>>> trips | UINT32 | R | 0...4294967295
29 | I4 | NEF4 | I0>>>> blocks | UINT32 | R | 0...4294967295
29 | S3 | NEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
29 | S4 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S5 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S6 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S7 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S8 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S9 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S10 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S11 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S12 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S13 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S14 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S15 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S16 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S17 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S18 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S19 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S20 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S21 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S22 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S23 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S24 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S25 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S26 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S27 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S28 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S29 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S30 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S31 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S32 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S33 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S34 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S35 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | O1 | NEF4 | I0>>>> START | SIGNAL_OUT | RW | 0...4294967295
29 | O2 | NEF4 | I0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
29 | O3 | NEF4 | I0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
29 | I5 | NEF4 | Newest Register | UINT32 | R | 0...12
29 | I6 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I7 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I8 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I9 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I10 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I11 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I12 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I13 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I14 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I15 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I16 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I17 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | S36 | NEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | S1 | DEF1 | I0dir> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
81 | V1 | DEF1 | I0dir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
81 | I1 | DEF1 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
81 | I2 | DEF1 | I0 Magnitude | FLOAT | R | 0...250
81 | I3 | DEF1 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
81 | I4 | DEF1 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
81 | I5 | DEF1 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
81 | I6 | DEF1 | DEF(1) Measured residual current change | FLOAT | R | 0...250
81 | I7 | DEF1 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
81 | I8 | DEF1 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
81 | I9 | DEF1 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
81 | I10 | DEF1 | I0 meas / I0 set now | FLOAT | R | -250...250
81 | I11 | DEF1 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
81 | I12 | DEF1 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
81 | I13 | DEF1 | U0 meas now | FLOAT | R | 0...500
81 | I14 | DEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
81 | I15 | DEF1 | I0dir> starts | UINT32 | R | 0...4294967295
81 | I16 | DEF1 | I0dir> trips | UINT32 | R | 0...4294967295
81 | I17 | DEF1 | I0dir> blocks | UINT32 | R | 0...4294967295
81 | S2 | DEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
81 | S3 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S4 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S5 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S6 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S7 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S8 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S9 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S10 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S11 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S12 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S13 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S14 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S15 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S16 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S17 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S18 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S19 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S20 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S21 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S22 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S23 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S24 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S25 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S26 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S27 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S28 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S29 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S30 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S31 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S32 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S33 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S34 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S35 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S36 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S37 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S38 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S39 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S40 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S41 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S42 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S43 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S44 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S45 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S46 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S47 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S48 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S49 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S50 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S51 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S52 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S53 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S54 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S55 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S56 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S57 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S58 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S59 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S60 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S61 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S62 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S63 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S64 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S65 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S66 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S67 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S68 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S69 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S70 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S71 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S72 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S73 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S74 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S75 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S76 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S77 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S78 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S79 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S80 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S81 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S82 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S83 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S84 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S85 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S86 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S87 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S88 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S89 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S90 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S91 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S92 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S93 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S94 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S95 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S96 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S97 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S98 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S99 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S100 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S101 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S102 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S103 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S104 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S105 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S106 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S107 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S108 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S109 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S110 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S111 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S112 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S113 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S114 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S115 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S116 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S117 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S118 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S119 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S120 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S121 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S122 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | O1 | DEF1 | I0dir> START (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O2 | DEF1 | I0dir> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O3 | DEF1 | I0dir> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O4 | DEF1 | I0dir> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O5 | DEF1 | I0dir> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O6 | DEF1 | I0dir> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O7 | DEF1 | I0dir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
81 | I18 | DEF1 | Newest Register | UINT32 | R | 0...12
81 | I19 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I20 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I21 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I22 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I23 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I24 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I25 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I26 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I27 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I28 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I29 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I30 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I31 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I32 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I33 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I34 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I35 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I36 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I37 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I38 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I39 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I40 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I41 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I42 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I43 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I44 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I45 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I46 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I47 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I48 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I49 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I50 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I51 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I52 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I53 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I54 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I55 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I56 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I57 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I58 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I59 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I60 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I61 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I62 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I63 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I64 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I65 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I66 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I67 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I68 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I69 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I70 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I71 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I72 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I73 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I74 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I75 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I76 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I77 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I78 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I79 | DEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | I80 | DEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
82 | S1 | DEF2 | I0dir>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
82 | V1 | DEF2 | I0dir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
82 | I1 | DEF2 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
82 | I2 | DEF2 | I0 Magnitude | FLOAT | R | 0...250
82 | I3 | DEF2 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
82 | I4 | DEF2 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
82 | I5 | DEF2 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
82 | I6 | DEF2 | DEF(1) Measured residual current change | FLOAT | R | 0...250
82 | I7 | DEF2 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
82 | I8 | DEF2 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
82 | I9 | DEF2 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
82 | I10 | DEF2 | I0 meas / I0 set now | FLOAT | R | -250...250
82 | I11 | DEF2 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
82 | I12 | DEF2 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
82 | I13 | DEF2 | U0 meas now | FLOAT | R | 0...500
82 | I14 | DEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
82 | I15 | DEF2 | I0dir>> starts | UINT32 | R | 0...4294967295
82 | I16 | DEF2 | I0dir>> trips | UINT32 | R | 0...4294967295
82 | I17 | DEF2 | I0dir>> blocks | UINT32 | R | 0...4294967295
82 | S2 | DEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
82 | S3 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S4 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S5 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S6 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S7 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S8 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S9 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S10 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S11 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S12 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S13 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S14 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S15 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S16 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S17 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S18 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S19 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S20 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S21 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S22 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S23 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S24 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S25 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S26 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S27 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S28 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S29 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S30 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S31 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S32 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S33 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S34 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S35 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S36 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S37 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S38 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S39 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S40 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S41 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S42 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S43 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S44 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S45 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S46 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S47 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S48 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S49 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S50 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S51 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S52 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S53 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S54 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S55 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S56 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S57 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S58 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S59 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S60 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S61 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S62 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S63 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S64 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S65 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S66 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S67 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S68 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S69 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S70 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S71 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S72 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S73 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S74 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S75 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S76 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S77 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S78 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S79 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S80 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S81 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S82 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S83 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S84 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S85 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S86 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S87 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S88 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S89 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S90 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S91 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S92 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S93 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S94 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S95 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S96 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S97 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S98 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S99 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S100 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S101 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S102 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S103 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S104 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S105 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S106 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S107 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S108 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S109 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S110 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S111 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S112 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S113 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S114 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S115 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S116 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S117 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S118 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S119 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S120 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S121 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S122 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | O1 | DEF2 | I0dir>> START (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O2 | DEF2 | I0dir>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O3 | DEF2 | I0dir>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O4 | DEF2 | I0dir>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O5 | DEF2 | I0dir>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O6 | DEF2 | I0dir>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O7 | DEF2 | I0dir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
82 | I18 | DEF2 | Newest Register | UINT32 | R | 0...12
82 | I19 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I20 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I21 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I22 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I23 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I24 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I25 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I26 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I27 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I28 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I29 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I30 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I31 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I32 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I33 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I34 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I35 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I36 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I37 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I38 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I39 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I40 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I41 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I42 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I43 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I44 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I45 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I46 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I47 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I48 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I49 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I50 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I51 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I52 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I53 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I54 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I55 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I56 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I57 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I58 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I59 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I60 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I61 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I62 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I63 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I64 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I65 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I66 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I67 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I68 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I69 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I70 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I71 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I72 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I73 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I74 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I75 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I76 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I77 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I78 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I79 | DEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
82 | I80 | DEF2 | EventMaskHi | UINT32 | RW | 0...4294967295
83 | S1 | DEF3 | I0dir>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
83 | V1 | DEF3 | I0dir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
83 | I1 | DEF3 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
83 | I2 | DEF3 | I0 Magnitude | FLOAT | R | 0...250
83 | I3 | DEF3 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
83 | I4 | DEF3 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
83 | I5 | DEF3 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
83 | I6 | DEF3 | DEF(1) Measured residual current change | FLOAT | R | 0...250
83 | I7 | DEF3 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
83 | I8 | DEF3 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
83 | I9 | DEF3 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
83 | I10 | DEF3 | I0 meas / I0 set now | FLOAT | R | -250...250
83 | I11 | DEF3 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
83 | I12 | DEF3 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
83 | I13 | DEF3 | U0 meas now | FLOAT | R | 0...500
83 | I14 | DEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
83 | I15 | DEF3 | I0dir>>> starts | UINT32 | R | 0...4294967295
83 | I16 | DEF3 | I0dir>>> trips | UINT32 | R | 0...4294967295
83 | I17 | DEF3 | I0dir>>> blocks | UINT32 | R | 0...4294967295
83 | S2 | DEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
83 | S3 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S4 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S5 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S6 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S7 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S8 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S9 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S10 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S11 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S12 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S13 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S14 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S15 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S16 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S17 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S18 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S19 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S20 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S21 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S22 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S23 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S24 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S25 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S26 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S27 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S28 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S29 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S30 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S31 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S32 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S33 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S34 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S35 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S36 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S37 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S38 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S39 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S40 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S41 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S42 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S43 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S44 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S45 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S46 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S47 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S48 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S49 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S50 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S51 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S52 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S53 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S54 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S55 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S56 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S57 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S58 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S59 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S60 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S61 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S62 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S63 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S64 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S65 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S66 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S67 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S68 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S69 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S70 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S71 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S72 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S73 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S74 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S75 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S76 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S77 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S78 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S79 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S80 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S81 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S82 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S83 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S84 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S85 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S86 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S87 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S88 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S89 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S90 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S91 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S92 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S93 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S94 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S95 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S96 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S97 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S98 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S99 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S100 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S101 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S102 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S103 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S104 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S105 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S106 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S107 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S108 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S109 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S110 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S111 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S112 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S113 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S114 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S115 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S116 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S117 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S118 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S119 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S120 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S121 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S122 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | O1 | DEF3 | I0dir>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O2 | DEF3 | I0dir>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O3 | DEF3 | I0dir>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O4 | DEF3 | I0dir>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O5 | DEF3 | I0dir>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O6 | DEF3 | I0dir>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O7 | DEF3 | I0dir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
83 | I18 | DEF3 | Newest Register | UINT32 | R | 0...12
83 | I19 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I20 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I21 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I22 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I23 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I24 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I25 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I26 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I27 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I28 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I29 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I30 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I31 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I32 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I33 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I34 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I35 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I36 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I37 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I38 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I39 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I40 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I41 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I42 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I43 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I44 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I45 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I46 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I47 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I48 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I49 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I50 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I51 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I52 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I53 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I54 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I55 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I56 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I57 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I58 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I59 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I60 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I61 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I62 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I63 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I64 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I65 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I66 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I67 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I68 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I69 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I70 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I71 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I72 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I73 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I74 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I75 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I76 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I77 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I78 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I79 | DEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
83 | I80 | DEF3 | EventMaskHi | UINT32 | RW | 0...4294967295
84 | S1 | DEF4 | I0dir>>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
84 | V1 | DEF4 | I0dir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
84 | I1 | DEF4 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
84 | I2 | DEF4 | I0 Magnitude | FLOAT | R | 0...250
84 | I3 | DEF4 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
84 | I4 | DEF4 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
84 | I5 | DEF4 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
84 | I6 | DEF4 | DEF(1) Measured residual current change | FLOAT | R | 0...250
84 | I7 | DEF4 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
84 | I8 | DEF4 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
84 | I9 | DEF4 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
84 | I10 | DEF4 | I0 meas / I0 set now | FLOAT | R | -250...250
84 | I11 | DEF4 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
84 | I12 | DEF4 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
84 | I13 | DEF4 | U0 meas now | FLOAT | R | 0...500
84 | I14 | DEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
84 | I15 | DEF4 | I0dir>>>> starts | UINT32 | R | 0...4294967295
84 | I16 | DEF4 | I0dir>>>> trips | UINT32 | R | 0...4294967295
84 | I17 | DEF4 | I0dir>>>> blocks | UINT32 | R | 0...4294967295
84 | S2 | DEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
84 | S3 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S4 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S5 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S6 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S7 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S8 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S9 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S10 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S11 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S12 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S13 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S14 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S15 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S16 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S17 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S18 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S19 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S20 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S21 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S22 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S23 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S24 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S25 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S26 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S27 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S28 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S29 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S30 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S31 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S32 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S33 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S34 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S35 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S36 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S37 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S38 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S39 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S40 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S41 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S42 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S43 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S44 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S45 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S46 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S47 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S48 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S49 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S50 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S51 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S52 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S53 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S54 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S55 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S56 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S57 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S58 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S59 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S60 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S61 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S62 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S63 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S64 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S65 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S66 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S67 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S68 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S69 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S70 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S71 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S72 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S73 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S74 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S75 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S76 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S77 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S78 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S79 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S80 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S81 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S82 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S83 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S84 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S85 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S86 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S87 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S88 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S89 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S90 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S91 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S92 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S93 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S94 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S95 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S96 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S97 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S98 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S99 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S100 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S101 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S102 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S103 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S104 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S105 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S106 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S107 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S108 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S109 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S110 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S111 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S112 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S113 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S114 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S115 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S116 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S117 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S118 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S119 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S120 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S121 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S122 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | O1 | DEF4 | I0dir>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O2 | DEF4 | I0dir>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O3 | DEF4 | I0dir>>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O4 | DEF4 | I0dir>>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O5 | DEF4 | I0dir>>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O6 | DEF4 | I0dir>>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O7 | DEF4 | I0dir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
84 | I18 | DEF4 | Newest Register | UINT32 | R | 0...12
84 | I19 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I20 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I21 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I22 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I23 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I24 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I25 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I26 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I27 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I28 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I29 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I30 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I31 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I32 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I33 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I34 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I35 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I36 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I37 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I38 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I39 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I40 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I41 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I42 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I43 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I44 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I45 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I46 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I47 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I48 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I49 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I50 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I51 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I52 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I53 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I54 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I55 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I56 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I57 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I58 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I59 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I60 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I61 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I62 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I63 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I64 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I65 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I66 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I67 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I68 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I69 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I70 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I71 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I72 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I73 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I74 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I75 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I76 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I77 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I78 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I79 | DEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
84 | I80 | DEF4 | EventMaskHi | UINT32 | RW | 0...4294967295
114 | S1 | IEF1 | I0Int> [67NT] mode | UINT32 | RW | 0=Disabled;1=Activated
114 | V1 | IEF1 | I0Int> condition | UINT32 | R | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
114 | I1 | IEF1 | Spikes needed for trip > | UINT32 | R | 0...4294967295
114 | I2 | IEF1 | I0Int> starts FWD | UINT32 | R | 0...4294967295
114 | I3 | IEF1 | I0Int> starts REV | UINT32 | R | 0...4294967295
114 | I4 | IEF1 | I0Int> trips | UINT32 | R | 0...4294967295
114 | I5 | IEF1 | I0Int> blocks | UINT32 | R | 0...4294967295
114 | S2 | IEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
114 | S3 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S4 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S5 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S6 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S7 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S8 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S9 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S10 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S11 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S12 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S13 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S14 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S15 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S16 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S17 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S18 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S19 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S20 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S21 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S22 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S23 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S24 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S25 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S26 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S27 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S28 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S29 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S30 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S31 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S32 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S33 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S34 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S35 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S36 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S37 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S38 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S39 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S40 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S41 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S42 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S43 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S44 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S45 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S46 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S47 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S48 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S49 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S50 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | O1 | IEF1 | I0Int> IEF DETECTED | SIGNAL_OUT | RW | 0...4294967295
114 | O2 | IEF1 | I0Int> STARTFWD | SIGNAL_OUT | RW | 0...4294967295
114 | O3 | IEF1 | I0Int> STARTREV | SIGNAL_OUT | RW | 0...4294967295
114 | O4 | IEF1 | I0Int> TRIP | SIGNAL_OUT | RW | 0...4294967295
114 | O5 | IEF1 | I0Int> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
114 | I6 | IEF1 | Newest Register | UINT32 | R | 0...12
114 | I7 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I8 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I9 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I10 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I11 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I12 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I13 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I14 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I15 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I16 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I17 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I18 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I19 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I20 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I21 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I22 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I23 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I24 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I25 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I26 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I27 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I28 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I29 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I30 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I31 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I32 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I33 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I34 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I35 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I36 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I37 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I38 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I39 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I40 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I41 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I42 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I43 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I44 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I45 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I46 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I47 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I48 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I49 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I50 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I51 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I52 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I53 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I54 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I55 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I56 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I57 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I58 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I59 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I60 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I61 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I62 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I63 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I64 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I65 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I66 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | S51 | IEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
114 | S52 | IEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
32 | S1 | CUB1 | I2> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
32 | V1 | CUB1 | I2> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
32 | I1 | CUB1 | I2> starts | UINT32 | R | 0...4294967295
32 | I2 | CUB1 | I2> trips | UINT32 | R | 0...4294967295
32 | I3 | CUB1 | I2> blocks | UINT32 | R | 0...4294967295
32 | S2 | CUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
32 | I4 | CUB1 | I2> I2I1 relation | FLOAT | R | 0...100000
32 | I5 | CUB1 | I2 meas/I2 set | FLOAT | R | 0...100000
32 | S3 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S4 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S5 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S6 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S7 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S8 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S9 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S10 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S11 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S12 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S13 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S14 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S15 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S16 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S17 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S18 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S19 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S20 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S21 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S22 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S23 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S24 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S25 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S26 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S27 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S28 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S29 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S30 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S31 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S32 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S33 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S34 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | O1 | CUB1 | I2> START | SIGNAL_OUT | RW | 0...4294967295
32 | O2 | CUB1 | I2> TRIP | SIGNAL_OUT | RW | 0...4294967295
32 | O3 | CUB1 | I2> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
32 | I6 | CUB1 | Newest Register | UINT32 | R | 0...12
32 | I7 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I8 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I9 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I10 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I11 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I12 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I13 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I14 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I15 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I16 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I17 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I18 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I19 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I20 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I21 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I22 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I23 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I24 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I25 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I26 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I27 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I28 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I29 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I30 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | S35 | CUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
33 | S1 | CUB2 | I2>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
33 | V1 | CUB2 | I2>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
33 | I1 | CUB2 | I2>> starts | UINT32 | R | 0...4294967295
33 | I2 | CUB2 | I2>> trips | UINT32 | R | 0...4294967295
33 | I3 | CUB2 | I2>> blocks | UINT32 | R | 0...4294967295
33 | S2 | CUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
33 | I4 | CUB2 | I2>> I2I1 relation | FLOAT | R | 0...100000
33 | I5 | CUB2 | I2 meas/I2 set | FLOAT | R | 0...100000
33 | S3 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S4 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S5 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S6 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S7 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S8 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S9 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S10 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S11 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S12 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S13 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S14 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S15 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S16 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S17 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S18 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S19 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S20 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S21 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S22 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S23 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S24 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S25 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S26 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S27 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S28 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S29 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S30 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S31 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S32 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S33 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S34 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | O1 | CUB2 | I2>> START | SIGNAL_OUT | RW | 0...4294967295
33 | O2 | CUB2 | I2>> TRIP | SIGNAL_OUT | RW | 0...4294967295
33 | O3 | CUB2 | I2>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
33 | I6 | CUB2 | Newest Register | UINT32 | R | 0...12
33 | I7 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I8 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I9 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I10 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I11 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I12 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I13 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I14 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I15 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I16 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I17 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I18 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I19 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I20 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I21 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I22 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I23 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I24 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I25 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I26 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I27 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I28 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I29 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I30 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | S35 | CUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
34 | S1 | CUB3 | I2>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
34 | V1 | CUB3 | I2>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
34 | I1 | CUB3 | I2>>> starts | UINT32 | R | 0...4294967295
34 | I2 | CUB3 | I2>>> trips | UINT32 | R | 0...4294967295
34 | I3 | CUB3 | I2>>> blocks | UINT32 | R | 0...4294967295
34 | S2 | CUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
34 | I4 | CUB3 | I2>>> I2I1 relation | FLOAT | R | 0...100000
34 | I5 | CUB3 | I2 meas/I2 set | FLOAT | R | 0...100000
34 | S3 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S4 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S5 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S6 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S7 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S8 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S9 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S10 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S11 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S12 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S13 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S14 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S15 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S16 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S17 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S18 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S19 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S20 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S21 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S22 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S23 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S24 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S25 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S26 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S27 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S28 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S29 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S30 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S31 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S32 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S33 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S34 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | O1 | CUB3 | I2>>> START | SIGNAL_OUT | RW | 0...4294967295
34 | O2 | CUB3 | I2>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
34 | O3 | CUB3 | I2>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
34 | I6 | CUB3 | Newest Register | UINT32 | R | 0...12
34 | I7 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I8 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I9 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I10 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I11 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I12 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I13 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I14 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I15 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I16 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I17 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I18 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I19 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I20 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I21 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I22 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I23 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I24 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I25 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I26 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I27 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I28 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I29 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I30 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | S35 | CUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
35 | S1 | CUB4 | I2>>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
35 | V1 | CUB4 | I2>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
35 | I1 | CUB4 | I2>>>> starts | UINT32 | R | 0...4294967295
35 | I2 | CUB4 | I2>>>> trips | UINT32 | R | 0...4294967295
35 | I3 | CUB4 | I2>>>> blocks | UINT32 | R | 0...4294967295
35 | S2 | CUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
35 | I4 | CUB4 | I2>>>> I2I1 relation | FLOAT | R | 0...100000
35 | I5 | CUB4 | I2 meas/I2 set | FLOAT | R | 0...100000
35 | S3 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S4 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S5 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S6 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S7 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S8 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S9 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S10 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S11 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S12 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S13 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S14 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S15 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S16 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S17 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S18 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S19 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S20 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S21 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S22 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S23 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S24 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S25 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S26 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S27 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S28 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S29 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S30 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S31 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S32 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S33 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S34 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | O1 | CUB4 | I2>>>> START | SIGNAL_OUT | RW | 0...4294967295
35 | O2 | CUB4 | I2>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
35 | O3 | CUB4 | I2>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
35 | I6 | CUB4 | Newest Register | UINT32 | R | 0...12
35 | I7 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I8 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I9 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I10 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I11 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I12 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I13 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I14 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I15 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I16 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I17 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I18 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I19 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I20 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I21 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I22 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I23 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I24 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I25 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I26 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I27 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I28 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I29 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I30 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | S35 | CUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
37 | S1 | HOC1 | Ih> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
37 | V1 | HOC1 | Ih> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
37 | I1 | HOC1 | Ih> starts | UINT32 | R | 0...4294967295
37 | I2 | HOC1 | Ih> trips | UINT32 | R | 0...4294967295
37 | I3 | HOC1 | Ih> blocks | UINT32 | R | 0...4294967295
37 | S2 | HOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
37 | I4 | HOC1 | Ih meas/ Ih set | FLOAT | R | 0...100000
37 | S3 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S4 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S5 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S6 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S7 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S8 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S9 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S10 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S11 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S12 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S13 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S14 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S15 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S16 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S17 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S18 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S19 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S20 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S21 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S22 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S23 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S24 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S25 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S26 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S27 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S28 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S29 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S30 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S31 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S32 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S33 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S34 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | O1 | HOC1 | Ih> START | SIGNAL_OUT | RW | 0...4294967295
37 | O2 | HOC1 | Ih> TRIP | SIGNAL_OUT | RW | 0...4294967295
37 | O3 | HOC1 | Ih> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
37 | I5 | HOC1 | Newest Register | UINT32 | R | 0...12
37 | I6 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I7 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I8 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I9 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I10 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I11 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I12 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I13 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I14 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I15 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I16 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I17 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I18 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I19 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I20 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I21 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I22 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I23 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I24 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I25 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I26 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I27 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I28 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I29 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I30 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I31 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I32 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I33 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I34 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I35 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I36 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I37 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I38 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I39 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I40 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I41 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I42 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I43 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I44 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I45 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I46 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I47 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I48 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I49 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I50 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I51 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I52 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I53 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I54 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I55 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I56 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I57 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I58 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I59 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I60 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I61 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I62 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I63 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I64 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I65 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | S35 | HOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
38 | S1 | HOC2 | Ih>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
38 | V1 | HOC2 | Ih>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
38 | I1 | HOC2 | Ih>> starts | UINT32 | R | 0...4294967295
38 | I2 | HOC2 | Ih>> trips | UINT32 | R | 0...4294967295
38 | I3 | HOC2 | Ih>> blocks | UINT32 | R | 0...4294967295
38 | S2 | HOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
38 | I4 | HOC2 | Ih meas/ Ih set | FLOAT | R | 0...100000
38 | S3 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S4 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S5 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S6 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S7 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S8 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S9 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S10 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S11 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S12 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S13 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S14 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S15 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S16 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S17 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S18 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S19 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S20 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S21 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S22 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S23 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S24 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S25 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S26 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S27 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S28 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S29 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S30 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S31 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S32 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S33 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S34 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | O1 | HOC2 | Ih>> START | SIGNAL_OUT | RW | 0...4294967295
38 | O2 | HOC2 | Ih>> TRIP | SIGNAL_OUT | RW | 0...4294967295
38 | O3 | HOC2 | Ih>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
38 | I5 | HOC2 | Newest Register | UINT32 | R | 0...12
38 | I6 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I7 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I8 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I9 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I10 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I11 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I12 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I13 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I14 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I15 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I16 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I17 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I18 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I19 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I20 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I21 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I22 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I23 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I24 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I25 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I26 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I27 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I28 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I29 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I30 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I31 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I32 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I33 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I34 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I35 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I36 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I37 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I38 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I39 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I40 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I41 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I42 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I43 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I44 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I45 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I46 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I47 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I48 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I49 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I50 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I51 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I52 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I53 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I54 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I55 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I56 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I57 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I58 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I59 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I60 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I61 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I62 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I63 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I64 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I65 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | S35 | HOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
39 | S1 | HOC3 | Ih>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
39 | V1 | HOC3 | Ih>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
39 | I1 | HOC3 | Ih>>> starts | UINT32 | R | 0...4294967295
39 | I2 | HOC3 | Ih>>> trips | UINT32 | R | 0...4294967295
39 | I3 | HOC3 | Ih>>> blocks | UINT32 | R | 0...4294967295
39 | S2 | HOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
39 | I4 | HOC3 | Ih meas/ Ih set | FLOAT | R | 0...100000
39 | S3 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S4 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S5 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S6 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S7 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S8 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S9 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S10 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S11 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S12 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S13 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S14 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S15 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S16 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S17 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S18 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S19 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S20 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S21 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S22 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S23 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S24 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S25 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S26 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S27 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S28 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S29 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S30 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S31 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S32 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S33 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S34 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | O1 | HOC3 | Ih>>> START | SIGNAL_OUT | RW | 0...4294967295
39 | O2 | HOC3 | Ih>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
39 | O3 | HOC3 | Ih>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
39 | I5 | HOC3 | Newest Register | UINT32 | R | 0...12
39 | I6 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I7 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I8 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I9 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I10 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I11 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I12 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I13 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I14 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I15 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I16 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I17 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I18 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I19 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I20 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I21 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I22 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I23 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I24 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I25 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I26 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I27 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I28 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I29 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I30 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I31 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I32 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I33 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I34 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I35 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I36 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I37 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I38 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I39 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I40 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I41 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I42 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I43 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I44 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I45 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I46 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I47 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I48 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I49 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I50 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I51 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I52 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I53 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I54 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I55 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I56 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I57 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I58 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I59 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I60 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I61 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I62 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I63 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I64 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I65 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | S35 | HOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
40 | S1 | HOC4 | Ih>>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
40 | V1 | HOC4 | Ih>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
40 | I1 | HOC4 | Ih>>>> starts | UINT32 | R | 0...4294967295
40 | I2 | HOC4 | Ih>>>> trips | UINT32 | R | 0...4294967295
40 | I3 | HOC4 | Ih>>>> blocks | UINT32 | R | 0...4294967295
40 | S2 | HOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
40 | I4 | HOC4 | Ih meas/ Ih set | FLOAT | R | 0...100000
40 | S3 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S4 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S5 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S6 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S7 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S8 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S9 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S10 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S11 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S12 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S13 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S14 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S15 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S16 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S17 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S18 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S19 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S20 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S21 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S22 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S23 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S24 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S25 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S26 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S27 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S28 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S29 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S30 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S31 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S32 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S33 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S34 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | O1 | HOC4 | Ih>>>> START | SIGNAL_OUT | RW | 0...4294967295
40 | O2 | HOC4 | Ih>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
40 | O3 | HOC4 | Ih>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
40 | I5 | HOC4 | Newest Register | UINT32 | R | 0...12
40 | I6 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I7 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I8 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I9 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I10 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I11 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I12 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I13 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I14 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I15 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I16 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I17 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I18 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I19 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I20 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I21 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I22 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I23 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I24 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I25 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I26 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I27 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I28 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I29 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I30 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I31 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I32 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I33 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I34 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I35 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I36 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I37 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I38 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I39 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I40 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I41 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I42 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I43 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I44 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I45 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I46 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I47 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I48 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I49 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I50 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I51 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I52 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I53 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I54 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I55 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I56 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I57 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I58 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I59 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I60 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I61 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I62 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I63 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I64 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I65 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | S35 | HOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
42 | S1 | CLP1 | CLP mode | UINT32 | RW | 0=Disabled;1=Activated
42 | V1 | CLP1 | CLP condition | UINT32 | R | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
42 | I1 | CLP1 | CLP starts | UINT32 | R | 0...4294967295
42 | I2 | CLP1 | CLP blocks | UINT32 | R | 0...4294967295
42 | S2 | CLP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
42 | S3 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S4 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S5 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S6 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S7 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S8 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S9 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S10 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S11 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S12 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S13 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S14 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S15 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S16 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S17 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S18 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S19 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S20 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S21 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S22 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S23 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S24 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S25 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S26 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S27 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S28 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S29 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S30 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S31 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S32 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S33 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S34 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S35 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S36 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S37 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S38 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S39 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S40 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S41 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S42 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S43 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S44 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S45 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S46 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S47 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S48 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S49 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S50 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | O1 | CLP1 | CLPU ACT | SIGNAL_OUT | RW | 0...4294967295
42 | O2 | CLP1 | CLPU BLOCKED | SIGNAL_OUT | RW | 0...4294967295
42 | I3 | CLP1 | Newest Register | UINT32 | R | 0...12
42 | I4 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I5 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I6 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I7 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I8 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I9 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I10 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I11 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I12 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I13 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I14 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I15 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I16 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I17 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I18 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I19 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I20 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I21 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I22 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I23 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I24 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I25 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I26 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I27 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I28 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I29 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I30 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I31 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I32 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I33 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I34 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I35 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I36 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I37 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I38 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I39 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | S51 | CLP1 | EventMaskLo | UINT32 | RW | 0...4294967295
44 | S1 | CBF1 | CBFP [50BF] mode | UINT32 | RW | 0=Disabled;1=Activated
44 | V1 | CBF1 | CBFP condition | UINT32 | R | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
44 | I1 | CBF1 | Retrips | UINT32 | R | 0...4294967295
44 | I2 | CBF1 | CBFPs | UINT32 | R | 0...4294967295
44 | I3 | CBF1 | CBFP starts | UINT32 | R | 0...4294967295
44 | I4 | CBF1 | CBFP blocks | UINT32 | R | 0...4294967295
44 | S2 | CBF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
44 | S3 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S4 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S5 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S6 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S7 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S8 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S9 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S10 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S11 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S12 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S13 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S14 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S15 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S16 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S17 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S18 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S19 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S20 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S21 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S22 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S23 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S24 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S25 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S26 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S27 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S28 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S29 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S30 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S31 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S32 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S33 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S34 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S35 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S36 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S37 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S38 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S39 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S40 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S41 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S42 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S43 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S44 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S45 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S46 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S47 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S48 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S49 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S50 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S51 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S52 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S53 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S54 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S55 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S56 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S57 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S58 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | O1 | CBF1 | CBFP START | SIGNAL_OUT | RW | 0...4294967295
44 | O2 | CBF1 | CBFP RETRIP | SIGNAL_OUT | RW | 0...4294967295
44 | O3 | CBF1 | CBFP ACT | SIGNAL_OUT | RW | 0...4294967295
44 | O4 | CBF1 | CBFP BLOCKED | SIGNAL_OUT | RW | 0...4294967295
44 | I5 | CBF1 | Newest Register | UINT32 | R | 0...12
44 | I6 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I7 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I8 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I9 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I10 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I11 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I12 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I13 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I14 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I15 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I16 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I17 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I18 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I19 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I20 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I21 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I22 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I23 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I24 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I25 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I26 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I27 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I28 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I29 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I30 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I31 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I32 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I33 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I34 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I35 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I36 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I37 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I38 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I39 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I40 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I41 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I42 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I43 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I44 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I45 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I46 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I47 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I48 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I49 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I50 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I51 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I52 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I53 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | S59 | CBF1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S1 | MST1 | MST mode | UINT32 | R | 0=Disabled; 1=Activated
62 | V1 | MST1 | Motor is now | UINT32 | R | 0=Stopped;1=Starting;2=Running;3=Stalled
62 | I1 | MST1 | Times motor started | UINT32 | R | 0...4294967295
62 | I2 | MST1 | Times motor starts succeed | UINT32 | R | 0...4294967295
62 | I3 | MST1 | Times motor stopped | UINT32 | R | 0...4294967295
62 | S2 | MST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
62 | I4 | MST1 | Run after last start | UINT32 | R | 0...4294967295
62 | I5 | MST1 | Total motor run time | UINT32 | R | 0...4294967295
62 | I6 | MST1 | Last start duration | UINT32 | R | 0...4294967295
62 | I7 | MST1 | Total starting time | UINT32 | R | 0...4294967295
62 | I8 | MST1 | Last stopped duration | UINT32 | R | 0...4294967295
62 | I9 | MST1 | Total stopped time | UINT32 | R | 0...4294967295
62 | S3 | MST1 | Clear total times | UINT32 | W | 0=-;1=Clear
62 | S4 | MST1 | Per unitize relay currents to Motor In | UINT32 | RW | 0=No, use CT nominal as pu.;1=Yes, scale all to Imot
62 | S5 | MST1 | Motor nominal current | FLOAT | RW | 0.1...10000
62 | S6 | MST1 | Nominal Starting current | FLOAT | RW | 0.1...40
62 | S7 | MST1 | Start detect current | FLOAT | RW | 0.1...40
62 | S8 | MST1 | Min locked rotor current | FLOAT | RW | 0.1...40
62 | S9 | MST1 | Max locked rotor current | FLOAT | RW | 0.1...40
62 | S10 | MST1 | Maximum overload current | FLOAT | RW | 0.1...40
62 | S11 | MST1 | No Load current | FLOAT | RW | 0.1...40
62 | S12 | MST1 | Motor service factor | FLOAT | RW | 0.01...5
62 | S13 | MST1 | Hot condition theta limit | FLOAT | RW | 0...100
62 | S14 | MST1 | Safe stall time cold | FLOAT | RW | 0.1...600
62 | S15 | MST1 | Safe stall time hot | FLOAT | RW | 0.1...600
62 | S16 | MST1 | Allowed Starts when cold | UINT32 | RW | 1...100
62 | S17 | MST1 | Allowed Starts when hot | UINT32 | RW | 1...100
62 | S18 | MST1 | Given Hot/Cold starts in time of: | FLOAT | RW | 0.01...1800
62 | S19 | MST1 | Min time betw. starts | FLOAT | RW | 0...3600
62 | S20 | MST1 | Overall differential protection | UINT32 | RW | 0=Machine diff. (Yy);1=Diff.with trafo(Xx)
62 | O1 | MST1 | Motor stopped | SIGNAL_OUT | RW | 0...4294967295
62 | O2 | MST1 | Motor starting | SIGNAL_OUT | RW | 0...4294967295
62 | O3 | MST1 | Motor running | SIGNAL_OUT | RW | 0...4294967295
62 | O4 | MST1 | Motor stalled | SIGNAL_OUT | RW | 0...4294967295
62 | O5 | MST1 | Missing phase | SIGNAL_OUT | RW | 0...4294967295
62 | O6 | MST1 | Load Normal | SIGNAL_OUT | RW | 0...4294967295
62 | O7 | MST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
62 | O8 | MST1 | High overcurrent | SIGNAL_OUT | RW | 0...4294967295
62 | I10 | MST1 | Newest Register | UINT32 | R | 0...12
62 | I11 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I12 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I13 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I14 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I15 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I16 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I17 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I18 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I19 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I20 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I21 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I22 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I23 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I24 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I25 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I26 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I27 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I28 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I29 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I30 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I31 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I32 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I33 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I34 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I35 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I36 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I37 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I38 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I39 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I40 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I41 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I42 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I43 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I44 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I45 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I46 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I47 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I48 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I49 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I50 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I51 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I52 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I53 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I54 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I55 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I56 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I57 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I58 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I59 | MST1 | Motor load | FLOAT | R | 0...250
62 | I60 | MST1 | Motor load | FLOAT | R | 0...250
62 | I61 | MST1 | Motor load | FLOAT | R | 0...250
62 | I62 | MST1 | Motor load | FLOAT | R | 0...250
62 | I63 | MST1 | Motor load | FLOAT | R | 0...250
62 | I64 | MST1 | Motor load | FLOAT | R | 0...250
62 | I65 | MST1 | Motor load | FLOAT | R | 0...250
62 | I66 | MST1 | Motor load | FLOAT | R | 0...250
62 | I67 | MST1 | Motor load | FLOAT | R | 0...250
62 | I68 | MST1 | Motor load | FLOAT | R | 0...250
62 | I69 | MST1 | Motor load | FLOAT | R | 0...250
62 | I70 | MST1 | Motor load | FLOAT | R | 0...250
62 | S21 | MST1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S22 | MST1 | EventMaskHi | UINT32 | RW | 0...4294967295
72 | V1 | TRF1 | Transformer is now | UINT32 | R | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
72 | I1 | TRF1 | Times Overloaded | UINT32 | R | 0...4294967295
72 | I2 | TRF1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
72 | S1 | TRF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
72 | I3 | TRF1 | Normal loading | UINT32 | R | 0...4294967295
72 | I4 | TRF1 | Overloading cumulative | UINT32 | R | 0...4294967295
72 | I5 | TRF1 | Last overload duration | UINT32 | R | 0...4294967295
72 | I6 | TRF1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
72 | I7 | TRF1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
72 | S2 | TRF1 | Clear total times | UINT32 | W | 0=-;1=Clear
72 | S3 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.1...500
72 | S4 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...500
72 | S5 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...500
72 | S6 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S7 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | V2 | TRF1 | Bias selection | UINT32 | R | 0=Selection Ok;1=Selection different
72 | V3 | TRF1 | Pick-up setting | UINT32 | R | 0=not checked;1=Setting seems ok;2=Sensitive ok;3=Too sensitive;4=False trip likely;5=Coarse ok;6=Insensitive;7=Dangerously high
72 | V4 | TRF1 | Turnpoint1 setting | UINT32 | R | 0=not checked;1=Ok;2=Seems average;3=Is sensitive;4=Ok;5=Is conservative;6=Is sensitive;7=Ok;8=Is average;9=Is conservative;10=Ok;11=Too conservative;12=Too sensitive
72 | V5 | TRF1 | Slope1 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V6 | TRF1 | Turnpoint2 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V7 | TRF1 | Slope2 setting | UINT32 | R | 0=not checked;1=Ok;2=Wrong;
72 | O1 | TRF1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
72 | O2 | TRF1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O3 | TRF1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O4 | TRF1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
72 | O5 | TRF1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | O6 | TRF1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | I8 | TRF1 | Newest Register | UINT32 | R | 0...12
72 | I9 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I10 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I11 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I12 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I13 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I14 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I15 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I16 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I17 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I18 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I19 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I20 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I21 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I22 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I23 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I24 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I25 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I26 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I27 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I28 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I29 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I30 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I31 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I32 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I33 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I34 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I35 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I36 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I37 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I38 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I39 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I40 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I41 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I42 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I43 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I44 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I45 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I46 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I47 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I48 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I49 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I50 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I51 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I52 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I53 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I54 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I55 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I56 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I57 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I58 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I59 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I60 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I61 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I62 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I63 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I64 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I65 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I66 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I67 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I68 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I69 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I70 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I71 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I72 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I73 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I74 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I75 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I76 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I77 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I78 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I79 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I80 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | S8 | TRF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S1 | DIF1 | Idx> [87T/87N] mode | UINT32 | RW | 0=Disabled;1=Activated
71 | V1 | DIF1 | Idx> condition | UINT32 | R | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On
71 | V2 | DIF1 | REFHV> condition | UINT32 | R | 0b=HV REF Blocked;1b=HV REF Trip
71 | V3 | DIF1 | REFLV> condition | UINT32 | R | 0b=LV REF Blocked;1b=LV REF Trip
71 | I1 | DIF1 | Idb> trips | UINT32 | R | 0...4294967295
71 | I2 | DIF1 | Idb> f2h blocks | UINT32 | R | 0...4294967295
71 | I3 | DIF1 | Idb> f5h blocks | UINT32 | R | 0...4294967295
71 | I4 | DIF1 | Idb> Ext blocks | UINT32 | R | 0...4294967295
71 | I5 | DIF1 | Idi> trips | UINT32 | R | 0...4294967295
71 | I6 | DIF1 | Idi> Ext blocks | UINT32 | R | 0...4294967295
71 | I7 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I8 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | I9 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I10 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | S2 | DIF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
71 | I11 | DIF1 | L1 Bias current | FLOAT | R | 0...50
71 | I12 | DIF1 | L1 Diff current | FLOAT | R | 0...4000
71 | I13 | DIF1 | L1 Char current | FLOAT | R | 0...4000
71 | I14 | DIF1 | L2 Bias current | FLOAT | R | 0...50
71 | I15 | DIF1 | L2 Diff current | FLOAT | R | 0...4000
71 | I16 | DIF1 | L2 Char current | FLOAT | R | 0...4000
71 | I17 | DIF1 | L3 Bias current | FLOAT | R | 0...50
71 | I18 | DIF1 | L3 Diff current | FLOAT | R | 0...4000
71 | I19 | DIF1 | L3 Char current | FLOAT | R | 0...4000
71 | I20 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...50
71 | I21 | DIF1 | HV I0d> Diff current | FLOAT | R | 0...4000
71 | I22 | DIF1 | HV I0d> Char current | FLOAT | R | 0...4000
71 | I23 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...50
71 | I24 | DIF1 | LV I0d> Diff current | FLOAT | R | 0...4000
71 | I25 | DIF1 | LV I0d> Char current | FLOAT | R | 0...4000
71 | S3 | DIF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
71 | V4 | DIF1 | L1 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V5 | DIF1 | L2 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V6 | DIF1 | L3 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | I26 | DIF1 | L1 Mag. diff. | FLOAT | R | 0...50
71 | I27 | DIF1 | L1 Ang. diff. | FLOAT | R | -360...360
71 | I28 | DIF1 | L2 Mag. diff. | FLOAT | R | 0...50
71 | I29 | DIF1 | L2 Ang. diff. | FLOAT | R | -360...360
71 | I30 | DIF1 | L3 Mag. diff. | FLOAT | R | 0...50
71 | I31 | DIF1 | L3 Ang. diff. | FLOAT | R | -360...360
71 | S4 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S5 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S6 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S7 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S8 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S9 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S10 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S11 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S12 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S13 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S14 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S15 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S16 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S17 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S18 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S19 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S20 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S21 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S22 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S23 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S24 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S25 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S26 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S27 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S28 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S29 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S30 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S31 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S32 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S33 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S34 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S35 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S36 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S37 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S38 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S39 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S40 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S41 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S42 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S43 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S44 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S45 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S46 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S47 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S48 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S49 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S50 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S51 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S52 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S53 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S54 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S55 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S56 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S57 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S58 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S59 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S60 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S61 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S62 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S63 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S64 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S65 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S66 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S67 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S68 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S69 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S70 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S71 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S72 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S73 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S74 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S75 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S76 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S77 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S78 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S79 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S80 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S81 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S82 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S83 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S84 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S85 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S86 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S87 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S88 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S89 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S90 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S91 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S92 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S93 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S94 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S95 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S96 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S97 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S98 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S99 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S100 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S101 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S102 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S103 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S104 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S105 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S106 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S107 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S108 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S109 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S110 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S111 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S112 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S113 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S114 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S115 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S116 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S117 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S118 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S119 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S120 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S121 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S122 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S123 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S124 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S125 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S126 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S127 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S128 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S129 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S130 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S131 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S132 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S133 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S134 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S135 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S136 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S137 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S138 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S139 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S140 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S141 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S142 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S143 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S144 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S145 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S146 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S147 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S148 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S149 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S150 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S151 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S152 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S153 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S154 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S155 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S156 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S157 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S158 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S159 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S160 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S161 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S162 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S163 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S164 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S165 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S166 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S167 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S168 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S169 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S170 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S171 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S172 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S173 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S174 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S175 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S176 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S177 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S178 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S179 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S180 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S181 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S182 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S183 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S184 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S185 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S186 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S187 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S188 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S189 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S190 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S191 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S192 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S193 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S194 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S195 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S196 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S197 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S198 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S199 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S200 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S201 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S202 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S203 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S204 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S205 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S206 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S207 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S208 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S209 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S210 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S211 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | O1 | DIF1 | Idb> BIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O2 | DIF1 | Idb> BIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O3 | DIF1 | Idi> NOBIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O4 | DIF1 | Idi> NOBIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O5 | DIF1 | Id> 2nd harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O6 | DIF1 | Id> 5th harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O7 | DIF1 | HV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O8 | DIF1 | HV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O9 | DIF1 | LV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O10 | DIF1 | LV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | I32 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I33 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I34 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I35 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I36 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I37 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I38 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I39 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I40 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I41 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I42 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I43 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I44 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I45 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I46 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I47 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I48 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I49 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I50 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I51 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I52 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I53 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I54 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I55 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I56 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I57 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I58 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I59 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I60 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I61 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I62 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I63 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I64 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I65 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I66 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I67 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I68 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I69 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I70 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I71 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I72 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I73 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I74 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I75 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I76 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I77 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I78 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I79 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I80 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I81 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I82 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I83 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I84 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I85 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I86 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I87 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I88 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I89 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I90 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I91 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I92 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I93 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I94 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I95 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I96 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I97 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I98 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I99 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I100 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I101 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I102 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I103 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I104 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I105 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I106 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I107 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I108 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I109 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I110 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I111 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I112 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I113 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I114 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I115 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I116 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I117 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I118 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I119 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I120 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I121 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I122 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I123 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I124 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I125 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I126 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I127 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I128 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I129 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I130 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I131 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I132 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I133 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I134 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I135 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I136 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I137 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I138 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I139 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I140 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | V7 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V8 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V9 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V10 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V11 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V12 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V13 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V14 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V15 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V16 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V17 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V18 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | I141 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I142 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I143 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I144 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I145 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I146 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I147 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I148 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I149 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I150 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I151 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I152 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I153 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I154 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I155 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I156 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I157 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I158 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I159 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I160 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I161 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I162 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I163 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I164 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I165 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I166 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I167 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I168 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I169 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I170 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I171 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I172 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I173 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I174 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I175 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I176 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I177 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I178 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I179 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I180 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I181 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I182 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I183 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I184 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I185 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I186 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I187 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I188 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I189 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I190 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I191 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I192 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I193 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I194 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I195 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I196 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I197 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I198 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I199 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I200 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I201 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I202 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I203 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I204 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I205 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I206 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I207 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I208 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I209 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I210 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I211 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I212 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I213 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I214 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | S212 | DIF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S213 | DIF1 | EventMaskHi | UINT32 | RW | 0...4294967295
66 | S1 | REF1 | I0d> [87N] mode | UINT32 | RW | 0=Disabled;1=Activated
66 | V1 | REF1 | I0d> condition | UINT32 | R | 0=Normal;1=Trip;2=Blocked
66 | S2 | REF1 | Select | UINT32 | RW | 0=Primary A;1=Secondary A;2=Per Unit
66 | S3 | REF1 | Select | UINT32 | RW | 0=REF Curr
66 | I1 | REF1 | I0d> Bias current | FLOAT | R | 0...50
66 | I2 | REF1 | I0d> Diff current | FLOAT | R | 0...50
66 | I3 | REF1 | I0d> Char current | FLOAT | R | 0...50
66 | I4 | REF1 | Calculated I0 (I0Calc) | FLOAT | R | 0...50
66 | I5 | REF1 | Measured I0 (3I0) | FLOAT | R | 0...50
66 | S4 | REF1 | REF or Cable end Diff | UINT32 | RW | 0=REF;1=CED
66 | S5 | REF1 | Comp. natural unbal. | UINT32 | RW | 0=-;1=Comp
66 | I6 | REF1 | Natural unbalance | FLOAT | R | 0...50
66 | I7 | REF1 | Natural unbalance ang | FLOAT | R | -360...360
66 | I8 | REF1 | Current for CED | FLOAT | R | 0...50
66 | I9 | REF1 | Angle for CED | FLOAT | R | -360...360
66 | S6 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S7 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S8 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S9 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S10 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S11 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S12 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S13 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S14 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S15 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S16 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S17 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S18 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S19 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S20 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S21 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S22 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S23 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S24 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S25 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S26 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S27 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S28 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S29 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S30 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S31 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S32 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S33 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S34 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S35 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S36 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S37 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S38 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S39 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S40 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S41 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S42 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S43 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S44 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S45 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S46 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S47 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S48 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S49 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S50 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S51 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S52 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S53 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S54 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S55 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S56 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S57 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S58 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S59 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S60 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S61 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S62 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S63 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S64 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S65 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S66 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S67 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S68 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S69 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S70 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S71 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S72 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S73 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S74 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S75 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S76 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S77 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | O1 | REF1 | I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
66 | O2 | REF1 | I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
66 | I10 | REF1 | Newest Register | UINT32 | R | 0...12
66 | I11 | REF1 | Bias current | FLOAT | R | 0...250
66 | I12 | REF1 | Bias current | FLOAT | R | 0...250
66 | I13 | REF1 | Bias current | FLOAT | R | 0...250
66 | I14 | REF1 | Bias current | FLOAT | R | 0...250
66 | I15 | REF1 | Bias current | FLOAT | R | 0...250
66 | I16 | REF1 | Bias current | FLOAT | R | 0...250
66 | I17 | REF1 | Bias current | FLOAT | R | 0...250
66 | I18 | REF1 | Bias current | FLOAT | R | 0...250
66 | I19 | REF1 | Bias current | FLOAT | R | 0...250
66 | I20 | REF1 | Bias current | FLOAT | R | 0...250
66 | I21 | REF1 | Bias current | FLOAT | R | 0...250
66 | I22 | REF1 | Bias current | FLOAT | R | 0...250
66 | I23 | REF1 | Differential current | FLOAT | R | 0...250
66 | I24 | REF1 | Differential current | FLOAT | R | 0...250
66 | I25 | REF1 | Differential current | FLOAT | R | 0...250
66 | I26 | REF1 | Differential current | FLOAT | R | 0...250
66 | I27 | REF1 | Differential current | FLOAT | R | 0...250
66 | I28 | REF1 | Differential current | FLOAT | R | 0...250
66 | I29 | REF1 | Differential current | FLOAT | R | 0...250
66 | I30 | REF1 | Differential current | FLOAT | R | 0...250
66 | I31 | REF1 | Differential current | FLOAT | R | 0...250
66 | I32 | REF1 | Differential current | FLOAT | R | 0...250
66 | I33 | REF1 | Differential current | FLOAT | R | 0...250
66 | I34 | REF1 | Differential current | FLOAT | R | 0...250
66 | I35 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I36 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I37 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I38 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I39 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I40 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I41 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I42 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I43 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I44 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I45 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I46 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | S78 | REF1 | EventMaskLo | UINT32 | RW | 0...4294967295
66 | S79 | REF1 | EventMaskHi | UINT32 | RW | 0...4294967295
73 | S1 | TOLT1 | TT> [49T] mode | UINT32 | RW | 0=Disabled;1=Activated
73 | V1 | TOLT1 | TT> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
73 | V2 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
73 | V3 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
73 | V4 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
73 | V5 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
73 | V6 | TOLT1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
73 | I1 | TOLT1 | IN thermal cap current | FLOAT | RW | 0...40
73 | I2 | TOLT1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
73 | S2 | TOLT1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
73 | S3 | TOLT1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
73 | I3 | TOLT1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
73 | I4 | TOLT1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
73 | S4 | TOLT1 | tau1 (t const heating) | FLOAT | RW | 0...500
73 | S5 | TOLT1 | tau2 (t const cooling) | FLOAT | RW | 0...500
73 | S6 | TOLT1 | kSF (service factor) | FLOAT | RW | 0.01...5
73 | S7 | TOLT1 | Cold Reset default theta | FLOAT | RW | 0...150
73 | V7 | TOLT1 | TT> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
73 | I5 | TOLT1 | TT> Time to 100% Theta | UINT32 | R | 0...4294967295
73 | I6 | TOLT1 | TT> Reference T curr. | FLOAT | R | 0...50
73 | I7 | TOLT1 | TT> Active meas curr. | FLOAT | R | 0...50
73 | I8 | TOLT1 | TT> T est.with act. curr. | FLOAT | R | 0...500
73 | I9 | TOLT1 | TT> T at the moment | FLOAT | R | 0...500
73 | I10 | TOLT1 | TT> Max.Temp.Rise All. | FLOAT | R | 0...250
73 | I11 | TOLT1 | TT> Temp.Rise atm. | FLOAT | R | 0...250
73 | I12 | TOLT1 | TT> Hot Spot estimate | FLOAT | R | 0...250
73 | I13 | TOLT1 | TT> Hot Spot Max. All | FLOAT | R | 0...250
73 | I14 | TOLT1 | TT> Used k for amb. temp | FLOAT | R | 0...3
73 | I15 | TOLT1 | TT> Trip delay remaining | UINT32 | R | 0...4294967295
73 | I16 | TOLT1 | TT> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
73 | I17 | TOLT1 | TT> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
73 | I18 | TOLT1 | TT> Inhibit time to rel. | UINT32 | R | 0...4294967295
73 | I19 | TOLT1 | TT> Trip time to rel. | UINT32 | R | 0...4294967295
73 | I20 | TOLT1 | TT> Thermal cap used | FLOAT | R | 0...500
73 | I21 | TOLT1 | Alarm1 inits | UINT32 | R | 0...4294967295
73 | I22 | TOLT1 | Alarm2 inits | UINT32 | R | 0...4294967295
73 | I23 | TOLT1 | Restart Inhibits | UINT32 | R | 0...4294967295
73 | I24 | TOLT1 | Trips | UINT32 | R | 0...4294967295
73 | I25 | TOLT1 | Trips Blocked | UINT32 | R | 0...4294967295
73 | S8 | TOLT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
73 | S9 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S10 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S11 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S12 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S13 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S14 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S15 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S16 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S17 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S18 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S19 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S20 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S21 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S22 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S23 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S24 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S25 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S26 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S27 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S28 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S29 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S30 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S31 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S32 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S33 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S34 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S35 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S36 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S37 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S38 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S39 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S40 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S41 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S42 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S43 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S44 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S45 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S46 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S47 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S48 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S49 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S50 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S51 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S52 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S53 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S54 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S55 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S56 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S57 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S58 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S59 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S60 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S61 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S62 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S63 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S64 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S65 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S66 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S67 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S68 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S69 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S70 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S71 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S72 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | O1 | TOLT1 | TT> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
73 | O2 | TOLT1 | TT> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
73 | O3 | TOLT1 | TT> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
73 | O4 | TOLT1 | TT> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
73 | O5 | TOLT1 | TT> Trip | SIGNAL_OUT | RW | 0...4294967295
73 | I26 | TOLT1 | Newest Register | UINT32 | R | 0...12
73 | I27 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I28 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I29 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I30 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I31 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I32 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I33 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I34 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I35 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I36 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I37 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I38 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I39 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I40 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I41 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I42 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I43 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I44 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I45 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I46 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I47 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I48 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I49 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I50 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I51 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I52 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I53 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I54 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I55 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I56 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I57 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I58 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I59 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I60 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I61 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I62 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | S73 | TOLT1 | EventMaskLo | UINT32 | RW | 0...4294967295
73 | S74 | TOLT1 | EventMaskHi | UINT32 | RW | 0...4294967295
67 | S1 | TOLF1 | TF> [49F] mode | UINT32 | RW | 0=Disabled;1=Activated
67 | V1 | TOLF1 | TF> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
67 | V2 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
67 | V3 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
67 | V4 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
67 | V5 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
67 | V6 | TOLF1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
67 | I1 | TOLF1 | IN thermal cap current | FLOAT | RW | 0...40
67 | I2 | TOLF1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
67 | I3 | TOLF1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
67 | I4 | TOLF1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
67 | I5 | TOLF1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
67 | I6 | TOLF1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
67 | S2 | TOLF1 | tau (t const) | FLOAT | RW | 0...500
67 | S3 | TOLF1 | Nominal current | FLOAT | RW | 1...9999999
67 | S4 | TOLF1 | kSF (service factor) | FLOAT | RW | 0.01...5
67 | I7 | TOLF1 | TF> Time to 100% Theta | UINT32 | R | 0...4294967295
67 | I8 | TOLF1 | TF> Reference T curr. | FLOAT | R | 0...50
67 | I9 | TOLF1 | TF> Active meas curr. | FLOAT | R | 0...50
67 | I10 | TOLF1 | TF> T est.with act. curr. | FLOAT | R | 0...500
67 | I11 | TOLF1 | TF> T at the moment | FLOAT | R | 0...500
67 | I12 | TOLF1 | TF> Max.Temp.Rise All. | FLOAT | R | 0...250
67 | I13 | TOLF1 | TF> Temp.Rise atm. | FLOAT | R | 0...250
67 | I14 | TOLF1 | TF> Hot Spot estimate | FLOAT | R | 0...250
67 | I15 | TOLF1 | TF> Hot Spot Max. All | FLOAT | R | 0...250
67 | I16 | TOLF1 | TF> Used k for amb. temp | FLOAT | R | 0...3
67 | I17 | TOLF1 | TF> Trip delay remaining | UINT32 | R | 0...4294967295
67 | I18 | TOLF1 | TF> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
67 | I19 | TOLF1 | TF> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
67 | I20 | TOLF1 | TF> Inhibit time to rel. | UINT32 | R | 0...4294967295
67 | I21 | TOLF1 | TF> Trip time to rel. | UINT32 | R | 0...4294967295
67 | I22 | TOLF1 | TF> Thermal cap used | FLOAT | R | 0...500
67 | I23 | TOLF1 | Alarm1 inits | UINT32 | R | 0...4294967295
67 | I24 | TOLF1 | Alarm2 inits | UINT32 | R | 0...4294967295
67 | I25 | TOLF1 | Restart Inhibits | UINT32 | R | 0...4294967295
67 | I26 | TOLF1 | Trips | UINT32 | R | 0...4294967295
67 | I27 | TOLF1 | Trips Blocked | UINT32 | R | 0...4294967295
67 | S5 | TOLF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
67 | S6 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S7 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S8 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S9 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S10 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S11 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S12 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S13 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S14 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S15 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S16 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S17 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S18 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S19 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S20 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S21 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S22 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S23 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S24 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S25 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S26 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S27 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S28 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S29 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S30 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S31 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S32 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S33 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S34 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S35 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S36 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S37 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S38 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S39 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S40 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S41 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S42 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S43 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S44 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S45 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S46 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S47 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S48 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S49 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S50 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S51 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S52 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S53 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S54 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S55 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S56 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S57 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S58 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S59 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S60 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S61 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S62 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S63 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S64 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S65 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S66 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S67 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S68 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S69 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | O1 | TOLF1 | TF> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
67 | O2 | TOLF1 | TF> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
67 | O3 | TOLF1 | TF> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
67 | O4 | TOLF1 | TF> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
67 | O5 | TOLF1 | TF> Trip | SIGNAL_OUT | RW | 0...4294967295
67 | I28 | TOLF1 | Newest Register | UINT32 | R | 0...12
67 | I29 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I30 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I31 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I32 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I33 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I34 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I35 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I36 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I37 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I38 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I39 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I40 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I41 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I42 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I43 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I44 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I45 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I46 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I47 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I48 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I49 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I50 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I51 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I52 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I53 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I54 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I55 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I56 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I57 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I58 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I59 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I60 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I61 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I62 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I63 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I64 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I65 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I66 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I67 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I68 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I69 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I70 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I71 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I72 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I73 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I74 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I75 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I76 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | S70 | TOLF1 | EventMaskLo | UINT32 | RW | 0...4294967295
67 | S71 | TOLF1 | EventMaskHi | UINT32 | RW | 0...4294967295
68 | S1 | TOLM1 | TM> [49M] mode | UINT32 | RW | 0=Disabled; 1=Activated
68 | V1 | TOLM1 | TM> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
68 | V2 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
68 | V3 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
68 | V4 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
68 | V5 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
68 | V6 | TOLM1 | Motor status | UINT32 | R | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
68 | S2 | TOLM1 | Pick-up current (x In) | FLOAT | RW | 0...40
68 | S3 | TOLM1 | NPS Biasing in use | UINT32 | RW | 0=No NPS biasing;1=NPS Biasing in use
68 | S4 | TOLM1 | NPS Bias factor | FLOAT | RW | 0.1...10
68 | S5 | TOLM1 | Time constants | UINT32 | RW | 0=Single;1=Multiple
68 | S6 | TOLM1 | Long Heat T const (cold) | FLOAT | RW | 0...500
68 | S7 | TOLM1 | Long Heat T const (hot) | FLOAT | RW | 0...500
68 | S8 | TOLM1 | Long Cool T const Run | FLOAT | RW | 0...3000
68 | S9 | TOLM1 | Long Cool T const Stop | FLOAT | RW | 0...3000
68 | S10 | TOLM1 | Short Heat T const (cold) | FLOAT | RW | 0...500
68 | S11 | TOLM1 | Short Heat T const (hot) | FLOAT | RW | 0...500
68 | S12 | TOLM1 | Short Cool T const | FLOAT | RW | 0...3000
68 | S13 | TOLM1 | Wf factor for L/S T const | FLOAT | RW | 0...1
68 | S14 | TOLM1 | T const dyn. balancing | UINT32 | RW | 0=Fixed;1=Dynamic
68 | S15 | TOLM1 | Short Cool T used when stop | FLOAT | RW | 0...3000
68 | S16 | TOLM1 | Cold Reset Theta Default | FLOAT | RW | 0...150
68 | I1 | TOLM1 | Wf in use | FLOAT | R | 0...1
68 | I2 | TOLM1 | Long heat TC in use | FLOAT | R | 0...500
68 | I3 | TOLM1 | Short heat TC in use | FLOAT | R | 0...500
68 | I4 | TOLM1 | Long cool TC in use | FLOAT | R | 0...500
68 | I5 | TOLM1 | Short cool TC in use | FLOAT | R | 0...500
68 | I6 | TOLM1 | Cold stall time | FLOAT | R | 0...500
68 | I7 | TOLM1 | Hot stall time | FLOAT | R | 0...500
68 | S17 | TOLM1 | Dev.Temp (tmax) | UINT32 | RW | 0=A;1=B;2=F;3=H;4=Manual set
68 | S18 | TOLM1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
68 | S19 | TOLM1 | Amb. T Selection | UINT32 | RW | 0=Manual set;1=RTD
68 | S20 | TOLM1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
68 | V7 | TOLM1 | TM> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
68 | I8 | TOLM1 | TM> Time to 100% T | UINT32 | R | 0...4294967295
68 | I9 | TOLM1 | TM> Reference T curr. | FLOAT | R | 0...50
68 | I10 | TOLM1 | TM> Active meas curr. | FLOAT | R | 0...50
68 | I11 | TOLM1 | TM> T est.with act. curr. | FLOAT | R | 0...500
68 | I12 | TOLM1 | TM> T at the moment | FLOAT | R | 0...500
68 | I13 | TOLM1 | TM> Max.Temp.Rise All. | FLOAT | R | 0...250
68 | I14 | TOLM1 | TM> Temp.Rise atm. | FLOAT | R | 0...250
68 | I15 | TOLM1 | TM> Hot Spot estimate | FLOAT | R | 0...250
68 | I16 | TOLM1 | TM> Hot Spot Max. All | FLOAT | R | 0...250
68 | I17 | TOLM1 | TM> Used k for amb. temp | FLOAT | R | 0...5
68 | I18 | TOLM1 | TM> Trip delay remaining | UINT32 | R | 0...4294967295
68 | I19 | TOLM1 | TM> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
68 | I20 | TOLM1 | TM> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
68 | I21 | TOLM1 | TM> Inhibit time to rel. | UINT32 | R | 0...4294967295
68 | I22 | TOLM1 | TM> Trip time to rel. | UINT32 | R | 0...4294967295
68 | I23 | TOLM1 | TM> Thermal cap used | FLOAT | R | 0...500
68 | I24 | TOLM1 | Alarm1 inits | UINT32 | R | 0...4294967295
68 | I25 | TOLM1 | Alarm2 inits | UINT32 | R | 0...4294967295
68 | I26 | TOLM1 | Restart Inhibits | UINT32 | R | 0...4294967295
68 | I27 | TOLM1 | Trips | UINT32 | R | 0...4294967295
68 | I28 | TOLM1 | Trips Blocked | UINT32 | R | 0...4294967295
68 | S21 | TOLM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
68 | S22 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S23 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S24 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S25 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S26 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S27 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S28 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S29 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S30 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S31 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S32 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S33 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S34 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S35 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S36 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S37 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S38 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S39 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S40 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S41 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S42 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S43 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S44 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S45 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S46 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S47 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S48 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S49 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S50 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S51 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S52 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S53 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S54 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S55 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S56 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S57 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S58 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S59 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S60 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S61 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S62 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S63 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S64 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S65 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S66 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S67 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S68 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S69 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S70 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S71 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S72 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S73 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S74 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S75 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S76 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S77 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S78 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S79 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S80 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S81 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S82 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S83 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S84 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S85 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | O1 | TOLM1 | TM> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
68 | O2 | TOLM1 | TM> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
68 | O3 | TOLM1 | TM> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
68 | O4 | TOLM1 | TM> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
68 | O5 | TOLM1 | TM> Trip | SIGNAL_OUT | RW | 0...4294967295
68 | I29 | TOLM1 | Newest Register | UINT32 | R | 0...12
68 | I30 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I31 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I32 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I33 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I34 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I35 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I36 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I37 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I38 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I39 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I40 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I41 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I42 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I43 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I44 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I45 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I46 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I47 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I48 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I49 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I50 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I51 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I52 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I53 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I54 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I55 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I56 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I57 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I58 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I59 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I60 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I61 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I62 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I63 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I64 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I65 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I66 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I67 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I68 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I69 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I70 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I71 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I72 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I73 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I74 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I75 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I76 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I77 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I78 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I79 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I80 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I81 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I82 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I83 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I84 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I85 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I86 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I87 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I88 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I89 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I90 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I91 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I92 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I93 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I94 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I95 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I96 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I97 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I98 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I99 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I100 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I101 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I102 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I103 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I104 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I105 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I106 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I107 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I108 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I109 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I110 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I111 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I112 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I113 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I114 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I115 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I116 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I117 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I118 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I119 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I120 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I121 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I122 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I123 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I124 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I125 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I126 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I127 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I128 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I129 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I130 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I131 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I132 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I133 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I134 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I135 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I136 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I137 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | S86 | TOLM1 | EventMaskLo | UINT32 | RW | 0...4294967295
68 | S87 | TOLM1 | EventMaskHi | UINT32 | RW | 0...4294967295
57 | S1 | LCR1 | ISt> [48/14/50LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
57 | V1 | LCR1 | ISt> condition | UINT32 | R | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
57 | I1 | LCR1 | ISt> starts | UINT32 | R | 0...4294967295
57 | I2 | LCR1 | ISt> Set cap used in last start | FLOAT | R | 0...500
57 | I3 | LCR1 | ISt> Max cap used in last start | FLOAT | R | 0...500
57 | I4 | LCR1 | ISt> Set time trips | UINT32 | R | 0...4294967295
57 | I5 | LCR1 | ISt> Max cap trips | UINT32 | R | 0...4294967295
57 | I6 | LCR1 | ISt> blocks | UINT32 | R | 0...4294967295
57 | S2 | LCR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
57 | S3 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S4 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S5 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S6 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S7 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S8 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S9 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S10 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S11 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S12 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S13 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S14 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S15 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S16 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S17 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S18 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S19 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S20 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S21 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S22 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S23 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S24 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S25 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S26 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S27 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S28 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S29 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S30 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S31 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S32 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S33 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S34 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S35 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S36 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S37 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S38 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S39 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S40 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S41 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S42 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S43 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S44 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S45 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S46 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S47 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S48 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S49 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S50 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | O1 | LCR1 | ISt> START | SIGNAL_OUT | RW | 0...4294967295
57 | O2 | LCR1 | ISt> Set time TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O3 | LCR1 | ISt> Machine cap.TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O4 | LCR1 | ISt> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
57 | I7 | LCR1 | Newest Register | UINT32 | R | 0...12
57 | I8 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I9 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I10 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I11 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I12 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I13 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I14 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I15 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I16 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I17 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I18 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I19 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I20 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I21 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I22 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I23 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I24 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I25 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I26 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I27 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I28 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I29 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I30 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I31 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I32 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I33 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I34 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I35 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I36 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I37 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I38 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I39 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I40 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I41 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I42 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I43 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I44 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I45 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I46 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I47 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I48 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I49 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I50 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I51 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I52 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I53 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I54 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I55 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I56 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I57 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I58 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I59 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I60 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I61 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I62 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I63 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I64 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I65 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I66 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I67 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I68 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I69 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I70 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I71 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I72 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I73 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I74 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I75 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I76 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I77 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I78 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I79 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I80 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I81 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I82 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I83 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I84 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I85 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I86 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I87 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I88 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I89 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I90 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I91 | LCR1 | Phase C current | FLOAT | R | 0...250
56 | S1 | FSP1 | N> [66/86] mode | UINT32 | RW | 0=Disabled; 1=Activated
56 | V1 | FSP1 | N> condition | UINT32 | R | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
56 | I1 | FSP1 | N> alarms | UINT32 | R | 0...4294967295
56 | I2 | FSP1 | N> Inhibits | UINT32 | R | 0...4294967295
56 | I3 | FSP1 | N> blocks | UINT32 | R | 0...4294967295
56 | S2 | FSP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
56 | I4 | FSP1 | Start monitoring time left | UINT32 | R | 0...4294967295
56 | I5 | FSP1 | Inhibit time on | UINT32 | R | 0...4294967295
56 | I6 | FSP1 | Alarm time on | UINT32 | R | 0...4294967295
56 | I7 | FSP1 | Time since last start | UINT32 | R | 0...4294967295
56 | I8 | FSP1 | Start count atm. | UINT32 | R | 0...4294967295
56 | I9 | FSP1 | Starts left atm. | UINT32 | R | 0...4294967295
56 | S3 | FSP1 | Give one more start (Warning! Motor may overheat) | UINT32 | W | 0=-;1=Deduct one start
56 | O1 | FSP1 | N> One start remaining (Alarm) | SIGNAL_OUT | RW | 0...4294967295
56 | O2 | FSP1 | N> INHIBIT ON (General) | SIGNAL_OUT | RW | 0...4294967295
56 | O3 | FSP1 | N> INHIBIT ON Mot Running | SIGNAL_OUT | RW | 0...4294967295
56 | O4 | FSP1 | N> INHIBIT ON Mot Stopped | SIGNAL_OUT | RW | 0...4294967295
56 | O5 | FSP1 | N> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
56 | I10 | FSP1 | Newest Register | UINT32 | R | 0...12
56 | S4 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S5 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S6 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S7 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S8 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S9 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S10 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S11 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S12 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S13 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S14 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S15 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S16 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S17 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S18 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S19 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S20 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S21 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S22 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S23 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S24 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S25 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S26 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S27 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S28 | FSP1 | Start count | FLOAT | R | 0...250
56 | S29 | FSP1 | Start count | FLOAT | R | 0...250
56 | S30 | FSP1 | Start count | FLOAT | R | 0...250
56 | S31 | FSP1 | Start count | FLOAT | R | 0...250
56 | S32 | FSP1 | Start count | FLOAT | R | 0...250
56 | S33 | FSP1 | Start count | FLOAT | R | 0...250
56 | S34 | FSP1 | Start count | FLOAT | R | 0...250
56 | S35 | FSP1 | Start count | FLOAT | R | 0...250
56 | S36 | FSP1 | Start count | FLOAT | R | 0...250
56 | S37 | FSP1 | Start count | FLOAT | R | 0...250
56 | S38 | FSP1 | Start count | FLOAT | R | 0...250
56 | S39 | FSP1 | Start count | FLOAT | R | 0...250
56 | S40 | FSP1 | EventMaskLo | UINT32 | RW | 0...4294967295
60 | S1 | NUC1 | I< [37] mode | UINT32 | RW | 0=Disabled; 1=Activated
60 | V1 | NUC1 | I< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
60 | I1 | NUC1 | I< starts | UINT32 | R | 0...4294967295
60 | I2 | NUC1 | I< trips | UINT32 | R | 0...4294967295
60 | I3 | NUC1 | I< blocks | UINT32 | R | 0...4294967295
60 | S2 | NUC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
60 | S3 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S4 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S5 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S6 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S7 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S8 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S9 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S10 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S11 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S12 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S13 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S14 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S15 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S16 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S17 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S18 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S19 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S20 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S21 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S22 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S23 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S24 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S25 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S26 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | O1 | NUC1 | I< START | SIGNAL_OUT | RW | 0...4294967295
60 | O2 | NUC1 | I< TRIP | SIGNAL_OUT | RW | 0...4294967295
60 | O3 | NUC1 | I< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
60 | I4 | NUC1 | Newest Register | UINT32 | R | 0...12
60 | I5 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I6 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I7 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I8 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I9 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I10 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I11 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I12 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I13 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I14 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I15 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I16 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I17 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I18 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I19 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I20 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I21 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I22 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I23 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I24 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I25 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I26 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I27 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I28 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I29 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I30 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I31 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I32 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I33 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I34 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I35 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I36 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I37 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I38 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I39 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I40 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | S27 | NUC1 | EventMaskLo | UINT32 | RW | 0...4294967295
59 | S1 | MJP1 | Im> [51LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
59 | V1 | MJP1 | Im> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
59 | I1 | MJP1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
59 | I2 | MJP1 | Im> starts | UINT32 | R | 0...4294967295
59 | I3 | MJP1 | Im> trips | UINT32 | R | 0...4294967295
59 | I4 | MJP1 | Im> blocks | UINT32 | R | 0...4294967295
59 | S2 | MJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
59 | S3 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S4 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S5 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S6 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S7 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S8 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S9 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S10 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S11 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S12 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S13 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S14 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S15 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S16 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S17 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S18 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | O1 | MJP1 | Im> START | SIGNAL_OUT | RW | 0...4294967295
59 | O2 | MJP1 | Im> TRIP | SIGNAL_OUT | RW | 0...4294967295
59 | O3 | MJP1 | Im> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
59 | I5 | MJP1 | Newest Register | UINT32 | R | 0...12
59 | I6 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I7 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I8 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I9 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I10 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I11 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I12 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I13 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I14 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I15 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I16 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I17 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I18 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I19 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I20 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I21 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I22 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I23 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I24 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I25 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I26 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I27 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I28 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I29 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I30 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I31 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I32 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I33 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I34 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I35 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I36 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I37 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I38 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I39 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I40 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I41 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | S19 | MJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
85 | S1 | OV1 | U> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
85 | V1 | OV1 | U> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
85 | I1 | OV1 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
85 | I2 | OV1 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
85 | I3 | OV1 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
85 | I4 | OV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
85 | I5 | OV1 | U> starts | UINT32 | R | 0...4294967295
85 | I6 | OV1 | U> trips | UINT32 | R | 0...4294967295
85 | I7 | OV1 | U> blocks | UINT32 | R | 0...4294967295
85 | S2 | OV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
85 | S3 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S4 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S5 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S6 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S7 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S8 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S9 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S10 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S11 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S12 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S13 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S14 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S15 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S16 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S17 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S18 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S19 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S20 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S21 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S22 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S23 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S24 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S25 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S26 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | O1 | OV1 | U> START | SIGNAL_OUT | RW | 0...4294967295
85 | O2 | OV1 | U> TRIP | SIGNAL_OUT | RW | 0...4294967295
85 | O3 | OV1 | U> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
85 | I8 | OV1 | Newest Register | UINT32 | R | 0...12
85 | I9 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I10 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I11 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I12 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I13 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I14 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I15 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I16 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I17 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I18 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I19 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I20 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I21 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I22 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I23 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I24 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I25 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I26 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I27 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I28 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I29 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I30 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I31 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I32 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I33 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I34 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I35 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I36 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I37 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I38 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I39 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I40 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I41 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I42 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I43 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I44 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | S27 | OV1 | EventMaskLo | UINT32 | RW | 0...4294967295
86 | S1 | OV2 | U>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
86 | V1 | OV2 | U>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
86 | I1 | OV2 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
86 | I2 | OV2 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
86 | I3 | OV2 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
86 | I4 | OV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
86 | I5 | OV2 | U>> starts | UINT32 | R | 0...4294967295
86 | I6 | OV2 | U>> trips | UINT32 | R | 0...4294967295
86 | I7 | OV2 | U>> blocks | UINT32 | R | 0...4294967295
86 | S2 | OV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
86 | S3 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S4 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S5 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S6 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S7 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S8 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S9 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S10 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S11 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S12 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S13 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S14 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S15 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S16 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S17 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S18 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S19 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S20 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S21 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S22 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S23 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S24 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S25 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S26 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | O1 | OV2 | U>> START | SIGNAL_OUT | RW | 0...4294967295
86 | O2 | OV2 | U>> TRIP | SIGNAL_OUT | RW | 0...4294967295
86 | O3 | OV2 | U>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
86 | I8 | OV2 | Newest Register | UINT32 | R | 0...12
86 | I9 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I10 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I11 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I12 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I13 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I14 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I15 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I16 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I17 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I18 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I19 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I20 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I21 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I22 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I23 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I24 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I25 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I26 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I27 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I28 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I29 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I30 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I31 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I32 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I33 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I34 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I35 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I36 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I37 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I38 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I39 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I40 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I41 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I42 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I43 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I44 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | S27 | OV2 | EventMaskLo | UINT32 | RW | 0...4294967295
87 | S1 | OV3 | U>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
87 | V1 | OV3 | U>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
87 | I1 | OV3 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
87 | I2 | OV3 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
87 | I3 | OV3 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
87 | I4 | OV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
87 | I5 | OV3 | U>>> starts | UINT32 | R | 0...4294967295
87 | I6 | OV3 | U>>> trips | UINT32 | R | 0...4294967295
87 | I7 | OV3 | U>>> blocks | UINT32 | R | 0...4294967295
87 | S2 | OV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
87 | S3 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S4 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S5 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S6 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S7 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S8 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S9 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S10 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S11 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S12 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S13 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S14 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S15 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S16 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S17 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S18 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S19 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S20 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S21 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S22 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S23 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S24 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S25 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S26 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | O1 | OV3 | U>>> START | SIGNAL_OUT | RW | 0...4294967295
87 | O2 | OV3 | U>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
87 | O3 | OV3 | U>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
87 | I8 | OV3 | Newest Register | UINT32 | R | 0...12
87 | I9 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I10 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I11 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I12 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I13 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I14 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I15 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I16 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I17 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I18 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I19 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I20 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I21 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I22 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I23 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I24 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I25 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I26 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I27 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I28 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I29 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I30 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I31 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I32 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I33 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I34 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I35 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I36 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I37 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I38 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I39 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I40 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I41 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I42 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I43 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I44 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | S27 | OV3 | EventMaskLo | UINT32 | RW | 0...4294967295
88 | S1 | OV4 | U>>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
88 | V1 | OV4 | U>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
88 | I1 | OV4 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
88 | I2 | OV4 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
88 | I3 | OV4 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
88 | I4 | OV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
88 | I5 | OV4 | U>>>> starts | UINT32 | R | 0...4294967295
88 | I6 | OV4 | U>>>> trips | UINT32 | R | 0...4294967295
88 | I7 | OV4 | U>>>> blocks | UINT32 | R | 0...4294967295
88 | S2 | OV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
88 | S3 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S4 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S5 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S6 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S7 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S8 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S9 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S10 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S11 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S12 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S13 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S14 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S15 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S16 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S17 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S18 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S19 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S20 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S21 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S22 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S23 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S24 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S25 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S26 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | O1 | OV4 | U>>>> START | SIGNAL_OUT | RW | 0...4294967295
88 | O2 | OV4 | U>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
88 | O3 | OV4 | U>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
88 | I8 | OV4 | Newest Register | UINT32 | R | 0...12
88 | I9 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I10 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I11 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I12 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I13 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I14 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I15 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I16 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I17 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I18 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I19 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I20 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I21 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I22 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I23 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I24 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I25 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I26 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I27 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I28 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I29 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I30 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I31 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I32 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I33 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I34 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I35 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I36 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I37 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I38 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I39 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I40 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I41 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I42 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I43 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I44 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | S27 | OV4 | EventMaskLo | UINT32 | RW | 0...4294967295
89 | S1 | UV1 | U< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
89 | V1 | UV1 | U< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
89 | I1 | UV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
89 | I2 | UV1 | U< starts | UINT32 | R | 0...4294967295
89 | I3 | UV1 | U< trips | UINT32 | R | 0...4294967295
89 | I4 | UV1 | U< blocks | UINT32 | R | 0...4294967295
89 | S2 | UV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
89 | S3 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S4 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S5 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S6 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S7 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S8 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S9 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S10 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S11 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S12 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S13 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S14 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S15 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S16 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S17 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S18 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S19 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S20 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S21 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S22 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S23 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S24 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S25 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S26 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S27 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S28 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S29 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S30 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S31 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S32 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S33 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S34 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | O1 | UV1 | U< START | SIGNAL_OUT | RW | 0...4294967295
89 | O2 | UV1 | U< TRIP | SIGNAL_OUT | RW | 0...4294967295
89 | O3 | UV1 | U< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
89 | I5 | UV1 | Newest Register | UINT32 | R | 0...12
89 | I6 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I7 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I8 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I9 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I10 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I11 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I12 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I13 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I14 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I15 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I16 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I17 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I18 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I19 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I20 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I21 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I22 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I23 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I24 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I25 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I26 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I27 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I28 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I29 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I30 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I31 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I32 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I33 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I34 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I35 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I36 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I37 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I38 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I39 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I40 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I41 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | S35 | UV1 | EventMaskLo | UINT32 | RW | 0...4294967295
90 | S1 | UV2 | U<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
90 | V1 | UV2 | U<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
90 | I1 | UV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
90 | I2 | UV2 | U<< starts | UINT32 | R | 0...4294967295
90 | I3 | UV2 | U<< trips | UINT32 | R | 0...4294967295
90 | I4 | UV2 | U<< blocks | UINT32 | R | 0...4294967295
90 | S2 | UV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
90 | S3 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S4 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S5 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S6 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S7 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S8 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S9 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S10 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S11 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S12 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S13 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S14 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S15 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S16 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S17 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S18 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S19 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S20 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S21 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S22 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S23 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S24 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S25 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S26 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S27 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S28 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S29 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S30 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S31 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S32 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S33 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S34 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | O1 | UV2 | U<< START | SIGNAL_OUT | RW | 0...4294967295
90 | O2 | UV2 | U<< TRIP | SIGNAL_OUT | RW | 0...4294967295
90 | O3 | UV2 | U<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
90 | I5 | UV2 | Newest Register | UINT32 | R | 0...12
90 | I6 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I7 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I8 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I9 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I10 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I11 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I12 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I13 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I14 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I15 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I16 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I17 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I18 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I19 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I20 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I21 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I22 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I23 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I24 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I25 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I26 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I27 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I28 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I29 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I30 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I31 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I32 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I33 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I34 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I35 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I36 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I37 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I38 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I39 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I40 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I41 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | S35 | UV2 | EventMaskLo | UINT32 | RW | 0...4294967295
91 | S1 | UV3 | U<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
91 | V1 | UV3 | U<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
91 | I1 | UV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
91 | I2 | UV3 | U<<< starts | UINT32 | R | 0...4294967295
91 | I3 | UV3 | U<<< trips | UINT32 | R | 0...4294967295
91 | I4 | UV3 | U<<< blocks | UINT32 | R | 0...4294967295
91 | S2 | UV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
91 | S3 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S4 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S5 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S6 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S7 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S8 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S9 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S10 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S11 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S12 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S13 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S14 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S15 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S16 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S17 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S18 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S19 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S20 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S21 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S22 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S23 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S24 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S25 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S26 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S27 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S28 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S29 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S30 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S31 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S32 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S33 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S34 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | O1 | UV3 | U<<< START | SIGNAL_OUT | RW | 0...4294967295
91 | O2 | UV3 | U<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
91 | O3 | UV3 | U<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
91 | I5 | UV3 | Newest Register | UINT32 | R | 0...12
91 | I6 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I7 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I8 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I9 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I10 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I11 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I12 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I13 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I14 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I15 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I16 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I17 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I18 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I19 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I20 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I21 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I22 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I23 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I24 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I25 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I26 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I27 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I28 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I29 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I30 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I31 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I32 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I33 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I34 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I35 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I36 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I37 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I38 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I39 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I40 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I41 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | S35 | UV3 | EventMaskLo | UINT32 | RW | 0...4294967295
92 | S1 | UV4 | U<<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
92 | V1 | UV4 | U<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
92 | I1 | UV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
92 | I2 | UV4 | U<<<< starts | UINT32 | R | 0...4294967295
92 | I3 | UV4 | U<<<< trips | UINT32 | R | 0...4294967295
92 | I4 | UV4 | U<<<< blocks | UINT32 | R | 0...4294967295
92 | S2 | UV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
92 | S3 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S4 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S5 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S6 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S7 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S8 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S9 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S10 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S11 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S12 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S13 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S14 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S15 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S16 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S17 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S18 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S19 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S20 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S21 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S22 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S23 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S24 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S25 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S26 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S27 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S28 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S29 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S30 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S31 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S32 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S33 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S34 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | O1 | UV4 | U<<<< START | SIGNAL_OUT | RW | 0...4294967295
92 | O2 | UV4 | U<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
92 | O3 | UV4 | U<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
92 | I5 | UV4 | Newest Register | UINT32 | R | 0...12
92 | I6 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I7 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I8 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I9 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I10 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I11 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I12 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I13 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I14 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I15 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I16 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I17 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I18 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I19 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I20 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I21 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I22 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I23 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I24 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I25 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I26 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I27 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I28 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I29 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I30 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I31 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I32 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I33 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I34 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I35 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I36 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I37 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I38 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I39 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I40 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I41 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | S35 | UV4 | EventMaskLo | UINT32 | RW | 0...4294967295
93 | S1 | NOV1 | U0> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
93 | V1 | NOV1 | U0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
93 | I1 | NOV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
93 | I2 | NOV1 | U0> starts | UINT32 | R | 0...4294967295
93 | I3 | NOV1 | U0> trips | UINT32 | R | 0...4294967295
93 | I4 | NOV1 | U0> blocks | UINT32 | R | 0...4294967295
93 | S2 | NOV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
93 | S3 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S4 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S5 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S6 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S7 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S8 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S9 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S10 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S11 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S12 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S13 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S14 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S15 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S16 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S17 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S18 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | O1 | NOV1 | U0> START | SIGNAL_OUT | RW | 0...4294967295
93 | O2 | NOV1 | U0> TRIP | SIGNAL_OUT | RW | 0...4294967295
93 | O3 | NOV1 | U0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
93 | I5 | NOV1 | Newest Register | UINT32 | R | 0...12
93 | I6 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I7 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I8 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I9 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I10 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I11 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I12 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I13 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I14 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I15 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I16 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I17 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I18 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I19 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I20 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I21 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I22 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I23 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I24 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I25 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I26 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I27 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I28 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I29 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | S19 | NOV1 | EventMaskLo | UINT32 | RW | 0...4294967295
94 | S1 | NOV2 | U0>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
94 | V1 | NOV2 | U0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
94 | I1 | NOV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
94 | I2 | NOV2 | U0>> starts | UINT32 | R | 0...4294967295
94 | I3 | NOV2 | U0>> trips | UINT32 | R | 0...4294967295
94 | I4 | NOV2 | U0>> blocks | UINT32 | R | 0...4294967295
94 | S2 | NOV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
94 | S3 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S4 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S5 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S6 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S7 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S8 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S9 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S10 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S11 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S12 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S13 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S14 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S15 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S16 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S17 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S18 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | O1 | NOV2 | U0>> START | SIGNAL_OUT | RW | 0...4294967295
94 | O2 | NOV2 | U0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
94 | O3 | NOV2 | U0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
94 | I5 | NOV2 | Newest Register | UINT32 | R | 0...12
94 | I6 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I7 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I8 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I9 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I10 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I11 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I12 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I13 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I14 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I15 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I16 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I17 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I18 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I19 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I20 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I21 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I22 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I23 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I24 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I25 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I26 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I27 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I28 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I29 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | S19 | NOV2 | EventMaskLo | UINT32 | RW | 0...4294967295
95 | S1 | NOV3 | U0>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
95 | V1 | NOV3 | U0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
95 | I1 | NOV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
95 | I2 | NOV3 | U0>>> starts | UINT32 | R | 0...4294967295
95 | I3 | NOV3 | U0>>> trips | UINT32 | R | 0...4294967295
95 | I4 | NOV3 | U0>>> blocks | UINT32 | R | 0...4294967295
95 | S2 | NOV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
95 | S3 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S4 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S5 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S6 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S7 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S8 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S9 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S10 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S11 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S12 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S13 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S14 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S15 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S16 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S17 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S18 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | O1 | NOV3 | U0>>> START | SIGNAL_OUT | RW | 0...4294967295
95 | O2 | NOV3 | U0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
95 | O3 | NOV3 | U0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
95 | I5 | NOV3 | Newest Register | UINT32 | R | 0...12
95 | I6 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I7 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I8 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I9 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I10 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I11 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I12 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I13 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I14 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I15 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I16 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I17 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I18 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I19 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I20 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I21 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I22 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I23 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I24 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I25 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I26 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I27 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I28 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I29 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | S19 | NOV3 | EventMaskLo | UINT32 | RW | 0...4294967295
96 | S1 | NOV4 | U0>>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
96 | V1 | NOV4 | U0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
96 | I1 | NOV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
96 | I2 | NOV4 | U0>>>> starts | UINT32 | R | 0...4294967295
96 | I3 | NOV4 | U0>>>> trips | UINT32 | R | 0...4294967295
96 | I4 | NOV4 | U0>>>> blocks | UINT32 | R | 0...4294967295
96 | S2 | NOV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
96 | S3 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S4 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S5 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S6 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S7 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S8 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S9 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S10 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S11 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S12 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S13 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S14 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S15 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S16 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S17 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S18 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | O1 | NOV4 | U0>>>> START | SIGNAL_OUT | RW | 0...4294967295
96 | O2 | NOV4 | U0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
96 | O3 | NOV4 | U0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
96 | I5 | NOV4 | Newest Register | UINT32 | R | 0...12
96 | I6 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I7 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I8 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I9 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I10 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I11 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I12 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I13 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I14 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I15 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I16 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I17 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I18 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I19 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I20 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I21 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I22 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I23 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I24 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I25 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I26 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I27 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I28 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I29 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | S19 | NOV4 | EventMaskLo | UINT32 | RW | 0...4294967295
130 | S1 | VUB1 | U1/2 >/< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
130 | V1 | VUB1 | U1/2 >/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
130 | I1 | VUB1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
130 | I2 | VUB1 | U1/2 >/< starts | UINT32 | R | 0...4294967295
130 | I3 | VUB1 | U1/2 >/< trips | UINT32 | R | 0...4294967295
130 | I4 | VUB1 | U1/2 >/< blocks | UINT32 | R | 0...4294967295
130 | S2 | VUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
130 | S3 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S4 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S5 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S6 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S7 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S8 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S9 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S10 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S11 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S12 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S13 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S14 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S15 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S16 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S17 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S18 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S19 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S20 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S21 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S22 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S23 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S24 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S25 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S26 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S27 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S28 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S29 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S30 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S31 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S32 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S33 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S34 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | O1 | VUB1 | U1/2 >/< START | SIGNAL_OUT | RW | 0...4294967295
130 | O2 | VUB1 | U1/2 >/< TRIP | SIGNAL_OUT | RW | 0...4294967295
130 | O3 | VUB1 | U1/2 >/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
130 | I5 | VUB1 | Newest Register | UINT32 | R | 0...12
130 | I6 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I7 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I8 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I9 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I10 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I11 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I12 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I13 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I14 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I15 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I16 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I17 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I18 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I19 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I20 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I21 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I22 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I23 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I24 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I25 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I26 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I27 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I28 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I29 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | S35 | VUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
131 | S1 | VUB2 | U1/2 >>/<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
131 | V1 | VUB2 | U1/2 >>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
131 | I1 | VUB2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
131 | I2 | VUB2 | U1/2 >>/<< starts | UINT32 | R | 0...4294967295
131 | I3 | VUB2 | U1/2 >>/<< trips | UINT32 | R | 0...4294967295
131 | I4 | VUB2 | U1/2 >>/<< blocks | UINT32 | R | 0...4294967295
131 | S2 | VUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
131 | S3 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S4 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S5 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S6 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S7 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S8 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S9 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S10 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S11 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S12 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S13 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S14 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S15 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S16 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S17 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S18 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S19 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S20 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S21 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S22 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S23 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S24 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S25 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S26 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S27 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S28 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S29 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S30 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S31 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S32 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S33 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S34 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | O1 | VUB2 | U1/2 >>/<< START | SIGNAL_OUT | RW | 0...4294967295
131 | O2 | VUB2 | U1/2 >>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
131 | O3 | VUB2 | U1/2 >>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
131 | I5 | VUB2 | Newest Register | UINT32 | R | 0...12
131 | I6 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I7 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I8 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I9 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I10 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I11 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I12 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I13 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I14 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I15 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I16 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I17 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I18 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I19 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I20 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I21 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I22 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I23 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I24 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I25 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I26 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I27 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I28 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I29 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | S35 | VUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
132 | S1 | VUB3 | U1/2 >>>/<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
132 | V1 | VUB3 | U1/2 >>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
132 | I1 | VUB3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
132 | I2 | VUB3 | U1/2 >>>/<<< starts | UINT32 | R | 0...4294967295
132 | I3 | VUB3 | U1/2 >>>/<<< trips | UINT32 | R | 0...4294967295
132 | I4 | VUB3 | U1/2 >>>/<<< blocks | UINT32 | R | 0...4294967295
132 | S2 | VUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
132 | S3 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S4 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S5 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S6 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S7 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S8 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S9 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S10 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S11 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S12 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S13 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S14 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S15 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S16 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S17 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S18 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S19 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S20 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S21 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S22 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S23 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S24 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S25 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S26 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S27 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S28 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S29 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S30 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S31 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S32 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S33 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S34 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | O1 | VUB3 | U1/2 >>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
132 | O2 | VUB3 | U1/2 >>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
132 | O3 | VUB3 | U1/2 >>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
132 | I5 | VUB3 | Newest Register | UINT32 | R | 0...12
132 | I6 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I7 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I8 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I9 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I10 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I11 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I12 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I13 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I14 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I15 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I16 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I17 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I18 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I19 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I20 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I21 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I22 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I23 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I24 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I25 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I26 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I27 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I28 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I29 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | S35 | VUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
133 | S1 | VUB4 | U1/2 >>>>/<<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
133 | V1 | VUB4 | U1/2 >>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
133 | I1 | VUB4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
133 | I2 | VUB4 | U1/2 >>>>/<<<< starts | UINT32 | R | 0...4294967295
133 | I3 | VUB4 | U1/2 >>>>/<<<< trips | UINT32 | R | 0...4294967295
133 | I4 | VUB4 | U1/2 >>>>/<<<< blocks | UINT32 | R | 0...4294967295
133 | S2 | VUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
133 | S3 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S4 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S5 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S6 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S7 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S8 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S9 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S10 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S11 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S12 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S13 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S14 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S15 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S16 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S17 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S18 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S19 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S20 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S21 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S22 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S23 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S24 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S25 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S26 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S27 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S28 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S29 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S30 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S31 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S32 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S33 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S34 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | O1 | VUB4 | U1/2 >>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
133 | O2 | VUB4 | U1/2 >>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
133 | O3 | VUB4 | U1/2 >>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
133 | I5 | VUB4 | Newest Register | UINT32 | R | 0...12
133 | I6 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I7 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I8 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I9 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I10 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I11 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I12 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I13 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I14 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I15 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I16 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I17 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I18 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I19 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I20 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I21 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I22 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I23 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I24 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I25 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I26 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I27 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I28 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I29 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | S35 | VUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
99 | S1 | FRQV1 | f</> [81O/81U] mode | UINT32 | RW | 0=Disabled;1=Activated
99 | V1 | FRQV1 | f> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I1 | FRQV1 | f> fmeas / fset | FLOAT | R | 0...20
99 | S2 | FRQV1 | f>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V2 | FRQV1 | f>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I2 | FRQV1 | f>> fmeas / fset | FLOAT | R | 0...20
99 | S3 | FRQV1 | f>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V3 | FRQV1 | f>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I3 | FRQV1 | f>>> fmeas / fset | FLOAT | R | 0...20
99 | S4 | FRQV1 | f>>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V4 | FRQV1 | f>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I4 | FRQV1 | f>>>> fmeas / fset | FLOAT | R | 0...20
99 | S5 | FRQV1 | f< Enable | UINT32 | RW | 0=No;1=Yes
99 | V5 | FRQV1 | f< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I5 | FRQV1 | f< fmeas / fset | FLOAT | R | 0...20
99 | S6 | FRQV1 | f<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V6 | FRQV1 | f<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I6 | FRQV1 | f<< fmeas / fset | FLOAT | R | 0...20
99 | S7 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V7 | FRQV1 | f<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I7 | FRQV1 | f<<< fmeas / fset | FLOAT | R | 0...20
99 | S8 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V8 | FRQV1 | f<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I8 | FRQV1 | f<<<< fmeas / fset | FLOAT | R | 0...20
99 | I9 | FRQV1 | f> starts | UINT32 | R | 0...4294967295
99 | I10 | FRQV1 | f> trips | UINT32 | R | 0...4294967295
99 | I11 | FRQV1 | f> blocks | UINT32 | R | 0...4294967295
99 | I12 | FRQV1 | f>> starts | UINT32 | R | 0...4294967295
99 | I13 | FRQV1 | f>> trips | UINT32 | R | 0...4294967295
99 | I14 | FRQV1 | f>> blocks | UINT32 | R | 0...4294967295
99 | I15 | FRQV1 | f>>> starts | UINT32 | R | 0...4294967295
99 | I16 | FRQV1 | f>>> trips | UINT32 | R | 0...4294967295
99 | I17 | FRQV1 | f>>> blocks | UINT32 | R | 0...4294967295
99 | I18 | FRQV1 | f>>>> starts | UINT32 | R | 0...4294967295
99 | I19 | FRQV1 | f>>>> trips | UINT32 | R | 0...4294967295
99 | I20 | FRQV1 | f>>>> blocks | UINT32 | R | 0...4294967295
99 | I21 | FRQV1 | f< starts | UINT32 | R | 0...4294967295
99 | I22 | FRQV1 | f< trips | UINT32 | R | 0...4294967295
99 | I23 | FRQV1 | f< blocks | UINT32 | R | 0...4294967295
99 | I24 | FRQV1 | f<< starts | UINT32 | R | 0...4294967295
99 | I25 | FRQV1 | f<< trips | UINT32 | R | 0...4294967295
99 | I26 | FRQV1 | f<< blocks | UINT32 | R | 0...4294967295
99 | I27 | FRQV1 | f<<< starts | UINT32 | R | 0...4294967295
99 | I28 | FRQV1 | f<<< trips | UINT32 | R | 0...4294967295
99 | I29 | FRQV1 | f<<< blocks | UINT32 | R | 0...4294967295
99 | I30 | FRQV1 | f<<<< starts | UINT32 | R | 0...4294967295
99 | I31 | FRQV1 | f<<<< trips | UINT32 | R | 0...4294967295
99 | I32 | FRQV1 | f<<<< blocks | UINT32 | R | 0...4294967295
99 | S9 | FRQV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
99 | S10 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S11 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S12 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S13 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S14 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S15 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S16 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S17 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S18 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S19 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S20 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S21 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S22 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S23 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S24 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S25 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S26 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S27 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S28 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S29 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S30 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S31 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S32 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S33 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S34 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S35 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S36 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S37 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S38 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S39 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S40 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S41 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S42 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S43 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S44 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S45 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S46 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S47 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S48 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S49 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S50 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S51 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S52 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S53 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S54 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S55 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S56 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S57 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S58 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S59 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S60 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S61 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S62 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S63 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S64 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S65 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S66 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S67 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S68 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S69 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S70 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S71 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S72 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S73 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S74 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S75 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S76 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S77 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S78 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S79 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S80 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S81 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S82 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S83 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S84 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S85 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S86 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S87 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S88 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S89 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S90 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S91 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S92 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S93 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S94 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S95 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S96 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S97 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S98 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S99 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S100 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S101 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S102 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S103 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S104 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S105 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S106 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S107 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S108 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S109 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S110 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S111 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S112 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S113 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S114 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S115 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S116 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S117 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S118 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S119 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S120 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S121 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S122 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S123 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S124 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S125 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S126 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S127 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S128 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S129 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S130 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S131 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S132 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S133 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S134 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S135 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S136 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S137 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S138 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S139 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S140 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S141 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S142 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S143 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S144 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S145 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S146 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S147 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S148 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S149 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S150 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S151 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S152 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S153 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S154 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S155 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S156 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S157 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S158 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S159 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S160 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S161 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S162 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S163 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S164 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S165 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S166 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S167 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S168 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S169 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S170 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S171 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S172 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S173 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S174 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S175 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S176 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S177 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S178 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S179 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S180 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S181 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S182 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S183 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S184 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S185 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S186 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S187 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S188 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S189 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S190 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S191 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S192 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S193 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S194 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S195 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S196 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S197 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S198 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S199 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S200 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S201 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | O1 | FRQV1 | f> START | SIGNAL_OUT | RW | 0...4294967295
99 | O2 | FRQV1 | f> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O3 | FRQV1 | f> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O4 | FRQV1 | f>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O5 | FRQV1 | f>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O6 | FRQV1 | f>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O7 | FRQV1 | f>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O8 | FRQV1 | f>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O9 | FRQV1 | f>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O10 | FRQV1 | f>>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O11 | FRQV1 | f>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O12 | FRQV1 | f>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O13 | FRQV1 | f< START | SIGNAL_OUT | RW | 0...4294967295
99 | O14 | FRQV1 | f< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O15 | FRQV1 | f< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O16 | FRQV1 | f<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O17 | FRQV1 | f<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O18 | FRQV1 | f<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O19 | FRQV1 | f<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O20 | FRQV1 | f<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O21 | FRQV1 | f<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O22 | FRQV1 | f<<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O23 | FRQV1 | f<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O24 | FRQV1 | f<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | I33 | FRQV1 | Newest Register | UINT32 | R | 0...12
99 | I34 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I35 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I36 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I37 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I38 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I39 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I40 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I41 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I42 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I43 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I44 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I45 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | S202 | FRQV1 | EventMaskLo | UINT32 | RW | 0...4294967295
103 | S1 | DFT1 | df/dt >/< [81] mode | UINT32 | RW | 0=Disabled;1=Activated
103 | S2 | DFT1 | Max allowed df/dt rate | FLOAT | RW | 0.1...50
103 | I1 | DFT1 | Measured df/dt | FLOAT | R | 0...20
103 | S3 | DFT1 | df/dt >/< (1) Enable | UINT32 | RW | 0=No;1=Yes
103 | V1 | DFT1 | df/dt >/< (1) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I2 | DFT1 | df/dt >/< (1) fmeas / fset | FLOAT | R | 0...20
103 | S4 | DFT1 | df/dt >/< (2) Enable | UINT32 | RW | 0=No;1=Yes
103 | V2 | DFT1 | df/dt >/< (2) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I3 | DFT1 | df/dt >/< (2) fmeas / fset | FLOAT | R | 0...20
103 | S5 | DFT1 | df/dt >/< (3) Enable | UINT32 | RW | 0=No;1=Yes
103 | V3 | DFT1 | df/dt >/< (3) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I4 | DFT1 | df/dt >/< (3) fmeas / fset | FLOAT | R | 0...20
103 | S6 | DFT1 | df/dt >/< (4) Enable | UINT32 | RW | 0=No;1=Yes
103 | V4 | DFT1 | df/dt >/< (4) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I5 | DFT1 | df/dt >/< (4) fmeas / fset | FLOAT | R | 0...20
103 | S7 | DFT1 | df/dt >/< (5) Enable | UINT32 | RW | 0=No;1=Yes
103 | V5 | DFT1 | df/dt >/< (5) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I6 | DFT1 | df/dt >/< (5) fmeas / fset | FLOAT | R | 0...20
103 | S8 | DFT1 | df/dt >/< (6) Enable | UINT32 | RW | 0=No;1=Yes
103 | V6 | DFT1 | df/dt >/< (6) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I7 | DFT1 | df/dt >/< (6) fmeas / fset | FLOAT | R | 0...20
103 | S9 | DFT1 | df/dt >/< (7) Enable | UINT32 | RW | 0=No;1=Yes
103 | V7 | DFT1 | df/dt >/< (7) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I8 | DFT1 | df/dt >/< (7) fmeas / fset | FLOAT | R | 0...20
103 | S10 | DFT1 | df/dt >/< (8) Enable | UINT32 | RW | 0=No;1=Yes
103 | V8 | DFT1 | df/dt >/< (8) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I9 | DFT1 | df/dt >/< (8) fmeas / fset | FLOAT | R | 0...20
103 | I10 | DFT1 | df/dt >/< (1) starts | UINT32 | R | 0...4294967295
103 | I11 | DFT1 | df/dt >/< (1) trips | UINT32 | R | 0...4294967295
103 | I12 | DFT1 | df/dt >/< (1) blocks | UINT32 | R | 0...4294967295
103 | I13 | DFT1 | df/dt >/< (2) starts | UINT32 | R | 0...4294967295
103 | I14 | DFT1 | df/dt >/< (2) trips | UINT32 | R | 0...4294967295
103 | I15 | DFT1 | df/dt >/< (2) blocks | UINT32 | R | 0...4294967295
103 | I16 | DFT1 | df/dt >/< (3) starts | UINT32 | R | 0...4294967295
103 | I17 | DFT1 | df/dt >/< (3) trips | UINT32 | R | 0...4294967295
103 | I18 | DFT1 | df/dt >/< (3) blocks | UINT32 | R | 0...4294967295
103 | I19 | DFT1 | df/dt >/< (4) starts | UINT32 | R | 0...4294967295
103 | I20 | DFT1 | df/dt >/< (4) trips | UINT32 | R | 0...4294967295
103 | I21 | DFT1 | df/dt >/< (4) blocks | UINT32 | R | 0...4294967295
103 | I22 | DFT1 | df/dt >/< (5) starts | UINT32 | R | 0...4294967295
103 | I23 | DFT1 | df/dt >/< (5) trips | UINT32 | R | 0...4294967295
103 | I24 | DFT1 | df/dt >/< (5) blocks | UINT32 | R | 0...4294967295
103 | I25 | DFT1 | df/dt >/< (6) starts | UINT32 | R | 0...4294967295
103 | I26 | DFT1 | df/dt >/< (6) trips | UINT32 | R | 0...4294967295
103 | I27 | DFT1 | df/dt >/< (6) blocks | UINT32 | R | 0...4294967295
103 | I28 | DFT1 | df/dt >/< (7) starts | UINT32 | R | 0...4294967295
103 | I29 | DFT1 | df/dt >/< (7) trips | UINT32 | R | 0...4294967295
103 | I30 | DFT1 | df/dt >/< (7) blocks | UINT32 | R | 0...4294967295
103 | I31 | DFT1 | df/dt >/< (8) starts | UINT32 | R | 0...4294967295
103 | I32 | DFT1 | df/dt >/< (8) trips | UINT32 | R | 0...4294967295
103 | I33 | DFT1 | df/dt >/< (8) blocks | UINT32 | R | 0...4294967295
103 | S11 | DFT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
103 | S12 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S13 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S14 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S15 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S16 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S17 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S18 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S19 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S20 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S21 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S22 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S23 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S24 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S25 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S26 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S27 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S28 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S29 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S30 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S31 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S32 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S33 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S34 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S35 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S36 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S37 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S38 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S39 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S40 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S41 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S42 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S43 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S44 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S45 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S46 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S47 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S48 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S49 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S50 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S51 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S52 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S53 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S54 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S55 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S56 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S57 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S58 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S59 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S60 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S61 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S62 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S63 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S64 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S65 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S66 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S67 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S68 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S69 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S70 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S71 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S72 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S73 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S74 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S75 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S76 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S77 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S78 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S79 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S80 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S81 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S82 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S83 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S84 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S85 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S86 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S87 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S88 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S89 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S90 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S91 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S92 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S93 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S94 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S95 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S96 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S97 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S98 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S99 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S100 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S101 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S102 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S103 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S104 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S105 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S106 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S107 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S108 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S109 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S110 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S111 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S112 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S113 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S114 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S115 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S116 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S117 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S118 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S119 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S120 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S121 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S122 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S123 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S124 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S125 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S126 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S127 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S128 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S129 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S130 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S131 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S132 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S133 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S134 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S135 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S136 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S137 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S138 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S139 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S140 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S141 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S142 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S143 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S144 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S145 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S146 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S147 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S148 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S149 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S150 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S151 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S152 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S153 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S154 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S155 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S156 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S157 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S158 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S159 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S160 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S161 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S162 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S163 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S164 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S165 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S166 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S167 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S168 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S169 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S170 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S171 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S172 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S173 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S174 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S175 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S176 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S177 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S178 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S179 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S180 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S181 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S182 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S183 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S184 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S185 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S186 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S187 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S188 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S189 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S190 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S191 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S192 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S193 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S194 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S195 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S196 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S197 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S198 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S199 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S200 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S201 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S202 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S203 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S204 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S205 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S206 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S207 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S208 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S209 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S210 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S211 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S212 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S213 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S214 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S215 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S216 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S217 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S218 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S219 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S220 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S221 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S222 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S223 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S224 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S225 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S226 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S227 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S228 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S229 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S230 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S231 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S232 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S233 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S234 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S235 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S236 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S237 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S238 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S239 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S240 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S241 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S242 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S243 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S244 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S245 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S246 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S247 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S248 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S249 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S250 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S251 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S252 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S253 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S254 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S255 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S256 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S257 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S258 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S259 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S260 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S261 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S262 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S263 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S264 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S265 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S266 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S267 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S268 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S269 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S270 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S271 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S272 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S273 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S274 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S275 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S276 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S277 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S278 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S279 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S280 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S281 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S282 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S283 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S284 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S285 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S286 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S287 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S288 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S289 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S290 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S291 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S292 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S293 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S294 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S295 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S296 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S297 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S298 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S299 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S300 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S301 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S302 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S303 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S304 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S305 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S306 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S307 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S308 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S309 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S310 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S311 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S312 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S313 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S314 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S315 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S316 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S317 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S318 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S319 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S320 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S321 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S322 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S323 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S324 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S325 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S326 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S327 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S328 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S329 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S330 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S331 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S332 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S333 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S334 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S335 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S336 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S337 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S338 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S339 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S340 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S341 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S342 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S343 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S344 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S345 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S346 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S347 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S348 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S349 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S350 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S351 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S352 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S353 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S354 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S355 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S356 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S357 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S358 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S359 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S360 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S361 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S362 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S363 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S364 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S365 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S366 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S367 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S368 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S369 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S370 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S371 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S372 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S373 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S374 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S375 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S376 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S377 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S378 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S379 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S380 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S381 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S382 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S383 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S384 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S385 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S386 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S387 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S388 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S389 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S390 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S391 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S392 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S393 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S394 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S395 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S396 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S397 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S398 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S399 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S400 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S401 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S402 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S403 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S404 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S405 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S406 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S407 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S408 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S409 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S410 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S411 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S412 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S413 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S414 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S415 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S416 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S417 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S418 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S419 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S420 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S421 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S422 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S423 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S424 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S425 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S426 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S427 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S428 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S429 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S430 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S431 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S432 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S433 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S434 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S435 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S436 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S437 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S438 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S439 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S440 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S441 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S442 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S443 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S444 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S445 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S446 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S447 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S448 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S449 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S450 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S451 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S452 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S453 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S454 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S455 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S456 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S457 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S458 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S459 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | O1 | DFT1 | df/dt >/< (1) START | SIGNAL_OUT | RW | 0...4294967295
103 | O2 | DFT1 | df/dt >/< (1) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O3 | DFT1 | df/dt >/< (1) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O4 | DFT1 | df/dt >/< (2) START | SIGNAL_OUT | RW | 0...4294967295
103 | O5 | DFT1 | df/dt >/< (2) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O6 | DFT1 | df/dt >/< (2) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O7 | DFT1 | df/dt >/< (3) START | SIGNAL_OUT | RW | 0...4294967295
103 | O8 | DFT1 | df/dt >/< (3) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O9 | DFT1 | df/dt >/< (3) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O10 | DFT1 | df/dt >/< (4) START | SIGNAL_OUT | RW | 0...4294967295
103 | O11 | DFT1 | df/dt >/< (4) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O12 | DFT1 | df/dt >/< (4) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O13 | DFT1 | df/dt >/< (5) START | SIGNAL_OUT | RW | 0...4294967295
103 | O14 | DFT1 | df/dt >/< (5) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O15 | DFT1 | df/dt >/< (5) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O16 | DFT1 | df/dt >/< (6) START | SIGNAL_OUT | RW | 0...4294967295
103 | O17 | DFT1 | df/dt >/< (6) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O18 | DFT1 | df/dt >/< (6) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O19 | DFT1 | df/dt >/< (7) START | SIGNAL_OUT | RW | 0...4294967295
103 | O20 | DFT1 | df/dt >/< (7) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O21 | DFT1 | df/dt >/< (7) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O22 | DFT1 | df/dt >/< (8) START | SIGNAL_OUT | RW | 0...4294967295
103 | O23 | DFT1 | df/dt >/< (8) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O24 | DFT1 | df/dt >/< (8) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | I34 | DFT1 | Newest Register | UINT32 | R | 0...12
103 | I35 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I36 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I37 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I38 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I39 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I40 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I41 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I42 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I43 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I44 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I45 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I46 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I47 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I48 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I49 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I50 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I51 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I52 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I53 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I54 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I55 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I56 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I57 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I58 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | S460 | DFT1 | EventMaskLo | UINT32 | RW | 0...4294967295
183 | V1 | RHC1 | Counter is now | UINT32 | R | 0=Idle;1=Counting
183 | I1 | RHC1 | Running hours | UINT32 | RW | 0...4294967295
183 | I2 | RHC1 | Start count | UINT32 | RW | 0...4294967295
183 | I3 | RHC1 | Clear Hours | UINT32 | W | 0=-;1=Clear
183 | S1 | RHC1 | EventMaskLo | UINT32 | RW | 0...4294967295
113 | V1 | GST1 | Generator is now | UINT32 | R | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
113 | I1 | GST1 | Times Overloaded | UINT32 | R | 0...4294967295
113 | I2 | GST1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
113 | I3 | GST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
113 | I4 | GST1 | Generating time | UINT32 | R | 0...4294967295
113 | I5 | GST1 | Overloading cumulative | UINT32 | R | 0...4294967295
113 | I6 | GST1 | Last overload duration | UINT32 | R | 0...4294967295
113 | I7 | GST1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
113 | I8 | GST1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
113 | S1 | GST1 | Clear total times | UINT32 | W | 0=-;1=Clear
113 | S2 | GST1 | Generator nominal MVA (S) | FLOAT | RW | 0.1...500
113 | S3 | GST1 | Generator nominal Voltage (Vt) | FLOAT | RW | 0.1...25
113 | S4 | GST1 | Prime mover max power output (Pmax) | FLOAT | RW | 0.1...500
113 | S5 | GST1 | Block trafo in protection area | UINT32 | RW | 0=No;1=Yes
113 | S6 | GST1 | Generator voltage measurement | UINT32 | RW | 0=LV side VT (no corrections);1=HV side VT(Reduce to LV);2=HV side VT(HV measurements)
113 | S7 | GST1 | Ratio for generator nominal voltage scaling (1 p.u.) | UINT32 | RW | 0=Generator nominal voltage;1=Transformer LV nominal voltage;2=Set Un ratio by hand
113 | I9 | GST1 | Transformer ratio HV -> LV Trafo. | FLOAT | R | 0.01...100
113 | I10 | GST1 | Transformer ratio HV -> LV Gen. | FLOAT | R | 0.01...100
113 | I11 | GST1 | Voltage ratio | FLOAT | RW | 0.001...100
113 | I12 | GST1 | Voltage scaling | FLOAT | R | 0.01...100
113 | S8 | GST1 | Transformer nominal MVA | FLOAT | RW | 0.001...500
113 | S9 | GST1 | HV side nominal voltage | FLOAT | RW | 0.001...500
113 | S10 | GST1 | LV side nominal voltage | FLOAT | RW | 0.001...500
113 | S11 | GST1 | Transformer Zk % | FLOAT | RW | 0.001...25
113 | S12 | GST1 | Transformer nom freq. | FLOAT | RW | 10...75
113 | S13 | GST1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
113 | I13 | GST1 | HV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I14 | GST1 | HV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I15 | GST1 | HV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I16 | GST1 | LV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I17 | GST1 | LV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I18 | GST1 | LV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I19 | GST1 | Transformer nom impedance | FLOAT | R | 0.01...250
113 | I20 | GST1 | Transformer nom Zk ohm | FLOAT | R | 0.01...250
113 | I21 | GST1 | Transformer nom SC inductance | FLOAT | R | 0.001...100
113 | I22 | GST1 | LV side max 3ph SC curr | FLOAT | R | 0.001...500
113 | I23 | GST1 | LV side 3ph SC to HV side | FLOAT | R | 0.001...500
113 | I24 | GST1 | LV side max 2ph SC curr | FLOAT | R | 0.001...500
113 | I25 | GST1 | LV side 2ph SC to HV side | FLOAT | R | 0.001...500
113 | I26 | GST1 | Trafo HV nominal current | FLOAT | R | 0.01...50000
113 | I27 | GST1 | Trafo LV nominal current | FLOAT | R | 0.01...50000
113 | O1 | GST1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
113 | O2 | GST1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O3 | GST1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O4 | GST1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
113 | O5 | GST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | O6 | GST1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | I28 | GST1 | Newest Register | UINT32 | R | 0...12
113 | I29 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I30 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I31 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I32 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I33 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I34 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I35 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I36 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I37 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I38 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I39 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I40 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I41 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I42 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I43 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I44 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I45 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I46 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I47 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I48 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I49 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I50 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I51 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I52 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I53 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I54 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I55 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I56 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I57 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I58 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I59 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I60 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I61 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I62 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I63 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I64 | GST1 | L3 Current | FLOAT | R | 0...250
113 | S14 | GST1 | EventMaskLo | UINT32 | RW | 0...4294967295
164 | S1 | PWR1 | PQS>/< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
164 | V1 | PWR1 | PQS>/< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
164 | I1 | PWR1 | Meas/Set at the moment | FLOAT | R | -1250...1250
164 | I2 | PWR1 | Meas/Nom at the moment | FLOAT | R | -1250...1250
164 | I3 | PWR1 | PQS>/< starts | UINT32 | R | 0...4294967295
164 | I4 | PWR1 | PQS>/< trips | UINT32 | R | 0...4294967295
164 | I5 | PWR1 | PQS>/< blocks | UINT32 | R | 0...4294967295
164 | S2 | PWR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
164 | S3 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S4 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S5 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S6 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S7 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S8 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S9 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S10 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S11 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S12 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S13 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S14 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S15 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S16 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S17 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S18 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | O1 | PWR1 | PQS>/< START | SIGNAL_OUT | RW | 0...4294967295
164 | O2 | PWR1 | PQS>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
164 | O3 | PWR1 | PQS>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
164 | I6 | PWR1 | Newest Register | UINT32 | R | 0...12
164 | I7 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I8 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I9 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I10 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I11 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I12 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I13 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I14 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I15 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I16 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I17 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I18 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | S19 | PWR1 | EventMaskLo | UINT32 | RW | 0...4294967295
165 | S1 | PWR2 | PQS>>/<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
165 | V1 | PWR2 | PQS>>/<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
165 | I1 | PWR2 | Meas/Set at the moment | FLOAT | R | -1250...1250
165 | I2 | PWR2 | Meas/Nom at the moment | FLOAT | R | -1250...1250
165 | I3 | PWR2 | PQS>>/<< starts | UINT32 | R | 0...4294967295
165 | I4 | PWR2 | PQS>>/<< trips | UINT32 | R | 0...4294967295
165 | I5 | PWR2 | PQS>>/<< blocks | UINT32 | R | 0...4294967295
165 | S2 | PWR2 | Clear statistics | UINT32 | W | 0=-;1=Clear
165 | S3 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S4 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S5 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S6 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S7 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S8 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S9 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S10 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S11 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S12 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S13 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S14 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S15 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S16 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S17 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S18 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | O1 | PWR2 | PQS>>/<< START | SIGNAL_OUT | RW | 0...4294967295
165 | O2 | PWR2 | PQS>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
165 | O3 | PWR2 | PQS>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
165 | I6 | PWR2 | Newest Register | UINT32 | R | 0...12
165 | I7 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I8 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I9 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I10 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I11 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I12 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I13 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I14 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I15 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I16 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I17 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I18 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | S19 | PWR2 | EventMaskLo | UINT32 | RW | 0...4294967295
166 | S1 | PWR3 | PQS>>>/<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
166 | V1 | PWR3 | PQS>>>/<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
166 | I1 | PWR3 | Meas/Set at the moment | FLOAT | R | -1250...1250
166 | I2 | PWR3 | Meas/Nom at the moment | FLOAT | R | -1250...1250
166 | I3 | PWR3 | PQS>>>/<<< starts | UINT32 | R | 0...4294967295
166 | I4 | PWR3 | PQS>>>/<<< trips | UINT32 | R | 0...4294967295
166 | I5 | PWR3 | PQS>>>/<<< blocks | UINT32 | R | 0...4294967295
166 | S2 | PWR3 | Clear statistics | UINT32 | W | 0=-;1=Clear
166 | S3 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S4 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S5 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S6 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S7 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S8 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S9 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S10 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S11 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S12 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S13 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S14 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S15 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S16 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S17 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S18 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | O1 | PWR3 | PQS>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
166 | O2 | PWR3 | PQS>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
166 | O3 | PWR3 | PQS>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
166 | I6 | PWR3 | Newest Register | UINT32 | R | 0...12
166 | I7 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I8 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I9 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I10 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I11 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I12 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I13 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I14 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I15 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I16 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I17 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I18 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | S19 | PWR3 | EventMaskLo | UINT32 | RW | 0...4294967295
167 | S1 | PWR4 | PQS>>>>/<<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
167 | V1 | PWR4 | PQS>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
167 | I1 | PWR4 | Meas/Set at the moment | FLOAT | R | -1250...1250
167 | I2 | PWR4 | Meas/Nom at the moment | FLOAT | R | -1250...1250
167 | I3 | PWR4 | PQS>>>>/<<<< starts | UINT32 | R | 0...4294967295
167 | I4 | PWR4 | PQS>>>>/<<<< trips | UINT32 | R | 0...4294967295
167 | I5 | PWR4 | PQS>>>>/<<<< blocks | UINT32 | R | 0...4294967295
167 | S2 | PWR4 | Clear statistics | UINT32 | W | 0=-;1=Clear
167 | S3 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S4 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S5 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S6 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S7 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S8 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S9 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S10 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S11 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S12 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S13 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S14 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S15 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S16 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S17 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S18 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | O1 | PWR4 | PQS>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
167 | O2 | PWR4 | PQS>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
167 | O3 | PWR4 | PQS>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
167 | I6 | PWR4 | Newest Register | UINT32 | R | 0...12
167 | I7 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I8 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I9 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I10 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I11 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I12 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I13 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I14 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I15 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I16 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I17 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I18 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | S19 | PWR4 | EventMaskLo | UINT32 | RW | 0...4294967295
100 | S1 | OPW1 | P> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
100 | V1 | OPW1 | P> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
100 | I1 | OPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
100 | I2 | OPW1 | P> starts | UINT32 | R | 0...4294967295
100 | I3 | OPW1 | P> trips | UINT32 | R | 0...4294967295
100 | I4 | OPW1 | P> blocks | UINT32 | R | 0...4294967295
100 | S2 | OPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
100 | S3 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S4 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S5 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S6 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S7 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S8 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S9 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S10 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S11 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S12 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S13 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S14 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S15 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S16 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S17 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S18 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | O1 | OPW1 | P> START | SIGNAL_OUT | RW | 0...4294967295
100 | O2 | OPW1 | P> TRIP | SIGNAL_OUT | RW | 0...4294967295
100 | O3 | OPW1 | P> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
100 | I5 | OPW1 | Newest Register | UINT32 | R | 0...12
100 | I6 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I7 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I8 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I9 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I10 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I11 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I12 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I13 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I14 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I15 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I16 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I17 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | S19 | OPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
101 | S1 | UPW1 | P< [37] mode | UINT32 | RW | 0=Disabled;1=Activated
101 | V1 | UPW1 | P< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
101 | I1 | UPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
101 | I2 | UPW1 | P< starts | UINT32 | R | 0...4294967295
101 | I3 | UPW1 | P< trips | UINT32 | R | 0...4294967295
101 | I4 | UPW1 | P< blocks | UINT32 | R | 0...4294967295
101 | S2 | UPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
101 | S3 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S4 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S5 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S6 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S7 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S8 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S9 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S10 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S11 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S12 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S13 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S14 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S15 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S16 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S17 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S18 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S19 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S20 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S21 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S22 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S23 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S24 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S25 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S26 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | O1 | UPW1 | P< START | SIGNAL_OUT | RW | 0...4294967295
101 | O2 | UPW1 | P< TRIP | SIGNAL_OUT | RW | 0...4294967295
101 | O3 | UPW1 | P< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
101 | I5 | UPW1 | Newest Register | UINT32 | R | 0...12
101 | I6 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I7 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I8 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I9 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I10 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I11 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I12 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I13 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I14 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I15 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I16 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I17 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | S27 | UPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
102 | S1 | RPW1 | Prev> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
102 | V1 | RPW1 | Prev> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
102 | I1 | RPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
102 | I2 | RPW1 | Prev> starts | UINT32 | R | 0...4294967295
102 | I3 | RPW1 | Prev> trips | UINT32 | R | 0...4294967295
102 | I4 | RPW1 | Prev> blocks | UINT32 | R | 0...4294967295
102 | S2 | RPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
102 | S3 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S4 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S5 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S6 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S7 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S8 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S9 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S10 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S11 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S12 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S13 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S14 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S15 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S16 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S17 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S18 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | O1 | RPW1 | Prev> START | SIGNAL_OUT | RW | 0...4294967295
102 | O2 | RPW1 | Prev> TRIP | SIGNAL_OUT | RW | 0...4294967295
102 | O3 | RPW1 | Prev> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
102 | I5 | RPW1 | Newest Register | UINT32 | R | 0...12
102 | I6 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I7 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I8 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I9 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I10 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I11 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I12 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I13 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I14 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I15 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I16 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I17 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | S19 | RPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
110 | S1 | SEF1 | U03rd< [64S] mode | UINT32 | RW | 0=Disabled; 1=Activated
110 | V1 | SEF1 | U03rd< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
110 | I1 | SEF1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
110 | I2 | SEF1 | Measured U0 3rd harm (%) | FLOAT | R | 0...1250
110 | I3 | SEF1 | Measured U0 3rd harm (Pri) | FLOAT | R | 0...1250
110 | I4 | SEF1 | U03rd< starts | UINT32 | R | 0...4294967295
110 | I5 | SEF1 | U03rd< trips | UINT32 | R | 0...4294967295
110 | I6 | SEF1 | U03rd< blocks | UINT32 | R | 0...4294967295
110 | S2 | SEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
110 | S3 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S4 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S5 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S6 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S7 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S8 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S9 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S10 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S11 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S12 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S13 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S14 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S15 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S16 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S17 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S18 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S19 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S20 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S21 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S22 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S23 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S24 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S25 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S26 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | O1 | SEF1 | U03rd< START | SIGNAL_OUT | RW | 0...4294967295
110 | O2 | SEF1 | U03rd< TRIP | SIGNAL_OUT | RW | 0...4294967295
110 | O3 | SEF1 | U03rd< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
110 | I7 | SEF1 | Newest Register | UINT32 | R | 0...12
110 | I8 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I9 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I10 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I11 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I12 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I13 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I14 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I15 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I16 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I17 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I18 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I19 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I20 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I21 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I22 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I23 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I24 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I25 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I26 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I27 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I28 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I29 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I30 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I31 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | S27 | SEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
109 | S1 | UEX1 | Q< [40] mode | UINT32 | RW | 0=Disabled; 1=Activated
109 | V1 | UEX1 | Q< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
109 | I1 | UEX1 | Qmeas/Qset at the moment | FLOAT | R | -1250...1250
109 | I2 | UEX1 | Q< starts | UINT32 | R | 0...4294967295
109 | I3 | UEX1 | Q< trips | UINT32 | R | 0...4294967295
109 | I4 | UEX1 | Q< blocks | UINT32 | R | 0...4294967295
109 | S2 | UEX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
109 | S3 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S4 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S5 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S6 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S7 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S8 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S9 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S10 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S11 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S12 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S13 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S14 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S15 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S16 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S17 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S18 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S19 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S20 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S21 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S22 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S23 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S24 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S25 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S26 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S27 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S28 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S29 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S30 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S31 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S32 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S33 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S34 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S35 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S36 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S37 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S38 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S39 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S40 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S41 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S42 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S43 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S44 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S45 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S46 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S47 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S48 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S49 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S50 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | O1 | UEX1 | Q< START | SIGNAL_OUT | RW | 0...4294967295
109 | O2 | UEX1 | Q< TRIP | SIGNAL_OUT | RW | 0...4294967295
109 | O3 | UEX1 | Q< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
109 | I5 | UEX1 | Newest Register | UINT32 | R | 0...12
109 | I6 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I7 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I8 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I9 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I10 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I11 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I12 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I13 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I14 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I15 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I16 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I17 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I18 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I19 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I20 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I21 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I22 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I23 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I24 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I25 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I26 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I27 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I28 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I29 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | S51 | UEX1 | EventMaskLo | UINT32 | RW | 0...4294967295
111 | S1 | UIM1 | Z< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
111 | V1 | UIM1 | Z< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
111 | I1 | UIM1 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
111 | I2 | UIM1 | Z< starts | UINT32 | R | 0...4294967295
111 | I3 | UIM1 | Z< trips | UINT32 | R | 0...4294967295
111 | I4 | UIM1 | Z< blocks | UINT32 | R | 0...4294967295
111 | S2 | UIM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
111 | S3 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S4 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S5 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S6 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S7 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S8 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S9 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S10 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S11 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S12 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S13 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S14 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S15 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S16 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S17 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S18 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | O1 | UIM1 | Z< START | SIGNAL_OUT | RW | 0...4294967295
111 | O2 | UIM1 | Z< TRIP | SIGNAL_OUT | RW | 0...4294967295
111 | O3 | UIM1 | Z< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
111 | I5 | UIM1 | Newest Register | UINT32 | R | 0...12
111 | I6 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I7 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I8 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I9 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I10 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I11 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I12 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I13 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I14 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I15 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I16 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I17 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I18 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I19 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I20 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I21 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I22 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I23 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I24 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I25 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I26 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I27 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I28 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I29 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I30 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I31 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I32 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I33 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I34 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I35 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I36 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I37 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I38 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I39 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I40 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I41 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | S19 | UIM1 | EventMaskLo | UINT32 | RW | 0...4294967295
149 | S1 | UIM2 | Z<< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
149 | V1 | UIM2 | Z<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
149 | I1 | UIM2 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
149 | I2 | UIM2 | Z<< starts | UINT32 | R | 0...4294967295
149 | I3 | UIM2 | Z<< trips | UINT32 | R | 0...4294967295
149 | I4 | UIM2 | Z<< blocks | UINT32 | R | 0...4294967295
149 | S2 | UIM2 | Clear statistics | UINT32 | W | 0=-;1=Clear
149 | S3 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S4 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S5 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S6 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S7 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S8 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S9 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S10 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S11 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S12 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S13 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S14 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S15 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S16 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S17 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S18 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | O1 | UIM2 | Z<< START | SIGNAL_OUT | RW | 0...4294967295
149 | O2 | UIM2 | Z<< TRIP | SIGNAL_OUT | RW | 0...4294967295
149 | O3 | UIM2 | Z<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
149 | I5 | UIM2 | Newest Register | UINT32 | R | 0...12
149 | I6 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I7 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I8 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I9 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I10 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I11 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I12 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I13 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I14 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I15 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I16 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I17 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I18 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I19 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I20 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I21 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I22 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I23 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I24 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I25 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I26 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I27 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I28 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I29 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I30 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I31 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I32 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I33 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I34 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I35 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I36 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I37 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I38 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I39 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I40 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I41 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | S19 | UIM2 | EventMaskLo | UINT32 | RW | 0...4294967295
112 | S1 | VOC1 | Iv> [51V] mode | UINT32 | RW | 0=Disabled; 1=Activated
112 | V1 | VOC1 | Iv> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
112 | I1 | VOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
112 | I2 | VOC1 | Iv> starts | UINT32 | R | 0...4294967295
112 | I3 | VOC1 | Iv> trips | UINT32 | R | 0...4294967295
112 | I4 | VOC1 | Iv> blocks | UINT32 | R | 0...4294967295
112 | S2 | VOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
112 | S3 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S4 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S5 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S6 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S7 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S8 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S9 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S10 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S11 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S12 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S13 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S14 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S15 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S16 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S17 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S18 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S19 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S20 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S21 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S22 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S23 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S24 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S25 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S26 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S27 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S28 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S29 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S30 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S31 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S32 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S33 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S34 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S35 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S36 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S37 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S38 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S39 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S40 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S41 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S42 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | O1 | VOC1 | Iv> START | SIGNAL_OUT | RW | 0...4294967295
112 | O2 | VOC1 | Iv> TRIP | SIGNAL_OUT | RW | 0...4294967295
112 | O3 | VOC1 | Iv> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
112 | I5 | VOC1 | Newest Register | UINT32 | R | 0...12
112 | I6 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I7 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I8 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I9 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I10 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I11 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I12 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I13 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I14 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I15 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I16 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I17 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I18 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I19 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I20 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I21 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I22 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I23 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I24 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I25 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I26 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I27 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I28 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I29 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I30 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I31 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I32 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I33 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I34 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I35 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I36 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I37 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I38 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I39 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I40 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I41 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I42 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I43 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I44 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I45 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I46 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I47 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I48 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I49 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I50 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I51 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I52 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I53 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I54 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I55 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I56 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I57 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I58 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I59 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I60 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I61 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I62 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I63 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I64 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I65 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | S43 | VOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
128 | S1 | VHZ1 | V/Hz > [24] mode | UINT32 | RW | 0=Disabled;1=Activated
128 | S2 | VHZ1 | V/Hz(1) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V1 | VHZ1 | V/Hz(1) > condition | UINT32 | R | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
128 | I1 | VHZ1 | V/Hz(1) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | S3 | VHZ1 | V/Hz(2) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V2 | VHZ1 | V/Hz(2) > condition | UINT32 | R | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
128 | I2 | VHZ1 | V/Hz(2) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | I3 | VHZ1 | U/f at the moment | FLOAT | R | -100...100
128 | I4 | VHZ1 | U/f atm to nominal U/f ratio | FLOAT | R | -100...100
128 | I5 | VHZ1 | V/Hz(1) > Starts | UINT32 | R | 0...4294967295
128 | I6 | VHZ1 | V/Hz(1) > Alarms | UINT32 | R | 0...4294967295
128 | I7 | VHZ1 | V/Hz(1) > Trips | UINT32 | R | 0...4294967295
128 | I8 | VHZ1 | V/Hz(1) > Blocks | UINT32 | R | 0...4294967295
128 | I9 | VHZ1 | V/Hz(2) > Starts | UINT32 | R | 0...4294967295
128 | I10 | VHZ1 | V/Hz(2) > Alarms | UINT32 | R | 0...4294967295
128 | I11 | VHZ1 | V/Hz(2) > Trips | UINT32 | R | 0...4294967295
128 | I12 | VHZ1 | V/Hz(2) > Blocks | UINT32 | R | 0...4294967295
128 | S4 | VHZ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
128 | S5 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S6 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S7 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S8 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S9 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S10 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S11 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S12 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S13 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S14 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S15 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S16 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S17 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S18 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S19 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S20 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S21 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S22 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S23 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S24 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S25 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S26 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S27 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S28 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S29 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S30 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S31 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S32 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S33 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S34 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S35 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S36 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S37 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S38 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S39 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S40 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S41 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S42 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S43 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S44 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S45 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S46 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S47 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S48 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S49 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S50 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S51 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S52 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | O1 | VHZ1 | V/Hz(1) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O2 | VHZ1 | V/Hz(1) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O3 | VHZ1 | V/Hz(1) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O4 | VHZ1 | V/Hz(1) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | O5 | VHZ1 | V/Hz(2) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O6 | VHZ1 | V/Hz(2) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O7 | VHZ1 | V/Hz(2) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O8 | VHZ1 | V/Hz(2) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | I13 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I14 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I15 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I16 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I17 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I18 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I19 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I20 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I21 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I22 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I23 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I24 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I25 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I26 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I27 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I28 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I29 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I30 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I31 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I32 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I33 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I34 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I35 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I36 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I37 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I38 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I39 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I40 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I41 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I42 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I43 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I44 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I45 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I46 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I47 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I48 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I49 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I50 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I51 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I52 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I53 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I54 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I55 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I56 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I57 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I58 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I59 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I60 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I61 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I62 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I63 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I64 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I65 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I66 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I67 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I68 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I69 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I70 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I71 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I72 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I73 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I74 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I75 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I76 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I77 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I78 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I79 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I80 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I81 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I82 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I83 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I84 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I85 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I86 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I87 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I88 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I89 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I90 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I91 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I92 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I93 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I94 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I95 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I96 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I97 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I98 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I99 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I100 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I101 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I102 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I103 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I104 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I105 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I106 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I107 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I108 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I109 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I110 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | S53 | VHZ1 | EventMaskLo | UINT32 | RW | 0...4294967295
129 | S1 | UPF1 | PF< [55] mode | UINT32 | RW | 0=Disabled; 1=Activated
129 | V1 | UPF1 | PF< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
129 | S2 | UPF1 | Available modes | UINT32 | RW | 0=Trip;1=Trip and Alarm
129 | I1 | UPF1 | PFmeas/PFalarm at the moment | FLOAT | R | 0...1250
129 | I2 | UPF1 | PFmeas/PFtrip at the moment | FLOAT | R | 0...1250
129 | I3 | UPF1 | PF< Alarm Starts | UINT32 | R | 0...4294967295
129 | I4 | UPF1 | PF< Alarms | UINT32 | R | 0...4294967295
129 | I5 | UPF1 | PF< Starts | UINT32 | R | 0...4294967295
129 | I6 | UPF1 | PF< Trips | UINT32 | R | 0...4294967295
129 | I7 | UPF1 | PF< Blocks | UINT32 | R | 0...4294967295
129 | S3 | UPF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
129 | S4 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S5 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S6 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S7 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S8 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S9 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S10 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S11 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S12 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S13 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S14 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S15 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S16 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S17 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S18 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S19 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S20 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S21 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S22 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S23 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S24 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S25 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S26 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S27 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S28 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S29 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S30 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S31 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S32 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S33 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S34 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S35 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | O1 | UPF1 | PF< START | SIGNAL_OUT | RW | 0...4294967295
129 | O2 | UPF1 | PF< TRIP | SIGNAL_OUT | RW | 0...4294967295
129 | O3 | UPF1 | PF< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
129 | I8 | UPF1 | Newest Register | UINT32 | R | 0...12
129 | I9 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I10 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I11 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I12 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I13 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I14 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I15 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I16 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I17 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I18 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I19 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I20 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | S36 | UPF1 | EventMaskLo | UINT32 | RW | 0...4294967295
141 | I1 | RTDIN | S1 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I2 | RTDIN | S1 Resistance | FLOAT | R | 0...4000.000
141 | I3 | RTDIN | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I4 | RTDIN | S1 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I5 | RTDIN | S2 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I6 | RTDIN | S2 Resistance | FLOAT | R | 0...4000.000
141 | I7 | RTDIN | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I8 | RTDIN | S2 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I9 | RTDIN | S3 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I10 | RTDIN | S3 Resistance | FLOAT | R | 0...4000.000
141 | I11 | RTDIN | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I12 | RTDIN | S3 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I13 | RTDIN | S4 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I14 | RTDIN | S4 Resistance | FLOAT | R | 0...4000.000
141 | I15 | RTDIN | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I16 | RTDIN | S4 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I17 | RTDIN | S5 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I18 | RTDIN | S5 Resistance | FLOAT | R | 0...4000.000
141 | I19 | RTDIN | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I20 | RTDIN | S5 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I21 | RTDIN | S6 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I22 | RTDIN | S6 Resistance | FLOAT | R | 0...4000.000
141 | I23 | RTDIN | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I24 | RTDIN | S6 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I25 | RTDIN | S7 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I26 | RTDIN | S7 Resistance | FLOAT | R | 0...4000.000
141 | I27 | RTDIN | S7 Measurement mA | FLOAT | R | 0.000...20.000
141 | I28 | RTDIN | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I29 | RTDIN | S7 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I30 | RTDIN | S8 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I31 | RTDIN | S8 Resistance | FLOAT | R | 0...4000.000
141 | I32 | RTDIN | S8 Measurement mA | FLOAT | R | 0.000...20.000
141 | I33 | RTDIN | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I34 | RTDIN | S8 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I35 | RTDIN | S9 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I36 | RTDIN | S9 Resistance | FLOAT | R | 0...4000.000
141 | I37 | RTDIN | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I38 | RTDIN | S9 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I39 | RTDIN | S10 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I40 | RTDIN | S10 Resistance | FLOAT | R | 0...4000.000
141 | I41 | RTDIN | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I42 | RTDIN | S10 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I43 | RTDIN | S11 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I44 | RTDIN | S11 Resistance | FLOAT | R | 0...4000.000
141 | I45 | RTDIN | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I46 | RTDIN | S11 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I47 | RTDIN | S12 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I48 | RTDIN | S12 Resistance | FLOAT | R | 0...4000.000
141 | I49 | RTDIN | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I50 | RTDIN | S12 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I51 | RTDIN | S13 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I52 | RTDIN | S13 Resistance | FLOAT | R | 0...4000.000
141 | I53 | RTDIN | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I54 | RTDIN | S13 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I55 | RTDIN | S14 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I56 | RTDIN | S14 Resistance | FLOAT | R | 0...4000.000
141 | I57 | RTDIN | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I58 | RTDIN | S14 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I59 | RTDIN | S15 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I60 | RTDIN | S15 Resistance | FLOAT | R | 0...4000.000
141 | I61 | RTDIN | S15 Measurement mA | FLOAT | R | 0.000...20.000
141 | I62 | RTDIN | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I63 | RTDIN | S15 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I64 | RTDIN | S16 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I65 | RTDIN | S16 Resistance | FLOAT | R | 0...4000.000
141 | I66 | RTDIN | S16 Measurement mA | FLOAT | R | 0.000...20.000
141 | I67 | RTDIN | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I68 | RTDIN | S16 Filtered measurement | FLOAT | R | -200.0...2000.0
69 | S1 | RTD1 | RTD mode | UINT32 | RW | 0=Disabled;1=Activated
69 | S2 | RTD1 | S1 enable | UINT32 | RW | 0=No;1=Yes
69 | I1 | RTD1 | S1 Measurement (Protection) | FLOAT | R | -200...2000
69 | V1 | RTD1 | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S3 | RTD1 | S1 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I2 | RTD1 | S1 Alarm1 act | UINT32 | R | 0...4294967295
69 | S4 | RTD1 | S1 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S5 | RTD1 | S1 Alarm1 | FLOAT | RW | -200...2000
69 | S6 | RTD1 | S1 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I3 | RTD1 | S1 Alarm2 act | UINT32 | R | 0...4294967295
69 | S7 | RTD1 | S1 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S8 | RTD1 | S1 Alarm2 | FLOAT | RW | -200...2000
69 | I4 | RTD1 | S2 Measurement (Protection) | FLOAT | R | -200...2000
69 | V2 | RTD1 | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S9 | RTD1 | S2 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I5 | RTD1 | S2 Alarm1 act | UINT32 | R | 0...4294967295
69 | S10 | RTD1 | S2 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S11 | RTD1 | S2 Alarm1 | FLOAT | RW | -200...2000
69 | S12 | RTD1 | S2 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I6 | RTD1 | S2 Alarm2 act | UINT32 | R | 0...4294967295
69 | S13 | RTD1 | S2 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S14 | RTD1 | S2 Alarm2 | FLOAT | RW | -200...2000
69 | I7 | RTD1 | S3 Measurement (Protection) | FLOAT | R | -200...2000
69 | V3 | RTD1 | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S15 | RTD1 | S3 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I8 | RTD1 | S3 Alarm1 act | UINT32 | R | 0...4294967295
69 | S16 | RTD1 | S3 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S17 | RTD1 | S3 Alarm1 | FLOAT | RW | -200...2000
69 | S18 | RTD1 | S3 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I9 | RTD1 | S3 Alarm2 act | UINT32 | R | 0...4294967295
69 | S19 | RTD1 | S3 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S20 | RTD1 | S3 Alarm2 | FLOAT | RW | -200...2000
69 | I10 | RTD1 | S4 Measurement (Protection) | FLOAT | R | -200...2000
69 | V4 | RTD1 | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S21 | RTD1 | S4 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I11 | RTD1 | S4 Alarm1 act | UINT32 | R | 0...4294967295
69 | S22 | RTD1 | S4 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S23 | RTD1 | S4 Alarm1 | FLOAT | RW | -200...2000
69 | S24 | RTD1 | S4 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I12 | RTD1 | S4 Alarm2 act | UINT32 | R | 0...4294967295
69 | S25 | RTD1 | S4 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S26 | RTD1 | S4 Alarm2 | FLOAT | RW | -200...2000
69 | I13 | RTD1 | S5 Measurement (Protection) | FLOAT | R | -200...2000
69 | V5 | RTD1 | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S27 | RTD1 | S5 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I14 | RTD1 | S5 Alarm1 act | UINT32 | R | 0...4294967295
69 | S28 | RTD1 | S5 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S29 | RTD1 | S5 Alarm1 | FLOAT | RW | -200...2000
69 | S30 | RTD1 | S5 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I15 | RTD1 | S5 Alarm2 act | UINT32 | R | 0...4294967295
69 | S31 | RTD1 | S5 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S32 | RTD1 | S5 Alarm2 | FLOAT | RW | -200...2000
69 | I16 | RTD1 | S6 Measurement (Protection) | FLOAT | R | -200...2000
69 | V6 | RTD1 | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S33 | RTD1 | S6 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I17 | RTD1 | S6 Alarm1 act | UINT32 | R | 0...4294967295
69 | S34 | RTD1 | S6 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S35 | RTD1 | S6 Alarm1 | FLOAT | RW | -200...2000
69 | S36 | RTD1 | S6 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I18 | RTD1 | S6 Alarm2 act | UINT32 | R | 0...4294967295
69 | S37 | RTD1 | S6 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S38 | RTD1 | S6 Alarm2 | FLOAT | RW | -200...2000
69 | I19 | RTD1 | S7 Measurement (Protection) | FLOAT | R | -200...2000
69 | V7 | RTD1 | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S39 | RTD1 | S7 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I20 | RTD1 | S7 Alarm1 act | UINT32 | R | 0...4294967295
69 | S40 | RTD1 | S7 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S41 | RTD1 | S7 Alarm1 | FLOAT | RW | -200...2000
69 | S42 | RTD1 | S7 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I21 | RTD1 | S7 Alarm2 act | UINT32 | R | 0...4294967295
69 | S43 | RTD1 | S7 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S44 | RTD1 | S7 Alarm2 | FLOAT | RW | -200...2000
69 | I22 | RTD1 | S8 Measurement (Protection) | FLOAT | R | -200...2000
69 | V8 | RTD1 | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S45 | RTD1 | S8 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I23 | RTD1 | S8 Alarm1 act | UINT32 | R | 0...4294967295
69 | S46 | RTD1 | S8 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S47 | RTD1 | S8 Alarm1 | FLOAT | RW | -200...2000
69 | S48 | RTD1 | S8 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I24 | RTD1 | S8 Alarm2 act | UINT32 | R | 0...4294967295
69 | S49 | RTD1 | S8 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S50 | RTD1 | S8 Alarm2 | FLOAT | RW | -200...2000
69 | I25 | RTD1 | S9 Measurement (Protection) | FLOAT | R | -200...2000
69 | V9 | RTD1 | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S51 | RTD1 | S9 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I26 | RTD1 | S9 Alarm1 act | UINT32 | R | 0...4294967295
69 | S52 | RTD1 | S9 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S53 | RTD1 | S9 Alarm1 | FLOAT | RW | -200...2000
69 | S54 | RTD1 | S9 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I27 | RTD1 | S9 Alarm2 act | UINT32 | R | 0...4294967295
69 | S55 | RTD1 | S9 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S56 | RTD1 | S9 Alarm2 | FLOAT | RW | -200...2000
69 | I28 | RTD1 | S10 Measurement (Protection) | FLOAT | R | -200...2000
69 | V10 | RTD1 | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S57 | RTD1 | S10 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I29 | RTD1 | S10 Alarm1 act | UINT32 | R | 0...4294967295
69 | S58 | RTD1 | S10 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S59 | RTD1 | S10 Alarm1 | FLOAT | RW | -200...2000
69 | S60 | RTD1 | S10 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I30 | RTD1 | S10 Alarm2 act | UINT32 | R | 0...4294967295
69 | S61 | RTD1 | S10 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S62 | RTD1 | S10 Alarm2 | FLOAT | RW | -200...2000
69 | I31 | RTD1 | S11 Measurement (Protection) | FLOAT | R | -200...2000
69 | V11 | RTD1 | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S63 | RTD1 | S11 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I32 | RTD1 | S11 Alarm1 act | UINT32 | R | 0...4294967295
69 | S64 | RTD1 | S11 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S65 | RTD1 | S11 Alarm1 | FLOAT | RW | -200...2000
69 | S66 | RTD1 | S11 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I33 | RTD1 | S11 Alarm2 act | UINT32 | R | 0...4294967295
69 | S67 | RTD1 | S11 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S68 | RTD1 | S11 Alarm2 | FLOAT | RW | -200...2000
69 | I34 | RTD1 | S12 Measurement (Protection) | FLOAT | R | -200...2000
69 | V12 | RTD1 | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S69 | RTD1 | S12 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I35 | RTD1 | S12 Alarm1 act | UINT32 | R | 0...4294967295
69 | S70 | RTD1 | S12 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S71 | RTD1 | S12 Alarm1 | FLOAT | RW | -200...2000
69 | S72 | RTD1 | S12 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I36 | RTD1 | S12 Alarm2 act | UINT32 | R | 0...4294967295
69 | S73 | RTD1 | S12 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S74 | RTD1 | S12 Alarm2 | FLOAT | RW | -200...2000
69 | I37 | RTD1 | S13 Measurement (Protection) | FLOAT | R | -200...2000
69 | V13 | RTD1 | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S75 | RTD1 | S13 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I38 | RTD1 | S13 Alarm1 act | UINT32 | R | 0...4294967295
69 | S76 | RTD1 | S13 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S77 | RTD1 | S13 Alarm1 | FLOAT | RW | -200...2000
69 | S78 | RTD1 | S13 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I39 | RTD1 | S13 Alarm2 act | UINT32 | R | 0...4294967295
69 | S79 | RTD1 | S13 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S80 | RTD1 | S13 Alarm2 | FLOAT | RW | -200...2000
69 | I40 | RTD1 | S14 Measurement (Protection) | FLOAT | R | -200...2000
69 | V14 | RTD1 | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S81 | RTD1 | S14 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I41 | RTD1 | S14 Alarm1 act | UINT32 | R | 0...4294967295
69 | S82 | RTD1 | S14 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S83 | RTD1 | S14 Alarm1 | FLOAT | RW | -200...2000
69 | S84 | RTD1 | S14 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I42 | RTD1 | S14 Alarm2 act | UINT32 | R | 0...4294967295
69 | S85 | RTD1 | S14 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S86 | RTD1 | S14 Alarm2 | FLOAT | RW | -200...2000
69 | I43 | RTD1 | S15 Measurement (Protection) | FLOAT | R | -200...2000
69 | V15 | RTD1 | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S87 | RTD1 | S15 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I44 | RTD1 | S15 Alarm1 act | UINT32 | R | 0...4294967295
69 | S88 | RTD1 | S15 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S89 | RTD1 | S15 Alarm1 | FLOAT | RW | -200...2000
69 | S90 | RTD1 | S15 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I45 | RTD1 | S15 Alarm2 act | UINT32 | R | 0...4294967295
69 | S91 | RTD1 | S15 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S92 | RTD1 | S15 Alarm2 | FLOAT | RW | -200...2000
69 | I46 | RTD1 | S16 Measurement (Protection) | FLOAT | R | -200...2000
69 | V16 | RTD1 | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S93 | RTD1 | S16 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I47 | RTD1 | S16 Alarm1 act | UINT32 | R | 0...4294967295
69 | S94 | RTD1 | S16 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S95 | RTD1 | S16 Alarm1 | FLOAT | RW | -200...2000
69 | S96 | RTD1 | S16 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I48 | RTD1 | S16 Alarm2 act | UINT32 | R | 0...4294967295
69 | S97 | RTD1 | S16 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S98 | RTD1 | S16 Alarm2 | FLOAT | RW | -200...2000
69 | O1 | RTD1 | S1 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O2 | RTD1 | S1 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O3 | RTD1 | S1 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O4 | RTD1 | S2 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O5 | RTD1 | S2 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O6 | RTD1 | S2 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O7 | RTD1 | S3 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O8 | RTD1 | S3 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O9 | RTD1 | S3 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O10 | RTD1 | S4 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O11 | RTD1 | S4 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O12 | RTD1 | S4 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O13 | RTD1 | S5 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O14 | RTD1 | S5 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O15 | RTD1 | S5 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O16 | RTD1 | S6 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O17 | RTD1 | S6 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O18 | RTD1 | S6 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O19 | RTD1 | S7 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O20 | RTD1 | S7 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O21 | RTD1 | S7 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O22 | RTD1 | S8 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O23 | RTD1 | S8 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O24 | RTD1 | S8 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O25 | RTD1 | S9 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O26 | RTD1 | S9 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O27 | RTD1 | S9 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O28 | RTD1 | S10 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O29 | RTD1 | S10 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O30 | RTD1 | S10 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O31 | RTD1 | S11 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O32 | RTD1 | S11 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O33 | RTD1 | S11 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O34 | RTD1 | S12 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O35 | RTD1 | S12 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O36 | RTD1 | S12 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O37 | RTD1 | S13 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O38 | RTD1 | S13 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O39 | RTD1 | S13 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O40 | RTD1 | S14 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O41 | RTD1 | S14 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O42 | RTD1 | S14 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O43 | RTD1 | S15 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O44 | RTD1 | S15 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O45 | RTD1 | S15 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O46 | RTD1 | S16 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O47 | RTD1 | S16 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O48 | RTD1 | S16 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | S99 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
69 | S100 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
70 | S1 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
70 | S2 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
74 | S1 | ARC1 | I/I0 Arc> [50ARC/50NARC] mode | UINT32 | RW | 0=Disabled;1=Activated
74 | S2 | ARC1 | I/I0 Arc> Self supervision test pulse | UINT32 | RW | 0=Disabled;1=On
74 | V1 | ARC1 | I/I0 Arc> condition | UINT32 | R | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
74 | V2 | ARC1 | Sensor status | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I1 | ARC1 | I/I0 Arc> Zone1 Trips | UINT32 | R | 0...4294967295
74 | I2 | ARC1 | I/I0 Arc> Zone1 Blocks | UINT32 | R | 0...4294967295
74 | I3 | ARC1 | I/I0 Arc> Zone2 Trips | UINT32 | R | 0...4294967295
74 | I4 | ARC1 | I/I0 Arc> Zone2 Blocks | UINT32 | R | 0...4294967295
74 | I5 | ARC1 | I/I0 Arc> Zone3 Trips | UINT32 | R | 0...4294967295
74 | I6 | ARC1 | I/I0 Arc> Zone3 Blocks | UINT32 | R | 0...4294967295
74 | I7 | ARC1 | I/I0 Arc> Zone4 Trips | UINT32 | R | 0...4294967295
74 | I8 | ARC1 | I/I0 Arc> Zone4 Blocks | UINT32 | R | 0...4294967295
74 | S3 | ARC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
74 | I9 | ARC1 | Channel 1 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I10 | ARC1 | Channel 1 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I11 | ARC1 | Channel 2 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I12 | ARC1 | Channel 2 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I13 | ARC1 | Channel 3 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I14 | ARC1 | Channel 3 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I15 | ARC1 | Channel 4 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I16 | ARC1 | Channel 4 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | S4 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S5 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S6 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S7 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S8 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S9 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S10 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S11 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S12 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S13 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S14 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S15 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S16 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S17 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S18 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S19 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S20 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S21 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S22 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S23 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S24 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S25 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S26 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S27 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S28 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S29 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S30 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S31 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S32 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S33 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S34 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S35 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S36 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S37 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S38 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S39 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S40 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S41 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S42 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S43 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S44 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S45 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S46 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S47 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S48 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S49 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S50 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S51 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S52 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S53 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S54 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S55 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S56 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S57 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S58 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S59 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S60 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S61 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S62 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S63 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S64 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S65 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S66 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S67 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S68 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S69 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S70 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S71 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S72 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S73 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S74 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S75 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S76 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S77 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S78 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S79 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S80 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S81 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S82 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S83 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S84 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S85 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S86 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S87 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S88 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S89 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S90 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S91 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S92 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S93 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S94 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S95 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S96 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S97 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S98 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S99 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S100 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S101 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S102 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S103 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S104 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S105 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S106 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S107 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S108 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S109 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S110 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S111 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S112 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S113 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S114 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S115 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S116 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S117 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S118 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S119 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S120 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S121 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S122 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S123 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S124 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S125 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S126 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S127 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S128 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S129 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S130 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S131 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S132 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S133 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S134 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S135 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S136 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S137 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S138 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S139 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S140 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S141 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S142 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S143 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S144 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S145 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S146 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S147 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S148 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S149 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S150 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S151 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S152 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S153 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S154 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S155 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S156 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S157 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S158 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S159 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S160 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S161 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S162 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S163 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S164 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S165 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S166 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S167 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S168 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S169 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S170 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S171 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S172 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S173 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S174 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S175 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S176 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S177 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S178 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S179 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S180 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S181 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S182 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S183 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S184 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S185 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S186 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S187 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S188 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S189 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S190 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S191 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S192 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S193 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S194 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S195 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S196 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S197 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S198 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S199 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S200 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S201 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S202 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S203 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S204 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S205 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S206 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S207 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S208 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S209 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S210 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S211 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S212 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S213 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S214 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S215 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S216 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S217 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S218 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S219 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S220 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S221 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S222 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S223 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S224 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S225 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S226 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S227 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S228 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S229 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S230 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S231 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S232 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S233 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S234 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S235 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S236 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S237 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S238 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S239 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S240 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S241 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S242 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S243 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S244 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S245 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S246 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S247 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S248 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S249 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S250 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S251 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S252 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S253 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S254 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S255 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S256 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S257 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S258 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S259 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S260 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S261 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S262 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S263 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S264 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S265 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S266 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S267 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S268 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S269 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S270 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S271 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S272 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S273 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S274 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S275 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S276 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S277 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S278 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S279 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S280 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S281 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S282 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S283 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S284 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S285 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S286 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S287 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S288 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S289 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S290 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S291 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S292 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S293 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S294 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S295 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S296 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S297 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S298 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S299 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S300 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S301 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S302 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S303 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S304 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S305 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S306 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S307 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S308 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S309 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S310 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S311 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S312 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S313 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S314 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S315 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S316 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S317 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S318 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S319 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S320 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S321 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S322 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S323 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S324 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S325 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S326 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S327 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S328 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S329 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S330 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S331 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S332 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S333 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S334 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S335 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S336 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S337 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S338 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S339 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S340 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S341 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S342 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S343 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S344 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S345 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S346 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S347 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S348 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S349 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S350 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S351 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S352 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S353 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S354 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S355 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S356 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S357 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S358 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S359 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S360 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S361 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S362 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S363 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S364 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S365 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S366 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S367 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S368 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S369 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S370 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S371 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S372 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S373 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S374 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S375 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S376 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S377 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S378 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S379 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S380 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S381 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S382 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S383 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S384 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S385 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S386 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S387 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S388 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S389 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S390 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S391 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S392 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S393 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S394 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S395 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S396 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S397 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S398 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S399 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S400 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S401 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S402 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S403 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S404 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S405 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S406 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S407 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S408 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S409 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S410 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S411 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | O1 | ARC1 | I/I0 Arc> Ph.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O2 | ARC1 | I/I0 Arc> Res.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O3 | ARC1 | I/I0 Arc> Zone1.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O4 | ARC1 | I/I0 Arc> Zone2.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O5 | ARC1 | I/I0 Arc> Zone3.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O6 | ARC1 | I/I0 Arc> Zone4.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O7 | ARC1 | I/I0 Arc> Ph.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O8 | ARC1 | I/I0 Arc> Res.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O9 | ARC1 | I/I0 Arc> Ph.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O10 | ARC1 | I/I0 Arc> Res.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O11 | ARC1 | I/I0 Arc> Zone1 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O12 | ARC1 | I/I0 Arc> Zone1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O13 | ARC1 | I/I0 Arc> Zone2 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O14 | ARC1 | I/I0 Arc> Zone2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O15 | ARC1 | I/I0 Arc> Zone3 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O16 | ARC1 | I/I0 Arc> Zone3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O17 | ARC1 | I/I0 Arc> Zone4 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O18 | ARC1 | I/I0 Arc> Zone4 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O19 | ARC1 | I/I0 Arc> S1 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O20 | ARC1 | I/I0 Arc> S2 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O21 | ARC1 | I/I0 Arc> S3 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O22 | ARC1 | I/I0 Arc> S4 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O23 | ARC1 | I/I0 Arc> IO unit fault | SIGNAL_OUT | RW | 0...4294967295
74 | I17 | ARC1 | Newest Register | UINT32 | R | 0...12
74 | I18 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I19 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I20 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I21 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I22 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I23 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I24 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I25 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I26 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I27 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I28 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I29 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I30 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I31 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I32 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I33 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I34 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I35 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I36 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I37 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I38 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I39 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I40 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I41 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I42 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I43 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I44 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I45 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I46 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I47 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I48 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I49 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I50 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I51 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I52 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I53 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I54 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I55 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I56 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I57 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I58 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I59 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I60 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I61 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I62 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I63 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I64 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I65 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I66 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I67 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I68 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I69 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I70 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I71 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I72 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I73 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I74 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I75 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I76 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I77 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | S412 | ARC1 | EventMaskLo | UINT32 | RW | 0...4294967295
74 | S413 | ARC1 | EventMaskHi | UINT32 | RW | 0...4294967295
52 | S1 | CTS1 | CTS1 mode | UINT32 | RW | 0=Disabled;1=Activated
52 | V1 | CTS1 | CTS1 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
52 | I1 | CTS1 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
52 | I2 | CTS1 | Natural unbalance ang | FLOAT | R | -360...360
52 | I3 | CTS1 | Measured current difference Isum, I0 | FLOAT | R | 0...50
52 | I4 | CTS1 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
52 | I5 | CTS1 | CTS1 alarms | UINT32 | R | 0...4294967295
52 | I6 | CTS1 | CTS1 blocks | UINT32 | R | 0...4294967295
52 | S2 | CTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
52 | S3 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S4 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S5 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S6 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S7 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S8 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S9 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S10 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S11 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S12 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S13 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S14 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S15 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S16 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S17 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S18 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S19 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S20 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S21 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S22 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S23 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S24 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S25 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S26 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S27 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S28 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S29 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S30 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S31 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S32 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S33 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S34 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S35 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S36 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S37 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S38 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S39 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S40 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S41 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S42 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S43 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S44 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S45 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S46 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S47 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S48 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S49 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S50 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | O1 | CTS1 | CTS1 ALARM | SIGNAL_OUT | RW | 0...4294967295
52 | O2 | CTS1 | CTS1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
52 | I7 | CTS1 | Newest Register | UINT32 | R | 0...12
52 | I8 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I9 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I10 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I11 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I12 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I13 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I14 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I15 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I16 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I17 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I18 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I19 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I20 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I21 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I22 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I23 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I24 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I25 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I26 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I27 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I28 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I29 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I30 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I31 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I32 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I33 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I34 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I35 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I36 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I37 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I38 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I39 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I40 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I41 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I42 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I43 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I44 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I45 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I46 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I47 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I48 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I49 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I50 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I51 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I52 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I53 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I54 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I55 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I56 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I57 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I58 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I59 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I60 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I61 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I62 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I63 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I64 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I65 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I66 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I67 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I68 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I69 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I70 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I71 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I72 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I73 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I74 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I75 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I76 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I77 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I78 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I79 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | S51 | CTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
52 | S52 | CTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
54 | S1 | CTS2 | CTS2 mode | UINT32 | RW | 0=Disabled;1=Activated
54 | V1 | CTS2 | CTS2 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
54 | I1 | CTS2 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
54 | I2 | CTS2 | Natural unbalance ang | FLOAT | R | -360...360
54 | I3 | CTS2 | Measured current difference Isum, I0 | FLOAT | R | 0...50
54 | I4 | CTS2 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
54 | I5 | CTS2 | CTS2 alarms | UINT32 | R | 0...4294967295
54 | I6 | CTS2 | CTS2 blocks | UINT32 | R | 0...4294967295
54 | S2 | CTS2 | Clear statistics | UINT32 | W | 0=-;1=Clear
54 | S3 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S4 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S5 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S6 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S7 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S8 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S9 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S10 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S11 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S12 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S13 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S14 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S15 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S16 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S17 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S18 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S19 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S20 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S21 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S22 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S23 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S24 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S25 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S26 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S27 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S28 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S29 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S30 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S31 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S32 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S33 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S34 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S35 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S36 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S37 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S38 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S39 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S40 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S41 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S42 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S43 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S44 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S45 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S46 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S47 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S48 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S49 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S50 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | O1 | CTS2 | CTS2 ALARM | SIGNAL_OUT | RW | 0...4294967295
54 | O2 | CTS2 | CTS2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
54 | I7 | CTS2 | Newest Register | UINT32 | R | 0...12
54 | I8 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I9 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I10 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I11 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I12 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I13 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I14 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I15 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I16 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I17 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I18 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I19 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I20 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I21 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I22 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I23 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I24 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I25 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I26 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I27 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I28 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I29 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I30 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I31 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I32 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I33 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I34 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I35 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I36 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I37 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I38 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I39 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I40 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I41 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I42 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I43 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I44 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I45 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I46 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I47 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I48 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I49 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I50 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I51 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I52 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I53 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I54 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I55 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I56 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I57 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I58 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I59 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I60 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I61 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I62 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I63 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I64 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I65 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I66 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I67 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I68 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I69 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I70 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I71 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I72 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I73 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I74 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I75 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I76 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I77 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I78 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I79 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | S51 | CTS2 | EventMaskLo | UINT32 | RW | 0...4294967295
54 | S52 | CTS2 | EventMaskHi | UINT32 | RW | 0...4294967295
53 | S1 | VTS1 | VTS [60] mode | UINT32 | RW | 0=Disabled;1=Activated
53 | V1 | VTS1 | VTS condition | UINT32 | R | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
53 | V2 | VTS1 | Bus voltages | UINT32 | R | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
53 | I1 | VTS1 | VTS Starts | UINT32 | R | 0...4294967295
53 | I2 | VTS1 | Line fuse fails | UINT32 | R | 0...4294967295
53 | I3 | VTS1 | Bus fuse fails | UINT32 | R | 0...4294967295
53 | I4 | VTS1 | VTS Blocks | UINT32 | R | 0...4294967295
53 | S2 | VTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
53 | S3 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S4 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S5 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S6 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S7 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S8 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S9 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S10 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S11 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S12 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S13 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S14 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S15 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S16 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S17 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S18 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S19 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S20 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S21 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S22 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S23 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S24 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S25 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S26 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S27 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S28 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S29 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S30 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S31 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S32 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S33 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S34 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S35 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S36 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S37 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S38 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S39 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S40 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S41 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S42 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S43 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S44 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S45 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S46 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S47 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S48 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S49 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S50 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | O1 | VTS1 | VTS Start | SIGNAL_OUT | RW | 0...4294967295
53 | O2 | VTS1 | VTS Fail Alarm Bus | SIGNAL_OUT | RW | 0...4294967295
53 | O3 | VTS1 | VTS Fail Alarm Line | SIGNAL_OUT | RW | 0...4294967295
53 | O4 | VTS1 | VTS Blocked(time delay) | SIGNAL_OUT | RW | 0...4294967295
53 | I5 | VTS1 | Newest Register | UINT32 | R | 0...12
53 | I6 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I7 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I8 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I9 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I10 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I11 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I12 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I13 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I14 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I15 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I16 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I17 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I18 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I19 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I20 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I21 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I22 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I23 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I24 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I25 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I26 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I27 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I28 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I29 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I30 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I31 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I32 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I33 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I34 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I35 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I36 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I37 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I38 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I39 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I40 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I41 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I42 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I43 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I44 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I45 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I46 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I47 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I48 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I49 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I50 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I51 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I52 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I53 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I54 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I55 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I56 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I57 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I58 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I59 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I60 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I61 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I62 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I63 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I64 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I65 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | S51 | VTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
53 | S52 | VTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
43 | S1 | FLX1 | Fault locator mode | UINT32 | RW | 0=Disabled;1=Activated
43 | V1 | FLX1 | Fault locator condition | UINT32 | R | 0=Idle;1=Triggered;2=Calc ready
43 | I1 | FLX1 | Times Flocator triggered | UINT32 | R | 0...4294967295
43 | I2 | FLX1 | Last fault reactance | FLOAT | R | -1800...1800
43 | I3 | FLX1 | Last fault distance | FLOAT | R | -1800...1800
43 | V2 | FLX1 | Last fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I4 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I5 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I6 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | I7 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I8 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I9 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | V3 | FLX1 | Last fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | S2 | FLX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
43 | S3 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S4 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S5 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S6 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S7 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S8 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S9 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S10 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S11 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S12 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S13 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S14 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S15 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S16 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S17 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S18 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | I10 | FLX1 | Newest Register | UINT32 | R | 0...12
43 | I11 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I12 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I13 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I14 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I15 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I16 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I17 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I18 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I19 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I20 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I21 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I22 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I23 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I24 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I25 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I26 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I27 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I28 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I29 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I30 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I31 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I32 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I33 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I34 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I35 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I36 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I37 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I38 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I39 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I40 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I41 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I42 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I43 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I44 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I45 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I46 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I47 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I48 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I49 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I50 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I51 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I52 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I53 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I54 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I55 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I56 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I57 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I58 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I59 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I60 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I61 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I62 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I63 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I64 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I65 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I66 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I67 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I68 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I69 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I70 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I71 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I72 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I73 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I74 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I75 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I76 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I77 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I78 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I79 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I80 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I81 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I82 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I83 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I84 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I85 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I86 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I87 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I88 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I89 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I90 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I91 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I92 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I93 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I94 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I95 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I96 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I97 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I98 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I99 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I100 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I101 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I102 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I103 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I104 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I105 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I106 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I107 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I108 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I109 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I110 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I111 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I112 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I113 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I114 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I115 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I116 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I117 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I118 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I119 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I120 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I121 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I122 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I123 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I124 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I125 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I126 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I127 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I128 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I129 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I130 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | S19 | FLX1 | EventMaskLo | UINT32 | RW | 0...4294967295
55 | S1 | THD1 | THD mode | UINT32 | RW | 0=Disabled;1=Activated
55 | V1 | THD1 | THD condition | UINT32 | R | 0=Normal;1=Start;2=Alarm;3=Blocked
55 | S2 | THD1 | Measurement magnitude | UINT32 | RW | 0=Amplitude;1=Power
55 | I1 | THD1 | THD starts | UINT32 | R | 0...4294967295
55 | I2 | THD1 | THD alarms | UINT32 | R | 0...4294967295
55 | I3 | THD1 | THD blocks | UINT32 | R | 0...4294967295
55 | S3 | THD1 | Clear statistics | UINT32 | W | 0=-;1=Clear
55 | S4 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S5 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S6 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S7 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S8 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S9 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S10 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S11 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S12 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S13 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S14 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S15 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S16 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S17 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S18 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S19 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S20 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S21 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S22 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S23 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S24 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S25 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S26 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S27 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S28 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S29 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S30 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S31 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S32 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S33 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S34 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S35 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S36 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S37 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S38 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S39 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S40 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S41 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S42 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S43 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S44 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S45 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S46 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S47 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S48 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S49 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S50 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S51 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S52 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S53 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S54 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S55 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S56 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S57 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S58 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S59 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S60 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S61 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S62 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S63 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S64 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S65 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S66 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S67 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S68 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S69 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S70 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S71 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S72 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S73 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S74 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S75 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | O1 | THD1 | THDPH> START | SIGNAL_OUT | RW | 0...4294967295
55 | O2 | THD1 | THDPH> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O3 | THD1 | THDI01> START | SIGNAL_OUT | RW | 0...4294967295
55 | O4 | THD1 | THDI01> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O5 | THD1 | THDI02> START | SIGNAL_OUT | RW | 0...4294967295
55 | O6 | THD1 | THDI02> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O7 | THD1 | THD> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
55 | I4 | THD1 | Newest Register | UINT32 | R | 0...12
55 | I5 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I6 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I7 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I8 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I9 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I10 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I11 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I12 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I13 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I14 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I15 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I16 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I17 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I18 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I19 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I20 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I21 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I22 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I23 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I24 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I25 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I26 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I27 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I28 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I29 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I30 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I31 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I32 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I33 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I34 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I35 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I36 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I37 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I38 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I39 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I40 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | S76 | THD1 | EventMaskLo | UINT32 | RW | 0...4294967295
58 | S1 | CBW1 | CBW mode | UINT32 | RW | 0=Disabled;1=Activated
58 | V1 | CBW1 | CBW condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On
58 | I1 | CBW1 | Breaker operations | UINT32 | R | 0...4294967295
58 | I2 | CBW1 | Alarm 1 counter | UINT32 | R | 0...4294967295
58 | I3 | CBW1 | Alarm 2 counter | UINT32 | R | 0...4294967295
58 | I4 | CBW1 | L1 Operations Left | FLOAT | R | 0...4294967295
58 | I5 | CBW1 | L2 Operations Left | FLOAT | R | 0...4294967295
58 | I6 | CBW1 | L3 Operations Left | FLOAT | R | 0...4294967295
58 | S2 | CBW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
58 | S3 | CBW1 | Alarm 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S4 | CBW1 | Alarm 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S5 | CBW1 | Alarm 1 Set | UINT32 | RW | 0...200000
58 | S6 | CBW1 | Alarm 2 Set | UINT32 | RW | 0...200000
58 | S7 | CBW1 | Operations 1 | FLOAT | RW | 0...200000
58 | S8 | CBW1 | Operations 2 | FLOAT | RW | 0...200000
58 | S9 | CBW1 | Current 1 | FLOAT | RW | 0...100
58 | S10 | CBW1 | Current 2 | FLOAT | RW | 0...100
58 | O1 | CBW1 | CBW Alarm 1 act | SIGNAL_OUT | RW | 0...4294967295
58 | I7 | CBW1 | Newest Register | UINT32 | R | 0...12
58 | I8 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I9 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I10 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I11 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I12 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I13 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I14 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I15 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I16 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I17 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I18 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I19 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I20 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I21 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I22 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I23 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I24 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I25 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I26 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I27 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I28 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I29 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I30 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I31 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I32 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I33 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I34 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I35 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I36 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I37 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I38 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I39 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I40 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I41 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I42 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I43 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | S11 | CBW1 | EventMaskLo | UINT32 | RW | 0...4294967295
97 | S1 | NJK1 | U0> RECL [79] mode | UINT32 | RW | 0=Disabled;1=Activated
97 | V1 | NJK1 | U0> RECL condition | UINT32 | R | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
97 | I1 | NJK1 | Requests | UINT32 | R | 0...4294967295
97 | I2 | NJK1 | Blocks | UINT32 | R | 0...4294967295
97 | I3 | NJK1 | Starts | UINT32 | R | 0...4294967295
97 | I4 | NJK1 | Breaker closes | UINT32 | R | 0...4294967295
97 | S2 | NJK1 | Clear statistics | UINT32 | W | 0=-;1=Clear
97 | S3 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S4 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S5 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S6 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S7 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S8 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S9 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S10 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | O1 | NJK1 | U0> RECL Blocked | SIGNAL_OUT | RW | 0...4294967295
97 | O2 | NJK1 | U0> RECL Active | SIGNAL_OUT | RW | 0...4294967295
97 | O3 | NJK1 | U0> RECL CLOSE | SIGNAL_OUT | RW | 0...4294967295
97 | O4 | NJK1 | U0> RECL BLKU0 | SIGNAL_OUT | RW | 0...4294967295
97 | I5 | NJK1 | Newest Register | UINT32 | R | 0...12
97 | I6 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I7 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I8 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I9 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I10 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I11 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I12 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I13 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I14 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I15 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I16 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I17 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I18 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I19 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I20 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I21 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I22 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I23 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I24 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I25 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I26 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I27 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I28 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I29 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | S11 | NJK1 | EventMaskLo | UINT32 | RW | 0...4294967295
61 | S1 | SOF1 | SOTF mode | UINT32 | RW | 0=Disabled;1=Activated
61 | V1 | SOF1 | SOTF condition | UINT32 | R | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
61 | I1 | SOF1 | Inits | UINT32 | R | 0...4294967295
61 | I2 | SOF1 | Starts | UINT32 | R | 0...4294967295
61 | I3 | SOF1 | Trips | UINT32 | R | 0...4294967295
61 | I4 | SOF1 | Blocks | UINT32 | R | 0...4294967295
61 | S2 | SOF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
61 | S3 | SOF1 | SG in use | UINT32 | RW | 0...255
61 | S4 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S5 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S6 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S7 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S8 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S9 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S10 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S11 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | O1 | SOF1 | SOTF Blocked | SIGNAL_OUT | RW | 0...4294967295
61 | O2 | SOF1 | SOTF Active | SIGNAL_OUT | RW | 0...4294967295
61 | O3 | SOF1 | SOTF Trip | SIGNAL_OUT | RW | 0...4294967295
61 | I5 | SOF1 | Newest Register | UINT32 | R | 0...12
61 | I6 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I7 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I8 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I9 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I10 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I11 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I12 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I13 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I14 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I15 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I16 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I17 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I18 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I19 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I20 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I21 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I22 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I23 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I24 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I25 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I26 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I27 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I28 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I29 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | S12 | SOF1 | EventMaskLo | UINT32 | RW | 0...4294967295
142 | S1 | DOS1 | Energy dose counter mode | UINT32 | RW | 0=Disabled;1=Activated
142 | S2 | DOS1 | Clear pulsecounters | UINT32 | W | 0=-;1=Clear
142 | S3 | DOS1 | DC 1 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S4 | DOS1 | DC 1 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I1 | DOS1 | DC 1 Input signal | FLOAT | R | -1000000...1000000
142 | S5 | DOS1 | DC 1 Pulse magnitude | FLOAT | RW | 0...1800
142 | S6 | DOS1 | DC 1 Pulse Lenght | FLOAT | RW | 0...1800
142 | I2 | DOS1 | DC 1 Pulses sent | UINT32 | R | 0...4294967295
142 | S7 | DOS1 | DC 2 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S8 | DOS1 | DC 2 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I3 | DOS1 | DC 2 Input signal | FLOAT | R | -1000000...1000000
142 | S9 | DOS1 | DC 2 Pulse magnitude | FLOAT | RW | 0...1800
142 | S10 | DOS1 | DC 2 Pulse Lenght | FLOAT | RW | 0...1800
142 | I4 | DOS1 | DC 2 Pulses sent | UINT32 | R | 0...4294967295
142 | S11 | DOS1 | DC 3 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S12 | DOS1 | DC 3 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I5 | DOS1 | DC 3 Input signal | FLOAT | R | -1000000...1000000
142 | S13 | DOS1 | DC 3 Pulse magnitude | FLOAT | RW | 0...1800
142 | S14 | DOS1 | DC 3 Pulse Lenght | FLOAT | RW | 0...1800
142 | I6 | DOS1 | DC 3 Pulses sent | UINT32 | R | 0...4294967295
142 | S15 | DOS1 | DC 4 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S16 | DOS1 | DC 4 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I7 | DOS1 | DC 4 Input signal | FLOAT | R | -1000000...1000000
142 | S17 | DOS1 | DC 4 Pulse magnitude | FLOAT | RW | 0...1800
142 | S18 | DOS1 | DC 4 Pulse Lenght | FLOAT | RW | 0...1800
142 | I8 | DOS1 | DC 4 Pulses sent | UINT32 | R | 0...4294967295
142 | O1 | DOS1 | DC 1 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O2 | DOS1 | DC 2 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O3 | DOS1 | DC 3 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O4 | DOS1 | DC 4 Pulse out | SIGNAL_OUT | RW | 0...4294967295
144 | V1 | PCS1 | PCS1 Switch Status | SIGNAL_OUT | RW | 0...4294967295
145 | V1 | PCS2 | PCS2 Switch Status | SIGNAL_OUT | RW | 0...4294967295
146 | V1 | PCS3 | PCS3 Switch Status | SIGNAL_OUT | RW | 0...4294967295
147 | V1 | PCS4 | PCS4 Switch Status | SIGNAL_OUT | RW | 0...4294967295
148 | V1 | PCS5 | PCS5 Switch Status | SIGNAL_OUT | RW | 0...4294967295
45 | S1 | SYN1 | Synchrocheck (SYN1,2,3) [25] mode | UINT32 | RW | 0=Disabled;1=Activated
45 | V1 | SYN1 | SYN1 Condition | UINT32 | R | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok
45 | V2 | SYN1 | SYN2 Condition | UINT32 | R | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok
45 | V3 | SYN1 | SYN3 Condition | UINT32 | R | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok
45 | I1 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I2 | SYN1 | SYN1 Mag diff | FLOAT | R | -120...120
45 | I3 | SYN1 | SYN1 Ang diff | FLOAT | R | -360...360
45 | I4 | SYN1 | SYN1 freq diff | FLOAT | R | -75...75
45 | I5 | SYN1 | SYN1 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S2 | SYN1 | Estimated BRK Closing time | FLOAT | R | 0...360
45 | S3 | SYN1 | Networks rotating time | FLOAT | R | 0...360
45 | S4 | SYN1 | Networks placement atm | FLOAT | R | -360...360
45 | I6 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I7 | SYN1 | SYN2 Mag diff | FLOAT | R | -120...120
45 | I8 | SYN1 | SYN2 Ang diff | FLOAT | R | -360...360
45 | I9 | SYN1 | SYN2 freq diff | FLOAT | R | -75...75
45 | I10 | SYN1 | SYN2 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S5 | SYN1 | SYN2 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S6 | SYN1 | SYN2 Networks rotating time | FLOAT | R | 0...360.000
45 | S7 | SYN1 | SYN2 Networks placement atm | FLOAT | R | -360.000...360.000
45 | I11 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I12 | SYN1 | SYN3 Mag diff | FLOAT | R | -120...120
45 | I13 | SYN1 | SYN3 Ang diff | FLOAT | R | -360...360
45 | I14 | SYN1 | SYN3 freq diff | FLOAT | R | -75...75
45 | I15 | SYN1 | SYN3 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S8 | SYN1 | SYN3 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S9 | SYN1 | SYN3 Networks rotating time | FLOAT | R | 0...360.000
45 | S10 | SYN1 | SYN3 Networks placement atm | FLOAT | R | -360.000...360.000
45 | S11 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S12 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S13 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S14 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S15 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S16 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S17 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S18 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S19 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S20 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S21 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S22 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S23 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S24 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S25 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S26 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S27 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S28 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S29 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S30 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S31 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S32 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S33 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S34 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S35 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S36 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S37 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S38 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S39 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S40 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S41 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S42 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S43 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S44 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S45 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S46 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S47 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S48 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S49 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S50 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S51 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S52 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S53 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S54 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S55 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S56 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S57 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S58 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S59 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S60 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S61 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S62 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S63 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S64 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S65 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S66 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S67 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S68 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S69 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S70 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S71 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S72 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S73 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S74 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S75 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S76 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S77 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S78 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S79 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S80 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S81 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S82 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S83 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S84 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S85 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S86 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S87 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S88 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S89 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S90 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S91 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S92 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S93 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S94 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S95 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S96 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S97 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S98 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S99 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S100 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S101 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S102 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S103 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S104 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S105 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S106 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S107 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S108 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S109 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S110 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S111 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S112 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S113 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S114 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S115 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S116 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S117 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S118 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S119 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S120 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S121 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S122 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S123 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S124 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S125 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S126 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S127 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S128 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S129 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S130 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S131 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S132 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S133 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S134 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S135 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S136 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S137 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S138 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S139 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S140 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S141 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S142 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S143 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S144 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S145 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S146 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S147 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S148 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S149 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S150 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S151 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S152 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S153 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S154 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S155 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S156 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S157 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S158 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S159 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S160 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S161 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S162 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S163 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S164 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S165 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S166 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S167 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S168 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S169 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S170 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S171 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S172 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S173 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S174 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S175 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S176 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S177 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S178 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S179 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S180 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S181 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S182 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S183 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S184 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S185 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S186 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S187 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S188 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S189 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S190 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S191 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S192 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S193 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S194 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S195 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S196 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S197 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S198 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S199 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S200 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S201 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S202 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S203 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S204 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S205 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S206 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S207 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S208 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S209 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S210 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S211 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S212 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S213 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S214 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S215 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S216 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S217 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S218 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S219 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S220 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S221 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S222 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S223 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S224 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S225 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S226 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S227 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S228 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S229 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S230 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S231 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S232 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S233 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S234 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S235 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S236 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S237 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S238 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S239 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S240 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S241 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S242 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S243 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S244 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S245 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S246 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S247 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S248 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S249 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S250 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S251 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S252 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S253 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S254 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S255 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S256 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S257 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S258 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S259 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S260 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S261 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S262 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S263 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S264 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S265 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S266 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S267 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S268 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S269 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S270 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S271 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S272 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S273 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S274 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | O1 | SYN1 | SYN1 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O2 | SYN1 | SYN1 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O3 | SYN1 | SYN1 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O4 | SYN1 | SYN1 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O5 | SYN1 | SYN1 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O6 | SYN1 | SYN1 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O7 | SYN1 | SYN1 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O8 | SYN1 | SYN1 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O9 | SYN1 | SYN1 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O10 | SYN1 | SYN1 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O11 | SYN1 | SYN1 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O12 | SYN1 | SYN1 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O13 | SYN1 | SYN1 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O14 | SYN1 | SYN1 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O15 | SYN1 | SYN1 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O16 | SYN1 | SYN1 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O17 | SYN1 | SYN1 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O18 | SYN1 | SYN1 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O19 | SYN1 | SYN1 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O20 | SYN1 | SYN1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O21 | SYN1 | SYN2 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O22 | SYN1 | SYN2 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O23 | SYN1 | SYN2 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O24 | SYN1 | SYN2 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O25 | SYN1 | SYN2 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O26 | SYN1 | SYN2 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O27 | SYN1 | SYN2 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O28 | SYN1 | SYN2 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O29 | SYN1 | SYN2 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O30 | SYN1 | SYN2 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O31 | SYN1 | SYN2 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O32 | SYN1 | SYN2 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O33 | SYN1 | SYN2 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O34 | SYN1 | SYN2 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O35 | SYN1 | SYN2 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O36 | SYN1 | SYN2 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O37 | SYN1 | SYN2 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O38 | SYN1 | SYN2 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O39 | SYN1 | SYN2 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O40 | SYN1 | SYN2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O41 | SYN1 | SYN3 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O42 | SYN1 | SYN3 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O43 | SYN1 | SYN3 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O44 | SYN1 | SYN3 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O45 | SYN1 | SYN3 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O46 | SYN1 | SYN3 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O47 | SYN1 | SYN3 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O48 | SYN1 | SYN3 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O49 | SYN1 | SYN3 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O50 | SYN1 | SYN3 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O51 | SYN1 | SYN3 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O52 | SYN1 | SYN3 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O53 | SYN1 | SYN3 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O54 | SYN1 | SYN3 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O55 | SYN1 | SYN3 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O56 | SYN1 | SYN3 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O57 | SYN1 | SYN3 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O58 | SYN1 | SYN3 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O59 | SYN1 | SYN3 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O60 | SYN1 | SYN3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | I16 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I17 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I18 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I19 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I20 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I21 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I22 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I23 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I24 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I25 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I26 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I27 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I28 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I29 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I30 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I31 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I32 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I33 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I34 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I35 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I36 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I37 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I38 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I39 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I40 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I41 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I42 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I43 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I44 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I45 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I46 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I47 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I48 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I49 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I50 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I51 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I52 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I53 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I54 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I55 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I56 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I57 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I58 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I59 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I60 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I61 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I62 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I63 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I64 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I65 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I66 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I67 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I68 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I69 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I70 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I71 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I72 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I73 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I74 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I75 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I76 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I77 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I78 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I79 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I80 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I81 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I82 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I83 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I84 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I85 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I86 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I87 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I88 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I89 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I90 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I91 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I92 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I93 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I94 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I95 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I96 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I97 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I98 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I99 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I100 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I101 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I102 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I103 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I104 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I105 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I106 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I107 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I108 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I109 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I110 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I111 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I112 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I113 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I114 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I115 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I116 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I117 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I118 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I119 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I120 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I121 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I122 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I123 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I124 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I125 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I126 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I127 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I128 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I129 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I130 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I131 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I132 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I133 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I134 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I135 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I136 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I137 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I138 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I139 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I140 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I141 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I142 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I143 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I144 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I145 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I146 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I147 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I148 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I149 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I150 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I151 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I152 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I153 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I154 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I155 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I156 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I157 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I158 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I159 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I160 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I161 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I162 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I163 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I164 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I165 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I166 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I167 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I168 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I169 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I170 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I171 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I172 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I173 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I174 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I175 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I176 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I177 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I178 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I179 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I180 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I181 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I182 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I183 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I184 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I185 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I186 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I187 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I188 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I189 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I190 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I191 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I192 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I193 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I194 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I195 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I196 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I197 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I198 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I199 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I200 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I201 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I202 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I203 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I204 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I205 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I206 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I207 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I208 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I209 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I210 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I211 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I212 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I213 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I214 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I215 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I216 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I217 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I218 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I219 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I220 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I221 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I222 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I223 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I224 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I225 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I226 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I227 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I228 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I229 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I230 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I231 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I232 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I233 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I234 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I235 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I236 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I237 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I238 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I239 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I240 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I241 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I242 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I243 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I244 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I245 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I246 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I247 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I248 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I249 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I250 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I251 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I252 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I253 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I254 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I255 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I256 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I257 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I258 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I259 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I260 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I261 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I262 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I263 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I264 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I265 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I266 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I267 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I268 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I269 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I270 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I271 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I272 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I273 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I274 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I275 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I276 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I277 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I278 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I279 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I280 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I281 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I282 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I283 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I284 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I285 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I286 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I287 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I288 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I289 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I290 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I291 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I292 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I293 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I294 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I295 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I296 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I297 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I298 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I299 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I300 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I301 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I302 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I303 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I304 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I305 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I306 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I307 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I308 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I309 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I310 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I311 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I312 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I313 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I314 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I315 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I316 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I317 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I318 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I319 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I320 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I321 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I322 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I323 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I324 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I325 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I326 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I327 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I328 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I329 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I330 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I331 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I332 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I333 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I334 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I335 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I336 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I337 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I338 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I339 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I340 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I341 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I342 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I343 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I344 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I345 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I346 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I347 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I348 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I349 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I350 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I351 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I352 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I353 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I354 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I355 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I356 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I357 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I358 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I359 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I360 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I361 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I362 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I363 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I364 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I365 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I366 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I367 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I368 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I369 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I370 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I371 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I372 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I373 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I374 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I375 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I376 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I377 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I378 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | S275 | SYN1 | EventMaskLo | UINT32 | RW | 0...4294967295
45 | S276 | SYN1 | EventMaskHi | UINT32 | RW | 0...4294967295
219 | S1 | SYNX1 | SYN1 Extra EventMaskLo | UINT32 | RW | 0...4294967295
219 | S2 | SYNX1 | SYN1 Extra EventMaskHi | UINT32 | RW | 0...4294967295
220 | S1 | SYNX2 | SYN2 Extra EventMaskLo | UINT32 | RW | 0...4294967295
220 | S2 | SYNX2 | SYN2 Extra EventMaskHi | UINT32 | RW | 0...4294967295
221 | S1 | SYNX3 | SYN3 Extra EventMaskLo | UINT32 | RW | 0...4294967295
221 | S2 | SYNX3 | SYN3 Extra EventMaskHi | UINT32 | RW | 0...4294967295
155 | S1 | VJP1 | <DELTA><alpha> > mode | UINT32 | RW | 0=Disabled;1=Activated
155 | V1 | VJP1 | <DELTA><alpha> > condition | UINT32 | R | 0=Normal;1=Blocked:2=Trip;3=Alarm
155 | S2 | VJP1 | Available stages | UINT32 | RW | 0=Trip;1=Trip and Alarm
155 | S3 | VJP1 | Monitored voltages | UINT32 | RW | 0=System all P-P Voltages;1=System any P-P Voltage;2=System L12 Voltage;3=System L23 Voltage;4=System L31 Voltage;5=System all P-E voltages;6=System any P-E voltage;7=System L1 Voltage;8=System L2 Voltage;9=System L3 Voltage;10=U3 Voltage;11=U4 Voltage
155 | V2 | VJP1 | Voltage meas selected | UINT32 | R | 0=Selection Ok;1=Selection not available
155 | I1 | VJP1 | <DELTA><alpha> > U1 Angle difference | FLOAT | R | -360...360
155 | I2 | VJP1 | <DELTA><alpha> U1meas/Set | FLOAT | R | -360...360
155 | I3 | VJP1 | <DELTA><alpha> U2 Angle difference | FLOAT | R | -360...360
155 | I4 | VJP1 | <DELTA><alpha> U2meas/Set | FLOAT | R | -360...360
155 | I5 | VJP1 | <DELTA><alpha> U3 Angle difference | FLOAT | R | -360...360
155 | I6 | VJP1 | <DELTA><alpha> U3meas/Set | FLOAT | R | -360...360
155 | I7 | VJP1 | <DELTA><alpha> > Alarms | UINT32 | R | 0...4294967295
155 | I8 | VJP1 | <DELTA><alpha> > Trips | UINT32 | R | 0...4294967295
155 | I9 | VJP1 | <DELTA><alpha> > Blocks | UINT32 | R | 0...4294967295
155 | S4 | VJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
155 | S5 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S6 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S7 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S8 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S9 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S10 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S11 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S12 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S13 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S14 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S15 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S16 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S17 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S18 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S19 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S20 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S21 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S22 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S23 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S24 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S25 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S26 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S27 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S28 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | O1 | VJP1 | <DELTA><alpha> > TRIP | SIGNAL_OUT | RW | 0...4294967295
155 | O2 | VJP1 | <DELTA><alpha> > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
155 | I10 | VJP1 | Newest Register | UINT32 | R | 0...12
155 | I11 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I12 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I13 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I14 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I15 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I16 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I17 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I18 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I19 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I20 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I21 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I22 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I23 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I24 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I25 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I26 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I27 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I28 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I29 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I30 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I31 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I32 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I33 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I34 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I35 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I36 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I37 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I38 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I39 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I40 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I41 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I42 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I43 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I44 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I45 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I46 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | S29 | VJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S1 | OBJ1 | Object1 mode | UINT32 | RW | 0=Disabled;1=Activated
46 | I1 | OBJ1 | Object1 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I2 | OBJ1 | Object1 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
46 | I3 | OBJ1 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | S2 | OBJ1 | Breaker traverse time | FLOAT | RW | 0.02...500
46 | S3 | OBJ1 | WD Cart traverse time | FLOAT | RW | 0.02...500
46 | S4 | OBJ1 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
46 | S5 | OBJ1 | Sync wait timeout | FLOAT | RW | 0.02...500
46 | S6 | OBJ1 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
46 | S7 | OBJ1 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
46 | S8 | OBJ1 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
46 | S9 | OBJ1 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
46 | S10 | OBJ1 | Control Termination Timeout | FLOAT | RW | 0.02...500
46 | O1 | OBJ1 | Object1 Status Open | SIGNAL_OUT | RW | 0...4294967295
46 | O2 | OBJ1 | Object1 Status Closed | SIGNAL_OUT | RW | 0...4294967295
46 | O3 | OBJ1 | Object1 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
46 | O4 | OBJ1 | Object1 Status Bad | SIGNAL_OUT | RW | 0...4294967295
46 | O5 | OBJ1 | Object1 Open Command | SIGNAL_OUT | RW | 0...4294967295
46 | O6 | OBJ1 | Object1 Close Command | SIGNAL_OUT | RW | 0...4294967295
46 | O7 | OBJ1 | Object1 Open Request | SIGNAL_OUT | RW | 0...4294967295
46 | O8 | OBJ1 | Object1 Close Request | SIGNAL_OUT | RW | 0...4294967295
46 | O9 | OBJ1 | Object1 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
46 | O10 | OBJ1 | Object1 No sync wait | SIGNAL_OUT | RW | 0...4294967295
46 | O11 | OBJ1 | Object1 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
46 | O12 | OBJ1 | Object1 No sync fail | SIGNAL_OUT | RW | 0...4294967295
46 | O13 | OBJ1 | Object1 Open timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O14 | OBJ1 | Object1 Close timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O15 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O16 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O17 | OBJ1 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
46 | S11 | OBJ1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S12 | OBJ1 | EventMaskHi | UINT32 | RW | 0...4294967295
46 | I4 | OBJ1 | Newest Register | UINT32 | R | 0...12
46 | I5 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I6 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I7 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I8 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I9 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I10 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I11 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I12 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I13 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I14 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I15 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I16 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I17 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I18 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I19 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I20 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I21 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I22 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I23 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I24 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I25 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I26 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I27 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I28 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I29 | OBJ1 | Open requests | UINT32 | R | 0...4294967295
46 | I30 | OBJ1 | Close requests | UINT32 | R | 0...4294967295
46 | I31 | OBJ1 | Open requests failed | UINT32 | R | 0...4294967295
46 | I32 | OBJ1 | Close requests failed | UINT32 | R | 0...4294967295
46 | S13 | OBJ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
47 | S1 | OBJ2 | Object2 mode | UINT32 | RW | 0=Disabled;1=Activated
47 | I1 | OBJ2 | Object2 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I2 | OBJ2 | Object2 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
47 | I3 | OBJ2 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | S2 | OBJ2 | Breaker traverse time | FLOAT | RW | 0.02...500
47 | S3 | OBJ2 | WD Cart traverse time | FLOAT | RW | 0.02...500
47 | S4 | OBJ2 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
47 | S5 | OBJ2 | Sync wait timeout | FLOAT | RW | 0.02...500
47 | S6 | OBJ2 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
47 | S7 | OBJ2 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
47 | S8 | OBJ2 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
47 | S9 | OBJ2 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
47 | S10 | OBJ2 | Control Termination Timeout | FLOAT | RW | 0.02...500
47 | O1 | OBJ2 | Object2 Status Open | SIGNAL_OUT | RW | 0...4294967295
47 | O2 | OBJ2 | Object2 Status Closed | SIGNAL_OUT | RW | 0...4294967295
47 | O3 | OBJ2 | Object2 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
47 | O4 | OBJ2 | Object2 Status Bad | SIGNAL_OUT | RW | 0...4294967295
47 | O5 | OBJ2 | Object2 Open Command | SIGNAL_OUT | RW | 0...4294967295
47 | O6 | OBJ2 | Object2 Close Command | SIGNAL_OUT | RW | 0...4294967295
47 | O7 | OBJ2 | Object2 Open Request | SIGNAL_OUT | RW | 0...4294967295
47 | O8 | OBJ2 | Object2 Close Request | SIGNAL_OUT | RW | 0...4294967295
47 | O9 | OBJ2 | Object2 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
47 | O10 | OBJ2 | Object2 No sync wait | SIGNAL_OUT | RW | 0...4294967295
47 | O11 | OBJ2 | Object2 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
47 | O12 | OBJ2 | Object2 No sync fail | SIGNAL_OUT | RW | 0...4294967295
47 | O13 | OBJ2 | Object2 Open timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O14 | OBJ2 | Object2 Close timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O15 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O16 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O17 | OBJ2 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
47 | S11 | OBJ2 | EventMaskLo | UINT32 | RW | 0...4294967295
47 | S12 | OBJ2 | EventMaskHi | UINT32 | RW | 0...4294967295
47 | I4 | OBJ2 | Newest Register | UINT32 | R | 0...12
47 | I5 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I6 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I7 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I8 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I9 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I10 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I11 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I12 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I13 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I14 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I15 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I16 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I17 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I18 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I19 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I20 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I21 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I22 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I23 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I24 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I25 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I26 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I27 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I28 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I29 | OBJ2 | Open requests | UINT32 | R | 0...4294967295
47 | I30 | OBJ2 | Close requests | UINT32 | R | 0...4294967295
47 | I31 | OBJ2 | Open requests failed | UINT32 | R | 0...4294967295
47 | I32 | OBJ2 | Close requests failed | UINT32 | R | 0...4294967295
47 | S13 | OBJ2 | Clear statistics | UINT32 | W | 0=-;1=Clear
48 | S1 | OBJ3 | Object3 mode | UINT32 | RW | 0=Disabled;1=Activated
48 | I1 | OBJ3 | Object3 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I2 | OBJ3 | Object3 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
48 | I3 | OBJ3 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | S2 | OBJ3 | Breaker traverse time | FLOAT | RW | 0.02...500
48 | S3 | OBJ3 | WD Cart traverse time | FLOAT | RW | 0.02...500
48 | S4 | OBJ3 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
48 | S5 | OBJ3 | Sync wait timeout | FLOAT | RW | 0.02...500
48 | S6 | OBJ3 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
48 | S7 | OBJ3 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
48 | S8 | OBJ3 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
48 | S9 | OBJ3 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
48 | S10 | OBJ3 | Control Termination Timeout | FLOAT | RW | 0.02...500
48 | O1 | OBJ3 | Object3 Status Open | SIGNAL_OUT | RW | 0...4294967295
48 | O2 | OBJ3 | Object3 Status Closed | SIGNAL_OUT | RW | 0...4294967295
48 | O3 | OBJ3 | Object3 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
48 | O4 | OBJ3 | Object3 Status Bad | SIGNAL_OUT | RW | 0...4294967295
48 | O5 | OBJ3 | Object3 Open Command | SIGNAL_OUT | RW | 0...4294967295
48 | O6 | OBJ3 | Object3 Close Command | SIGNAL_OUT | RW | 0...4294967295
48 | O7 | OBJ3 | Object3 Open Request | SIGNAL_OUT | RW | 0...4294967295
48 | O8 | OBJ3 | Object3 Close Request | SIGNAL_OUT | RW | 0...4294967295
48 | O9 | OBJ3 | Object3 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
48 | O10 | OBJ3 | Object3 No sync wait | SIGNAL_OUT | RW | 0...4294967295
48 | O11 | OBJ3 | Object3 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
48 | O12 | OBJ3 | Object3 No sync fail | SIGNAL_OUT | RW | 0...4294967295
48 | O13 | OBJ3 | Object3 Open timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O14 | OBJ3 | Object3 Close timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O15 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O16 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O17 | OBJ3 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
48 | S11 | OBJ3 | EventMaskLo | UINT32 | RW | 0...4294967295
48 | S12 | OBJ3 | EventMaskHi | UINT32 | RW | 0...4294967295
48 | I4 | OBJ3 | Newest Register | UINT32 | R | 0...12
48 | I5 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I6 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I7 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I8 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I9 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I10 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I11 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I12 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I13 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I14 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I15 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I16 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I17 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I18 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I19 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I20 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I21 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I22 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I23 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I24 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I25 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I26 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I27 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I28 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I29 | OBJ3 | Open requests | UINT32 | R | 0...4294967295
48 | I30 | OBJ3 | Close requests | UINT32 | R | 0...4294967295
48 | I31 | OBJ3 | Open requests failed | UINT32 | R | 0...4294967295
48 | I32 | OBJ3 | Close requests failed | UINT32 | R | 0...4294967295
48 | S13 | OBJ3 | Clear statistics | UINT32 | W | 0=-;1=Clear
49 | S1 | OBJ4 | Object4 mode | UINT32 | RW | 0=Disabled;1=Activated
49 | I1 | OBJ4 | Object4 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I2 | OBJ4 | Object4 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
49 | I3 | OBJ4 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | S2 | OBJ4 | Breaker traverse time | FLOAT | RW | 0.02...500
49 | S3 | OBJ4 | WD Cart traverse time | FLOAT | RW | 0.02...500
49 | S4 | OBJ4 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
49 | S5 | OBJ4 | Sync wait timeout | FLOAT | RW | 0.02...500
49 | S6 | OBJ4 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
49 | S7 | OBJ4 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
49 | S8 | OBJ4 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
49 | S9 | OBJ4 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
49 | S10 | OBJ4 | Control Termination Timeout | FLOAT | RW | 0.02...500
49 | O1 | OBJ4 | Object4 Status Open | SIGNAL_OUT | RW | 0...4294967295
49 | O2 | OBJ4 | Object4 Status Closed | SIGNAL_OUT | RW | 0...4294967295
49 | O3 | OBJ4 | Object4 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
49 | O4 | OBJ4 | Object4 Status Bad | SIGNAL_OUT | RW | 0...4294967295
49 | O5 | OBJ4 | Object4 Open Command | SIGNAL_OUT | RW | 0...4294967295
49 | O6 | OBJ4 | Object4 Close Command | SIGNAL_OUT | RW | 0...4294967295
49 | O7 | OBJ4 | Object4 Open Request | SIGNAL_OUT | RW | 0...4294967295
49 | O8 | OBJ4 | Object4 Close Request | SIGNAL_OUT | RW | 0...4294967295
49 | O9 | OBJ4 | Object4 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
49 | O10 | OBJ4 | Object4 No sync wait | SIGNAL_OUT | RW | 0...4294967295
49 | O11 | OBJ4 | Object4 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
49 | O12 | OBJ4 | Object4 No sync fail | SIGNAL_OUT | RW | 0...4294967295
49 | O13 | OBJ4 | Object4 Open timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O14 | OBJ4 | Object4 Close timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O15 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O16 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O17 | OBJ4 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
49 | S11 | OBJ4 | EventMaskLo | UINT32 | RW | 0...4294967295
49 | S12 | OBJ4 | EventMaskHi | UINT32 | RW | 0...4294967295
49 | I4 | OBJ4 | Newest Register | UINT32 | R | 0...12
49 | I5 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I6 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I7 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I8 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I9 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I10 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I11 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I12 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I13 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I14 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I15 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I16 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I17 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I18 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I19 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I20 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I21 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I22 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I23 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I24 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I25 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I26 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I27 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I28 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I29 | OBJ4 | Open requests | UINT32 | R | 0...4294967295
49 | I30 | OBJ4 | Close requests | UINT32 | R | 0...4294967295
49 | I31 | OBJ4 | Open requests failed | UINT32 | R | 0...4294967295
49 | I32 | OBJ4 | Close requests failed | UINT32 | R | 0...4294967295
49 | S13 | OBJ4 | Clear statistics | UINT32 | W | 0=-;1=Clear
50 | S1 | OBJ5 | Object5 mode | UINT32 | RW | 0=Disabled;1=Activated
50 | I1 | OBJ5 | Object5 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I2 | OBJ5 | Object5 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
50 | I3 | OBJ5 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | S2 | OBJ5 | Breaker traverse time | FLOAT | RW | 0.02...500
50 | S3 | OBJ5 | WD Cart traverse time | FLOAT | RW | 0.02...500
50 | S4 | OBJ5 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
50 | S5 | OBJ5 | Sync wait timeout | FLOAT | RW | 0.02...500
50 | S6 | OBJ5 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
50 | S7 | OBJ5 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
50 | S8 | OBJ5 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
50 | S9 | OBJ5 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
50 | S10 | OBJ5 | Control Termination Timeout | FLOAT | RW | 0.02...500
50 | O1 | OBJ5 | Object5 Status Open | SIGNAL_OUT | RW | 0...4294967295
50 | O2 | OBJ5 | Object5 Status Closed | SIGNAL_OUT | RW | 0...4294967295
50 | O3 | OBJ5 | Object5 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
50 | O4 | OBJ5 | Object5 Status Bad | SIGNAL_OUT | RW | 0...4294967295
50 | O5 | OBJ5 | Object5 Open Command | SIGNAL_OUT | RW | 0...4294967295
50 | O6 | OBJ5 | Object5 Close Command | SIGNAL_OUT | RW | 0...4294967295
50 | O7 | OBJ5 | Object5 Open Request | SIGNAL_OUT | RW | 0...4294967295
50 | O8 | OBJ5 | Object5 Close Request | SIGNAL_OUT | RW | 0...4294967295
50 | O9 | OBJ5 | Object5 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
50 | O10 | OBJ5 | Object5 No sync wait | SIGNAL_OUT | RW | 0...4294967295
50 | O11 | OBJ5 | Object5 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
50 | O12 | OBJ5 | Object5 No sync fail | SIGNAL_OUT | RW | 0...4294967295
50 | O13 | OBJ5 | Object5 Open timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O14 | OBJ5 | Object5 Close timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O15 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O16 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O17 | OBJ5 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
50 | S11 | OBJ5 | EventMaskLo | UINT32 | RW | 0...4294967295
50 | S12 | OBJ5 | EventMaskHi | UINT32 | RW | 0...4294967295
50 | I4 | OBJ5 | Newest Register | UINT32 | R | 0...12
50 | I5 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I6 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I7 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I8 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I9 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I10 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I11 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I12 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I13 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I14 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I15 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I16 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I17 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I18 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I19 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I20 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I21 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I22 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I23 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I24 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I25 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I26 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I27 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I28 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I29 | OBJ5 | Open requests | UINT32 | R | 0...4294967295
50 | I30 | OBJ5 | Close requests | UINT32 | R | 0...4294967295
50 | I31 | OBJ5 | Open requests failed | UINT32 | R | 0...4294967295
50 | I32 | OBJ5 | Close requests failed | UINT32 | R | 0...4294967295
50 | S13 | OBJ5 | Clear statistics | UINT32 | W | 0=-;1=Clear
150 | S1 | OBJ6 | Object6 mode | UINT32 | RW | 0=Disabled;1=Activated
150 | I1 | OBJ6 | Object6 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I2 | OBJ6 | Object6 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
150 | I3 | OBJ6 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | S2 | OBJ6 | Breaker traverse time | FLOAT | RW | 0.02...500
150 | S3 | OBJ6 | WD Cart traverse time | FLOAT | RW | 0.02...500
150 | S4 | OBJ6 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
150 | S5 | OBJ6 | Sync wait timeout | FLOAT | RW | 0.02...500
150 | S6 | OBJ6 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
150 | S7 | OBJ6 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
150 | S8 | OBJ6 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
150 | S9 | OBJ6 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
150 | S10 | OBJ6 | Control Termination Timeout | FLOAT | RW | 0.02...500
150 | O1 | OBJ6 | Object6 Status Open | SIGNAL_OUT | RW | 0...4294967295
150 | O2 | OBJ6 | Object6 Status Closed | SIGNAL_OUT | RW | 0...4294967295
150 | O3 | OBJ6 | Object6 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
150 | O4 | OBJ6 | Object6 Status Bad | SIGNAL_OUT | RW | 0...4294967295
150 | O5 | OBJ6 | Object6 Open Command | SIGNAL_OUT | RW | 0...4294967295
150 | O6 | OBJ6 | Object6 Close Command | SIGNAL_OUT | RW | 0...4294967295
150 | O7 | OBJ6 | Object6 Open Request | SIGNAL_OUT | RW | 0...4294967295
150 | O8 | OBJ6 | Object6 Close Request | SIGNAL_OUT | RW | 0...4294967295
150 | O9 | OBJ6 | Object6 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
150 | O10 | OBJ6 | Object6 No sync wait | SIGNAL_OUT | RW | 0...4294967295
150 | O11 | OBJ6 | Object6 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
150 | O12 | OBJ6 | Object6 No sync fail | SIGNAL_OUT | RW | 0...4294967295
150 | O13 | OBJ6 | Object6 Open timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O14 | OBJ6 | Object6 Close timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O15 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O16 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O17 | OBJ6 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
150 | S11 | OBJ6 | EventMaskLo | UINT32 | RW | 0...4294967295
150 | S12 | OBJ6 | EventMaskHi | UINT32 | RW | 0...4294967295
150 | I4 | OBJ6 | Newest Register | UINT32 | R | 0...12
150 | I5 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I6 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I7 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I8 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I9 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I10 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I11 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I12 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I13 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I14 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I15 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I16 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I17 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I18 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I19 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I20 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I21 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I22 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I23 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I24 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I25 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I26 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I27 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I28 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I29 | OBJ6 | Open requests | UINT32 | R | 0...4294967295
150 | I30 | OBJ6 | Close requests | UINT32 | R | 0...4294967295
150 | I31 | OBJ6 | Open requests failed | UINT32 | R | 0...4294967295
150 | I32 | OBJ6 | Close requests failed | UINT32 | R | 0...4294967295
150 | S13 | OBJ6 | Clear statistics | UINT32 | W | 0=-;1=Clear
151 | S1 | OBJ7 | Object7 mode | UINT32 | RW | 0=Disabled;1=Activated
151 | I1 | OBJ7 | Object7 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I2 | OBJ7 | Object7 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
151 | I3 | OBJ7 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | S2 | OBJ7 | Breaker traverse time | FLOAT | RW | 0.02...500
151 | S3 | OBJ7 | WD Cart traverse time | FLOAT | RW | 0.02...500
151 | S4 | OBJ7 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
151 | S5 | OBJ7 | Sync wait timeout | FLOAT | RW | 0.02...500
151 | S6 | OBJ7 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
151 | S7 | OBJ7 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
151 | S8 | OBJ7 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
151 | S9 | OBJ7 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
151 | S10 | OBJ7 | Control Termination Timeout | FLOAT | RW | 0.02...500
151 | O1 | OBJ7 | Object7 Status Open | SIGNAL_OUT | RW | 0...4294967295
151 | O2 | OBJ7 | Object7 Status Closed | SIGNAL_OUT | RW | 0...4294967295
151 | O3 | OBJ7 | Object7 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
151 | O4 | OBJ7 | Object7 Status Bad | SIGNAL_OUT | RW | 0...4294967295
151 | O5 | OBJ7 | Object7 Open Command | SIGNAL_OUT | RW | 0...4294967295
151 | O6 | OBJ7 | Object7 Close Command | SIGNAL_OUT | RW | 0...4294967295
151 | O7 | OBJ7 | Object7 Open Request | SIGNAL_OUT | RW | 0...4294967295
151 | O8 | OBJ7 | Object7 Close Request | SIGNAL_OUT | RW | 0...4294967295
151 | O9 | OBJ7 | Object7 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
151 | O10 | OBJ7 | Object7 No sync wait | SIGNAL_OUT | RW | 0...4294967295
151 | O11 | OBJ7 | Object7 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
151 | O12 | OBJ7 | Object7 No sync fail | SIGNAL_OUT | RW | 0...4294967295
151 | O13 | OBJ7 | Object7 Open timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O14 | OBJ7 | Object7 Close timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O15 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O16 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O17 | OBJ7 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
151 | S11 | OBJ7 | EventMaskLo | UINT32 | RW | 0...4294967295
151 | S12 | OBJ7 | EventMaskHi | UINT32 | RW | 0...4294967295
151 | I4 | OBJ7 | Newest Register | UINT32 | R | 0...12
151 | I5 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I6 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I7 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I8 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I9 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I10 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I11 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I12 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I13 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I14 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I15 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I16 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I17 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I18 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I19 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I20 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I21 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I22 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I23 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I24 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I25 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I26 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I27 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I28 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I29 | OBJ7 | Open requests | UINT32 | R | 0...4294967295
151 | I30 | OBJ7 | Close requests | UINT32 | R | 0...4294967295
151 | I31 | OBJ7 | Open requests failed | UINT32 | R | 0...4294967295
151 | I32 | OBJ7 | Close requests failed | UINT32 | R | 0...4294967295
151 | S13 | OBJ7 | Clear statistics | UINT32 | W | 0=-;1=Clear
152 | S1 | OBJ8 | Object8 mode | UINT32 | RW | 0=Disabled;1=Activated
152 | I1 | OBJ8 | Object8 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I2 | OBJ8 | Object8 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
152 | I3 | OBJ8 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | S2 | OBJ8 | Breaker traverse time | FLOAT | RW | 0.02...500
152 | S3 | OBJ8 | WD Cart traverse time | FLOAT | RW | 0.02...500
152 | S4 | OBJ8 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
152 | S5 | OBJ8 | Sync wait timeout | FLOAT | RW | 0.02...500
152 | S6 | OBJ8 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
152 | S7 | OBJ8 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
152 | S8 | OBJ8 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
152 | S9 | OBJ8 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
152 | S10 | OBJ8 | Control Termination Timeout | FLOAT | RW | 0.02...500
152 | O1 | OBJ8 | Object8 Status Open | SIGNAL_OUT | RW | 0...4294967295
152 | O2 | OBJ8 | Object8 Status Closed | SIGNAL_OUT | RW | 0...4294967295
152 | O3 | OBJ8 | Object8 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
152 | O4 | OBJ8 | Object8 Status Bad | SIGNAL_OUT | RW | 0...4294967295
152 | O5 | OBJ8 | Object8 Open Command | SIGNAL_OUT | RW | 0...4294967295
152 | O6 | OBJ8 | Object8 Close Command | SIGNAL_OUT | RW | 0...4294967295
152 | O7 | OBJ8 | Object8 Open Request | SIGNAL_OUT | RW | 0...4294967295
152 | O8 | OBJ8 | Object8 Close Request | SIGNAL_OUT | RW | 0...4294967295
152 | O9 | OBJ8 | Object8 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
152 | O10 | OBJ8 | Object8 No sync wait | SIGNAL_OUT | RW | 0...4294967295
152 | O11 | OBJ8 | Object8 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
152 | O12 | OBJ8 | Object8 No sync fail | SIGNAL_OUT | RW | 0...4294967295
152 | O13 | OBJ8 | Object8 Open timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O14 | OBJ8 | Object8 Close timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O15 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O16 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O17 | OBJ8 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
152 | S11 | OBJ8 | EventMaskLo | UINT32 | RW | 0...4294967295
152 | S12 | OBJ8 | EventMaskHi | UINT32 | RW | 0...4294967295
152 | I4 | OBJ8 | Newest Register | UINT32 | R | 0...12
152 | I5 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I6 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I7 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I8 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I9 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I10 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I11 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I12 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I13 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I14 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I15 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I16 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I17 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I18 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I19 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I20 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I21 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I22 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I23 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I24 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I25 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I26 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I27 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I28 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I29 | OBJ8 | Open requests | UINT32 | R | 0...4294967295
152 | I30 | OBJ8 | Close requests | UINT32 | R | 0...4294967295
152 | I31 | OBJ8 | Open requests failed | UINT32 | R | 0...4294967295
152 | I32 | OBJ8 | Close requests failed | UINT32 | R | 0...4294967295
152 | S13 | OBJ8 | Clear statistics | UINT32 | W | 0=-;1=Clear
153 | S1 | OBJ9 | Object9 mode | UINT32 | RW | 0=Disabled;1=Activated
153 | I1 | OBJ9 | Object9 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I2 | OBJ9 | Object9 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
153 | I3 | OBJ9 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | S2 | OBJ9 | Breaker traverse time | FLOAT | RW | 0.02...500
153 | S3 | OBJ9 | WD Cart traverse time | FLOAT | RW | 0.02...500
153 | S4 | OBJ9 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
153 | S5 | OBJ9 | Sync wait timeout | FLOAT | RW | 0.02...500
153 | S6 | OBJ9 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
153 | S7 | OBJ9 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
153 | S8 | OBJ9 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
153 | S9 | OBJ9 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
153 | S10 | OBJ9 | Control Termination Timeout | FLOAT | RW | 0.02...500
153 | O1 | OBJ9 | Object9 Status Open | SIGNAL_OUT | RW | 0...4294967295
153 | O2 | OBJ9 | Object9 Status Closed | SIGNAL_OUT | RW | 0...4294967295
153 | O3 | OBJ9 | Object9 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
153 | O4 | OBJ9 | Object9 Status Bad | SIGNAL_OUT | RW | 0...4294967295
153 | O5 | OBJ9 | Object9 Open Command | SIGNAL_OUT | RW | 0...4294967295
153 | O6 | OBJ9 | Object9 Close Command | SIGNAL_OUT | RW | 0...4294967295
153 | O7 | OBJ9 | Object9 Open Request | SIGNAL_OUT | RW | 0...4294967295
153 | O8 | OBJ9 | Object9 Close Request | SIGNAL_OUT | RW | 0...4294967295
153 | O9 | OBJ9 | Object9 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
153 | O10 | OBJ9 | Object9 No sync wait | SIGNAL_OUT | RW | 0...4294967295
153 | O11 | OBJ9 | Object9 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
153 | O12 | OBJ9 | Object9 No sync fail | SIGNAL_OUT | RW | 0...4294967295
153 | O13 | OBJ9 | Object9 Open timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O14 | OBJ9 | Object9 Close timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O15 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O16 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O17 | OBJ9 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
153 | S11 | OBJ9 | EventMaskLo | UINT32 | RW | 0...4294967295
153 | S12 | OBJ9 | EventMaskHi | UINT32 | RW | 0...4294967295
153 | I4 | OBJ9 | Newest Register | UINT32 | R | 0...12
153 | I5 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I6 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I7 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I8 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I9 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I10 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I11 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I12 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I13 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I14 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I15 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I16 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I17 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I18 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I19 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I20 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I21 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I22 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I23 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I24 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I25 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I26 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I27 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I28 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I29 | OBJ9 | Open requests | UINT32 | R | 0...4294967295
153 | I30 | OBJ9 | Close requests | UINT32 | R | 0...4294967295
153 | I31 | OBJ9 | Open requests failed | UINT32 | R | 0...4294967295
153 | I32 | OBJ9 | Close requests failed | UINT32 | R | 0...4294967295
153 | S13 | OBJ9 | Clear statistics | UINT32 | W | 0=-;1=Clear
154 | S1 | OBJ10 | Object10 mode | UINT32 | RW | 0=Disabled;1=Activated
154 | I1 | OBJ10 | Object10 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I2 | OBJ10 | Object10 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
154 | I3 | OBJ10 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | S2 | OBJ10 | Breaker traverse time | FLOAT | RW | 0.02...500
154 | S3 | OBJ10 | WD Cart traverse time | FLOAT | RW | 0.02...500
154 | S4 | OBJ10 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
154 | S5 | OBJ10 | Sync wait timeout | FLOAT | RW | 0.02...500
154 | S6 | OBJ10 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
154 | S7 | OBJ10 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
154 | S8 | OBJ10 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
154 | S9 | OBJ10 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
154 | S10 | OBJ10 | Control Termination Timeout | FLOAT | RW | 0.02...500
154 | O1 | OBJ10 | Object10 Status Open | SIGNAL_OUT | RW | 0...4294967295
154 | O2 | OBJ10 | Object10 Status Closed | SIGNAL_OUT | RW | 0...4294967295
154 | O3 | OBJ10 | Object10 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
154 | O4 | OBJ10 | Object10 Status Bad | SIGNAL_OUT | RW | 0...4294967295
154 | O5 | OBJ10 | Object10 Open Command | SIGNAL_OUT | RW | 0...4294967295
154 | O6 | OBJ10 | Object10 Close Command | SIGNAL_OUT | RW | 0...4294967295
154 | O7 | OBJ10 | Object10 Open Request | SIGNAL_OUT | RW | 0...4294967295
154 | O8 | OBJ10 | Object10 Close Request | SIGNAL_OUT | RW | 0...4294967295
154 | O9 | OBJ10 | Object10 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
154 | O10 | OBJ10 | Object10 No sync wait | SIGNAL_OUT | RW | 0...4294967295
154 | O11 | OBJ10 | Object10 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
154 | O12 | OBJ10 | Object10 No sync fail | SIGNAL_OUT | RW | 0...4294967295
154 | O13 | OBJ10 | Object10 Open timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O14 | OBJ10 | Object10 Close timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O15 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O16 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O17 | OBJ10 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
154 | S11 | OBJ10 | EventMaskLo | UINT32 | RW | 0...4294967295
154 | S12 | OBJ10 | EventMaskHi | UINT32 | RW | 0...4294967295
154 | I4 | OBJ10 | Newest Register | UINT32 | R | 0...12
154 | I5 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I6 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I7 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I8 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I9 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I10 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I11 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I12 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I13 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I14 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I15 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I16 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I17 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I18 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I19 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I20 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I21 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I22 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I23 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I24 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I25 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I26 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I27 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I28 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I29 | OBJ10 | Open requests | UINT32 | R | 0...4294967295
154 | I30 | OBJ10 | Close requests | UINT32 | R | 0...4294967295
154 | I31 | OBJ10 | Open requests failed | UINT32 | R | 0...4294967295
154 | I32 | OBJ10 | Close requests failed | UINT32 | R | 0...4294967295
154 | S13 | OBJ10 | Clear statistics | UINT32 | W | 0=-;1=Clear
104 | S1 | CIN1 | Indicator 1 mode | UINT32 | RW | 0=Disabled;1=Activated
104 | S2 | CIN1 | Ind.1 traverse time | FLOAT | RW | 0.02...500
104 | I1 | CIN1 | Ind.1 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
105 | S1 | CIN2 | Indicator 2 mode | UINT32 | RW | 0=Disabled;1=Activated
105 | S2 | CIN2 | Ind.2 traverse time | FLOAT | RW | 0.02...500
105 | I1 | CIN2 | Ind.2 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
106 | S1 | CIN3 | Indicator 3 mode | UINT32 | RW | 0=Disabled;1=Activated
106 | S2 | CIN3 | Ind.3 traverse time | FLOAT | RW | 0.02...500
106 | I1 | CIN3 | Ind.3 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
107 | S1 | CIN4 | Indicator 4 mode | UINT32 | RW | 0=Disabled;1=Activated
107 | S2 | CIN4 | Ind.4 traverse time | FLOAT | RW | 0.02...500
107 | I1 | CIN4 | Ind.4 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
108 | S1 | CIN5 | Indicator 5 mode | UINT32 | RW | 0=Disabled;1=Activated
108 | S2 | CIN5 | Ind.5 traverse time | FLOAT | RW | 0.02...500
108 | I1 | CIN5 | Ind.5 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
63 | S1 | AR1 | Auto-recloser [79] Mode | UINT32 | RW | 0=Disabled;1=Activated
63 | V1 | AR1 | AR Status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear
63 | V2 | AR1 | Timer active | UINT32 | R | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
63 | I1 | AR1 | AR Timer value | FLOAT | R | 0...1800
63 | I2 | AR1 | AR Started | UINT32 | R | 0...4294967295
63 | I3 | AR1 | Shot 1 Started | UINT32 | R | 0...4294967295
63 | I4 | AR1 | Shot 2 Started | UINT32 | R | 0...4294967295
63 | I5 | AR1 | Shot 3 Started | UINT32 | R | 0...4294967295
63 | I6 | AR1 | Shot 4 Started | UINT32 | R | 0...4294967295
63 | I7 | AR1 | Shot 5 Started | UINT32 | R | 0...4294967295
63 | I8 | AR1 | Shot 1 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I9 | AR1 | Shot 2 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I10 | AR1 | Shot 3 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I11 | AR1 | Shot 4 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I12 | AR1 | Shot 5 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I13 | AR1 | Shot 1 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I14 | AR1 | Shot 2 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I15 | AR1 | Shot 3 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I16 | AR1 | Shot 4 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I17 | AR1 | Shot 5 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I18 | AR1 | Shot 1 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I19 | AR1 | Shot 2 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I20 | AR1 | Shot 3 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I21 | AR1 | Shot 4 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I22 | AR1 | Shot 5 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I23 | AR1 | Shot 1 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I24 | AR1 | Shot 2 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I25 | AR1 | Shot 3 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I26 | AR1 | Shot 4 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I27 | AR1 | Shot 5 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I28 | AR1 | Shot 1 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I29 | AR1 | Shot 2 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I30 | AR1 | Shot 3 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I31 | AR1 | Shot 4 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I32 | AR1 | Shot 5 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I33 | AR1 | Shots failed | UINT32 | R | 0...4294967295
63 | I34 | AR1 | Shots cleared | UINT32 | R | 0...4294967295
63 | I35 | AR1 | Final trips | UINT32 | R | 0...4294967295
63 | S2 | AR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
63 | S3 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S4 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S5 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S6 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S7 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S8 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S9 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S10 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S11 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S12 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S13 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S14 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S15 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S16 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S17 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S18 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S19 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S20 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S21 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S22 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S23 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S24 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S25 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S26 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S27 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S28 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S29 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S30 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S31 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S32 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S33 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S34 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S35 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S36 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S37 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S38 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S39 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S40 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S41 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S42 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S43 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S44 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S45 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S46 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S47 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S48 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S49 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S50 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S51 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S52 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S53 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S54 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S55 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S56 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S57 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S58 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S59 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S60 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S61 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S62 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S63 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S64 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S65 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S66 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S67 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S68 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S69 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S70 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S71 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S72 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S73 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S74 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S75 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S76 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S77 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S78 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S79 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S80 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S81 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S82 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S83 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S84 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S85 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S86 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S87 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S88 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S89 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S90 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S91 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S92 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S93 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S94 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S95 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S96 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S97 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S98 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S99 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S100 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S101 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S102 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S103 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S104 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S105 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S106 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S107 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S108 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S109 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S110 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S111 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S112 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S113 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S114 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S115 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S116 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S117 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S118 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S119 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S120 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S121 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S122 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S123 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S124 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S125 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S126 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S127 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S128 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S129 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S130 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S131 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S132 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S133 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S134 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S135 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S136 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S137 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S138 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S139 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S140 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S141 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S142 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S143 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S144 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S145 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S146 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S147 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S148 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S149 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S150 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S151 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S152 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S153 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S154 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S155 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S156 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S157 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S158 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S159 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S160 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S161 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S162 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S163 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S164 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S165 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S166 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S167 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S168 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S169 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S170 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S171 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S172 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S173 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S174 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S175 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S176 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S177 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S178 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S179 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S180 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S181 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S182 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S183 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S184 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S185 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S186 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S187 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S188 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S189 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S190 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S191 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S192 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S193 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S194 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S195 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S196 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S197 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S198 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S199 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S200 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S201 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S202 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S203 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S204 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S205 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S206 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S207 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S208 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S209 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S210 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S211 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S212 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S213 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S214 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S215 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S216 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S217 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S218 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S219 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S220 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S221 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S222 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S223 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S224 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S225 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S226 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S227 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S228 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S229 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S230 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S231 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S232 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S233 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S234 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S235 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S236 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S237 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S238 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S239 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S240 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S241 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S242 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S243 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S244 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S245 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S246 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S247 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S248 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S249 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S250 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S251 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S252 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S253 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S254 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S255 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S256 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S257 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S258 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S259 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S260 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S261 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S262 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S263 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S264 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S265 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S266 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S267 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S268 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S269 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S270 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S271 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S272 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S273 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S274 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S275 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S276 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S277 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S278 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S279 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S280 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S281 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S282 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S283 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S284 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S285 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S286 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S287 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S288 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S289 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S290 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S291 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S292 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S293 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S294 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S295 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S296 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S297 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S298 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S299 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S300 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S301 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S302 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S303 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S304 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S305 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S306 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S307 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S308 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S309 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S310 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S311 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S312 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S313 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S314 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S315 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S316 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S317 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S318 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S319 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S320 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S321 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S322 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S323 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S324 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S325 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S326 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S327 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S328 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S329 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S330 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S331 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S332 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S333 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S334 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S335 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S336 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S337 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S338 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S339 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S340 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S341 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S342 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S343 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S344 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S345 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S346 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S347 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S348 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S349 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S350 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S351 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S352 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S353 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S354 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S355 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S356 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S357 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S358 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S359 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S360 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S361 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S362 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S363 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S364 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S365 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S366 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S367 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S368 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S369 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S370 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S371 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S372 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S373 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S374 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S375 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S376 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S377 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S378 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S379 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S380 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S381 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S382 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S383 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S384 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S385 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S386 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S387 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S388 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S389 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S390 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S391 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S392 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S393 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S394 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S395 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S396 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S397 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S398 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S399 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S400 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S401 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S402 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S403 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S404 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S405 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S406 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S407 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S408 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S409 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S410 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S411 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S412 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S413 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S414 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S415 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S416 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S417 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S418 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S419 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S420 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S421 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S422 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S423 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S424 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S425 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S426 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S427 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S428 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S429 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S430 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S431 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S432 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S433 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S434 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S435 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S436 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S437 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S438 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S439 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S440 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S441 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S442 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S443 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S444 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S445 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S446 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S447 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S448 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S449 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S450 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S451 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S452 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S453 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S454 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S455 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S456 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S457 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S458 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S459 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S460 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S461 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S462 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S463 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S464 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S465 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S466 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S467 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S468 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S469 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S470 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S471 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S472 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S473 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S474 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S475 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S476 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S477 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S478 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S479 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S480 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S481 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S482 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S483 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S484 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S485 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S486 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S487 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S488 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S489 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S490 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S491 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S492 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S493 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S494 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S495 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S496 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S497 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S498 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S499 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S500 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S501 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S502 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S503 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S504 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S505 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S506 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S507 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S508 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S509 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S510 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S511 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S512 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S513 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S514 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S515 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S516 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S517 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S518 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S519 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S520 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S521 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S522 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S523 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S524 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S525 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S526 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S527 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S528 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S529 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S530 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S531 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S532 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S533 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S534 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S535 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S536 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S537 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S538 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S539 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S540 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S541 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S542 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S543 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S544 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S545 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S546 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S547 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S548 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S549 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S550 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S551 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S552 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S553 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S554 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S555 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S556 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S557 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S558 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S559 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S560 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S561 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S562 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S563 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S564 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S565 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S566 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S567 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S568 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S569 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S570 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S571 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S572 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S573 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S574 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S575 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S576 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S577 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S578 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S579 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S580 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S581 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S582 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S583 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S584 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S585 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S586 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S587 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S588 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S589 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S590 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S591 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S592 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S593 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S594 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S595 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S596 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S597 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S598 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S599 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S600 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S601 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S602 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S603 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S604 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S605 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S606 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S607 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S608 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S609 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S610 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S611 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S612 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S613 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S614 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S615 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S616 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S617 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S618 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S619 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S620 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S621 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S622 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S623 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S624 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S625 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S626 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S627 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S628 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S629 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S630 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S631 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S632 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S633 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S634 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S635 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S636 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S637 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S638 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S639 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S640 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S641 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S642 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S643 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S644 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S645 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S646 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S647 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S648 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S649 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S650 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S651 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S652 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S653 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S654 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S655 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S656 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S657 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S658 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S659 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S660 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S661 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S662 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S663 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S664 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S665 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S666 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S667 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S668 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S669 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S670 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S671 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S672 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S673 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S674 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S675 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S676 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S677 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S678 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S679 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S680 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S681 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S682 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S683 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S684 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S685 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S686 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S687 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S688 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S689 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S690 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S691 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S692 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S693 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S694 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S695 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S696 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S697 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S698 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S699 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S700 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S701 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S702 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S703 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S704 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S705 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S706 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S707 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S708 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S709 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S710 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S711 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S712 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S713 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S714 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S715 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S716 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S717 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S718 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S719 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S720 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S721 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S722 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S723 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S724 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S725 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S726 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S727 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S728 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S729 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S730 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S731 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S732 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S733 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S734 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S735 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S736 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S737 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S738 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S739 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S740 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S741 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S742 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S743 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S744 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S745 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S746 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S747 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S748 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S749 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S750 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S751 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S752 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S753 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S754 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S755 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S756 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S757 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S758 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S759 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S760 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S761 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S762 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S763 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S764 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S765 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S766 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S767 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S768 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S769 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S770 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S771 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S772 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S773 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S774 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S775 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S776 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S777 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S778 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S779 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S780 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S781 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S782 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S783 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S784 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S785 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S786 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S787 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S788 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S789 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S790 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S791 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S792 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S793 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S794 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S795 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S796 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S797 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S798 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S799 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S800 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S801 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S802 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S803 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S804 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S805 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S806 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S807 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S808 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S809 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S810 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S811 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S812 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S813 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S814 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S815 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S816 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S817 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S818 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S819 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S820 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S821 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S822 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S823 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S824 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S825 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S826 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S827 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S828 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S829 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S830 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S831 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S832 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S833 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S834 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S835 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S836 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S837 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S838 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S839 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S840 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S841 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S842 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S843 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S844 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S845 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S846 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S847 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S848 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S849 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S850 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S851 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S852 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S853 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S854 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S855 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S856 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S857 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S858 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S859 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S860 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S861 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S862 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S863 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S864 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S865 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S866 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S867 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S868 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S869 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S870 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S871 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S872 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S873 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S874 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S875 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S876 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S877 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S878 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S879 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S880 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S881 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S882 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S883 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S884 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S885 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S886 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S887 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S888 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S889 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S890 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S891 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S892 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S893 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S894 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S895 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S896 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S897 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S898 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S899 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S900 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S901 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S902 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S903 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S904 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S905 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S906 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S907 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S908 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S909 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S910 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S911 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S912 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S913 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S914 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S915 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S916 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S917 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S918 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S919 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S920 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S921 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S922 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S923 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S924 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S925 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S926 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S927 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S928 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S929 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S930 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S931 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S932 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S933 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S934 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S935 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S936 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S937 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S938 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S939 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S940 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S941 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S942 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S943 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S944 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S945 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S946 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S947 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S948 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S949 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S950 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S951 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S952 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S953 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S954 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S955 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S956 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S957 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S958 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S959 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S960 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S961 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S962 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S963 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S964 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S965 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S966 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S967 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S968 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S969 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S970 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S971 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S972 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S973 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S974 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S975 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S976 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S977 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S978 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S979 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S980 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S981 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S982 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S983 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S984 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S985 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S986 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S987 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S988 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S989 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S990 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S991 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S992 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S993 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S994 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S995 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S996 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S997 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S998 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S999 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1000 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1001 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1002 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1003 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1004 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1005 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1006 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1007 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1008 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1009 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1010 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1011 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1012 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1013 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1014 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1015 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1016 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1017 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1018 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1019 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1020 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1021 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1022 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1023 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1024 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1025 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1026 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1027 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1028 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1029 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1030 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1031 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1032 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1033 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1034 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1035 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1036 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1037 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1038 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1039 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1040 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1041 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1042 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1043 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1044 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1045 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1046 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1047 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1048 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1049 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1050 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1051 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1052 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1053 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1054 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1055 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1056 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1057 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1058 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1059 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1060 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1061 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1062 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1063 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1064 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1065 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1066 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1067 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1068 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1069 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1070 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1071 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1072 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1073 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1074 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1075 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1076 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1077 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1078 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1079 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1080 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1081 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1082 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1083 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1084 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1085 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1086 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1087 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1088 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1089 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1090 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1091 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1092 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1093 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1094 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1095 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1096 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1097 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1098 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1099 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1100 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1101 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1102 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1103 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1104 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1105 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1106 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1107 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1108 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1109 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1110 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1111 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1112 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1113 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1114 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1115 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1116 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1117 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1118 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1119 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1120 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1121 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1122 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1123 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1124 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1125 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1126 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1127 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1128 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1129 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1130 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1131 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1132 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1133 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1134 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1135 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1136 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1137 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1138 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1139 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1140 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1141 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1142 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1143 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1144 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1145 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1146 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1147 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1148 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1149 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1150 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1151 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1152 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1153 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1154 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1155 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1156 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1157 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1158 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1159 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1160 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1161 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1162 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1163 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1164 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1165 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1166 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1167 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1168 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1169 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1170 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1171 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1172 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1173 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1174 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1175 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1176 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1177 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1178 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1179 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1180 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1181 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1182 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1183 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1184 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1185 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1186 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1187 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1188 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1189 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1190 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1191 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1192 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1193 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1194 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1195 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1196 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1197 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1198 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1199 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1200 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1201 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1202 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1203 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1204 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1205 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1206 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1207 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1208 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1209 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1210 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1211 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1212 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1213 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1214 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1215 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1216 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1217 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1218 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1219 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1220 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1221 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1222 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1223 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1224 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1225 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1226 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1227 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1228 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1229 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1230 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1231 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1232 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1233 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1234 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1235 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1236 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1237 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1238 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1239 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1240 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1241 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1242 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1243 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1244 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1245 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1246 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1247 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1248 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1249 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1250 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | O1 | AR1 | AR On | SIGNAL_OUT | RW | 0...4294967295
63 | O2 | AR1 | AR Off | SIGNAL_OUT | RW | 0...4294967295
63 | O3 | AR1 | AR In Progress | SIGNAL_OUT | RW | 0...4294967295
63 | O4 | AR1 | AR1 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O5 | AR1 | AR2 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O6 | AR1 | AR3 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O7 | AR1 | AR4 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O8 | AR1 | AR5 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O9 | AR1 | AR Running | SIGNAL_OUT | RW | 0...4294967295
63 | O10 | AR1 | AR Shot 1 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O11 | AR1 | AR Shot 2 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O12 | AR1 | AR Shot 3 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O13 | AR1 | AR Shot 4 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O14 | AR1 | AR Shot 5 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O15 | AR1 | AR Sequence finished | SIGNAL_OUT | RW | 0...4294967295
63 | O16 | AR1 | AR Final Trip | SIGNAL_OUT | RW | 0...4294967295
63 | O17 | AR1 | Dead time on | SIGNAL_OUT | RW | 0...4294967295
63 | O18 | AR1 | ARC time on | SIGNAL_OUT | RW | 0...4294967295
63 | O19 | AR1 | Reclaim time on | SIGNAL_OUT | RW | 0...4294967295
63 | O20 | AR1 | AR Ready | SIGNAL_OUT | RW | 0...4294967295
63 | O21 | AR1 | AR Lockout after successfull sequence | SIGNAL_OUT | RW | 0...4294967295
63 | O22 | AR1 | AR Operation Inhibit | SIGNAL_OUT | RW | 0...4294967295
63 | O23 | AR1 | AR Locked | SIGNAL_OUT | RW | 0...4294967295
63 | I36 | AR1 | Newest Register | UINT32 | R | 0...12
63 | I37 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I38 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I39 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I40 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I41 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I42 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I43 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I44 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I45 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I46 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I47 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I48 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I49 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I50 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I51 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I52 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I53 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I54 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I55 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I56 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I57 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I58 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I59 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I60 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I61 | AR1 | Active time | FLOAT | R | 0...1800
63 | I62 | AR1 | Active time | FLOAT | R | 0...1800
63 | I63 | AR1 | Active time | FLOAT | R | 0...1800
63 | I64 | AR1 | Active time | FLOAT | R | 0...1800
63 | I65 | AR1 | Active time | FLOAT | R | 0...1800
63 | I66 | AR1 | Active time | FLOAT | R | 0...1800
63 | I67 | AR1 | Active time | FLOAT | R | 0...1800
63 | I68 | AR1 | Active time | FLOAT | R | 0...1800
63 | I69 | AR1 | Active time | FLOAT | R | 0...1800
63 | I70 | AR1 | Active time | FLOAT | R | 0...1800
63 | I71 | AR1 | Active time | FLOAT | R | 0...1800
63 | I72 | AR1 | Active time | FLOAT | R | 0...1800
63 | S1251 | AR1 | EventMaskLo | UINT32 | RW | 0...4294967295
63 | S1252 | AR1 | EventMaskHi | UINT32 | RW | 0...4294967295
115 | S1 | VRG1 | Vreg [AVR/90] mode | UINT32 | RW | 0=Disabled;1=Activated
115 | V1 | VRG1 | Vreg settings condition | UINT32 | R | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok
115 | V2 | VRG1 | Vreg condition | UINT32 | R | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on
115 | V3 | VRG1 | Vreg timer active | UINT32 | R | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
115 | I1 | VRG1 | Time left to operation | FLOAT | R | 0...1800
115 | I2 | VRG1 | Voltage now | FLOAT | R | 0...140
115 | I3 | VRG1 | Voltage difference to set target | FLOAT | R | -140...140
115 | I4 | VRG1 | Voltage set now to | FLOAT | R | -50000...50000
115 | I5 | VRG1 | Tap location now (- 0 +) | FLOAT | R | -30...30
115 | I6 | VRG1 | Absolute tap location | FLOAT | R | 0...50
115 | V4 | VRG1 | Tap changer on high border | UINT32 | R | 0=No;1=Yes
115 | V5 | VRG1 | Tap changer on low border | UINT32 | R | 0=No;1=Yes
115 | I7 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual (loc&rem)
115 | V6 | VRG1 | Remote tap control input | UINT32 | RW | 0=Stop;1=Lower;2=Higher
115 | S2 | VRG1 | Control pulselength max | FLOAT | RW | 0...1800
115 | S3 | VRG1 | Control pulselength min | FLOAT | RW | 0...1800
115 | S4 | VRG1 | Min time between pulses | FLOAT | RW | 0...1800
115 | V7 | VRG1 | Tap position ind. Setting | UINT32 | R | 0=Not selected;1=Set Ok;2=Wrong setting;3=Meas.Quality Fault.
115 | I8 | VRG1 | AVR rised voltage | UINT32 | R | 0...4294967295
115 | I9 | VRG1 | AVR reduced voltage | UINT32 | R | 0...4294967295
115 | I10 | VRG1 | AVR control blocked | UINT32 | R | 0...4294967295
115 | I11 | VRG1 | AVR Undervoltage blocked | UINT32 | R | 0...4294967295
115 | I12 | VRG1 | AVR Overcurrent blocked | UINT32 | R | 0...4294967295
115 | S5 | VRG1 | Clear statistics | UINT32 | W | 0=-;1=Clear
115 | S6 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S7 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S8 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S9 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S10 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S11 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S12 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S13 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S14 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S15 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S16 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S17 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S18 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S19 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S20 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S21 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S22 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S23 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S24 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S25 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S26 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S27 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S28 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S29 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S30 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S31 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S32 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S33 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S34 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S35 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S36 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S37 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S38 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S39 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S40 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S41 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S42 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S43 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S44 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S45 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S46 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S47 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S48 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S49 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S50 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S51 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S52 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S53 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S54 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S55 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S56 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S57 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S58 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S59 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S60 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S61 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S62 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S63 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S64 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S65 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S66 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S67 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S68 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S69 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S70 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S71 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S72 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S73 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S74 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S75 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S76 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S77 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S78 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S79 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S80 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S81 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S82 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S83 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S84 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S85 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S86 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S87 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S88 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S89 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S90 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S91 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S92 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S93 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S94 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S95 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S96 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S97 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S98 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S99 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S100 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S101 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S102 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S103 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S104 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S105 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S106 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S107 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S108 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S109 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S110 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S111 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S112 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S113 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S114 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S115 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S116 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S117 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S118 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S119 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S120 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S121 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S122 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S123 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S124 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S125 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S126 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S127 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S128 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S129 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S130 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S131 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S132 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S133 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | I13 | VRG1 | AVR to Manual control | SIGNAL_IN | RW | 0...4294967295
115 | O1 | VRG1 | AVR Raise Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O2 | VRG1 | AVR Lower Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O3 | VRG1 | AVR In manual control | SIGNAL_OUT | RW | 0...4294967295
115 | O4 | VRG1 | AVR U>/< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O5 | VRG1 | AVR U>>/<< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O6 | VRG1 | AVR Outputs blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O7 | VRG1 | AVR Operation blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O8 | VRG1 | AVR Control wait on | SIGNAL_OUT | RW | 0...4294967295
115 | O9 | VRG1 | AVR U< block active | SIGNAL_OUT | RW | 0...4294967295
115 | O10 | VRG1 | AVR I> block active | SIGNAL_OUT | RW | 0...4294967295
115 | O11 | VRG1 | AVR Tap in highlimit | SIGNAL_OUT | RW | 0...4294967295
115 | O12 | VRG1 | AVR Tap in lowlimit | SIGNAL_OUT | RW | 0...4294967295
115 | I14 | VRG1 | Newest Register | UINT32 | R | 0...12
115 | I15 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I16 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I17 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I18 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I19 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I20 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I21 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I22 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I23 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I24 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I25 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I26 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I27 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I28 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I29 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I30 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I31 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I32 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I33 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I34 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I35 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I36 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I37 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I38 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I39 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I40 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I41 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I42 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I43 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I44 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I45 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I46 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I47 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I48 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I49 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I50 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I51 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I52 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I53 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I54 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I55 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I56 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I57 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I58 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I59 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I60 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I61 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I62 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | S134 | VRG1 | EventMaskLo | UINT32 | RW | 0...4294967295
115 | S135 | VRG1 | EventMaskHi | UINT32 | RW | 0...4294967295
135 | S1 | EMON1 | Monitor mode | UINT32 | RW | 0=Disabled;1=Activated
135 | S2 | EMON1 | I> (50) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V1 | EMON1 | I> (50) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S3 | EMON1 | I0> (50N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S4 | EMON1 | I0> (50N) I0input | UINT32 | RW | 0=I01;1=I02;2=I0Calc
135 | V2 | EMON1 | I0> (50N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S5 | EMON1 | Idir> (67) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V3 | EMON1 | Idir> (67) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S6 | EMON1 | I0dir> (67N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S7 | EMON1 | I0dir> (67N) I0input | UINT32 | RW | 0=I01;1=I02
135 | S8 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=select
135 | S9 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V4 | EMON1 | I0dir> (67N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S10 | EMON1 | I0Int> (67NT) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S11 | EMON1 | I0Int> (67NT) I0input | UINT32 | RW | 0=I01;1=I02
135 | V5 | EMON1 | I0Int> (67NT) Monitor condition | UINT32 | R | 0=Normal;1=FLT FW;2=FLT REV
135 | S12 | EMON1 | U< (27) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S13 | EMON1 | U< (27) Measured magnitude | UINT32 | RW | 0=P-P Voltages;1=P-E Voltages
135 | S14 | EMON1 | U< (27) Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
135 | V6 | EMON1 | U< (27) Monitor condition | UINT32 | R | 0=Normal;1=Undervoltage;2=No voltage
135 | S15 | EMON1 | U0> (59N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S16 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=Select
135 | S17 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V7 | EMON1 | U0> (59N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S18 | EMON1 | FL (21FL) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V8 | EMON1 | FL (21FL) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | I1 | EMON1 | I> (50) Alarms | UINT32 | R | 0...4294967295
135 | I2 | EMON1 | I0> (50N) Alarms | UINT32 | R | 0...4294967295
135 | I3 | EMON1 | Idir> (67) Alarms | UINT32 | R | 0...4294967295
135 | I4 | EMON1 | I0dir> (67N) Alarms | UINT32 | R | 0...4294967295
135 | I5 | EMON1 | I0Int> (67) Alarms FWD | UINT32 | R | 0...4294967295
135 | I6 | EMON1 | I0Int> (67) Alarms REV | UINT32 | R | 0...4294967295
135 | I7 | EMON1 | U< (27) Undervoltage Alarms | UINT32 | R | 0...4294967295
135 | I8 | EMON1 | U< (27) No voltage Alarms | UINT32 | R | 0...4294967295
135 | I9 | EMON1 | U0> (59N) Alarms | UINT32 | R | 0...4294967295
135 | I10 | EMON1 | FL (21FL) Triggered | UINT32 | R | 0...4294967295
135 | S19 | EMON1 | Clear statistics | UINT32 | W | 0=-;1=Clear
135 | S20 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S21 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S22 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S23 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S24 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S25 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S26 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S27 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S28 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S29 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S30 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S31 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S32 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S33 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S34 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S35 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S36 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S37 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S38 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S39 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S40 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S41 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S42 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S43 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S44 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S45 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S46 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S47 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S48 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S49 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S50 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S51 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S52 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S53 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S54 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S55 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S56 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S57 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S58 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S59 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S60 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S61 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S62 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S63 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S64 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S65 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S66 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S67 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S68 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S69 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S70 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S71 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S72 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S73 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S74 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S75 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S76 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S77 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S78 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S79 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S80 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S81 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S82 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S83 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S84 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S85 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S86 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S87 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S88 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S89 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S90 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S91 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S92 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S93 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S94 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S95 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S96 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S97 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S98 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S99 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S100 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S101 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S102 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S103 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S104 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S105 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S106 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S107 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S108 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S109 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S110 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S111 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S112 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S113 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S114 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S115 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S116 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S117 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S118 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S119 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S120 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S121 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S122 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S123 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S124 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S125 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S126 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S127 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S128 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S129 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S130 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S131 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S132 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S133 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S134 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S135 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S136 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S137 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S138 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S139 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S140 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S141 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S142 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S143 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S144 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S145 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S146 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S147 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S148 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S149 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S150 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S151 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S152 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S153 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S154 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S155 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S156 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S157 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S158 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S159 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S160 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S161 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S162 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S163 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S164 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S165 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S166 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S167 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S168 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S169 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S170 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S171 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S172 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S173 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S174 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S175 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S176 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S177 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S178 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S179 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S180 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S181 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S182 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S183 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S184 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S185 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S186 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S187 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S188 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S189 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S190 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S191 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S192 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S193 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S194 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S195 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S196 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S197 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S198 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S199 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S200 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S201 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S202 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S203 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S204 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S205 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S206 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S207 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S208 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S209 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S210 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S211 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S212 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S213 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S214 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S215 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S216 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S217 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S218 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S219 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S220 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S221 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S222 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S223 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S224 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S225 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S226 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S227 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | O1 | EMON1 | I> (50) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O2 | EMON1 | I0> (50N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O3 | EMON1 | Idir> (67) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O4 | EMON1 | I0dir> (67N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O5 | EMON1 | I0int> (67NT) Alarm FWD | SIGNAL_OUT | RW | 0...4294967295
135 | O6 | EMON1 | I0int> (67NT) Alarm REV | SIGNAL_OUT | RW | 0...4294967295
135 | O7 | EMON1 | U< (27) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O8 | EMON1 | U< (27) No voltage | SIGNAL_OUT | RW | 0...4294967295
135 | O9 | EMON1 | U0> (59N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O10 | EMON1 | FL (21FL) Triggered | SIGNAL_OUT | RW | 0...4294967295
135 | I11 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I12 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I13 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I14 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I15 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I16 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I17 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I18 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I19 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I20 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I21 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I22 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I23 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I24 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I25 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I26 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I27 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I28 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I29 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I30 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I31 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I32 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I33 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I34 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I35 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I36 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I37 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I38 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I39 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I40 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I41 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I42 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I43 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I44 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I45 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I46 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I47 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I48 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I49 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I50 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I51 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I52 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I53 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I54 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I55 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I56 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I57 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I58 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I59 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I60 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I61 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I62 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I63 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I64 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I65 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I66 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I67 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I68 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I69 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I70 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I71 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I72 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I73 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I74 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I75 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I76 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I77 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I78 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I79 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I80 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I81 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I82 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I83 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I84 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I85 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I86 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I87 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I88 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I89 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I90 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I91 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I92 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I93 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I94 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I95 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I96 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I97 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I98 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I99 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I100 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I101 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I102 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I103 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I104 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I105 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I106 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I107 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I108 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I109 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I110 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I111 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I112 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I113 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I114 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I115 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I116 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I117 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I118 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I119 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I120 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I121 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I122 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I123 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I124 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I125 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I126 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I127 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I128 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I129 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I130 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I131 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I132 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I133 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I134 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I135 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I136 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I137 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I138 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I139 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I140 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I141 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I142 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I143 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I144 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I145 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I146 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I147 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I148 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I149 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I150 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I151 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I152 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I153 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I154 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I155 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I156 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I157 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I158 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I159 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I160 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I161 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I162 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I163 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I164 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I165 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I166 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I167 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I168 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I169 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I170 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I171 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I172 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I173 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I174 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I175 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I176 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I177 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I178 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I179 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I180 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I181 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I182 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I183 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I184 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I185 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I186 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I187 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I188 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I189 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I190 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I191 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I192 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I193 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I194 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I195 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I196 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I197 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I198 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I199 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I200 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I201 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I202 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I203 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I204 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I205 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I206 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I207 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I208 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I209 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I210 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I211 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I212 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I213 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I214 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I215 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I216 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I217 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I218 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I219 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I220 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I221 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I222 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I223 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I224 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I225 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I226 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I227 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I228 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I229 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I230 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I231 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I232 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I233 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I234 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I235 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I236 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I237 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I238 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I239 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I240 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I241 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I242 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I243 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I244 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I245 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I246 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I247 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I248 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I249 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I250 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I251 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I252 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I253 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I254 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I255 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I256 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I257 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I258 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | S228 | EMON1 | EventMaskLo | UINT32 | RW | 0...4294967295
135 | S229 | EMON1 | EventMaskHi | UINT32 | RW | 0...4294967295
143 | O1 | ALARM | ALARM 1 | SIGNAL_IN | RW | 0...4294967295
143 | O2 | ALARM | ALARM 2 | SIGNAL_IN | RW | 0...4294967295
143 | O3 | ALARM | ALARM 3 | SIGNAL_IN | RW | 0...4294967295
143 | O4 | ALARM | ALARM 4 | SIGNAL_IN | RW | 0...4294967295
143 | O5 | ALARM | ALARM 5 | SIGNAL_IN | RW | 0...4294967295
143 | O6 | ALARM | ALARM 6 | SIGNAL_IN | RW | 0...4294967295
143 | O7 | ALARM | ALARM 7 | SIGNAL_IN | RW | 0...4294967295
143 | O8 | ALARM | ALARM 8 | SIGNAL_IN | RW | 0...4294967295
143 | O9 | ALARM | ALARM 9 | SIGNAL_IN | RW | 0...4294967295
143 | O10 | ALARM | ALARM 10 | SIGNAL_IN | RW | 0...4294967295
143 | O11 | ALARM | ALARM 11 | SIGNAL_IN | RW | 0...4294967295
143 | O12 | ALARM | ALARM 12 | SIGNAL_IN | RW | 0...4294967295
143 | O13 | ALARM | ALARM 13 | SIGNAL_IN | RW | 0...4294967295
143 | O14 | ALARM | ALARM 14 | SIGNAL_IN | RW | 0...4294967295
143 | O15 | ALARM | ALARM 15 | SIGNAL_IN | RW | 0...4294967295
143 | O16 | ALARM | ALARM 16 | SIGNAL_IN | RW | 0...4294967295
143 | O17 | ALARM | ALARM 17 | SIGNAL_IN | RW | 0...4294967295
143 | O18 | ALARM | ALARM 18 | SIGNAL_IN | RW | 0...4294967295
143 | O19 | ALARM | ALARM 19 | SIGNAL_IN | RW | 0...4294967295
143 | O20 | ALARM | ALARM 20 | SIGNAL_IN | RW | 0...4294967295
143 | O21 | ALARM | ALARM 21 | SIGNAL_IN | RW | 0...4294967295
143 | O22 | ALARM | ALARM 22 | SIGNAL_IN | RW | 0...4294967295
143 | O23 | ALARM | ALARM 23 | SIGNAL_IN | RW | 0...4294967295
143 | O24 | ALARM | ALARM 24 | SIGNAL_IN | RW | 0...4294967295
143 | O25 | ALARM | ALARM 25 | SIGNAL_IN | RW | 0...4294967295
143 | O26 | ALARM | ALARM 26 | SIGNAL_IN | RW | 0...4294967295
143 | O27 | ALARM | ALARM 27 | SIGNAL_IN | RW | 0...4294967295
143 | O28 | ALARM | ALARM 28 | SIGNAL_IN | RW | 0...4294967295
143 | O29 | ALARM | ALARM 29 | SIGNAL_IN | RW | 0...4294967295
143 | O30 | ALARM | ALARM 30 | SIGNAL_IN | RW | 0...4294967295
143 | O31 | ALARM | ALARM 31 | SIGNAL_IN | RW | 0...4294967295
143 | O32 | ALARM | ALARM 32 | SIGNAL_IN | RW | 0...4294967295
143 | O33 | ALARM | ALARM 33 | SIGNAL_IN | RW | 0...4294967295
143 | O34 | ALARM | ALARM 34 | SIGNAL_IN | RW | 0...4294967295
143 | O35 | ALARM | ALARM 35 | SIGNAL_IN | RW | 0...4294967295
143 | O36 | ALARM | ALARM 36 | SIGNAL_IN | RW | 0...4294967295
143 | O37 | ALARM | ALARM 37 | SIGNAL_IN | RW | 0...4294967295
143 | O38 | ALARM | ALARM 38 | SIGNAL_IN | RW | 0...4294967295
143 | O39 | ALARM | ALARM 39 | SIGNAL_IN | RW | 0...4294967295
143 | O40 | ALARM | ALARM 40 | SIGNAL_IN | RW | 0...4294967295
143 | O41 | ALARM | ALARM 41 | SIGNAL_IN | RW | 0...4294967295
143 | O42 | ALARM | ALARM 42 | SIGNAL_IN | RW | 0...4294967295
143 | O43 | ALARM | ALARM 43 | SIGNAL_IN | RW | 0...4294967295
143 | O44 | ALARM | ALARM 44 | SIGNAL_IN | RW | 0...4294967295
143 | O45 | ALARM | ALARM 45 | SIGNAL_IN | RW | 0...4294967295
143 | O46 | ALARM | ALARM 46 | SIGNAL_IN | RW | 0...4294967295
143 | O47 | ALARM | ALARM 47 | SIGNAL_IN | RW | 0...4294967295
143 | O48 | ALARM | ALARM 48 | SIGNAL_IN | RW | 0...4294967295
143 | O49 | ALARM | ALARM 49 | SIGNAL_IN | RW | 0...4294967295
143 | O50 | ALARM | ALARM 50 | SIGNAL_IN | RW | 0...4294967295
143 | O51 | ALARM | ALARM 51 | SIGNAL_IN | RW | 0...4294967295
143 | O52 | ALARM | ALARM 52 | SIGNAL_IN | RW | 0...4294967295
143 | O53 | ALARM | ALARM 53 | SIGNAL_IN | RW | 0...4294967295
143 | O54 | ALARM | ALARM 54 | SIGNAL_IN | RW | 0...4294967295
143 | O55 | ALARM | ALARM 55 | SIGNAL_IN | RW | 0...4294967295
143 | O56 | ALARM | ALARM 56 | SIGNAL_IN | RW | 0...4294967295
143 | O57 | ALARM | ALARM 57 | SIGNAL_IN | RW | 0...4294967295
143 | O58 | ALARM | ALARM 58 | SIGNAL_IN | RW | 0...4294967295
143 | O59 | ALARM | ALARM 59 | SIGNAL_IN | RW | 0...4294967295
143 | O60 | ALARM | ALARM 60 | SIGNAL_IN | RW | 0...4294967295
143 | O61 | ALARM | ALARM 61 | SIGNAL_IN | RW | 0...4294967295
143 | O62 | ALARM | ALARM 62 | SIGNAL_IN | RW | 0...4294967295
143 | O63 | ALARM | ALARM 63 | SIGNAL_IN | RW | 0...4294967295
143 | O64 | ALARM | ALARM 64 | SIGNAL_IN | RW | 0...4294967295
159 | S1 | ALARM1 | EventMaskLo | UINT32 | RW | 0...4294967295
159 | S2 | ALARM1 | EventMaskHi | UINT32 | RW | 0...4294967295
160 | S1 | ALARM2 | EventMaskLo | UINT32 | RW | 0...4294967295
160 | S2 | ALARM2 | EventMaskHi | UINT32 | RW | 0...4294967295
162 | S1 | GSYN | Synchronizer mode | UINT32 | RW | 0=Disabled;1=Activated
162 | S2 | GSYN | Synchronizer reference voltage input | UINT32 | RW | 0=U4 Input;1=U3 Input
162 | S3 | GSYN | Voltage difference calculation mode | UINT32 | RW | 0=System is reference;1=U3/U4 Input is reference
162 | S4 | GSYN | Synchronizer voltage reference | UINT32 | RW | 0=UL12;1=UL23;2=UL31;3=UL1;4=UL2;5=UL3
162 | S5 | GSYN | Synchronizer measurement settings | UINT32 | R | 0=Meas.Conf.Incorrect;1=PP and PE voltages;2=PP Voltages;
162 | S6 | GSYN | Synchronizer status | UINT32 | R | 0=Conf.Error;1=Idle Ready;2=Synchronizing;3=Blocked
162 | S7 | GSYN | Force control signals on | UINT32 | RW | 0=None;1=Blocked On;2=Running On;3=Increase U On;4=Decrease U On;5=Increase F On;6=Decrease F On;7=CB Close On;8=LongSyncTime On
162 | S8 | GSYN | Synchronizing by | UINT32 | RW | 0=Autosynchronizer;1=Manual commands
162 | S9 | GSYN | Manual switching mode | UINT32 | RW | 0=Assisted synchroswitch;1=I know what I am doing
162 | S10 | GSYN | Synchroswitch status | UINT32 | R | 0=Standstill;1=Departing;2=Enclosing
162 | S11 | GSYN | Magnitude side A | FLOAT | R | 0.000...200.000
162 | S12 | GSYN | Magnitude side B | FLOAT | R | 0.000...200.000
162 | S13 | GSYN | Frequency side A | FLOAT | R | 0.000...75.000
162 | S14 | GSYN | Frequency side B | FLOAT | R | 0.000...75.000
162 | S15 | GSYN | Magnitude difference | FLOAT | R | -200...200
162 | S16 | GSYN | Frequency difference | FLOAT | R | -100...100
162 | S17 | GSYN | Angle difference | FLOAT | R | -360...360
162 | S18 | GSYN | Magnitude difference on closing BRK | FLOAT | R | -200...200
162 | S19 | GSYN | Frequency difference on closing BRK | FLOAT | R | -100...100
162 | S20 | GSYN | Angle difference on closing BRK | FLOAT | R | -360...360
162 | S21 | GSYN | Estimated BRK Closing time | FLOAT | R | 0...360
162 | S22 | GSYN | Networks rotating time | FLOAT | R | 0...360
162 | S23 | GSYN | Networks placement atm | FLOAT | R | -360...360
162 | S24 | GSYN | Synchronizing time left | FLOAT | R | 0...1800
162 | S25 | GSYN | Get measurement errors for fine tuning | UINT32 | RW | 0=-;1=Get errors
162 | S26 | GSYN | Magnitude difference fine tune | FLOAT | RW | -200...200
162 | S27 | GSYN | Frequency difference fine tune | FLOAT | RW | -100...100
162 | S28 | GSYN | Angle difference fine tune | FLOAT | RW | -360...360
162 | S29 | GSYN | Minimum voltage allowed for synchronizing | FLOAT | RW | 0...105
162 | S30 | GSYN | Maximum voltage allowed for synchronizing | FLOAT | RW | 0...200
162 | S31 | GSYN | Maximum zero voltage allowed for synchronizing (100% disabled) | FLOAT | RW | 0...100
162 | S32 | GSYN | Maximum allowed voltage difference | FLOAT | RW | 0.1...50
162 | S33 | GSYN | Maximum allowed overfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S34 | GSYN | Maximum allowed underfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S35 | GSYN | Max.Time for synchronizing | FLOAT | RW | 0...1800
162 | S36 | GSYN | Maximum allowed angular disposition to allow synchronizing | FLOAT | RW | 0.01...25
162 | S37 | GSYN | Adjustment for measurement inaccuracy or set of desired volt. offset | FLOAT | RW | -95...95
162 | S38 | GSYN | Adjustment for measurement inaccuracy or set of desired angular offset | FLOAT | RW | -60...60
162 | S39 | GSYN | Adjustment for measurement inaccuracy or set of desired freq. offset | FLOAT | RW | -0.5...2
162 | S40 | GSYN | Voltage adjustment slope | FLOAT | RW | 0...25
162 | S41 | GSYN | Volt. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S42 | GSYN | Volt. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S43 | GSYN | Volt. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S44 | GSYN | Freq. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S45 | GSYN | Freq. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S46 | GSYN | Freq. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S47 | GSYN | Maximum allowed voltage difference to start synchronizing | FLOAT | RW | 0...50
162 | S48 | GSYN | Integrator sum when voltage adjustment pulse is generated | FLOAT | RW | 0...50
162 | S49 | GSYN | Voltage adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S50 | GSYN | Frequency adjustment slope when increasing | FLOAT | RW | 0...10
162 | S51 | GSYN | Frequency adjustment slope when decreasing | FLOAT | RW | -10...0
162 | S52 | GSYN | Maximum allowed frequency difference to start synchronizing | FLOAT | RW | 0...25
162 | S53 | GSYN | Integrator sum when frequency adjustment pulse is generated | FLOAT | RW | 0...50
162 | S54 | GSYN | Frequency adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S55 | GSYN | Filter time for angle derivative | FLOAT | RW | 0...1800
162 | S56 | GSYN | Circuit breaker pre-closing adjustment constant | FLOAT | RW | 0...10
162 | S57 | GSYN | Circuit breaker pre-closing time incl auxiliary relays | FLOAT | RW | 0...1800
162 | S58 | GSYN | Lenght of circuit breaker closing pulse | FLOAT | RW | 0...1800
162 | I1 | GSYN | Start Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I2 | GSYN | Stop Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I3 | GSYN | Block and Interrupt Synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I4 | GSYN | Breaker Closed | SIGNAL_IN | RW | 0...4294967295
162 | I5 | GSYN | Manual increase voltage | SIGNAL_IN | RW | 0...4294967295
162 | I6 | GSYN | Manual decrease voltage | SIGNAL_IN | RW | 0...4294967295
162 | I7 | GSYN | Manual increase frequency | SIGNAL_IN | RW | 0...4294967295
162 | I8 | GSYN | Manual decrease frequency | SIGNAL_IN | RW | 0...4294967295
162 | I9 | GSYN | Manual Close Breaker | SIGNAL_IN | RW | 0...4294967295
162 | O1 | GSYN | GSYN Voltage Mag.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O2 | GSYN | GSYN Voltage Freq.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O3 | GSYN | GSYN Voltage Ang.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O4 | GSYN | GSYN Blocked | SIGNAL_OUT | RW | 0...4294967295
162 | O5 | GSYN | GSYN Running | SIGNAL_OUT | RW | 0...4294967295
162 | O6 | GSYN | GSYN Increase Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O7 | GSYN | GSYN Decrease Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O8 | GSYN | GSYN Increase Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O9 | GSYN | GSYN Decrease Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O10 | GSYN | GSYN Breaker Close Pulse | SIGNAL_OUT | RW | 0...4294967295
162 | O11 | GSYN | GSYN Long Sync Time | SIGNAL_OUT | RW | 0...4294967295
162 | O12 | GSYN | GSYN Nets Standstill | SIGNAL_OUT | RW | 0...4294967295
162 | O13 | GSYN | GSYN Nets Departing | SIGNAL_OUT | RW | 0...4294967295
162 | O14 | GSYN | GSYN Nets Enclosing | SIGNAL_OUT | RW | 0...4294967295
162 | S59 | GSYN | Control EventMaskLo | UINT32 | RW | 0...4294967295
162 | S60 | GSYN | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | S1 | VREC | Measurement value recorder mode | UINT32 | RW | 0=Disabled;1=Activated
163 | S2 | VREC | Scale current values to primary | UINT32 | RW | 0=No;1=Yes
163 | S3 | VREC | Record fault types (Overcurrrent & Voltage Over/Under) faults | UINT32 | RW | 0=No;1=Yes
163 | I1 | VREC | Trigger register to memory | SIGNAL_IN | RW | 0...4294967295
163 | I2 | VREC | Tripped stage | UINT32 | R | 0=-;1=I> Trip;2=I>> Trip;3=I>>> Trip;4=I>>>> Trip;5=IDir> Trip;6=IDir>> Trip;7=IDir>>> Trip;8=IDir>>>> Trip;9=U> Trip;10=U>> Trip;11=U>>> Trip;12=U>>>> Trip;13=U< Trip;14=U<< Trip;15=U<<< Trip;16=U<<<< Trip;17=I0> TRIP;18=I0>> Trip;19=I0>>> Trip;20=I0>>>> Trip;21=I0Dir> Trip;22=I0Dir>> Trip;23=I0Dir>>> Trip;24=I0Dir>>>> Trip;25=f> Trip;26=f>> Trip;27=f>>> Trip;28=f>>>> Trip;29=f< Trip;30=f<< Trip;31=f<<< Trip;32=f<<<< Trip;33=P> Trip;34=P< Trip;35=Prev> Trip;36=T> Trip;37=I2> Trip;38=I2>> Trip;39=I2>>> Trip;40=I2>>>> Trip;41=U1/2 > Trip;42=U1/2 >> Trip;43=U1/2 >>> Trip;44=U1/2 >>>> Trip;45=U0> Trip;46=U0>> Trip;47=U0>>> Trip;48=U0>>>> Trip
163 | I3 | VREC | Overcurrent fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;
163 | I4 | VREC | Voltage fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C;8=-;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I5 | VREC | VREC Magnitude 1 | FLOAT | R | 0...1800
163 | I6 | VREC | VREC Magnitude 2 | FLOAT | R | 0...1800
163 | I7 | VREC | VREC Magnitude 3 | FLOAT | R | 0...1800
163 | I8 | VREC | VREC Magnitude 4 | FLOAT | R | 0...1800
163 | I9 | VREC | VREC Magnitude 5 | FLOAT | R | 0...1800
163 | I10 | VREC | VREC Magnitude 6 | FLOAT | R | 0...1800
163 | I11 | VREC | VREC Magnitude 7 | FLOAT | R | 0...1800
163 | I12 | VREC | VREC Magnitude 8 | FLOAT | R | 0...1800
163 | I13 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I14 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I15 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I16 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I17 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I18 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I19 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I20 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I21 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I22 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I23 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I24 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295

## G SPA map AQ-210 v2.1.1.3-233
SPA Ch | SPA Data | Ch Name | Description | Type | Access | Range
46 | V1 | OBJ1 | Open Select | UINT32 | W | 1=Select
46 | V2 | OBJ1 | Close Select | UINT32 | W | 1=Select
46 | V3 | OBJ1 | Execute | UINT32 | W | 1=Execute
46 | V4 | OBJ1 | Cancel | UINT32 | W | 1=Cancel
46 | V5 | OBJ1 | Direct Open | UINT32 | W | 1=Open
46 | V6 | OBJ1 | Direct Close | UINT32 | W | 1=Close
47 | V1 | OBJ2 | Open Select | UINT32 | W | 1=Select
47 | V2 | OBJ2 | Close Select | UINT32 | W | 1=Select
47 | V3 | OBJ2 | Execute | UINT32 | W | 1=Execute
47 | V4 | OBJ2 | Cancel | UINT32 | W | 1=Cancel
47 | V5 | OBJ2 | Direct Open | UINT32 | W | 1=Open
47 | V6 | OBJ2 | Direct Close | UINT32 | W | 1=Close
48 | V1 | OBJ3 | Open Select | UINT32 | W | 1=Select
48 | V2 | OBJ3 | Close Select | UINT32 | W | 1=Select
48 | V3 | OBJ3 | Execute | UINT32 | W | 1=Execute
48 | V4 | OBJ3 | Cancel | UINT32 | W | 1=Cancel
48 | V5 | OBJ3 | Direct Open | UINT32 | W | 1=Open
48 | V6 | OBJ3 | Direct Close | UINT32 | W | 1=Close
49 | V1 | OBJ4 | Open Select | UINT32 | W | 1=Select
49 | V2 | OBJ4 | Close Select | UINT32 | W | 1=Select
49 | V3 | OBJ4 | Execute | UINT32 | W | 1=Execute
49 | V4 | OBJ4 | Cancel | UINT32 | W | 1=Cancel
49 | V5 | OBJ4 | Direct Open | UINT32 | W | 1=Open
49 | V6 | OBJ4 | Direct Close | UINT32 | W | 1=Close
50 | V1 | OBJ5 | Open Select | UINT32 | W | 1=Select
50 | V2 | OBJ5 | Close Select | UINT32 | W | 1=Select
50 | V3 | OBJ5 | Execute | UINT32 | W | 1=Execute
50 | V4 | OBJ5 | Cancel | UINT32 | W | 1=Cancel
50 | V5 | OBJ5 | Direct Open | UINT32 | W | 1=Open
50 | V6 | OBJ5 | Direct Close | UINT32 | W | 1=Close
150 | V1 | OBJ6 | Open Select | UINT32 | W | 1=Select
150 | V2 | OBJ6 | Close Select | UINT32 | W | 1=Select
150 | V3 | OBJ6 | Execute | UINT32 | W | 1=Execute
150 | V4 | OBJ6 | Cancel | UINT32 | W | 1=Cancel
150 | V5 | OBJ6 | Direct Open | UINT32 | W | 1=Open
150 | V6 | OBJ6 | Direct Close | UINT32 | W | 1=Close
151 | V1 | OBJ7 | Open Select | UINT32 | W | 1=Select
151 | V2 | OBJ7 | Close Select | UINT32 | W | 1=Select
151 | V3 | OBJ7 | Execute | UINT32 | W | 1=Execute
151 | V4 | OBJ7 | Cancel | UINT32 | W | 1=Cancel
151 | V5 | OBJ7 | Direct Open | UINT32 | W | 1=Open
151 | V6 | OBJ7 | Direct Close | UINT32 | W | 1=Close
152 | V1 | OBJ8 | Open Select | UINT32 | W | 1=Select
152 | V2 | OBJ8 | Close Select | UINT32 | W | 1=Select
152 | V3 | OBJ8 | Execute | UINT32 | W | 1=Execute
152 | V4 | OBJ8 | Cancel | UINT32 | W | 1=Cancel
152 | V5 | OBJ8 | Direct Open | UINT32 | W | 1=Open
152 | V6 | OBJ8 | Direct Close | UINT32 | W | 1=Close
153 | V1 | OBJ9 | Open Select | UINT32 | W | 1=Select
153 | V2 | OBJ9 | Close Select | UINT32 | W | 1=Select
153 | V3 | OBJ9 | Execute | UINT32 | W | 1=Execute
153 | V4 | OBJ9 | Cancel | UINT32 | W | 1=Cancel
153 | V5 | OBJ9 | Direct Open | UINT32 | W | 1=Open
153 | V6 | OBJ9 | Direct Close | UINT32 | W | 1=Close
154 | V1 | OBJ10 | Open Select | UINT32 | W | 1=Select
154 | V2 | OBJ10 | Close Select | UINT32 | W | 1=Select
154 | V3 | OBJ10 | Execute | UINT32 | W | 1=Execute
154 | V4 | OBJ10 | Cancel | UINT32 | W | 1=Cancel
154 | V5 | OBJ10 | Direct Open | UINT32 | W | 1=Open
154 | V6 | OBJ10 | Direct Close | UINT32 | W | 1=Close
116 | S1 | MEAS1 | Side 1 Current meas update interval | UINT32 | RW | 5...10000
116 | I1 | MEAS1 | Pri.Pha.curr.IL1 | FLOAT | R | 0...100000
116 | I2 | MEAS1 | Pri.Pha.curr.IL2 | FLOAT | R | 0...100000
116 | I3 | MEAS1 | Pri.Pha.curr.IL3 | FLOAT | R | 0...100000
116 | I4 | MEAS1 | Pri.Res.curr.I01 | FLOAT | R | 0...100000
116 | I5 | MEAS1 | Pri.Res.curr.I02 | FLOAT | R | 0...100000
116 | I6 | MEAS1 | Pha.angle IL1 | FLOAT | R | -360...360
116 | I7 | MEAS1 | Pha.angle IL2 | FLOAT | R | -360...360
116 | I8 | MEAS1 | Pha.angle IL3 | FLOAT | R | -360...360
116 | I9 | MEAS1 | Res.curr.angle I01 | FLOAT | R | -360...360
116 | I10 | MEAS1 | Res.curr.angle I02 | FLOAT | R | -360...360
116 | I11 | MEAS1 | Pri.calc.I0 | FLOAT | R | 0...100000
116 | I12 | MEAS1 | calc.I0 Pha.angle | FLOAT | R | -360...360
116 | I13 | MEAS1 | Pha.curr.IL1 TRMS Pri | FLOAT | R | 0...100000
116 | I14 | MEAS1 | Pha.curr.IL2 TRMS Pri | FLOAT | R | 0...100000
116 | I15 | MEAS1 | Pha.curr.IL3 TRMS Pri | FLOAT | R | 0...100000
116 | I16 | MEAS1 | Pri.Pos.seq.curr. | FLOAT | R | 0...100000
116 | I17 | MEAS1 | Pri.Neg.seq.curr. | FLOAT | R | 0...100000
116 | I18 | MEAS1 | Pri.Zero seq.curr. | FLOAT | R | 0...100000
116 | I19 | MEAS1 | Pos.seq.curr.angle | FLOAT | R | -360...360
116 | I20 | MEAS1 | Neg.seq.curr.angle | FLOAT | R | -360...360
116 | I21 | MEAS1 | Zero seq.curr.angle | FLOAT | R | -360...360
116 | I22 | MEAS1 | Res.curr.I01 TRMS Pri | FLOAT | R | 0...100000
116 | I23 | MEAS1 | Res.curr.I02 TRMS Pri | FLOAT | R | 0...100000
116 | I24 | MEAS1 | Pha.L1 ampl. THD | FLOAT | R | 0...100
116 | I25 | MEAS1 | Pha.L1 pow. THD | FLOAT | R | 0...100
116 | I26 | MEAS1 | Pha.L2 ampl. THD | FLOAT | R | 0...100
116 | I27 | MEAS1 | Pha.L2 pow. THD | FLOAT | R | 0...100
116 | I28 | MEAS1 | Pha.L3 ampl. THD | FLOAT | R | 0...100
116 | I29 | MEAS1 | Pha.L3 pow. THD | FLOAT | R | 0...100
116 | I30 | MEAS1 | Res.I01 ampl. THD | FLOAT | R | 0...100
116 | I31 | MEAS1 | Res.I01 pow. THD | FLOAT | R | 0...100
116 | I32 | MEAS1 | Res.I02 ampl. THD | FLOAT | R | 0...100
116 | I33 | MEAS1 | Res.I02 pow. THD | FLOAT | R | 0...100
116 | I34 | MEAS1 | Meas1 IL ang. Ref | FLOAT | R | -360...360
117 | S1 | MEAS2 | Side 2 Current meas update interval | UINT32 | RW | 5...10000
117 | I1 | MEAS2 | Pri.Pha.curr.I''L1 | FLOAT | R | 0...100000
117 | I2 | MEAS2 | Pri.Pha.curr.I''L2 | FLOAT | R | 0...100000
117 | I3 | MEAS2 | Pri.Pha.curr.I''L3 | FLOAT | R | 0...100000
117 | I4 | MEAS2 | Pha.angle I''L1 | FLOAT | R | -360...360
117 | I5 | MEAS2 | Pha.angle I''L2 | FLOAT | R | -360...360
117 | I6 | MEAS2 | Pha.angle I''L3 | FLOAT | R | -360...360
117 | I7 | MEAS2 | Pri.Res.curr.I''01 | FLOAT | R | 0...100000
117 | I8 | MEAS2 | Res.curr.angle I''01 | FLOAT | R | -360...360
117 | I9 | MEAS2 | Pri.Res.curr.I''02 | FLOAT | R | 0...100000
117 | I10 | MEAS2 | Res.curr.angle I''02 | FLOAT | R | -360...360
117 | I11 | MEAS2 | Pri.calc.I''0 | FLOAT | R | 0...100000
117 | I12 | MEAS2 | calc.I''0 Pha.angle | FLOAT | R | -360...360
117 | I13 | MEAS2 | Pha.curr.I''L1 TRMS Pri | FLOAT | R | 0...100000
117 | I14 | MEAS2 | Pha.curr.I''L2 TRMS Pri | FLOAT | R | 0...100000
117 | I15 | MEAS2 | Pha.curr.I''L3 TRMS Pri | FLOAT | R | 0...100000
117 | I16 | MEAS2 | I'' Pri.Pos.seq.curr. | FLOAT | R | 0...100000
117 | I17 | MEAS2 | I'' Pri.Neg.seq.curr. | FLOAT | R | 0...100000
117 | I18 | MEAS2 | I'' Pri.Zero seq.curr. | FLOAT | R | 0...100000
117 | I19 | MEAS2 | I'' Pos.seq.curr.angle | FLOAT | R | -360...360
117 | I20 | MEAS2 | I'' Neg.seq.curr.angle | FLOAT | R | -360...360
117 | I21 | MEAS2 | I'' Zero seq.curr.angle | FLOAT | R | -360...360
117 | I22 | MEAS2 | Res.curr.I''01 TRMS Pri | FLOAT | R | 0...100000
117 | I23 | MEAS2 | Res.curr.I''02 TRMS Pri | FLOAT | R | 0...100000
117 | I24 | MEAS2 | Pha.I''L1 ampl. THD | FLOAT | R | 0...100
117 | I25 | MEAS2 | Pha.I''L1 pow. THD | FLOAT | R | 0...100
117 | I26 | MEAS2 | Pha.I''L2 ampl. THD | FLOAT | R | 0...100
117 | I27 | MEAS2 | Pha.I''L2 pow. THD | FLOAT | R | 0...100
117 | I28 | MEAS2 | Pha.I''L3 ampl. THD | FLOAT | R | 0...100
117 | I29 | MEAS2 | Pha.I''L3 pow. THD | FLOAT | R | 0...100
117 | I30 | MEAS2 | Res.I''01 ampl. THD | FLOAT | R | 0...100
117 | I31 | MEAS2 | Res.I''01 pow. THD | FLOAT | R | 0...100
117 | I32 | MEAS2 | Res.I''02 ampl. THD | FLOAT | R | 0...100
117 | I33 | MEAS2 | Res.I''02 pow. THD | FLOAT | R | 0...100
117 | I34 | MEAS2 | MEAS2 IL ang. Ref | FLOAT | R | -360...360
118 | S1 | MEAS3 | Voltage meas update interval | UINT32 | RW | 5...10000
118 | I1 | MEAS3 | Pos.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I2 | MEAS3 | Neg.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I3 | MEAS3 | Zero.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I4 | MEAS3 | Pos.Seq volt.Angle | FLOAT | R | -360...360
118 | I5 | MEAS3 | Neg.Seq.volt.Angle | FLOAT | R | -360...360
118 | I6 | MEAS3 | Zero.Seq.volt.Angle | FLOAT | R | -360...360
118 | I7 | MEAS3 | System volt UL12 mag | FLOAT | R | 0...1000000
118 | I8 | MEAS3 | System volt UL12 mag(kV) | FLOAT | R | 0...1000
118 | I9 | MEAS3 | System volt UL12 ang | FLOAT | R | -360...360
118 | I10 | MEAS3 | System volt UL23 mag | FLOAT | R | 0...1000000
118 | I11 | MEAS3 | System volt UL23 mag(kV) | FLOAT | R | 0...1000
118 | I12 | MEAS3 | System volt UL23 ang | FLOAT | R | -360...360
118 | I13 | MEAS3 | System volt UL31 mag | FLOAT | R | 0...1000000
118 | I14 | MEAS3 | System volt UL31 mag(kV) | FLOAT | R | 0...1000
118 | I15 | MEAS3 | System volt UL31 ang | FLOAT | R | -360...360
118 | I16 | MEAS3 | System volt UL1 mag | FLOAT | R | 0...1000000
118 | I17 | MEAS3 | System volt UL1 mag(kV) | FLOAT | R | 0...1000
118 | I18 | MEAS3 | System volt UL1 ang | FLOAT | R | -360...360
118 | I19 | MEAS3 | System volt UL2 mag | FLOAT | R | 0...1000000
118 | I20 | MEAS3 | System volt UL2 mag(kV) | FLOAT | R | 0...1000
118 | I21 | MEAS3 | System volt UL2 ang | FLOAT | R | -360...360
118 | I22 | MEAS3 | System volt UL3 mag | FLOAT | R | 0...1000000
118 | I23 | MEAS3 | System volt UL3 mag(kV) | FLOAT | R | 0...1000
118 | I24 | MEAS3 | System volt UL3 ang | FLOAT | R | -360...360
118 | I25 | MEAS3 | System volt U0 mag | FLOAT | R | 0...1000000
118 | I26 | MEAS3 | System volt U0 mag(kV) | FLOAT | R | 0...1000
118 | I27 | MEAS3 | System volt U0 mag(%) | FLOAT | R | 0...120
118 | I28 | MEAS3 | System volt U0 ang | FLOAT | R | -360...360
118 | I29 | MEAS3 | System volt U3 mag | FLOAT | R | 0...1000000
118 | I30 | MEAS3 | System volt U3 mag(kV) | FLOAT | R | 0...1000
118 | I31 | MEAS3 | System volt U3 ang | FLOAT | R | -360...360
118 | I32 | MEAS3 | System volt U4 mag | FLOAT | R | 0...1000000
118 | I33 | MEAS3 | System volt U4 mag(kV) | FLOAT | R | 0...1000
118 | I34 | MEAS3 | System volt U4 ang | FLOAT | R | -360...360
188 | I1 | IMERX | IL1 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I2 | IMERX | IL1 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I3 | IMERX | IL2 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I4 | IMERX | IL2 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I5 | IMERX | IL3 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I6 | IMERX | IL3 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I7 | IMERX | Pos.seq. Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I8 | IMERX | Pos.Seq. Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I9 | IMERX | I01 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I10 | IMERX | I01 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I11 | IMERX | I02 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I12 | IMERX | I02 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I13 | IMERX | I01 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I14 | IMERX | I01 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
188 | I15 | IMERX | I02 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I16 | IMERX | I02 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
119 | S1 | POW1 | Power meas update interval | UINT32 | RW | 5...10000
119 | S2 | POW1 | Nominal Power kVA | FLOAT | RW | 0.1...500000
119 | I1 | POW1 | PQ Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Ind;2=Q2 Rev Cap;3=Q3 Rev Ind;4=Q4 Fwd Cap
119 | I2 | POW1 | VA Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Cap, AV;2=Q2 Rev Ind AV;3=Q3 Rev Cap VA;4=Q4 Fwd Ind VA
119 | I3 | POW1 | Export Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I4 | POW1 | Export Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I5 | POW1 | Import Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I6 | POW1 | Import Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I7 | POW1 | Active Energy (P) Export/Import balance MWh | INT32 | R | -2147483647...2147483647
119 | I8 | POW1 | Active Energy (P) Export/Import balance kWh | INT32 | R | -2147483647...2147483647
119 | I9 | POW1 | Exported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I10 | POW1 | Exported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I11 | POW1 | Imported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I12 | POW1 | Imported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I13 | POW1 | Reactive Energy (Q) balance while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I14 | POW1 | Reactive Energy (Q) balance while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I15 | POW1 | Exported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I16 | POW1 | Exported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I17 | POW1 | Imported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I18 | POW1 | Imported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I19 | POW1 | Reactive Energy (Q) balance while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I20 | POW1 | Reactive Energy (Q) balance while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I21 | POW1 | Apparent Energy (S) while Export (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I22 | POW1 | Apparent Energy (S) while Export (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I23 | POW1 | Apparent Energy (S) while Import (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I24 | POW1 | Apparent Energy (S) while Import (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I25 | POW1 | Apparent Energy (S) Net | INT32 | R | -2147483647...2147483647
119 | I26 | POW1 | Real Energy (P) Net | INT32 | RW | -2147483647...2147483647
119 | I27 | POW1 | Reactive Energy (Q) Net | INT32 | RW | -2147483647...2147483647
119 | I28 | POW1 | Real Energy (P) Supply (Default supply direction towards busbar) | INT32 | RW | -2147483647...2147483647
119 | I29 | POW1 | Reactive Energy (Q) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
119 | I30 | POW1 | Real Energy (P) Demand (Default demand direction from busbar) | INT32 | RW | -2147483647...2147483647
119 | I31 | POW1 | Reactive Energy (Q) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
119 | S3 | POW1 | Reset 3ph Energies | UINT32 | RW | 0=-;1=Reset
119 | I32 | POW1 | POW1 L1 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I33 | POW1 | POW1 L1 Active power (P) | FLOAT | R | -1000000...1000000
119 | I34 | POW1 | POW1 L1 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I35 | POW1 | POW1 L1 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I36 | POW1 | POW1 L1 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I37 | POW1 | L1 PF | FLOAT | R | -1000000...1000000
119 | I38 | POW1 | POW1 L2 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I39 | POW1 | POW1 L2 Active power (P) | FLOAT | R | -1000000...1000000
119 | I40 | POW1 | POW1 L2 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I41 | POW1 | POW1 L2 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I42 | POW1 | POW1 L2 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I43 | POW1 | L2 PF | FLOAT | R | -1000000...1000000
119 | I44 | POW1 | POW1 L3 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I45 | POW1 | POW1 L3 Active power (P) | FLOAT | R | -1000000...1000000
119 | I46 | POW1 | POW1 L3 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I47 | POW1 | POW1 L3 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I48 | POW1 | POW1 L3 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I49 | POW1 | L3 PF | FLOAT | R | -1000000...1000000
119 | I50 | POW1 | POW1 3PH Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I51 | POW1 | POW1 3PH Apparent power (S MVA) | FLOAT | R | -1000000...1000000
119 | I52 | POW1 | POW1 3PH Active power (P) | FLOAT | R | -1000000...1000000
119 | I53 | POW1 | POW1 3PH Active power (P MW) | FLOAT | R | -1000000...1000000
119 | I54 | POW1 | POW1 3PH Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I55 | POW1 | POW1 3PH Reactive power (QMVar) | FLOAT | R | -1000000...1000000
119 | I56 | POW1 | POW1 3PH Tan(phi) | FLOAT | R | -1000000...1000000
119 | I57 | POW1 | POW1 3PH Cos(phi) | FLOAT | R | -1000000...1000000
119 | I58 | POW1 | 3PH PF | FLOAT | R | -1000000...1000000
136 | S1 | IMP1 | Impedance meas. update interval | UINT32 | RW | 500...10000
136 | I1 | IMP1 | Primary L12 R | FLOAT | R | -1000000...1000000
136 | I2 | IMP1 | Primary L12 X | FLOAT | R | -1000000...1000000
136 | I3 | IMP1 | Primary L23 R | FLOAT | R | -1000000...1000000
136 | I4 | IMP1 | Primary L23 X | FLOAT | R | -1000000...1000000
136 | I5 | IMP1 | Primary L31 R | FLOAT | R | -1000000...1000000
136 | I6 | IMP1 | Primary L31 X | FLOAT | R | -1000000...1000000
136 | I7 | IMP1 | Primary Z12 | FLOAT | R | -1000000...1000000
136 | I8 | IMP1 | Primary Z23 | FLOAT | R | -1000000...1000000
136 | I9 | IMP1 | Primary Z31 | FLOAT | R | -1000000...1000000
136 | I10 | IMP1 | Angle Z12 | FLOAT | R | -360...360
136 | I11 | IMP1 | Angle Z23 | FLOAT | R | -360...360
136 | I12 | IMP1 | Angle Z31 | FLOAT | R | -360...360
136 | I13 | IMP1 | Primary L1 R | FLOAT | R | -1000000...1000000
136 | I14 | IMP1 | Primary L1 X | FLOAT | R | -1000000...1000000
136 | I15 | IMP1 | Primary L2 R | FLOAT | R | -1000000...1000000
136 | I16 | IMP1 | Primary L2 X | FLOAT | R | -1000000...1000000
136 | I17 | IMP1 | Primary L3 R | FLOAT | R | -1000000...1000000
136 | I18 | IMP1 | Primary L3 X | FLOAT | R | -1000000...1000000
136 | I19 | IMP1 | Primary Z1 | FLOAT | R | -1000000...1000000
136 | I20 | IMP1 | Primary Z2 | FLOAT | R | -1000000...1000000
136 | I21 | IMP1 | Primary Z3 | FLOAT | R | -1000000...1000000
136 | I22 | IMP1 | Angle Z1 | FLOAT | R | -360...360
136 | I23 | IMP1 | Angle Z2 | FLOAT | R | -360...360
136 | I24 | IMP1 | Angle Z3 | FLOAT | R | -360...360
137 | I1 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I2 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I3 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I4 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I5 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I6 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I7 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I8 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I9 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I10 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I11 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I12 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
120 | S1 | FREQS | Smpl mode | UINT32 | RW | 0=Fixed;1=Tracking
120 | S2 | FREQS | Max. Tracking freq. allowed (+Nom f) | FLOAT | RW | 0.001...75
120 | S3 | FREQS | Sys.nom.f | FLOAT | RW | 7...75
120 | S4 | FREQS | Min. Tracking freq. allowed (- Nom f) | FLOAT | RW | 0.001...75
120 | I1 | FREQS | Track.sys.f | FLOAT | R | 0...75
120 | I2 | FREQS | f atm. Protections (when not measurable returns to nominal) | FLOAT | R | 0...75
120 | I3 | FREQS | f atm. Display (when not measurable is 0Hz) | FLOAT | R | 0...75
10 | I1 | DIGI | Dis 1-32 | UINT32 | R | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32
10 | I2 | DIGI | Dis 33-64 | UINT32 | R | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51
10 | I3 | DIGI | DI1 | SIGNAL_OUT | R | 0...4294967295
10 | V1 | DIGI | DI1 Counter | UINT32 | R | 0...4294967295
10 | V2 | DIGI | DI1 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I4 | DIGI | DI2 | SIGNAL_OUT | R | 0...4294967295
10 | V3 | DIGI | DI2 Counter | UINT32 | R | 0...4294967295
10 | V4 | DIGI | DI2 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I5 | DIGI | DI3 | SIGNAL_OUT | R | 0...4294967295
10 | V5 | DIGI | DI3 Counter | UINT32 | R | 0...4294967295
10 | V6 | DIGI | DI3 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I6 | DIGI | DI4 | SIGNAL_OUT | R | 0...4294967295
10 | V7 | DIGI | DI4 Counter | UINT32 | R | 0...4294967295
10 | V8 | DIGI | DI4 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I7 | DIGI | DI5 | SIGNAL_OUT | R | 0...4294967295
10 | V9 | DIGI | DI5 Counter | UINT32 | R | 0...4294967295
10 | V10 | DIGI | DI5 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I8 | DIGI | DI6 | SIGNAL_OUT | R | 0...4294967295
10 | V11 | DIGI | DI6 Counter | UINT32 | R | 0...4294967295
10 | V12 | DIGI | DI6 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I9 | DIGI | DI7 | SIGNAL_OUT | R | 0...4294967295
10 | V13 | DIGI | DI7 Counter | UINT32 | R | 0...4294967295
10 | V14 | DIGI | DI7 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I10 | DIGI | DI8 | SIGNAL_OUT | R | 0...4294967295
10 | V15 | DIGI | DI8 Counter | UINT32 | R | 0...4294967295
10 | V16 | DIGI | DI8 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I11 | DIGI | DI9 | SIGNAL_OUT | R | 0...4294967295
10 | V17 | DIGI | DI9 Counter | UINT32 | R | 0...4294967295
10 | V18 | DIGI | DI9 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I12 | DIGI | DI10 | SIGNAL_OUT | R | 0...4294967295
10 | V19 | DIGI | DI10 Counter | UINT32 | R | 0...4294967295
10 | V20 | DIGI | DI10 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I13 | DIGI | DI11 | SIGNAL_OUT | R | 0...4294967295
10 | V21 | DIGI | DI11 Counter | UINT32 | R | 0...4294967295
10 | V22 | DIGI | DI11 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I14 | DIGI | DI12 | SIGNAL_OUT | R | 0...4294967295
10 | V23 | DIGI | DI12 Counter | UINT32 | R | 0...4294967295
10 | V24 | DIGI | DI12 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I15 | DIGI | DI13 | SIGNAL_OUT | R | 0...4294967295
10 | V25 | DIGI | DI13 Counter | UINT32 | R | 0...4294967295
10 | V26 | DIGI | DI13 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I16 | DIGI | DI14 | SIGNAL_OUT | R | 0...4294967295
10 | V27 | DIGI | DI14 Counter | UINT32 | R | 0...4294967295
10 | V28 | DIGI | DI14 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I17 | DIGI | DI15 | SIGNAL_OUT | R | 0...4294967295
10 | V29 | DIGI | DI15 Counter | UINT32 | R | 0...4294967295
10 | V30 | DIGI | DI15 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I18 | DIGI | DI16 | SIGNAL_OUT | R | 0...4294967295
10 | V31 | DIGI | DI16 Counter | UINT32 | R | 0...4294967295
10 | V32 | DIGI | DI16 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I19 | DIGI | DI17 | SIGNAL_OUT | R | 0...4294967295
10 | V33 | DIGI | DI17 Counter | UINT32 | R | 0...4294967295
10 | V34 | DIGI | DI17 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I20 | DIGI | DI18 | SIGNAL_OUT | R | 0...4294967295
10 | V35 | DIGI | DI18 Counter | UINT32 | R | 0...4294967295
10 | V36 | DIGI | DI18 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I21 | DIGI | DI19 | SIGNAL_OUT | R | 0...4294967295
10 | V37 | DIGI | DI19 Counter | UINT32 | R | 0...4294967295
10 | V38 | DIGI | DI19 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I22 | DIGI | DI20 | SIGNAL_OUT | R | 0...4294967295
10 | V39 | DIGI | DI20 Counter | UINT32 | R | 0...4294967295
10 | V40 | DIGI | DI20 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I23 | DIGI | DI21 | SIGNAL_OUT | R | 0...4294967295
10 | V41 | DIGI | DI21 Counter | UINT32 | R | 0...4294967295
10 | V42 | DIGI | DI21 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I24 | DIGI | DI22 | SIGNAL_OUT | R | 0...4294967295
10 | V43 | DIGI | DI22 Counter | UINT32 | R | 0...4294967295
10 | V44 | DIGI | DI22 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I25 | DIGI | DI23 | SIGNAL_OUT | R | 0...4294967295
10 | V45 | DIGI | DI23 Counter | UINT32 | R | 0...4294967295
10 | V46 | DIGI | DI23 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I26 | DIGI | DI24 | SIGNAL_OUT | R | 0...4294967295
10 | V47 | DIGI | DI24 Counter | UINT32 | R | 0...4294967295
10 | V48 | DIGI | DI24 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I27 | DIGI | DI25 | SIGNAL_OUT | R | 0...4294967295
10 | V49 | DIGI | DI25 Counter | UINT32 | R | 0...4294967295
10 | V50 | DIGI | DI25 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I28 | DIGI | DI26 | SIGNAL_OUT | R | 0...4294967295
10 | V51 | DIGI | DI26 Counter | UINT32 | R | 0...4294967295
10 | V52 | DIGI | DI26 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I29 | DIGI | DI27 | SIGNAL_OUT | R | 0...4294967295
10 | V53 | DIGI | DI27 Counter | UINT32 | R | 0...4294967295
10 | V54 | DIGI | DI27 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I30 | DIGI | DI28 | SIGNAL_OUT | R | 0...4294967295
10 | V55 | DIGI | DI28 Counter | UINT32 | R | 0...4294967295
10 | V56 | DIGI | DI28 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I31 | DIGI | DI29 | SIGNAL_OUT | R | 0...4294967295
10 | V57 | DIGI | DI29 Counter | UINT32 | R | 0...4294967295
10 | V58 | DIGI | DI29 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I32 | DIGI | DI30 | SIGNAL_OUT | R | 0...4294967295
10 | V59 | DIGI | DI30 Counter | UINT32 | R | 0...4294967295
10 | V60 | DIGI | DI30 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I33 | DIGI | DI31 | SIGNAL_OUT | R | 0...4294967295
10 | V61 | DIGI | DI31 Counter | UINT32 | R | 0...4294967295
10 | V62 | DIGI | DI31 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I34 | DIGI | DI32 | SIGNAL_OUT | R | 0...4294967295
10 | V63 | DIGI | DI32 Counter | UINT32 | R | 0...4294967295
10 | V64 | DIGI | DI32 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I35 | DIGI | DI33 | SIGNAL_OUT | R | 0...4294967295
10 | V65 | DIGI | DI33 Counter | UINT32 | R | 0...4294967295
10 | V66 | DIGI | DI33 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I36 | DIGI | DI34 | SIGNAL_OUT | R | 0...4294967295
10 | V67 | DIGI | DI34 Counter | UINT32 | R | 0...4294967295
10 | V68 | DIGI | DI34 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I37 | DIGI | DI35 | SIGNAL_OUT | R | 0...4294967295
10 | V69 | DIGI | DI35 Counter | UINT32 | R | 0...4294967295
10 | V70 | DIGI | DI35 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I38 | DIGI | DI36 | SIGNAL_OUT | R | 0...4294967295
10 | V71 | DIGI | DI36 Counter | UINT32 | R | 0...4294967295
10 | V72 | DIGI | DI36 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I39 | DIGI | DI37 | SIGNAL_OUT | R | 0...4294967295
10 | V73 | DIGI | DI37 Counter | UINT32 | R | 0...4294967295
10 | V74 | DIGI | DI37 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I40 | DIGI | DI38 | SIGNAL_OUT | R | 0...4294967295
10 | V75 | DIGI | DI38 Counter | UINT32 | R | 0...4294967295
10 | V76 | DIGI | DI38 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I41 | DIGI | DI39 | SIGNAL_OUT | R | 0...4294967295
10 | V77 | DIGI | DI39 Counter | UINT32 | R | 0...4294967295
10 | V78 | DIGI | DI39 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I42 | DIGI | DI40 | SIGNAL_OUT | R | 0...4294967295
10 | V79 | DIGI | DI40 Counter | UINT32 | R | 0...4294967295
10 | V80 | DIGI | DI40 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I43 | DIGI | DI41 | SIGNAL_OUT | R | 0...4294967295
10 | V81 | DIGI | DI41 Counter | UINT32 | R | 0...4294967295
10 | V82 | DIGI | DI41 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I44 | DIGI | DI42 | SIGNAL_OUT | R | 0...4294967295
10 | V83 | DIGI | DI42 Counter | UINT32 | R | 0...4294967295
10 | V84 | DIGI | DI42 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I45 | DIGI | DI43 | SIGNAL_OUT | R | 0...4294967295
10 | V85 | DIGI | DI43 Counter | UINT32 | R | 0...4294967295
10 | V86 | DIGI | DI43 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I46 | DIGI | DI44 | SIGNAL_OUT | R | 0...4294967295
10 | V87 | DIGI | DI44 Counter | UINT32 | R | 0...4294967295
10 | V88 | DIGI | DI44 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I47 | DIGI | DI45 | SIGNAL_OUT | R | 0...4294967295
10 | V89 | DIGI | DI45 Counter | UINT32 | R | 0...4294967295
10 | V90 | DIGI | DI45 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I48 | DIGI | DI46 | SIGNAL_OUT | R | 0...4294967295
10 | V91 | DIGI | DI46 Counter | UINT32 | R | 0...4294967295
10 | V92 | DIGI | DI46 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I49 | DIGI | DI47 | SIGNAL_OUT | R | 0...4294967295
10 | V93 | DIGI | DI47 Counter | UINT32 | R | 0...4294967295
10 | V94 | DIGI | DI47 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I50 | DIGI | DI48 | SIGNAL_OUT | R | 0...4294967295
10 | V95 | DIGI | DI48 Counter | UINT32 | R | 0...4294967295
10 | V96 | DIGI | DI48 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I51 | DIGI | DI49 | SIGNAL_OUT | R | 0...4294967295
10 | V97 | DIGI | DI49 Counter | UINT32 | R | 0...4294967295
10 | V98 | DIGI | DI49 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I52 | DIGI | DI50 | SIGNAL_OUT | R | 0...4294967295
10 | V99 | DIGI | DI50 Counter | UINT32 | R | 0...4294967295
10 | V100 | DIGI | DI50 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I53 | DIGI | DI51 | SIGNAL_OUT | R | 0...4294967295
10 | V101 | DIGI | DI51 Counter | UINT32 | R | 0...4294967295
10 | V102 | DIGI | DI51 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | S1 | DIGI | EventMaskLo | UINT32 | RW | 0...4294967295
10 | S2 | DIGI | EventMaskHi | UINT32 | RW | 0...4294967295
11 | S1 | DIGI2 | EventMaskLo | UINT32 | RW | 0...4294967295
11 | S2 | DIGI2 | EventMaskHi | UINT32 | RW | 0...4294967295
15 | O1 | RELE | Outputs status | UINT32 | R | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15
15 | O2 | RELE | OUT1 | SIGNAL_IN | RW | 0...4294967295
15 | O3 | RELE | OUT2 | SIGNAL_IN | RW | 0...4294967295
15 | O4 | RELE | OUT3 | SIGNAL_IN | RW | 0...4294967295
15 | O5 | RELE | OUT4 | SIGNAL_IN | RW | 0...4294967295
15 | O6 | RELE | OUT5 | SIGNAL_IN | RW | 0...4294967295
15 | O7 | RELE | OUT6 | SIGNAL_IN | RW | 0...4294967295
15 | O8 | RELE | OUT7 | SIGNAL_IN | RW | 0...4294967295
15 | O9 | RELE | OUT8 | SIGNAL_IN | RW | 0...4294967295
15 | O10 | RELE | OUT9 | SIGNAL_IN | RW | 0...4294967295
15 | O11 | RELE | OUT10 | SIGNAL_IN | RW | 0...4294967295
15 | O12 | RELE | OUT11 | SIGNAL_IN | RW | 0...4294967295
15 | O13 | RELE | OUT12 | SIGNAL_IN | RW | 0...4294967295
15 | O14 | RELE | OUT13 | SIGNAL_IN | RW | 0...4294967295
15 | O15 | RELE | OUT14 | SIGNAL_IN | RW | 0...4294967295
15 | O16 | RELE | OUT15 | SIGNAL_IN | RW | 0...4294967295
121 | O1 | LED | LED START | SIGNAL_IN | RW | 0...4294967295
121 | O2 | LED | LED TRIP | SIGNAL_IN | RW | 0...4294967295
121 | O3 | LED | User LED 1 | SIGNAL_IN | RW | 0...4294967295
121 | O4 | LED | User LED 2 | SIGNAL_IN | RW | 0...4294967295
121 | O5 | LED | User LED 3 | SIGNAL_IN | RW | 0...4294967295
121 | O6 | LED | User LED 4 | SIGNAL_IN | RW | 0...4294967295
121 | O7 | LED | User LED 5 | SIGNAL_IN | RW | 0...4294967295
121 | O8 | LED | User LED 6 | SIGNAL_IN | RW | 0...4294967295
121 | O9 | LED | User LED 7 | SIGNAL_IN | RW | 0...4294967295
121 | O10 | LED | User LED 8 | SIGNAL_IN | RW | 0...4294967295
121 | O11 | LED | User LED 9 | SIGNAL_IN | RW | 0...4294967295
121 | O12 | LED | User LED 10 | SIGNAL_IN | RW | 0...4294967295
121 | O13 | LED | User LED 11 | SIGNAL_IN | RW | 0...4294967295
121 | O14 | LED | User LED 12 | SIGNAL_IN | RW | 0...4294967295
121 | O15 | LED | User LED 13 | SIGNAL_IN | RW | 0...4294967295
121 | O16 | LED | User LED 14 | SIGNAL_IN | RW | 0...4294967295
121 | O17 | LED | User LED 15 | SIGNAL_IN | RW | 0...4294967295
121 | O18 | LED | User LED 16 | SIGNAL_IN | RW | 0...4294967295
122 | O1 | LEDX | User LED 17 | SIGNAL_IN | RW | 0...4294967295
122 | O2 | LEDX | User LED 18 | SIGNAL_IN | RW | 0...4294967295
122 | O3 | LEDX | User LED 19 | SIGNAL_IN | RW | 0...4294967295
122 | O4 | LEDX | User LED 20 | SIGNAL_IN | RW | 0...4294967295
122 | O5 | LEDX | User LED 21 | SIGNAL_IN | RW | 0...4294967295
122 | O6 | LEDX | User LED 22 | SIGNAL_IN | RW | 0...4294967295
122 | O7 | LEDX | User LED 23 | SIGNAL_IN | RW | 0...4294967295
122 | O8 | LEDX | User LED 24 | SIGNAL_IN | RW | 0...4294967295
122 | O9 | LEDX | User LED 25 | SIGNAL_IN | RW | 0...4294967295
122 | O10 | LEDX | User LED 26 | SIGNAL_IN | RW | 0...4294967295
122 | O11 | LEDX | User LED 27 | SIGNAL_IN | RW | 0...4294967295
122 | O12 | LEDX | User LED 28 | SIGNAL_IN | RW | 0...4294967295
122 | O13 | LEDX | User LED 29 | SIGNAL_IN | RW | 0...4294967295
122 | O14 | LEDX | User LED 30 | SIGNAL_IN | RW | 0...4294967295
122 | O15 | LEDX | User LED 31 | SIGNAL_IN | RW | 0...4294967295
122 | O16 | LEDX | User LED 32 | SIGNAL_IN | RW | 0...4294967295
122 | O17 | LEDX | User LED 33 | SIGNAL_IN | RW | 0...4294967295
122 | O18 | LEDX | User LED 34 | SIGNAL_IN | RW | 0...4294967295
122 | O19 | LEDX | User LED 35 | SIGNAL_IN | RW | 0...4294967295
122 | O20 | LEDX | User LED 36 | SIGNAL_IN | RW | 0...4294967295
122 | O21 | LEDX | User LED 37 | SIGNAL_IN | RW | 0...4294967295
122 | O22 | LEDX | User LED 38 | SIGNAL_IN | RW | 0...4294967295
122 | O23 | LEDX | User LED 39 | SIGNAL_IN | RW | 0...4294967295
122 | O24 | LEDX | User LED 40 | SIGNAL_IN | RW | 0...4294967295
122 | O25 | LEDX | User LED 41 | SIGNAL_IN | RW | 0...4294967295
122 | O26 | LEDX | User LED 42 | SIGNAL_IN | RW | 0...4294967295
122 | O27 | LEDX | User LED 43 | SIGNAL_IN | RW | 0...4294967295
122 | O28 | LEDX | User LED 44 | SIGNAL_IN | RW | 0...4294967295
122 | O29 | LEDX | User LED 45 | SIGNAL_IN | RW | 0...4294967295
122 | O30 | LEDX | User LED 46 | SIGNAL_IN | RW | 0...4294967295
122 | O31 | LEDX | User LED 47 | SIGNAL_IN | RW | 0...4294967295
122 | O32 | LEDX | User LED 48 | SIGNAL_IN | RW | 0...4294967295
65 | V1 | SGS | Active setting group | UINT32 | R | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
65 | S1 | SGS | Force SG | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | S2 | SGS | Force SG change | UINT32 | RW | 0=Disabled;1=Enabled
65 | S3 | SGS | Used setting groups | UINT32 | RW | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
65 | S4 | SGS | Remote SG change | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | O1 | SGS | Forced SG in use | SIGNAL_OUT | RW | 0...4294967295
65 | O2 | SGS | SG1 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O3 | SGS | SG2 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O4 | SGS | SG3 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O5 | SGS | SG4 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O6 | SGS | SG5 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O7 | SGS | SG6 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O8 | SGS | SG7 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O9 | SGS | SG8 Active | SIGNAL_OUT | RW | 0...4294967295
7 | I1 | CTRL | Local/Remote status | UINT32 | R | 0=Remote;1=Local
123 | V1 | DEV | Serial number | UINT32 | R | 0...4294967295
123 | V2 | DEV | SW version | STRING | R | ...32
124 | S1 | EVENT | Clear Events | UINT32 | RW | 0=-;1=Clear
125 | I1 | DIAG | Diagnostic alarm status | UINT32 | R | 0b=Temp. out of range;1b=Voltage out of range;2b=HW configuration invalid;3b=Relay output failure;4b=Option card A alarm;5b=Option card B alarm;6b=Option card C alarm;7b=Option card D alarm;8b=Option card E alarm;9b=Option card F alarm;10b=GOOSE invalid;
125 | S1 | DIAG | Clear diagnostic alarm | UINT32 | W | 0=-;1=Clear
125 | I2 | DIAG | Internal temperature | FLOAT | R | 0...200
125 | I3 | DIAG | Internal voltage 24V | FLOAT | R | 0...50
125 | I4 | DIAG | Internal voltage 24V max | FLOAT | R | 0...50
125 | I5 | DIAG | Internal voltage 24V min | FLOAT | R | 0...50
125 | I6 | DIAG | Internal voltage 24V deviation | FLOAT | R | 0...50
138 | I1 | MBIO | Input value | FLOAT | R | -101...2000
138 | I2 | MBIO | Input value | FLOAT | R | -101...2000
138 | I3 | MBIO | Input value | FLOAT | R | -101...2000
138 | I4 | MBIO | Input value | FLOAT | R | -101...2000
138 | I5 | MBIO | Input value | FLOAT | R | -101...2000
138 | I6 | MBIO | Input value | FLOAT | R | -101...2000
138 | I7 | MBIO | Input value | FLOAT | R | -101...2000
138 | I8 | MBIO | Input value | FLOAT | R | -101...2000
138 | I9 | MBIO | Input value | FLOAT | R | -101...2000
138 | I10 | MBIO | Input value | FLOAT | R | -101...2000
138 | I11 | MBIO | Input value | FLOAT | R | -101...2000
138 | I12 | MBIO | Input value | FLOAT | R | -101...2000
138 | I13 | MBIO | Input value | FLOAT | R | -101...2000
138 | I14 | MBIO | Input value | FLOAT | R | -101...2000
138 | I15 | MBIO | Input value | FLOAT | R | -101...2000
138 | I16 | MBIO | Input value | FLOAT | R | -101...2000
138 | I17 | MBIO | Input value | FLOAT | R | -101...2000
138 | I18 | MBIO | Input value | FLOAT | R | -101...2000
138 | I19 | MBIO | Input value | FLOAT | R | -101...2000
138 | I20 | MBIO | Input value | FLOAT | R | -101...2000
138 | I21 | MBIO | Input value | FLOAT | R | -101...2000
138 | I22 | MBIO | Input value | FLOAT | R | -101...2000
138 | I23 | MBIO | Input value | FLOAT | R | -101...2000
138 | I24 | MBIO | Input value | FLOAT | R | -101...2000
138 | I25 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I26 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I27 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I28 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I29 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I30 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I31 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I32 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I33 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I34 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I35 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I36 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I37 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I38 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I39 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I40 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I41 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I42 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I43 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I44 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I45 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I46 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I47 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I48 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | O1 | MBIO | MBIO ModA Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O2 | MBIO | MBIO ModA Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O3 | MBIO | MBIO ModA Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O4 | MBIO | MBIO ModA Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O5 | MBIO | MBIO ModA Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O6 | MBIO | MBIO ModA Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O7 | MBIO | MBIO ModA Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O8 | MBIO | MBIO ModA Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O9 | MBIO | MBIO ModB Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O10 | MBIO | MBIO ModB Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O11 | MBIO | MBIO ModB Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O12 | MBIO | MBIO ModB Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O13 | MBIO | MBIO ModB Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O14 | MBIO | MBIO ModB Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O15 | MBIO | MBIO ModB Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O16 | MBIO | MBIO ModB Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O17 | MBIO | MBIO ModC Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O18 | MBIO | MBIO ModC Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O19 | MBIO | MBIO ModC Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O20 | MBIO | MBIO ModC Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O21 | MBIO | MBIO ModC Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O22 | MBIO | MBIO ModC Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O23 | MBIO | MBIO ModC Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O24 | MBIO | MBIO ModC Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
139 | V1 | LOGIC | Reset Latches | UINT32 | RW | 0=-;1=Reset
8 | O1 | LOGIC1 | Logic out 1-32 | UINT32 | RW | 0...4294967295
139 | O1 | LOGIC | Logical Output 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O2 | LOGIC | Logical Output 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O3 | LOGIC | Logical Output 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O4 | LOGIC | Logical Output 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O5 | LOGIC | Logical Output 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O6 | LOGIC | Logical Output 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O7 | LOGIC | Logical Output 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O8 | LOGIC | Logical Output 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O9 | LOGIC | Logical Output 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O10 | LOGIC | Logical Output 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O11 | LOGIC | Logical Output 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O12 | LOGIC | Logical Output 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O13 | LOGIC | Logical Output 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O14 | LOGIC | Logical Output 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O15 | LOGIC | Logical Output 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O16 | LOGIC | Logical Output 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O17 | LOGIC | Logical Output 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O18 | LOGIC | Logical Output 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O19 | LOGIC | Logical Output 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O20 | LOGIC | Logical Output 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O21 | LOGIC | Logical Output 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O22 | LOGIC | Logical Output 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O23 | LOGIC | Logical Output 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O24 | LOGIC | Logical Output 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O25 | LOGIC | Logical Output 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O26 | LOGIC | Logical Output 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O27 | LOGIC | Logical Output 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O28 | LOGIC | Logical Output 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O29 | LOGIC | Logical Output 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O30 | LOGIC | Logical Output 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O31 | LOGIC | Logical Output 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O32 | LOGIC | Logical Output 32 | SIGNAL_OUT | RW | 0...4294967295
139 | O33 | LOGIC | Logical Input 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O34 | LOGIC | Logical Input 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O35 | LOGIC | Logical Input 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O36 | LOGIC | Logical Input 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O37 | LOGIC | Logical Input 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O38 | LOGIC | Logical Input 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O39 | LOGIC | Logical Input 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O40 | LOGIC | Logical Input 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O41 | LOGIC | Logical Input 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O42 | LOGIC | Logical Input 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O43 | LOGIC | Logical Input 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O44 | LOGIC | Logical Input 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O45 | LOGIC | Logical Input 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O46 | LOGIC | Logical Input 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O47 | LOGIC | Logical Input 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O48 | LOGIC | Logical Input 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O49 | LOGIC | Logical Input 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O50 | LOGIC | Logical Input 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O51 | LOGIC | Logical Input 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O52 | LOGIC | Logical Input 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O53 | LOGIC | Logical Input 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O54 | LOGIC | Logical Input 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O55 | LOGIC | Logical Input 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O56 | LOGIC | Logical Input 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O57 | LOGIC | Logical Input 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O58 | LOGIC | Logical Input 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O59 | LOGIC | Logical Input 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O60 | LOGIC | Logical Input 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O61 | LOGIC | Logical Input 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O62 | LOGIC | Logical Input 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O63 | LOGIC | Logical Input 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O64 | LOGIC | Logical Input 32 | SIGNAL_OUT | RW | 0...4294967295
8 | S1 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
8 | S2 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
9 | S1 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
9 | S2 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
140 | O1 | TIMER | Timer1 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O2 | TIMER | Timer2 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O3 | TIMER | Timer3 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O4 | TIMER | Timer4 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O5 | TIMER | Timer5 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O6 | TIMER | Timer6 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O7 | TIMER | Timer7 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O8 | TIMER | Timer8 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O9 | TIMER | Timer9 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O10 | TIMER | Timer10 Output | SIGNAL_OUT | RW | 0...4294967295
2 | I1 | IRF | Internal Relay Fault status | UINT32 | R | 0b=Storage error;1b=Logic file missing;2b=Aquisition unit error;3b=Measurement config error;4b=Relay hardware setup error;5b=System overload error;6b=Not configured yet;7b=Firmware upgrade done;8b=Slot supervision error;9b=Software inconsistency error;10b=Safe setting mode active;
2 | S1 | IRF | Clear Fault status | UINT32 | W | 0=-;1=Clear
2 | I2 | IRF | Option card health status | UINT32 | R | 0b=Baseboard fault;1b=Card slot A fault;2b=Card slot B fault;3b=Card slot C fault;4b=Card slot D fault;5b=Card slot E fault;6b=Card slot F fault;
20 | S1 | NOC1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
20 | V1 | NOC1 | I> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
20 | V2 | NOC1 | I> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
20 | I1 | NOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
20 | I2 | NOC1 | I> starts | UINT32 | R | 0...4294967295
20 | I3 | NOC1 | I> trips | UINT32 | R | 0...4294967295
20 | I4 | NOC1 | I> blocks | UINT32 | R | 0...4294967295
20 | S2 | NOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
20 | S3 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S4 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S5 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S6 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S7 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S8 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S9 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S10 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S11 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S12 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S13 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S14 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S15 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S16 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S17 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S18 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S19 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S20 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S21 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S22 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S23 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S24 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S25 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S26 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S27 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S28 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S29 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S30 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S31 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S32 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S33 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S34 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | O1 | NOC1 | I> START (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O2 | NOC1 | I> START(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O3 | NOC1 | I> START(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O4 | NOC1 | I> START(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O5 | NOC1 | I> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O6 | NOC1 | I> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O7 | NOC1 | I> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O8 | NOC1 | I> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O9 | NOC1 | I> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
20 | V3 | NOC1 | Newest Register | UINT32 | R | 0...12
20 | V4 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V5 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V6 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V7 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V8 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V9 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V10 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V11 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V12 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V13 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V14 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V15 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V16 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V17 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V18 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V19 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V20 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V21 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V22 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V23 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V24 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V25 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V26 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V27 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V28 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V29 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V30 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V31 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V32 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V33 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V34 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V35 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V36 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V37 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V38 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V39 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | S35 | NOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
21 | S1 | NOC2 | I>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
21 | S2 | NOC2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
21 | V1 | NOC2 | I>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
21 | V2 | NOC2 | I>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
21 | I1 | NOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
21 | I2 | NOC2 | I>> starts | UINT32 | R | 0...4294967295
21 | I3 | NOC2 | I>> trips | UINT32 | R | 0...4294967295
21 | I4 | NOC2 | I>> blocks | UINT32 | R | 0...4294967295
21 | S3 | NOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
21 | S4 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S5 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S6 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S7 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S8 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S9 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S10 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S11 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S12 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S13 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S14 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S15 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S16 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S17 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S18 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S19 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S20 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S21 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S22 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S23 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S24 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S25 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S26 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S27 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S28 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S29 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S30 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S31 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S32 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S33 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S34 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S35 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | O1 | NOC2 | I>> START (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O2 | NOC2 | I>> START(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O3 | NOC2 | I>> START(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O4 | NOC2 | I>> START(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O5 | NOC2 | I>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O6 | NOC2 | I>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O7 | NOC2 | I>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O8 | NOC2 | I>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O9 | NOC2 | I>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
21 | V3 | NOC2 | Newest Register | UINT32 | R | 0...12
21 | V4 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V5 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V6 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V7 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V8 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V9 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V10 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V11 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V12 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V13 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V14 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V15 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V16 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V17 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V18 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V19 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V20 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V21 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V22 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V23 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V24 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V25 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V26 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V27 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V28 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V29 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V30 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V31 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V32 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V33 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V34 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V35 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V36 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V37 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V38 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V39 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | S36 | NOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
22 | S1 | NOC3 | I>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
22 | S2 | NOC3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
22 | V1 | NOC3 | I>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
22 | V2 | NOC3 | I>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
22 | I1 | NOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
22 | I2 | NOC3 | I>>> starts | UINT32 | R | 0...4294967295
22 | I3 | NOC3 | I>>> trips | UINT32 | R | 0...4294967295
22 | I4 | NOC3 | I>>> blocks | UINT32 | R | 0...4294967295
22 | S3 | NOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
22 | S4 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S5 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S6 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S7 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S8 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S9 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S10 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S11 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S12 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S13 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S14 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S15 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S16 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S17 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S18 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S19 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S20 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S21 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S22 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S23 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S24 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S25 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S26 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S27 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S28 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S29 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S30 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S31 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S32 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S33 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S34 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S35 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | O1 | NOC3 | I>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O2 | NOC3 | I>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O3 | NOC3 | I>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O4 | NOC3 | I>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O5 | NOC3 | I>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O6 | NOC3 | I>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O7 | NOC3 | I>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O8 | NOC3 | I>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O9 | NOC3 | I>>>BLOCKED | SIGNAL_OUT | RW | 0...4294967295
22 | V3 | NOC3 | Newest Register | UINT32 | R | 0...12
22 | V4 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V5 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V6 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V7 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V8 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V9 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V10 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V11 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V12 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V13 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V14 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V15 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V16 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V17 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V18 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V19 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V20 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V21 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V22 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V23 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V24 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V25 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V26 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V27 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V28 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V29 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V30 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V31 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V32 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V33 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V34 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V35 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V36 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V37 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V38 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V39 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | S36 | NOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
23 | S1 | NOC4 | I>>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
23 | S2 | NOC4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
23 | V1 | NOC4 | I>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
23 | V2 | NOC4 | I>>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
23 | I1 | NOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
23 | I2 | NOC4 | I>>>> starts | UINT32 | R | 0...4294967295
23 | I3 | NOC4 | I>>>> trips | UINT32 | R | 0...4294967295
23 | I4 | NOC4 | I>>>> blocks | UINT32 | R | 0...4294967295
23 | S3 | NOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
23 | S4 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S5 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S6 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S7 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S8 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S9 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S10 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S11 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S12 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S13 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S14 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S15 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S16 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S17 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S18 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S19 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S20 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S21 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S22 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S23 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S24 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S25 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S26 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S27 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S28 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S29 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S30 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S31 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S32 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S33 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S34 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S35 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | O1 | NOC4 | I>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O2 | NOC4 | I>>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O3 | NOC4 | I>>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O4 | NOC4 | I>>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O5 | NOC4 | I>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O6 | NOC4 | I>>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O7 | NOC4 | I>>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O8 | NOC4 | I>>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O9 | NOC4 | I>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
23 | V3 | NOC4 | Newest Register | UINT32 | R | 0...12
23 | V4 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V5 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V6 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V7 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V8 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V9 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V10 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V11 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V12 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V13 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V14 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V15 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V16 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V17 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V18 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V19 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V20 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V21 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V22 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V23 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V24 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V25 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V26 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V27 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V28 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V29 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V30 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V31 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V32 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V33 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V34 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V35 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V36 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V37 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V38 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V39 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | S36 | NOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
205 | V1 | ROC1 | Idrw> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
205 | I1 | ROC1 | Idrw> Imeas/Iset at the moment | FLOAT | R | -1250...1250
205 | I2 | ROC1 | Idrw> I/U Angle atm. | FLOAT | R | -360...360
205 | I3 | ROC1 | Idrw> I measured p.u. | FLOAT | R | 0...1250
205 | I4 | ROC1 | Idrw> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
205 | I5 | ROC1 | Idrw> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
205 | I6 | ROC1 | Idrw> U measured p.u. | FLOAT | R | 0...1250
205 | I7 | ROC1 | Idrw> starts | UINT32 | R | 0...4294967295
205 | I8 | ROC1 | Idrw> trips | UINT32 | R | 0...4294967295
205 | I9 | ROC1 | Idrw> blocks | UINT32 | R | 0...4294967295
205 | S1 | ROC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
205 | S2 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S3 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S4 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S5 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S6 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S7 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S8 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S9 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S10 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S11 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S12 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S13 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S14 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S15 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S16 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S17 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S18 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S19 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S20 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S21 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S22 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S23 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S24 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S25 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S26 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S27 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S28 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S29 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S30 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S31 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S32 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S33 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S34 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S35 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S36 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S37 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S38 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S39 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S40 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S41 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S42 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S43 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S44 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S45 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S46 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S47 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S48 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S49 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S50 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S51 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S52 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S53 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S54 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S55 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S56 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S57 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S58 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S59 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S60 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S61 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S62 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S63 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S64 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S65 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | O1 | ROC1 | Idrw> START | SIGNAL_OUT | RW | 0...4294967295
205 | O2 | ROC1 | Idrw> TRIP | SIGNAL_OUT | RW | 0...4294967295
205 | O3 | ROC1 | Idrw> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
205 | V2 | ROC1 | Newest Register | UINT32 | R | 0...12
205 | V3 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V4 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V5 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V6 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V7 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V8 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V9 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V10 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V11 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V12 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V13 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V14 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V15 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V16 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V17 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V18 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V19 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V20 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V21 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V22 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V23 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V24 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V25 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V26 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | S66 | ROC1 | EventMaskLo | UINT32 | RW | 0...4294967295
206 | V1 | ROC2 | Idrw>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
206 | I1 | ROC2 | Idrw>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
206 | I2 | ROC2 | Idrw>> I/U Angle atm. | FLOAT | R | -360...360
206 | I3 | ROC2 | Idrw>> I measured p.u. | FLOAT | R | 0...1250
206 | I4 | ROC2 | Idrw>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
206 | I5 | ROC2 | Idrw>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
206 | I6 | ROC2 | Idrw>> U measured p.u. | FLOAT | R | 0...1250
206 | I7 | ROC2 | Idrw>> starts | UINT32 | R | 0...4294967295
206 | I8 | ROC2 | Idrw>> trips | UINT32 | R | 0...4294967295
206 | I9 | ROC2 | Idrw>> blocks | UINT32 | R | 0...4294967295
206 | S1 | ROC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
206 | S2 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S3 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S4 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S5 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S6 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S7 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S8 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S9 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S10 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S11 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S12 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S13 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S14 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S15 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S16 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S17 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S18 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S19 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S20 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S21 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S22 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S23 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S24 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S25 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S26 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S27 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S28 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S29 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S30 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S31 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S32 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S33 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S34 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S35 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S36 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S37 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S38 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S39 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S40 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S41 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S42 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S43 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S44 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S45 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S46 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S47 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S48 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S49 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S50 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S51 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S52 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S53 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S54 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S55 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S56 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S57 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S58 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S59 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S60 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S61 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S62 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S63 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S64 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S65 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | O1 | ROC2 | Idrw>> START | SIGNAL_OUT | RW | 0...4294967295
206 | O2 | ROC2 | Idrw>> TRIP | SIGNAL_OUT | RW | 0...4294967295
206 | O3 | ROC2 | Idrw>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
206 | V2 | ROC2 | Newest Register | UINT32 | R | 0...12
206 | V3 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V4 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V5 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V6 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V7 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V8 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V9 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V10 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V11 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V12 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V13 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V14 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V15 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V16 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V17 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V18 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V19 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V20 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V21 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V22 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V23 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V24 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V25 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V26 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | S66 | ROC2 | EventMaskLo | UINT32 | RW | 0...4294967295
207 | V1 | ROC3 | Idrw>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
207 | I1 | ROC3 | Idrw>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
207 | I2 | ROC3 | Idrw>>> I/U Angle atm. | FLOAT | R | -360...360
207 | I3 | ROC3 | Idrw>>> I measured p.u. | FLOAT | R | 0...1250
207 | I4 | ROC3 | Idrw>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
207 | I5 | ROC3 | Idrw>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
207 | I6 | ROC3 | Idrw>>> U measured p.u. | FLOAT | R | 0...1250
207 | I7 | ROC3 | Idrw>>> starts | UINT32 | R | 0...4294967295
207 | I8 | ROC3 | Idrw>>> trips | UINT32 | R | 0...4294967295
207 | I9 | ROC3 | Idrw>>> blocks | UINT32 | R | 0...4294967295
207 | S1 | ROC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
207 | S2 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S3 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S4 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S5 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S6 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S7 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S8 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S9 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S10 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S11 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S12 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S13 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S14 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S15 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S16 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S17 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S18 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S19 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S20 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S21 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S22 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S23 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S24 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S25 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S26 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S27 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S28 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S29 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S30 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S31 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S32 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S33 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S34 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S35 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S36 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S37 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S38 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S39 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S40 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S41 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S42 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S43 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S44 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S45 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S46 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S47 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S48 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S49 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S50 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S51 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S52 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S53 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S54 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S55 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S56 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S57 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S58 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S59 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S60 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S61 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S62 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S63 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S64 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S65 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | O1 | ROC3 | Idrw>>> START | SIGNAL_OUT | RW | 0...4294967295
207 | O2 | ROC3 | Idrw>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
207 | O3 | ROC3 | Idrw>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
207 | V2 | ROC3 | Newest Register | UINT32 | R | 0...12
207 | V3 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V4 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V5 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V6 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V7 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V8 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V9 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V10 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V11 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V12 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V13 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V14 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V15 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V16 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V17 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V18 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V19 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V20 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V21 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V22 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V23 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V24 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V25 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V26 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | S66 | ROC3 | EventMaskLo | UINT32 | RW | 0...4294967295
208 | V1 | ROC4 | Idrw>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
208 | I1 | ROC4 | Idrw>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
208 | I2 | ROC4 | Idrw>>>> I/U Angle atm. | FLOAT | R | -360...360
208 | I3 | ROC4 | Idrw>>>> I measured p.u. | FLOAT | R | 0...1250
208 | I4 | ROC4 | Idrw>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
208 | I5 | ROC4 | Idrw>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
208 | I6 | ROC4 | Idrw>>>> U measured p.u. | FLOAT | R | 0...1250
208 | I7 | ROC4 | Idrw>>>> starts | UINT32 | R | 0...4294967295
208 | I8 | ROC4 | Idrw>>>> trips | UINT32 | R | 0...4294967295
208 | I9 | ROC4 | Idrw>>>> blocks | UINT32 | R | 0...4294967295
208 | S1 | ROC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
208 | S2 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S3 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S4 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S5 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S6 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S7 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S8 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S9 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S10 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S11 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S12 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S13 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S14 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S15 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S16 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S17 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S18 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S19 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S20 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S21 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S22 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S23 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S24 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S25 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S26 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S27 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S28 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S29 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S30 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S31 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S32 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S33 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S34 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S35 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S36 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S37 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S38 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S39 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S40 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S41 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S42 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S43 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S44 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S45 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S46 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S47 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S48 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S49 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S50 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S51 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S52 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S53 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S54 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S55 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S56 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S57 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S58 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S59 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S60 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S61 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S62 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S63 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S64 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S65 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | O1 | ROC4 | Idrw>>>> START | SIGNAL_OUT | RW | 0...4294967295
208 | O2 | ROC4 | Idrw>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
208 | O3 | ROC4 | Idrw>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
208 | V2 | ROC4 | Newest Register | UINT32 | R | 0...12
208 | V3 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V4 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V5 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V6 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V7 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V8 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V9 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V10 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V11 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V12 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V13 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V14 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V15 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V16 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V17 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V18 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V19 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V20 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V21 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V22 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V23 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V24 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V25 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V26 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | S66 | ROC4 | EventMaskLo | UINT32 | RW | 0...4294967295
209 | V1 | ROC5 | Idrw>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
209 | I1 | ROC5 | Idrw>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
209 | I2 | ROC5 | Idrw>>>>> I/U Angle atm. | FLOAT | R | -360...360
209 | I3 | ROC5 | Idrw>>>>> I measured p.u. | FLOAT | R | 0...1250
209 | I4 | ROC5 | Idrw>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
209 | I5 | ROC5 | Idrw>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
209 | I6 | ROC5 | Idrw>>>>> U measured p.u. | FLOAT | R | 0...1250
209 | I7 | ROC5 | Idrw>>>>> starts | UINT32 | R | 0...4294967295
209 | I8 | ROC5 | Idrw>>>>> trips | UINT32 | R | 0...4294967295
209 | I9 | ROC5 | Idrw>>>>> blocks | UINT32 | R | 0...4294967295
209 | S1 | ROC5 | Clear statistics | UINT32 | W | 0=-;1=Clear
209 | S2 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S3 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S4 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S5 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S6 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S7 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S8 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S9 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S10 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S11 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S12 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S13 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S14 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S15 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S16 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S17 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S18 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S19 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S20 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S21 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S22 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S23 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S24 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S25 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S26 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S27 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S28 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S29 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S30 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S31 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S32 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S33 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S34 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S35 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S36 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S37 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S38 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S39 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S40 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S41 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S42 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S43 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S44 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S45 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S46 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S47 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S48 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S49 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S50 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S51 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S52 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S53 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S54 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S55 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S56 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S57 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S58 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S59 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S60 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S61 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S62 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S63 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S64 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S65 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | O1 | ROC5 | Idrw>>>>> START | SIGNAL_OUT | RW | 0...4294967295
209 | O2 | ROC5 | Idrw>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
209 | O3 | ROC5 | Idrw>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
209 | V2 | ROC5 | Newest Register | UINT32 | R | 0...12
209 | V3 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V4 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V5 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V6 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V7 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V8 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V9 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V10 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V11 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V12 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V13 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V14 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V15 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V16 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V17 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V18 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V19 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V20 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V21 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V22 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V23 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V24 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V25 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V26 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | S66 | ROC5 | EventMaskLo | UINT32 | RW | 0...4294967295
210 | V1 | ROC6 | Idrw>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
210 | I1 | ROC6 | Idrw>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
210 | I2 | ROC6 | Idrw>>>>>> I/U Angle atm. | FLOAT | R | -360...360
210 | I3 | ROC6 | Idrw>>>>>> I measured p.u. | FLOAT | R | 0...1250
210 | I4 | ROC6 | Idrw>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
210 | I5 | ROC6 | Idrw>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
210 | I6 | ROC6 | Idrw>>>>>> U measured p.u. | FLOAT | R | 0...1250
210 | I7 | ROC6 | Idrw>>>>>> starts | UINT32 | R | 0...4294967295
210 | I8 | ROC6 | Idrw>>>>>> trips | UINT32 | R | 0...4294967295
210 | I9 | ROC6 | Idrw>>>>>> blocks | UINT32 | R | 0...4294967295
210 | S1 | ROC6 | Clear statistics | UINT32 | W | 0=-;1=Clear
210 | S2 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S3 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S4 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S5 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S6 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S7 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S8 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S9 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S10 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S11 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S12 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S13 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S14 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S15 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S16 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S17 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S18 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S19 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S20 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S21 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S22 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S23 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S24 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S25 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S26 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S27 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S28 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S29 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S30 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S31 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S32 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S33 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S34 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S35 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S36 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S37 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S38 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S39 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S40 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S41 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S42 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S43 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S44 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S45 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S46 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S47 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S48 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S49 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S50 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S51 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S52 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S53 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S54 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S55 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S56 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S57 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S58 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S59 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S60 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S61 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S62 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S63 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S64 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S65 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | O1 | ROC6 | Idrw>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
210 | O2 | ROC6 | Idrw>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
210 | O3 | ROC6 | Idrw>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
210 | V2 | ROC6 | Newest Register | UINT32 | R | 0...12
210 | V3 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V4 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V5 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V6 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V7 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V8 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V9 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V10 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V11 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V12 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V13 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V14 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V15 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V16 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V17 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V18 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V19 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V20 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V21 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V22 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V23 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V24 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V25 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V26 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | S66 | ROC6 | EventMaskLo | UINT32 | RW | 0...4294967295
211 | V1 | ROC7 | Idrw>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
211 | I1 | ROC7 | Idrw>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
211 | I2 | ROC7 | Idrw>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
211 | I3 | ROC7 | Idrw>>>>>>> I measured p.u. | FLOAT | R | 0...1250
211 | I4 | ROC7 | Idrw>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
211 | I5 | ROC7 | Idrw>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
211 | I6 | ROC7 | Idrw>>>>>>> U measured p.u. | FLOAT | R | 0...1250
211 | I7 | ROC7 | Idrw>>>>>>> starts | UINT32 | R | 0...4294967295
211 | I8 | ROC7 | Idrw>>>>>>> trips | UINT32 | R | 0...4294967295
211 | I9 | ROC7 | Idrw>>>>>>> blocks | UINT32 | R | 0...4294967295
211 | S1 | ROC7 | Clear statistics | UINT32 | W | 0=-;1=Clear
211 | S2 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S3 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S4 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S5 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S6 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S7 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S8 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S9 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S10 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S11 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S12 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S13 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S14 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S15 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S16 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S17 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S18 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S19 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S20 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S21 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S22 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S23 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S24 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S25 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S26 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S27 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S28 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S29 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S30 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S31 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S32 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S33 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S34 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S35 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S36 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S37 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S38 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S39 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S40 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S41 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S42 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S43 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S44 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S45 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S46 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S47 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S48 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S49 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S50 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S51 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S52 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S53 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S54 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S55 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S56 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S57 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S58 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S59 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S60 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S61 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S62 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S63 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S64 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S65 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | O1 | ROC7 | Idrw>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
211 | O2 | ROC7 | Idrw>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
211 | O3 | ROC7 | Idrw>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
211 | V2 | ROC7 | Newest Register | UINT32 | R | 0...12
211 | V3 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V4 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V5 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V6 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V7 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V8 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V9 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V10 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V11 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V12 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V13 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V14 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V15 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V16 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V17 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V18 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V19 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V20 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V21 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V22 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V23 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V24 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V25 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V26 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | S66 | ROC7 | EventMaskLo | UINT32 | RW | 0...4294967295
212 | V1 | ROC8 | Idrw>>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
212 | I1 | ROC8 | Idrw>>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
212 | I2 | ROC8 | Idrw>>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
212 | I3 | ROC8 | Idrw>>>>>>>> I measured p.u. | FLOAT | R | 0...1250
212 | I4 | ROC8 | Idrw>>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
212 | I5 | ROC8 | Idrw>>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
212 | I6 | ROC8 | Idrw>>>>>>>> U measured p.u. | FLOAT | R | 0...1250
212 | I7 | ROC8 | Idrw>>>>>>>> starts | UINT32 | R | 0...4294967295
212 | I8 | ROC8 | Idrw>>>>>>>> trips | UINT32 | R | 0...4294967295
212 | I9 | ROC8 | Idrw>>>>>>>> blocks | UINT32 | R | 0...4294967295
212 | S1 | ROC8 | Clear statistics | UINT32 | W | 0=-;1=Clear
212 | S2 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S3 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S4 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S5 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S6 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S7 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S8 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S9 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S10 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S11 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S12 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S13 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S14 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S15 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S16 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S17 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S18 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S19 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S20 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S21 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S22 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S23 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S24 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S25 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S26 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S27 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S28 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S29 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S30 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S31 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S32 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S33 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S34 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S35 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S36 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S37 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S38 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S39 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S40 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S41 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S42 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S43 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S44 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S45 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S46 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S47 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S48 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S49 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S50 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S51 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S52 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S53 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S54 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S55 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S56 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S57 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S58 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S59 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S60 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S61 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S62 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S63 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S64 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S65 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | O1 | ROC8 | Idrw>>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
212 | O2 | ROC8 | Idrw>>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
212 | O3 | ROC8 | Idrw>>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
212 | V2 | ROC8 | Newest Register | UINT32 | R | 0...12
212 | V3 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V4 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V5 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V6 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V7 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V8 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V9 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V10 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V11 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V12 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V13 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V14 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V15 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V16 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V17 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V18 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V19 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V20 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V21 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V22 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V23 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V24 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V25 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V26 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | S66 | ROC8 | EventMaskLo | UINT32 | RW | 0...4294967295
213 | V1 | ROV1 | Urw>/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
213 | I1 | ROV1 | Urw>/< Umeas/Uset at the moment | FLOAT | R | 0...1250
213 | I2 | ROV1 | Urw>/< U measured p.u. | FLOAT | R | 0...1250
213 | I3 | ROV1 | Urw>/< starts | UINT32 | R | 0...4294967295
213 | I4 | ROV1 | Urw>/< trips | UINT32 | R | 0...4294967295
213 | I5 | ROV1 | Urw>/< blocks | UINT32 | R | 0...4294967295
213 | S1 | ROV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
213 | S2 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S3 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S4 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S5 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S6 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S7 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S8 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S9 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S10 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S11 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S12 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S13 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S14 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S15 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S16 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S17 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S18 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S19 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S20 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S21 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S22 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S23 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S24 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S25 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S26 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S27 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S28 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S29 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S30 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S31 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S32 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S33 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S34 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S35 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S36 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S37 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S38 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S39 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S40 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S41 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S42 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S43 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S44 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S45 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S46 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S47 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S48 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S49 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | O1 | ROV1 | Urw>/< START | SIGNAL_OUT | RW | 0...4294967295
213 | O2 | ROV1 | Urw>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
213 | O3 | ROV1 | Urw>/< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
213 | O4 | ROV1 | Urw>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
213 | V2 | ROV1 | Newest Register | UINT32 | R | 0...12
213 | V3 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V4 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V5 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V6 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V7 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V8 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V9 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V10 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V11 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V12 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V13 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V14 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V15 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V16 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V17 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V18 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V19 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V20 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V21 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V22 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V23 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V24 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V25 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V26 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | S50 | ROV1 | EventMaskLo | UINT32 | RW | 0...4294967295
214 | V1 | ROV2 | Urw>>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
214 | I1 | ROV2 | Urw>>/<< Umeas/Uset at the moment | FLOAT | R | 0...1250
214 | I2 | ROV2 | Urw>>/<< U measured p.u. | FLOAT | R | 0...1250
214 | I3 | ROV2 | Urw>>/<< starts | UINT32 | R | 0...4294967295
214 | I4 | ROV2 | Urw>>/<< trips | UINT32 | R | 0...4294967295
214 | I5 | ROV2 | Urw>>/<< blocks | UINT32 | R | 0...4294967295
214 | S1 | ROV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
214 | S2 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S3 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S4 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S5 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S6 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S7 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S8 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S9 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S10 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S11 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S12 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S13 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S14 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S15 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S16 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S17 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S18 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S19 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S20 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S21 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S22 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S23 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S24 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S25 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S26 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S27 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S28 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S29 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S30 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S31 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S32 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S33 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S34 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S35 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S36 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S37 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S38 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S39 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S40 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S41 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S42 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S43 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S44 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S45 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S46 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S47 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S48 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S49 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | O1 | ROV2 | Urw>>/<< START | SIGNAL_OUT | RW | 0...4294967295
214 | O2 | ROV2 | Urw>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
214 | O3 | ROV2 | Urw>>/<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
214 | O4 | ROV2 | Urw>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
214 | V2 | ROV2 | Newest Register | UINT32 | R | 0...12
214 | V3 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V4 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V5 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V6 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V7 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V8 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V9 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V10 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V11 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V12 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V13 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V14 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V15 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V16 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V17 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V18 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V19 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V20 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V21 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V22 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V23 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V24 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V25 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V26 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | S50 | ROV2 | EventMaskLo | UINT32 | RW | 0...4294967295
215 | V1 | ROV3 | Urw>>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
215 | I1 | ROV3 | Urw>>>/<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
215 | I2 | ROV3 | Urw>>>/<<< U measured p.u. | FLOAT | R | 0...1250
215 | I3 | ROV3 | Urw>>>/<<< starts | UINT32 | R | 0...4294967295
215 | I4 | ROV3 | Urw>>>/<<< trips | UINT32 | R | 0...4294967295
215 | I5 | ROV3 | Urw>>>/<<< blocks | UINT32 | R | 0...4294967295
215 | S1 | ROV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
215 | S2 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S3 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S4 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S5 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S6 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S7 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S8 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S9 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S10 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S11 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S12 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S13 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S14 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S15 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S16 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S17 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S18 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S19 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S20 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S21 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S22 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S23 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S24 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S25 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S26 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S27 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S28 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S29 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S30 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S31 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S32 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S33 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S34 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S35 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S36 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S37 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S38 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S39 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S40 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S41 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S42 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S43 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S44 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S45 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S46 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S47 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S48 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S49 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | O1 | ROV3 | Urw>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
215 | O2 | ROV3 | Urw>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
215 | O3 | ROV3 | Urw>>>/<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
215 | O4 | ROV3 | Urw>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
215 | V2 | ROV3 | Newest Register | UINT32 | R | 0...12
215 | V3 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V4 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V5 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V6 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V7 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V8 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V9 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V10 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V11 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V12 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V13 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V14 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V15 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V16 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V17 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V18 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V19 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V20 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V21 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V22 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V23 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V24 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V25 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V26 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | S50 | ROV3 | EventMaskLo | UINT32 | RW | 0...4294967295
216 | V1 | ROV4 | Urw>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
216 | I1 | ROV4 | Urw>>>>/<<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
216 | I2 | ROV4 | Urw>>>>/<<<< U measured p.u. | FLOAT | R | 0...1250
216 | I3 | ROV4 | Urw>>>>/<<<< starts | UINT32 | R | 0...4294967295
216 | I4 | ROV4 | Urw>>>>/<<<< trips | UINT32 | R | 0...4294967295
216 | I5 | ROV4 | Urw>>>>/<<<< blocks | UINT32 | R | 0...4294967295
216 | S1 | ROV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
216 | S2 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S3 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S4 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S5 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S6 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S7 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S8 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S9 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S10 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S11 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S12 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S13 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S14 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S15 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S16 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S17 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S18 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S19 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S20 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S21 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S22 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S23 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S24 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S25 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S26 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S27 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S28 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S29 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S30 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S31 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S32 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S33 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S34 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S35 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S36 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S37 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S38 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S39 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S40 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S41 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S42 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S43 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S44 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S45 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S46 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S47 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S48 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S49 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | O1 | ROV4 | Urw>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
216 | O2 | ROV4 | Urw>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
216 | O3 | ROV4 | Urw>>>>/<<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
216 | O4 | ROV4 | Urw>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
216 | V2 | ROV4 | Newest Register | UINT32 | R | 0...12
216 | V3 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V4 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V5 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V6 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V7 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V8 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V9 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V10 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V11 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V12 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V13 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V14 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V15 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V16 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V17 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V18 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V19 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V20 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V21 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V22 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V23 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V24 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V25 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V26 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | S50 | ROV4 | EventMaskLo | UINT32 | RW | 0...4294967295
224 | I1 | CNU1 | Measured unbalance current | FLOAT | R | 0...50.00
224 | I2 | CNU1 | Unbalance current angle | FLOAT | R | -360.00...360.00
224 | S1 | CNU1 | Natural unbalance compensation | UINT32 | RW | 0=Not used;1=In use
224 | S2 | CNU1 | Compensate natural unbal. | UINT32 | RW | 0=-;1=Comp
224 | I3 | CNU1 | Natural unbalance | FLOAT | R | -50.00...50.00
224 | I4 | CNU1 | Natural unbalance ang | FLOAT | R | -360.00...360.00
224 | I5 | CNU1 | Compensated magnitude | FLOAT | R | -50.00...50.00
224 | I6 | CNU1 | Compensated angle | FLOAT | R | -360.00...360.00
217 | V1 | UCP1 | IUC> condition | UINT32 | R | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
217 | I1 | UCP1 | Unbalance current atm. | FLOAT | R | 0...1250
217 | I2 | UCP1 | Imeas/Iset (ALARM) atm. | FLOAT | R | 0...1250
217 | I3 | UCP1 | Imeas/Iset (TRIP) atm. | FLOAT | R | 0...1250
217 | I4 | UCP1 | IUC> Alarm Starts | UINT32 | R | 0...4294967295
217 | I5 | UCP1 | IUC> Alarms | UINT32 | R | 0...4294967295
217 | I6 | UCP1 | IUC> Starts | UINT32 | R | 0...4294967295
217 | I7 | UCP1 | IUC> Trips | UINT32 | R | 0...4294967295
217 | I8 | UCP1 | IUC> Blocks | UINT32 | R | 0...4294967295
217 | S1 | UCP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
217 | S2 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S3 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S4 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S5 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S6 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S7 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S8 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S9 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S10 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S11 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S12 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S13 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S14 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S15 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S16 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S17 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S18 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S19 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S20 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S21 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S22 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S23 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S24 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S25 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S26 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S27 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S28 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S29 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S30 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S31 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S32 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S33 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S34 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S35 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S36 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S37 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S38 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S39 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S40 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S41 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | O1 | UCP1 | IUC> ALARM START | SIGNAL_OUT | RW | 0...4294967295
217 | O2 | UCP1 | IUC> ALARM | SIGNAL_OUT | RW | 0...4294967295
217 | O3 | UCP1 | IUC> START | SIGNAL_OUT | RW | 0...4294967295
217 | O4 | UCP1 | IUC> TRIP | SIGNAL_OUT | RW | 0...4294967295
217 | O5 | UCP1 | IUC> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
217 | V2 | UCP1 | Newest Register | UINT32 | R | 0...12
217 | V3 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V4 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V5 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V6 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V7 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V8 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V9 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V10 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V11 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V12 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V13 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V14 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | S42 | UCP1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S1 | DOC1 | Idir> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
75 | V1 | DOC1 | Idir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
75 | I1 | DOC1 | Operating angle now | FLOAT | R | -360...360
75 | I2 | DOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
75 | I3 | DOC1 | Idir> starts | UINT32 | R | 0...4294967295
75 | I4 | DOC1 | Idir> trips | UINT32 | R | 0...4294967295
75 | I5 | DOC1 | Idir> blocks | UINT32 | R | 0...4294967295
75 | S2 | DOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
75 | S3 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S4 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S5 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S6 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S7 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S8 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S9 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S10 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S11 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S12 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S13 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S14 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S15 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S16 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S17 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S18 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S19 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S20 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S21 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S22 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S23 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S24 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S25 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S26 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S27 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S28 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S29 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S30 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S31 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S32 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S33 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S34 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S35 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S36 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S37 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S38 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S39 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S40 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S41 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S42 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S43 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S44 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S45 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S46 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S47 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S48 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S49 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S50 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S51 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S52 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S53 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S54 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S55 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S56 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S57 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S58 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | O1 | DOC1 | Idir> START | SIGNAL_OUT | RW | 0...4294967295
75 | O2 | DOC1 | Idir> TRIP | SIGNAL_OUT | RW | 0...4294967295
75 | O3 | DOC1 | Idir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
75 | S59 | DOC1 | Clear registers | UINT32 | W | 0=-;1=Clear
75 | I6 | DOC1 | Newest Register | UINT32 | R | 0...12
75 | I7 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I8 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I9 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I10 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I11 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I12 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I13 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I14 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I15 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I16 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I17 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I18 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I19 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I20 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I21 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I22 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I23 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I24 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I25 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I26 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I27 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I28 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I29 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I30 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I31 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I32 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I33 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I34 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I35 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I36 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I37 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I38 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I39 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I40 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I41 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I42 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I43 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I44 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I45 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I46 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I47 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I48 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I49 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I50 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I51 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I52 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I53 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I54 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | S60 | DOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S61 | DOC1 | EventMaskHi | UINT32 | RW | 0...4294967295
76 | S1 | DOC2 | Idir>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
76 | V1 | DOC2 | Idir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
76 | I1 | DOC2 | Operating angle now | FLOAT | R | -360.00...360.00
76 | I2 | DOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
76 | I3 | DOC2 | Idir>> starts | UINT32 | R | 0...4294967295
76 | I4 | DOC2 | Idir>> trips | UINT32 | R | 0...4294967295
76 | I5 | DOC2 | Idir>> blocks | UINT32 | R | 0...4294967295
76 | S2 | DOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
76 | S3 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S4 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S5 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S6 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S7 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S8 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S9 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S10 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S11 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S12 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S13 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S14 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S15 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S16 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S17 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S18 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S19 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S20 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S21 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S22 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S23 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S24 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S25 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S26 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S27 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S28 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S29 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S30 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S31 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S32 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S33 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S34 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S35 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S36 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S37 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S38 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S39 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S40 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S41 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S42 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S43 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S44 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S45 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S46 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S47 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S48 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S49 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S50 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S51 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S52 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S53 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S54 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S55 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S56 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S57 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S58 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | O1 | DOC2 | Idir>> START | SIGNAL_OUT | RW | 0...4294967295
76 | O2 | DOC2 | Idir>> TRIP | SIGNAL_OUT | RW | 0...4294967295
76 | O3 | DOC2 | Idir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
76 | S59 | DOC2 | Clear registers | UINT32 | W | 0=-;1=Clear
76 | I6 | DOC2 | Newest Register | UINT32 | R | 0...12
76 | I7 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I8 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I9 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I10 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I11 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I12 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I13 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I14 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I15 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I16 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I17 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I18 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I19 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I20 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I21 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I22 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I23 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I24 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I25 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I26 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I27 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I28 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I29 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I30 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I31 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I32 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I33 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I34 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I35 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I36 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I37 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I38 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I39 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I40 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I41 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I42 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I43 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I44 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I45 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I46 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I47 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I48 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I49 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I50 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I51 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I52 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I53 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I54 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | S60 | DOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
76 | S61 | DOC2 | EventMaskHi | UINT32 | RW | 0...4294967295
77 | S1 | DOC3 | Idir>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
77 | V1 | DOC3 | Idir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
77 | I1 | DOC3 | Operating angle now | FLOAT | R | -360...360
77 | I2 | DOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
77 | I3 | DOC3 | Idir>>> starts | UINT32 | R | 0...4294967295
77 | I4 | DOC3 | Idir>>> trips | UINT32 | R | 0...4294967295
77 | I5 | DOC3 | Idir>>> blocks | UINT32 | R | 0...4294967295
77 | S2 | DOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
77 | S3 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S4 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S5 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S6 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S7 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S8 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S9 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S10 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S11 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S12 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S13 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S14 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S15 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S16 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S17 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S18 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S19 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S20 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S21 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S22 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S23 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S24 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S25 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S26 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S27 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S28 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S29 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S30 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S31 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S32 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S33 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S34 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S35 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S36 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S37 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S38 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S39 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S40 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S41 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S42 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S43 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S44 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S45 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S46 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S47 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S48 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S49 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S50 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S51 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S52 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S53 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S54 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S55 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S56 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S57 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S58 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | O1 | DOC3 | Idir>>> START | SIGNAL_OUT | RW | 0...4294967295
77 | O2 | DOC3 | Idir>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
77 | O3 | DOC3 | Idir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
77 | S59 | DOC3 | Clear registers | UINT32 | W | 0=-;1=Clear
77 | I6 | DOC3 | Newest Register | UINT32 | R | 0...12
77 | I7 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I8 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I9 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I10 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I11 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I12 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I13 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I14 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I15 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I16 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I17 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I18 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I19 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I20 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I21 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I22 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I23 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I24 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I25 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I26 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I27 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I28 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I29 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I30 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I31 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I32 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I33 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I34 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I35 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I36 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I37 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I38 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I39 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I40 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I41 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I42 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I43 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I44 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I45 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I46 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I47 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I48 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I49 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I50 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I51 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I52 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I53 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I54 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | S60 | DOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
77 | S61 | DOC3 | EventMaskHi | UINT32 | RW | 0...4294967295
78 | S1 | DOC4 | Idir>>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
78 | V1 | DOC4 | Idir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
78 | I1 | DOC4 | Operating angle now | FLOAT | R | -360.00...360.00
78 | I2 | DOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
78 | I3 | DOC4 | Idir>>>> starts | UINT32 | R | 0...4294967295
78 | I4 | DOC4 | Idir>>>> trips | UINT32 | R | 0...4294967295
78 | I5 | DOC4 | Idir>>>> blocks | UINT32 | R | 0...4294967295
78 | S2 | DOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
78 | S3 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S4 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S5 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S6 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S7 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S8 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S9 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S10 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S11 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S12 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S13 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S14 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S15 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S16 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S17 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S18 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S19 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S20 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S21 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S22 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S23 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S24 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S25 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S26 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S27 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S28 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S29 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S30 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S31 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S32 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S33 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S34 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S35 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S36 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S37 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S38 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S39 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S40 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S41 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S42 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S43 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S44 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S45 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S46 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S47 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S48 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S49 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S50 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S51 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S52 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S53 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S54 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S55 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S56 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S57 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S58 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | O1 | DOC4 | Idir>>>> START | SIGNAL_OUT | RW | 0...4294967295
78 | O2 | DOC4 | Idir>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
78 | O3 | DOC4 | Idir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
78 | S59 | DOC4 | Clear registers | UINT32 | W | 0=-;1=Clear
78 | I6 | DOC4 | Newest Register | UINT32 | R | 0...12
78 | I7 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I8 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I9 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I10 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I11 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I12 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I13 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I14 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I15 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I16 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I17 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I18 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I19 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I20 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I21 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I22 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I23 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I24 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I25 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I26 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I27 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I28 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I29 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I30 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I31 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I32 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I33 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I34 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I35 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I36 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I37 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I38 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I39 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I40 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I41 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I42 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I43 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I44 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I45 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I46 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I47 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I48 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I49 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I50 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I51 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I52 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I53 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I54 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | S60 | DOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
78 | S61 | DOC4 | EventMaskHi | UINT32 | RW | 0...4294967295
26 | S1 | NEF1 | I0> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
26 | S2 | NEF1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
26 | V1 | NEF1 | I0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
26 | I1 | NEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
26 | I2 | NEF1 | I0> starts | UINT32 | R | 0...4294967295
26 | I3 | NEF1 | I0> trips | UINT32 | R | 0...4294967295
26 | I4 | NEF1 | I0> blocks | UINT32 | R | 0...4294967295
26 | S3 | NEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
26 | S4 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S5 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S6 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S7 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S8 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S9 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S10 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S11 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S12 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S13 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S14 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S15 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S16 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S17 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S18 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S19 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S20 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S21 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S22 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S23 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S24 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S25 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S26 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S27 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S28 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S29 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S30 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S31 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S32 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S33 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S34 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S35 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | O1 | NEF1 | I0> START | SIGNAL_OUT | RW | 0...4294967295
26 | O2 | NEF1 | I0> TRIP | SIGNAL_OUT | RW | 0...4294967295
26 | O3 | NEF1 | I0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
26 | I5 | NEF1 | Newest Register | UINT32 | R | 0...12
26 | I6 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I7 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I8 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I9 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I10 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I11 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I12 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I13 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I14 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I15 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I16 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I17 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | S36 | NEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
27 | S1 | NEF2 | I0>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
27 | S2 | NEF2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
27 | V1 | NEF2 | I0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
27 | I1 | NEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
27 | I2 | NEF2 | I0>> starts | UINT32 | R | 0...4294967295
27 | I3 | NEF2 | I0>> trips | UINT32 | R | 0...4294967295
27 | I4 | NEF2 | I0>> blocks | UINT32 | R | 0...4294967295
27 | S3 | NEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
27 | S4 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S5 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S6 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S7 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S8 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S9 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S10 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S11 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S12 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S13 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S14 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S15 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S16 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S17 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S18 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S19 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S20 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S21 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S22 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S23 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S24 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S25 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S26 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S27 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S28 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S29 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S30 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S31 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S32 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S33 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S34 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S35 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | O1 | NEF2 | I0>> START | SIGNAL_OUT | RW | 0...4294967295
27 | O2 | NEF2 | I0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
27 | O3 | NEF2 | I0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
27 | I5 | NEF2 | Newest Register | UINT32 | R | 0...12
27 | I6 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I7 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I8 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I9 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I10 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I11 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I12 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I13 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I14 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I15 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I16 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I17 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | S36 | NEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
28 | S1 | NEF3 | I0>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
28 | S2 | NEF3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
28 | V1 | NEF3 | I0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
28 | I1 | NEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
28 | I2 | NEF3 | I0>>> starts | UINT32 | R | 0...4294967295
28 | I3 | NEF3 | I0>>> trips | UINT32 | R | 0...4294967295
28 | I4 | NEF3 | I0>>> blocks | UINT32 | R | 0...4294967295
28 | S3 | NEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
28 | S4 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S5 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S6 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S7 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S8 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S9 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S10 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S11 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S12 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S13 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S14 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S15 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S16 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S17 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S18 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S19 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S20 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S21 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S22 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S23 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S24 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S25 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S26 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S27 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S28 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S29 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S30 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S31 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S32 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S33 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S34 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S35 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | O1 | NEF3 | I0>>> START | SIGNAL_OUT | RW | 0...4294967295
28 | O2 | NEF3 | I0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
28 | O3 | NEF3 | I0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
28 | I5 | NEF3 | Newest Register | UINT32 | R | 0...12
28 | I6 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I7 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I8 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I9 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I10 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I11 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I12 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I13 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I14 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I15 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I16 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I17 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | S36 | NEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
29 | S1 | NEF4 | I0>>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
29 | S2 | NEF4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
29 | V1 | NEF4 | I0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
29 | I1 | NEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
29 | I2 | NEF4 | I0>>>> starts | UINT32 | R | 0...4294967295
29 | I3 | NEF4 | I0>>>> trips | UINT32 | R | 0...4294967295
29 | I4 | NEF4 | I0>>>> blocks | UINT32 | R | 0...4294967295
29 | S3 | NEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
29 | S4 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S5 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S6 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S7 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S8 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S9 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S10 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S11 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S12 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S13 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S14 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S15 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S16 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S17 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S18 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S19 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S20 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S21 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S22 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S23 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S24 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S25 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S26 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S27 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S28 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S29 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S30 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S31 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S32 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S33 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S34 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S35 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | O1 | NEF4 | I0>>>> START | SIGNAL_OUT | RW | 0...4294967295
29 | O2 | NEF4 | I0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
29 | O3 | NEF4 | I0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
29 | I5 | NEF4 | Newest Register | UINT32 | R | 0...12
29 | I6 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I7 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I8 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I9 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I10 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I11 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I12 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I13 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I14 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I15 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I16 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I17 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | S36 | NEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | S1 | DEF1 | I0dir> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
81 | V1 | DEF1 | I0dir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
81 | I1 | DEF1 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
81 | I2 | DEF1 | I0 Magnitude | FLOAT | R | 0...250
81 | I3 | DEF1 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
81 | I4 | DEF1 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
81 | I5 | DEF1 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
81 | I6 | DEF1 | DEF(1) Measured residual current change | FLOAT | R | 0...250
81 | I7 | DEF1 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
81 | I8 | DEF1 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
81 | I9 | DEF1 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
81 | I10 | DEF1 | I0 meas / I0 set now | FLOAT | R | -250...250
81 | I11 | DEF1 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
81 | I12 | DEF1 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
81 | I13 | DEF1 | U0 meas now | FLOAT | R | 0...500
81 | I14 | DEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
81 | I15 | DEF1 | I0dir> starts | UINT32 | R | 0...4294967295
81 | I16 | DEF1 | I0dir> trips | UINT32 | R | 0...4294967295
81 | I17 | DEF1 | I0dir> blocks | UINT32 | R | 0...4294967295
81 | S2 | DEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
81 | S3 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S4 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S5 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S6 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S7 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S8 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S9 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S10 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S11 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S12 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S13 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S14 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S15 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S16 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S17 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S18 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S19 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S20 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S21 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S22 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S23 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S24 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S25 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S26 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S27 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S28 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S29 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S30 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S31 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S32 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S33 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S34 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S35 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S36 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S37 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S38 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S39 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S40 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S41 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S42 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S43 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S44 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S45 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S46 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S47 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S48 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S49 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S50 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S51 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S52 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S53 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S54 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S55 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S56 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S57 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S58 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S59 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S60 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S61 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S62 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S63 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S64 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S65 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S66 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S67 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S68 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S69 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S70 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S71 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S72 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S73 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S74 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S75 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S76 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S77 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S78 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S79 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S80 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S81 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S82 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S83 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S84 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S85 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S86 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S87 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S88 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S89 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S90 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S91 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S92 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S93 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S94 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S95 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S96 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S97 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S98 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S99 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S100 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S101 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S102 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S103 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S104 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S105 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S106 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S107 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S108 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S109 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S110 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S111 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S112 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S113 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S114 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S115 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S116 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S117 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S118 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S119 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S120 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S121 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S122 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | O1 | DEF1 | I0dir> START (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O2 | DEF1 | I0dir> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O3 | DEF1 | I0dir> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O4 | DEF1 | I0dir> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O5 | DEF1 | I0dir> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O6 | DEF1 | I0dir> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O7 | DEF1 | I0dir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
81 | I18 | DEF1 | Newest Register | UINT32 | R | 0...12
81 | I19 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I20 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I21 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I22 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I23 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I24 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I25 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I26 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I27 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I28 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I29 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I30 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I31 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I32 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I33 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I34 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I35 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I36 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I37 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I38 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I39 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I40 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I41 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I42 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I43 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I44 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I45 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I46 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I47 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I48 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I49 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I50 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I51 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I52 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I53 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I54 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I55 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I56 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I57 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I58 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I59 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I60 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I61 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I62 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I63 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I64 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I65 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I66 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I67 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I68 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I69 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I70 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I71 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I72 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I73 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I74 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I75 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I76 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I77 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I78 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I79 | DEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | I80 | DEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
82 | S1 | DEF2 | I0dir>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
82 | V1 | DEF2 | I0dir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
82 | I1 | DEF2 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
82 | I2 | DEF2 | I0 Magnitude | FLOAT | R | 0...250
82 | I3 | DEF2 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
82 | I4 | DEF2 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
82 | I5 | DEF2 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
82 | I6 | DEF2 | DEF(1) Measured residual current change | FLOAT | R | 0...250
82 | I7 | DEF2 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
82 | I8 | DEF2 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
82 | I9 | DEF2 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
82 | I10 | DEF2 | I0 meas / I0 set now | FLOAT | R | -250...250
82 | I11 | DEF2 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
82 | I12 | DEF2 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
82 | I13 | DEF2 | U0 meas now | FLOAT | R | 0...500
82 | I14 | DEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
82 | I15 | DEF2 | I0dir>> starts | UINT32 | R | 0...4294967295
82 | I16 | DEF2 | I0dir>> trips | UINT32 | R | 0...4294967295
82 | I17 | DEF2 | I0dir>> blocks | UINT32 | R | 0...4294967295
82 | S2 | DEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
82 | S3 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S4 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S5 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S6 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S7 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S8 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S9 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S10 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S11 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S12 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S13 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S14 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S15 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S16 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S17 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S18 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S19 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S20 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S21 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S22 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S23 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S24 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S25 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S26 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S27 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S28 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S29 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S30 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S31 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S32 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S33 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S34 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S35 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S36 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S37 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S38 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S39 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S40 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S41 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S42 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S43 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S44 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S45 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S46 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S47 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S48 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S49 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S50 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S51 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S52 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S53 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S54 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S55 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S56 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S57 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S58 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S59 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S60 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S61 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S62 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S63 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S64 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S65 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S66 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S67 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S68 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S69 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S70 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S71 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S72 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S73 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S74 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S75 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S76 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S77 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S78 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S79 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S80 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S81 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S82 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S83 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S84 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S85 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S86 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S87 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S88 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S89 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S90 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S91 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S92 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S93 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S94 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S95 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S96 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S97 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S98 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S99 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S100 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S101 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S102 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S103 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S104 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S105 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S106 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S107 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S108 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S109 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S110 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S111 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S112 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S113 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S114 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S115 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S116 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S117 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S118 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S119 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S120 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S121 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S122 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | O1 | DEF2 | I0dir>> START (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O2 | DEF2 | I0dir>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O3 | DEF2 | I0dir>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O4 | DEF2 | I0dir>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O5 | DEF2 | I0dir>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O6 | DEF2 | I0dir>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O7 | DEF2 | I0dir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
82 | I18 | DEF2 | Newest Register | UINT32 | R | 0...12
82 | I19 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I20 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I21 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I22 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I23 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I24 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I25 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I26 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I27 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I28 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I29 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I30 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I31 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I32 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I33 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I34 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I35 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I36 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I37 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I38 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I39 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I40 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I41 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I42 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I43 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I44 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I45 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I46 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I47 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I48 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I49 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I50 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I51 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I52 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I53 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I54 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I55 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I56 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I57 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I58 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I59 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I60 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I61 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I62 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I63 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I64 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I65 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I66 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I67 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I68 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I69 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I70 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I71 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I72 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I73 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I74 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I75 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I76 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I77 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I78 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I79 | DEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
82 | I80 | DEF2 | EventMaskHi | UINT32 | RW | 0...4294967295
83 | S1 | DEF3 | I0dir>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
83 | V1 | DEF3 | I0dir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
83 | I1 | DEF3 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
83 | I2 | DEF3 | I0 Magnitude | FLOAT | R | 0...250
83 | I3 | DEF3 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
83 | I4 | DEF3 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
83 | I5 | DEF3 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
83 | I6 | DEF3 | DEF(1) Measured residual current change | FLOAT | R | 0...250
83 | I7 | DEF3 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
83 | I8 | DEF3 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
83 | I9 | DEF3 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
83 | I10 | DEF3 | I0 meas / I0 set now | FLOAT | R | -250...250
83 | I11 | DEF3 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
83 | I12 | DEF3 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
83 | I13 | DEF3 | U0 meas now | FLOAT | R | 0...500
83 | I14 | DEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
83 | I15 | DEF3 | I0dir>>> starts | UINT32 | R | 0...4294967295
83 | I16 | DEF3 | I0dir>>> trips | UINT32 | R | 0...4294967295
83 | I17 | DEF3 | I0dir>>> blocks | UINT32 | R | 0...4294967295
83 | S2 | DEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
83 | S3 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S4 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S5 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S6 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S7 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S8 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S9 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S10 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S11 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S12 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S13 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S14 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S15 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S16 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S17 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S18 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S19 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S20 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S21 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S22 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S23 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S24 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S25 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S26 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S27 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S28 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S29 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S30 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S31 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S32 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S33 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S34 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S35 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S36 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S37 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S38 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S39 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S40 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S41 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S42 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S43 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S44 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S45 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S46 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S47 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S48 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S49 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S50 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S51 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S52 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S53 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S54 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S55 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S56 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S57 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S58 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S59 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S60 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S61 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S62 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S63 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S64 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S65 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S66 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S67 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S68 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S69 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S70 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S71 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S72 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S73 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S74 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S75 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S76 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S77 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S78 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S79 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S80 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S81 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S82 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S83 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S84 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S85 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S86 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S87 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S88 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S89 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S90 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S91 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S92 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S93 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S94 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S95 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S96 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S97 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S98 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S99 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S100 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S101 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S102 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S103 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S104 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S105 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S106 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S107 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S108 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S109 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S110 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S111 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S112 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S113 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S114 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S115 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S116 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S117 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S118 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S119 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S120 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S121 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S122 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | O1 | DEF3 | I0dir>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O2 | DEF3 | I0dir>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O3 | DEF3 | I0dir>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O4 | DEF3 | I0dir>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O5 | DEF3 | I0dir>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O6 | DEF3 | I0dir>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O7 | DEF3 | I0dir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
83 | I18 | DEF3 | Newest Register | UINT32 | R | 0...12
83 | I19 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I20 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I21 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I22 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I23 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I24 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I25 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I26 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I27 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I28 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I29 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I30 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I31 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I32 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I33 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I34 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I35 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I36 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I37 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I38 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I39 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I40 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I41 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I42 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I43 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I44 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I45 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I46 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I47 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I48 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I49 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I50 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I51 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I52 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I53 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I54 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I55 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I56 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I57 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I58 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I59 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I60 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I61 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I62 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I63 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I64 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I65 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I66 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I67 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I68 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I69 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I70 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I71 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I72 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I73 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I74 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I75 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I76 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I77 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I78 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I79 | DEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
83 | I80 | DEF3 | EventMaskHi | UINT32 | RW | 0...4294967295
84 | S1 | DEF4 | I0dir>>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
84 | V1 | DEF4 | I0dir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
84 | I1 | DEF4 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
84 | I2 | DEF4 | I0 Magnitude | FLOAT | R | 0...250
84 | I3 | DEF4 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
84 | I4 | DEF4 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
84 | I5 | DEF4 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
84 | I6 | DEF4 | DEF(1) Measured residual current change | FLOAT | R | 0...250
84 | I7 | DEF4 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
84 | I8 | DEF4 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
84 | I9 | DEF4 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
84 | I10 | DEF4 | I0 meas / I0 set now | FLOAT | R | -250...250
84 | I11 | DEF4 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
84 | I12 | DEF4 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
84 | I13 | DEF4 | U0 meas now | FLOAT | R | 0...500
84 | I14 | DEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
84 | I15 | DEF4 | I0dir>>>> starts | UINT32 | R | 0...4294967295
84 | I16 | DEF4 | I0dir>>>> trips | UINT32 | R | 0...4294967295
84 | I17 | DEF4 | I0dir>>>> blocks | UINT32 | R | 0...4294967295
84 | S2 | DEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
84 | S3 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S4 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S5 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S6 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S7 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S8 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S9 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S10 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S11 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S12 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S13 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S14 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S15 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S16 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S17 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S18 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S19 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S20 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S21 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S22 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S23 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S24 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S25 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S26 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S27 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S28 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S29 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S30 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S31 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S32 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S33 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S34 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S35 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S36 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S37 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S38 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S39 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S40 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S41 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S42 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S43 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S44 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S45 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S46 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S47 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S48 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S49 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S50 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S51 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S52 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S53 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S54 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S55 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S56 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S57 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S58 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S59 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S60 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S61 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S62 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S63 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S64 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S65 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S66 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S67 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S68 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S69 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S70 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S71 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S72 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S73 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S74 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S75 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S76 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S77 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S78 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S79 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S80 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S81 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S82 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S83 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S84 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S85 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S86 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S87 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S88 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S89 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S90 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S91 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S92 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S93 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S94 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S95 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S96 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S97 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S98 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S99 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S100 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S101 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S102 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S103 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S104 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S105 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S106 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S107 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S108 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S109 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S110 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S111 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S112 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S113 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S114 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S115 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S116 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S117 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S118 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S119 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S120 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S121 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S122 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | O1 | DEF4 | I0dir>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O2 | DEF4 | I0dir>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O3 | DEF4 | I0dir>>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O4 | DEF4 | I0dir>>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O5 | DEF4 | I0dir>>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O6 | DEF4 | I0dir>>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O7 | DEF4 | I0dir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
84 | I18 | DEF4 | Newest Register | UINT32 | R | 0...12
84 | I19 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I20 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I21 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I22 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I23 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I24 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I25 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I26 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I27 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I28 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I29 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I30 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I31 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I32 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I33 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I34 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I35 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I36 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I37 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I38 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I39 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I40 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I41 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I42 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I43 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I44 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I45 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I46 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I47 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I48 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I49 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I50 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I51 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I52 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I53 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I54 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I55 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I56 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I57 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I58 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I59 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I60 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I61 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I62 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I63 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I64 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I65 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I66 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I67 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I68 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I69 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I70 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I71 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I72 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I73 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I74 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I75 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I76 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I77 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I78 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I79 | DEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
84 | I80 | DEF4 | EventMaskHi | UINT32 | RW | 0...4294967295
114 | S1 | IEF1 | I0Int> [67NT] mode | UINT32 | RW | 0=Disabled;1=Activated
114 | V1 | IEF1 | I0Int> condition | UINT32 | R | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
114 | I1 | IEF1 | Spikes needed for trip > | UINT32 | R | 0...4294967295
114 | I2 | IEF1 | I0Int> starts FWD | UINT32 | R | 0...4294967295
114 | I3 | IEF1 | I0Int> starts REV | UINT32 | R | 0...4294967295
114 | I4 | IEF1 | I0Int> trips | UINT32 | R | 0...4294967295
114 | I5 | IEF1 | I0Int> blocks | UINT32 | R | 0...4294967295
114 | S2 | IEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
114 | S3 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S4 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S5 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S6 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S7 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S8 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S9 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S10 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S11 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S12 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S13 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S14 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S15 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S16 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S17 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S18 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S19 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S20 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S21 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S22 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S23 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S24 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S25 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S26 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S27 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S28 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S29 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S30 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S31 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S32 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S33 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S34 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S35 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S36 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S37 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S38 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S39 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S40 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S41 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S42 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S43 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S44 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S45 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S46 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S47 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S48 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S49 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S50 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | O1 | IEF1 | I0Int> IEF DETECTED | SIGNAL_OUT | RW | 0...4294967295
114 | O2 | IEF1 | I0Int> STARTFWD | SIGNAL_OUT | RW | 0...4294967295
114 | O3 | IEF1 | I0Int> STARTREV | SIGNAL_OUT | RW | 0...4294967295
114 | O4 | IEF1 | I0Int> TRIP | SIGNAL_OUT | RW | 0...4294967295
114 | O5 | IEF1 | I0Int> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
114 | I6 | IEF1 | Newest Register | UINT32 | R | 0...12
114 | I7 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I8 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I9 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I10 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I11 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I12 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I13 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I14 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I15 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I16 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I17 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I18 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I19 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I20 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I21 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I22 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I23 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I24 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I25 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I26 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I27 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I28 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I29 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I30 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I31 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I32 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I33 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I34 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I35 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I36 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I37 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I38 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I39 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I40 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I41 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I42 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I43 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I44 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I45 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I46 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I47 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I48 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I49 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I50 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I51 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I52 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I53 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I54 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I55 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I56 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I57 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I58 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I59 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I60 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I61 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I62 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I63 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I64 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I65 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I66 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | S51 | IEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
114 | S52 | IEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
32 | S1 | CUB1 | I2> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
32 | V1 | CUB1 | I2> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
32 | I1 | CUB1 | I2> starts | UINT32 | R | 0...4294967295
32 | I2 | CUB1 | I2> trips | UINT32 | R | 0...4294967295
32 | I3 | CUB1 | I2> blocks | UINT32 | R | 0...4294967295
32 | S2 | CUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
32 | I4 | CUB1 | I2> I2I1 relation | FLOAT | R | 0...100000
32 | I5 | CUB1 | I2 meas/I2 set | FLOAT | R | 0...100000
32 | S3 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S4 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S5 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S6 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S7 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S8 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S9 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S10 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S11 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S12 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S13 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S14 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S15 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S16 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S17 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S18 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S19 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S20 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S21 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S22 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S23 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S24 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S25 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S26 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S27 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S28 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S29 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S30 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S31 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S32 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S33 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S34 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | O1 | CUB1 | I2> START | SIGNAL_OUT | RW | 0...4294967295
32 | O2 | CUB1 | I2> TRIP | SIGNAL_OUT | RW | 0...4294967295
32 | O3 | CUB1 | I2> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
32 | I6 | CUB1 | Newest Register | UINT32 | R | 0...12
32 | I7 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I8 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I9 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I10 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I11 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I12 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I13 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I14 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I15 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I16 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I17 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I18 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I19 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I20 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I21 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I22 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I23 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I24 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I25 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I26 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I27 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I28 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I29 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I30 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | S35 | CUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
33 | S1 | CUB2 | I2>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
33 | V1 | CUB2 | I2>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
33 | I1 | CUB2 | I2>> starts | UINT32 | R | 0...4294967295
33 | I2 | CUB2 | I2>> trips | UINT32 | R | 0...4294967295
33 | I3 | CUB2 | I2>> blocks | UINT32 | R | 0...4294967295
33 | S2 | CUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
33 | I4 | CUB2 | I2>> I2I1 relation | FLOAT | R | 0...100000
33 | I5 | CUB2 | I2 meas/I2 set | FLOAT | R | 0...100000
33 | S3 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S4 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S5 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S6 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S7 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S8 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S9 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S10 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S11 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S12 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S13 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S14 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S15 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S16 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S17 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S18 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S19 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S20 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S21 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S22 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S23 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S24 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S25 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S26 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S27 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S28 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S29 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S30 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S31 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S32 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S33 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S34 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | O1 | CUB2 | I2>> START | SIGNAL_OUT | RW | 0...4294967295
33 | O2 | CUB2 | I2>> TRIP | SIGNAL_OUT | RW | 0...4294967295
33 | O3 | CUB2 | I2>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
33 | I6 | CUB2 | Newest Register | UINT32 | R | 0...12
33 | I7 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I8 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I9 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I10 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I11 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I12 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I13 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I14 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I15 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I16 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I17 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I18 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I19 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I20 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I21 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I22 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I23 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I24 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I25 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I26 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I27 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I28 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I29 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I30 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | S35 | CUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
34 | S1 | CUB3 | I2>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
34 | V1 | CUB3 | I2>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
34 | I1 | CUB3 | I2>>> starts | UINT32 | R | 0...4294967295
34 | I2 | CUB3 | I2>>> trips | UINT32 | R | 0...4294967295
34 | I3 | CUB3 | I2>>> blocks | UINT32 | R | 0...4294967295
34 | S2 | CUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
34 | I4 | CUB3 | I2>>> I2I1 relation | FLOAT | R | 0...100000
34 | I5 | CUB3 | I2 meas/I2 set | FLOAT | R | 0...100000
34 | S3 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S4 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S5 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S6 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S7 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S8 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S9 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S10 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S11 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S12 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S13 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S14 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S15 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S16 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S17 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S18 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S19 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S20 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S21 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S22 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S23 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S24 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S25 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S26 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S27 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S28 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S29 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S30 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S31 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S32 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S33 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S34 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | O1 | CUB3 | I2>>> START | SIGNAL_OUT | RW | 0...4294967295
34 | O2 | CUB3 | I2>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
34 | O3 | CUB3 | I2>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
34 | I6 | CUB3 | Newest Register | UINT32 | R | 0...12
34 | I7 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I8 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I9 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I10 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I11 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I12 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I13 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I14 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I15 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I16 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I17 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I18 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I19 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I20 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I21 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I22 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I23 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I24 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I25 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I26 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I27 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I28 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I29 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I30 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | S35 | CUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
35 | S1 | CUB4 | I2>>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
35 | V1 | CUB4 | I2>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
35 | I1 | CUB4 | I2>>>> starts | UINT32 | R | 0...4294967295
35 | I2 | CUB4 | I2>>>> trips | UINT32 | R | 0...4294967295
35 | I3 | CUB4 | I2>>>> blocks | UINT32 | R | 0...4294967295
35 | S2 | CUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
35 | I4 | CUB4 | I2>>>> I2I1 relation | FLOAT | R | 0...100000
35 | I5 | CUB4 | I2 meas/I2 set | FLOAT | R | 0...100000
35 | S3 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S4 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S5 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S6 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S7 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S8 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S9 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S10 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S11 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S12 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S13 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S14 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S15 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S16 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S17 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S18 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S19 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S20 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S21 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S22 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S23 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S24 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S25 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S26 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S27 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S28 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S29 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S30 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S31 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S32 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S33 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S34 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | O1 | CUB4 | I2>>>> START | SIGNAL_OUT | RW | 0...4294967295
35 | O2 | CUB4 | I2>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
35 | O3 | CUB4 | I2>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
35 | I6 | CUB4 | Newest Register | UINT32 | R | 0...12
35 | I7 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I8 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I9 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I10 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I11 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I12 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I13 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I14 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I15 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I16 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I17 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I18 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I19 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I20 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I21 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I22 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I23 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I24 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I25 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I26 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I27 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I28 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I29 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I30 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | S35 | CUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
37 | S1 | HOC1 | Ih> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
37 | V1 | HOC1 | Ih> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
37 | I1 | HOC1 | Ih> starts | UINT32 | R | 0...4294967295
37 | I2 | HOC1 | Ih> trips | UINT32 | R | 0...4294967295
37 | I3 | HOC1 | Ih> blocks | UINT32 | R | 0...4294967295
37 | S2 | HOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
37 | I4 | HOC1 | Ih meas/ Ih set | FLOAT | R | 0...100000
37 | S3 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S4 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S5 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S6 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S7 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S8 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S9 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S10 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S11 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S12 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S13 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S14 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S15 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S16 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S17 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S18 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S19 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S20 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S21 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S22 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S23 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S24 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S25 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S26 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S27 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S28 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S29 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S30 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S31 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S32 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S33 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S34 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | O1 | HOC1 | Ih> START | SIGNAL_OUT | RW | 0...4294967295
37 | O2 | HOC1 | Ih> TRIP | SIGNAL_OUT | RW | 0...4294967295
37 | O3 | HOC1 | Ih> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
37 | I5 | HOC1 | Newest Register | UINT32 | R | 0...12
37 | I6 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I7 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I8 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I9 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I10 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I11 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I12 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I13 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I14 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I15 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I16 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I17 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I18 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I19 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I20 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I21 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I22 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I23 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I24 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I25 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I26 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I27 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I28 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I29 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I30 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I31 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I32 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I33 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I34 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I35 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I36 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I37 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I38 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I39 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I40 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I41 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I42 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I43 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I44 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I45 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I46 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I47 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I48 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I49 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I50 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I51 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I52 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I53 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I54 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I55 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I56 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I57 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I58 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I59 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I60 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I61 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I62 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I63 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I64 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I65 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | S35 | HOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
38 | S1 | HOC2 | Ih>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
38 | V1 | HOC2 | Ih>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
38 | I1 | HOC2 | Ih>> starts | UINT32 | R | 0...4294967295
38 | I2 | HOC2 | Ih>> trips | UINT32 | R | 0...4294967295
38 | I3 | HOC2 | Ih>> blocks | UINT32 | R | 0...4294967295
38 | S2 | HOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
38 | I4 | HOC2 | Ih meas/ Ih set | FLOAT | R | 0...100000
38 | S3 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S4 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S5 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S6 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S7 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S8 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S9 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S10 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S11 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S12 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S13 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S14 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S15 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S16 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S17 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S18 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S19 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S20 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S21 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S22 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S23 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S24 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S25 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S26 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S27 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S28 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S29 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S30 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S31 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S32 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S33 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S34 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | O1 | HOC2 | Ih>> START | SIGNAL_OUT | RW | 0...4294967295
38 | O2 | HOC2 | Ih>> TRIP | SIGNAL_OUT | RW | 0...4294967295
38 | O3 | HOC2 | Ih>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
38 | I5 | HOC2 | Newest Register | UINT32 | R | 0...12
38 | I6 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I7 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I8 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I9 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I10 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I11 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I12 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I13 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I14 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I15 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I16 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I17 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I18 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I19 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I20 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I21 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I22 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I23 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I24 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I25 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I26 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I27 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I28 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I29 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I30 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I31 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I32 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I33 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I34 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I35 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I36 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I37 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I38 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I39 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I40 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I41 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I42 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I43 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I44 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I45 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I46 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I47 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I48 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I49 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I50 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I51 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I52 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I53 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I54 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I55 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I56 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I57 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I58 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I59 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I60 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I61 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I62 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I63 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I64 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I65 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | S35 | HOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
39 | S1 | HOC3 | Ih>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
39 | V1 | HOC3 | Ih>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
39 | I1 | HOC3 | Ih>>> starts | UINT32 | R | 0...4294967295
39 | I2 | HOC3 | Ih>>> trips | UINT32 | R | 0...4294967295
39 | I3 | HOC3 | Ih>>> blocks | UINT32 | R | 0...4294967295
39 | S2 | HOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
39 | I4 | HOC3 | Ih meas/ Ih set | FLOAT | R | 0...100000
39 | S3 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S4 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S5 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S6 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S7 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S8 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S9 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S10 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S11 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S12 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S13 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S14 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S15 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S16 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S17 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S18 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S19 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S20 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S21 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S22 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S23 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S24 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S25 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S26 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S27 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S28 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S29 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S30 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S31 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S32 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S33 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S34 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | O1 | HOC3 | Ih>>> START | SIGNAL_OUT | RW | 0...4294967295
39 | O2 | HOC3 | Ih>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
39 | O3 | HOC3 | Ih>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
39 | I5 | HOC3 | Newest Register | UINT32 | R | 0...12
39 | I6 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I7 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I8 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I9 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I10 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I11 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I12 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I13 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I14 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I15 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I16 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I17 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I18 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I19 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I20 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I21 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I22 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I23 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I24 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I25 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I26 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I27 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I28 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I29 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I30 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I31 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I32 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I33 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I34 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I35 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I36 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I37 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I38 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I39 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I40 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I41 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I42 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I43 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I44 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I45 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I46 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I47 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I48 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I49 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I50 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I51 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I52 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I53 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I54 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I55 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I56 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I57 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I58 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I59 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I60 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I61 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I62 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I63 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I64 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I65 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | S35 | HOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
40 | S1 | HOC4 | Ih>>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
40 | V1 | HOC4 | Ih>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
40 | I1 | HOC4 | Ih>>>> starts | UINT32 | R | 0...4294967295
40 | I2 | HOC4 | Ih>>>> trips | UINT32 | R | 0...4294967295
40 | I3 | HOC4 | Ih>>>> blocks | UINT32 | R | 0...4294967295
40 | S2 | HOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
40 | I4 | HOC4 | Ih meas/ Ih set | FLOAT | R | 0...100000
40 | S3 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S4 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S5 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S6 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S7 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S8 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S9 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S10 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S11 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S12 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S13 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S14 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S15 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S16 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S17 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S18 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S19 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S20 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S21 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S22 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S23 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S24 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S25 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S26 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S27 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S28 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S29 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S30 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S31 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S32 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S33 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S34 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | O1 | HOC4 | Ih>>>> START | SIGNAL_OUT | RW | 0...4294967295
40 | O2 | HOC4 | Ih>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
40 | O3 | HOC4 | Ih>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
40 | I5 | HOC4 | Newest Register | UINT32 | R | 0...12
40 | I6 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I7 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I8 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I9 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I10 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I11 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I12 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I13 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I14 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I15 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I16 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I17 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I18 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I19 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I20 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I21 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I22 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I23 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I24 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I25 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I26 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I27 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I28 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I29 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I30 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I31 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I32 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I33 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I34 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I35 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I36 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I37 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I38 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I39 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I40 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I41 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I42 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I43 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I44 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I45 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I46 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I47 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I48 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I49 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I50 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I51 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I52 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I53 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I54 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I55 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I56 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I57 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I58 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I59 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I60 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I61 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I62 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I63 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I64 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I65 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | S35 | HOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
42 | S1 | CLP1 | CLP mode | UINT32 | RW | 0=Disabled;1=Activated
42 | V1 | CLP1 | CLP condition | UINT32 | R | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
42 | I1 | CLP1 | CLP starts | UINT32 | R | 0...4294967295
42 | I2 | CLP1 | CLP blocks | UINT32 | R | 0...4294967295
42 | S2 | CLP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
42 | S3 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S4 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S5 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S6 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S7 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S8 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S9 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S10 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S11 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S12 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S13 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S14 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S15 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S16 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S17 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S18 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S19 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S20 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S21 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S22 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S23 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S24 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S25 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S26 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S27 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S28 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S29 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S30 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S31 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S32 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S33 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S34 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S35 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S36 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S37 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S38 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S39 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S40 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S41 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S42 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S43 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S44 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S45 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S46 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S47 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S48 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S49 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S50 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | O1 | CLP1 | CLPU ACT | SIGNAL_OUT | RW | 0...4294967295
42 | O2 | CLP1 | CLPU BLOCKED | SIGNAL_OUT | RW | 0...4294967295
42 | I3 | CLP1 | Newest Register | UINT32 | R | 0...12
42 | I4 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I5 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I6 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I7 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I8 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I9 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I10 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I11 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I12 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I13 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I14 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I15 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I16 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I17 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I18 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I19 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I20 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I21 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I22 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I23 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I24 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I25 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I26 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I27 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I28 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I29 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I30 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I31 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I32 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I33 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I34 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I35 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I36 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I37 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I38 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I39 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | S51 | CLP1 | EventMaskLo | UINT32 | RW | 0...4294967295
44 | S1 | CBF1 | CBFP [50BF] mode | UINT32 | RW | 0=Disabled;1=Activated
44 | V1 | CBF1 | CBFP condition | UINT32 | R | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
44 | I1 | CBF1 | Retrips | UINT32 | R | 0...4294967295
44 | I2 | CBF1 | CBFPs | UINT32 | R | 0...4294967295
44 | I3 | CBF1 | CBFP starts | UINT32 | R | 0...4294967295
44 | I4 | CBF1 | CBFP blocks | UINT32 | R | 0...4294967295
44 | S2 | CBF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
44 | S3 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S4 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S5 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S6 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S7 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S8 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S9 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S10 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S11 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S12 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S13 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S14 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S15 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S16 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S17 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S18 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S19 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S20 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S21 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S22 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S23 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S24 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S25 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S26 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S27 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S28 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S29 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S30 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S31 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S32 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S33 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S34 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S35 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S36 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S37 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S38 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S39 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S40 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S41 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S42 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S43 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S44 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S45 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S46 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S47 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S48 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S49 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S50 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S51 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S52 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S53 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S54 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S55 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S56 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S57 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S58 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | O1 | CBF1 | CBFP START | SIGNAL_OUT | RW | 0...4294967295
44 | O2 | CBF1 | CBFP RETRIP | SIGNAL_OUT | RW | 0...4294967295
44 | O3 | CBF1 | CBFP ACT | SIGNAL_OUT | RW | 0...4294967295
44 | O4 | CBF1 | CBFP BLOCKED | SIGNAL_OUT | RW | 0...4294967295
44 | I5 | CBF1 | Newest Register | UINT32 | R | 0...12
44 | I6 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I7 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I8 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I9 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I10 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I11 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I12 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I13 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I14 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I15 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I16 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I17 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I18 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I19 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I20 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I21 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I22 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I23 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I24 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I25 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I26 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I27 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I28 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I29 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I30 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I31 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I32 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I33 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I34 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I35 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I36 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I37 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I38 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I39 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I40 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I41 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I42 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I43 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I44 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I45 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I46 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I47 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I48 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I49 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I50 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I51 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I52 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I53 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | S59 | CBF1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S1 | MST1 | MST mode | UINT32 | R | 0=Disabled; 1=Activated
62 | V1 | MST1 | Motor is now | UINT32 | R | 0=Stopped;1=Starting;2=Running;3=Stalled
62 | I1 | MST1 | Times motor started | UINT32 | R | 0...4294967295
62 | I2 | MST1 | Times motor starts succeed | UINT32 | R | 0...4294967295
62 | I3 | MST1 | Times motor stopped | UINT32 | R | 0...4294967295
62 | S2 | MST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
62 | I4 | MST1 | Run after last start | UINT32 | R | 0...4294967295
62 | I5 | MST1 | Total motor run time | UINT32 | R | 0...4294967295
62 | I6 | MST1 | Last start duration | UINT32 | R | 0...4294967295
62 | I7 | MST1 | Total starting time | UINT32 | R | 0...4294967295
62 | I8 | MST1 | Last stopped duration | UINT32 | R | 0...4294967295
62 | I9 | MST1 | Total stopped time | UINT32 | R | 0...4294967295
62 | S3 | MST1 | Clear total times | UINT32 | W | 0=-;1=Clear
62 | S4 | MST1 | Per unitize relay currents to Motor In | UINT32 | RW | 0=No, use CT nominal as pu.;1=Yes, scale all to Imot
62 | S5 | MST1 | Motor nominal current | FLOAT | RW | 0.1...10000
62 | S6 | MST1 | Nominal Starting current | FLOAT | RW | 0.1...40
62 | S7 | MST1 | Start detect current | FLOAT | RW | 0.1...40
62 | S8 | MST1 | Min locked rotor current | FLOAT | RW | 0.1...40
62 | S9 | MST1 | Max locked rotor current | FLOAT | RW | 0.1...40
62 | S10 | MST1 | Maximum overload current | FLOAT | RW | 0.1...40
62 | S11 | MST1 | No Load current | FLOAT | RW | 0.1...40
62 | S12 | MST1 | Motor service factor | FLOAT | RW | 0.01...5
62 | S13 | MST1 | Hot condition theta limit | FLOAT | RW | 0...100
62 | S14 | MST1 | Safe stall time cold | FLOAT | RW | 0.1...600
62 | S15 | MST1 | Safe stall time hot | FLOAT | RW | 0.1...600
62 | S16 | MST1 | Allowed Starts when cold | UINT32 | RW | 1...100
62 | S17 | MST1 | Allowed Starts when hot | UINT32 | RW | 1...100
62 | S18 | MST1 | Given Hot/Cold starts in time of: | FLOAT | RW | 0.01...1800
62 | S19 | MST1 | Min time betw. starts | FLOAT | RW | 0...3600
62 | S20 | MST1 | Overall differential protection | UINT32 | RW | 0=Machine diff. (Yy);1=Diff.with trafo(Xx)
62 | O1 | MST1 | Motor stopped | SIGNAL_OUT | RW | 0...4294967295
62 | O2 | MST1 | Motor starting | SIGNAL_OUT | RW | 0...4294967295
62 | O3 | MST1 | Motor running | SIGNAL_OUT | RW | 0...4294967295
62 | O4 | MST1 | Motor stalled | SIGNAL_OUT | RW | 0...4294967295
62 | O5 | MST1 | Missing phase | SIGNAL_OUT | RW | 0...4294967295
62 | O6 | MST1 | Load Normal | SIGNAL_OUT | RW | 0...4294967295
62 | O7 | MST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
62 | O8 | MST1 | High overcurrent | SIGNAL_OUT | RW | 0...4294967295
62 | I10 | MST1 | Newest Register | UINT32 | R | 0...12
62 | I11 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I12 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I13 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I14 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I15 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I16 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I17 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I18 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I19 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I20 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I21 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I22 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I23 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I24 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I25 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I26 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I27 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I28 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I29 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I30 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I31 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I32 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I33 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I34 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I35 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I36 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I37 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I38 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I39 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I40 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I41 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I42 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I43 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I44 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I45 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I46 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I47 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I48 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I49 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I50 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I51 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I52 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I53 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I54 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I55 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I56 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I57 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I58 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I59 | MST1 | Motor load | FLOAT | R | 0...250
62 | I60 | MST1 | Motor load | FLOAT | R | 0...250
62 | I61 | MST1 | Motor load | FLOAT | R | 0...250
62 | I62 | MST1 | Motor load | FLOAT | R | 0...250
62 | I63 | MST1 | Motor load | FLOAT | R | 0...250
62 | I64 | MST1 | Motor load | FLOAT | R | 0...250
62 | I65 | MST1 | Motor load | FLOAT | R | 0...250
62 | I66 | MST1 | Motor load | FLOAT | R | 0...250
62 | I67 | MST1 | Motor load | FLOAT | R | 0...250
62 | I68 | MST1 | Motor load | FLOAT | R | 0...250
62 | I69 | MST1 | Motor load | FLOAT | R | 0...250
62 | I70 | MST1 | Motor load | FLOAT | R | 0...250
62 | S21 | MST1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S22 | MST1 | EventMaskHi | UINT32 | RW | 0...4294967295
72 | V1 | TRF1 | Transformer is now | UINT32 | R | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
72 | I1 | TRF1 | Times Overloaded | UINT32 | R | 0...4294967295
72 | I2 | TRF1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
72 | S1 | TRF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
72 | I3 | TRF1 | Normal loading | UINT32 | R | 0...4294967295
72 | I4 | TRF1 | Overloading cumulative | UINT32 | R | 0...4294967295
72 | I5 | TRF1 | Last overload duration | UINT32 | R | 0...4294967295
72 | I6 | TRF1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
72 | I7 | TRF1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
72 | S2 | TRF1 | Clear total times | UINT32 | W | 0=-;1=Clear
72 | S3 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.1...500
72 | S4 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...500
72 | S5 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...500
72 | S6 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S7 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | V2 | TRF1 | Bias selection | UINT32 | R | 0=Selection Ok;1=Selection different
72 | V3 | TRF1 | Pick-up setting | UINT32 | R | 0=not checked;1=Setting seems ok;2=Sensitive ok;3=Too sensitive;4=False trip likely;5=Coarse ok;6=Insensitive;7=Dangerously high
72 | V4 | TRF1 | Turnpoint1 setting | UINT32 | R | 0=not checked;1=Ok;2=Seems average;3=Is sensitive;4=Ok;5=Is conservative;6=Is sensitive;7=Ok;8=Is average;9=Is conservative;10=Ok;11=Too conservative;12=Too sensitive
72 | V5 | TRF1 | Slope1 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V6 | TRF1 | Turnpoint2 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V7 | TRF1 | Slope2 setting | UINT32 | R | 0=not checked;1=Ok;2=Wrong;
72 | O1 | TRF1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
72 | O2 | TRF1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O3 | TRF1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O4 | TRF1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
72 | O5 | TRF1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | O6 | TRF1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | I8 | TRF1 | Newest Register | UINT32 | R | 0...12
72 | I9 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I10 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I11 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I12 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I13 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I14 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I15 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I16 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I17 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I18 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I19 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I20 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I21 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I22 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I23 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I24 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I25 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I26 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I27 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I28 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I29 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I30 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I31 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I32 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I33 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I34 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I35 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I36 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I37 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I38 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I39 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I40 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I41 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I42 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I43 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I44 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I45 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I46 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I47 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I48 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I49 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I50 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I51 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I52 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I53 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I54 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I55 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I56 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I57 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I58 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I59 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I60 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I61 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I62 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I63 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I64 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I65 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I66 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I67 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I68 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I69 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I70 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I71 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I72 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I73 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I74 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I75 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I76 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I77 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I78 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I79 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I80 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | S8 | TRF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S1 | DIF1 | Idx> [87T/87N] mode | UINT32 | RW | 0=Disabled;1=Activated
71 | V1 | DIF1 | Idx> condition | UINT32 | R | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On
71 | V2 | DIF1 | REFHV> condition | UINT32 | R | 0b=HV REF Blocked;1b=HV REF Trip
71 | V3 | DIF1 | REFLV> condition | UINT32 | R | 0b=LV REF Blocked;1b=LV REF Trip
71 | I1 | DIF1 | Idb> trips | UINT32 | R | 0...4294967295
71 | I2 | DIF1 | Idb> f2h blocks | UINT32 | R | 0...4294967295
71 | I3 | DIF1 | Idb> f5h blocks | UINT32 | R | 0...4294967295
71 | I4 | DIF1 | Idb> Ext blocks | UINT32 | R | 0...4294967295
71 | I5 | DIF1 | Idi> trips | UINT32 | R | 0...4294967295
71 | I6 | DIF1 | Idi> Ext blocks | UINT32 | R | 0...4294967295
71 | I7 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I8 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | I9 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I10 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | S2 | DIF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
71 | I11 | DIF1 | L1 Bias current | FLOAT | R | 0...50
71 | I12 | DIF1 | L1 Diff current | FLOAT | R | 0...4000
71 | I13 | DIF1 | L1 Char current | FLOAT | R | 0...4000
71 | I14 | DIF1 | L2 Bias current | FLOAT | R | 0...50
71 | I15 | DIF1 | L2 Diff current | FLOAT | R | 0...4000
71 | I16 | DIF1 | L2 Char current | FLOAT | R | 0...4000
71 | I17 | DIF1 | L3 Bias current | FLOAT | R | 0...50
71 | I18 | DIF1 | L3 Diff current | FLOAT | R | 0...4000
71 | I19 | DIF1 | L3 Char current | FLOAT | R | 0...4000
71 | I20 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...50
71 | I21 | DIF1 | HV I0d> Diff current | FLOAT | R | 0...4000
71 | I22 | DIF1 | HV I0d> Char current | FLOAT | R | 0...4000
71 | I23 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...50
71 | I24 | DIF1 | LV I0d> Diff current | FLOAT | R | 0...4000
71 | I25 | DIF1 | LV I0d> Char current | FLOAT | R | 0...4000
71 | S3 | DIF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
71 | V4 | DIF1 | L1 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V5 | DIF1 | L2 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V6 | DIF1 | L3 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | I26 | DIF1 | L1 Mag. diff. | FLOAT | R | 0...50
71 | I27 | DIF1 | L1 Ang. diff. | FLOAT | R | -360...360
71 | I28 | DIF1 | L2 Mag. diff. | FLOAT | R | 0...50
71 | I29 | DIF1 | L2 Ang. diff. | FLOAT | R | -360...360
71 | I30 | DIF1 | L3 Mag. diff. | FLOAT | R | 0...50
71 | I31 | DIF1 | L3 Ang. diff. | FLOAT | R | -360...360
71 | S4 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S5 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S6 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S7 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S8 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S9 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S10 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S11 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S12 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S13 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S14 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S15 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S16 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S17 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S18 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S19 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S20 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S21 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S22 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S23 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S24 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S25 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S26 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S27 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S28 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S29 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S30 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S31 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S32 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S33 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S34 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S35 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S36 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S37 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S38 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S39 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S40 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S41 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S42 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S43 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S44 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S45 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S46 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S47 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S48 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S49 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S50 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S51 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S52 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S53 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S54 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S55 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S56 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S57 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S58 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S59 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S60 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S61 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S62 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S63 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S64 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S65 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S66 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S67 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S68 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S69 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S70 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S71 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S72 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S73 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S74 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S75 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S76 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S77 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S78 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S79 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S80 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S81 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S82 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S83 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S84 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S85 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S86 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S87 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S88 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S89 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S90 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S91 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S92 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S93 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S94 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S95 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S96 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S97 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S98 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S99 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S100 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S101 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S102 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S103 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S104 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S105 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S106 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S107 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S108 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S109 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S110 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S111 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S112 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S113 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S114 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S115 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S116 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S117 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S118 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S119 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S120 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S121 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S122 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S123 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S124 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S125 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S126 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S127 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S128 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S129 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S130 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S131 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S132 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S133 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S134 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S135 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S136 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S137 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S138 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S139 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S140 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S141 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S142 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S143 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S144 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S145 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S146 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S147 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S148 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S149 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S150 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S151 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S152 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S153 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S154 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S155 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S156 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S157 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S158 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S159 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S160 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S161 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S162 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S163 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S164 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S165 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S166 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S167 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S168 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S169 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S170 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S171 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S172 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S173 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S174 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S175 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S176 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S177 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S178 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S179 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S180 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S181 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S182 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S183 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S184 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S185 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S186 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S187 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S188 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S189 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S190 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S191 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S192 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S193 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S194 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S195 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S196 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S197 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S198 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S199 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S200 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S201 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S202 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S203 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S204 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S205 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S206 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S207 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S208 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S209 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S210 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S211 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | O1 | DIF1 | Idb> BIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O2 | DIF1 | Idb> BIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O3 | DIF1 | Idi> NOBIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O4 | DIF1 | Idi> NOBIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O5 | DIF1 | Id> 2nd harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O6 | DIF1 | Id> 5th harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O7 | DIF1 | HV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O8 | DIF1 | HV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O9 | DIF1 | LV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O10 | DIF1 | LV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | I32 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I33 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I34 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I35 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I36 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I37 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I38 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I39 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I40 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I41 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I42 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I43 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I44 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I45 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I46 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I47 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I48 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I49 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I50 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I51 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I52 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I53 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I54 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I55 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I56 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I57 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I58 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I59 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I60 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I61 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I62 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I63 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I64 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I65 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I66 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I67 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I68 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I69 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I70 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I71 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I72 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I73 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I74 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I75 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I76 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I77 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I78 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I79 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I80 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I81 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I82 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I83 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I84 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I85 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I86 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I87 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I88 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I89 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I90 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I91 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I92 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I93 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I94 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I95 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I96 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I97 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I98 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I99 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I100 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I101 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I102 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I103 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I104 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I105 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I106 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I107 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I108 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I109 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I110 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I111 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I112 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I113 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I114 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I115 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I116 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I117 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I118 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I119 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I120 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I121 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I122 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I123 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I124 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I125 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I126 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I127 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I128 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I129 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I130 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I131 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I132 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I133 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I134 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I135 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I136 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I137 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I138 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I139 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I140 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | V7 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V8 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V9 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V10 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V11 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V12 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V13 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V14 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V15 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V16 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V17 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V18 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | I141 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I142 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I143 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I144 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I145 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I146 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I147 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I148 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I149 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I150 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I151 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I152 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I153 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I154 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I155 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I156 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I157 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I158 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I159 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I160 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I161 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I162 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I163 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I164 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I165 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I166 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I167 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I168 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I169 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I170 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I171 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I172 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I173 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I174 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I175 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I176 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I177 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I178 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I179 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I180 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I181 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I182 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I183 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I184 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I185 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I186 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I187 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I188 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I189 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I190 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I191 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I192 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I193 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I194 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I195 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I196 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I197 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I198 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I199 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I200 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I201 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I202 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I203 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I204 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I205 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I206 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I207 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I208 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I209 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I210 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I211 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I212 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I213 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I214 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | S212 | DIF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S213 | DIF1 | EventMaskHi | UINT32 | RW | 0...4294967295
66 | S1 | REF1 | I0d> [87N] mode | UINT32 | RW | 0=Disabled;1=Activated
66 | V1 | REF1 | I0d> condition | UINT32 | R | 0=Normal;1=Trip;2=Blocked
66 | S2 | REF1 | Select | UINT32 | RW | 0=Primary A;1=Secondary A;2=Per Unit
66 | S3 | REF1 | Select | UINT32 | RW | 0=REF Curr
66 | I1 | REF1 | I0d> Bias current | FLOAT | R | 0...50
66 | I2 | REF1 | I0d> Diff current | FLOAT | R | 0...50
66 | I3 | REF1 | I0d> Char current | FLOAT | R | 0...50
66 | I4 | REF1 | Calculated I0 (I0Calc) | FLOAT | R | 0...50
66 | I5 | REF1 | Measured I0 (3I0) | FLOAT | R | 0...50
66 | S4 | REF1 | REF or Cable end Diff | UINT32 | RW | 0=REF;1=CED
66 | S5 | REF1 | Comp. natural unbal. | UINT32 | RW | 0=-;1=Comp
66 | I6 | REF1 | Natural unbalance | FLOAT | R | 0...50
66 | I7 | REF1 | Natural unbalance ang | FLOAT | R | -360...360
66 | I8 | REF1 | Current for CED | FLOAT | R | 0...50
66 | I9 | REF1 | Angle for CED | FLOAT | R | -360...360
66 | S6 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S7 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S8 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S9 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S10 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S11 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S12 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S13 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S14 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S15 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S16 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S17 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S18 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S19 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S20 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S21 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S22 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S23 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S24 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S25 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S26 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S27 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S28 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S29 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S30 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S31 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S32 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S33 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S34 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S35 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S36 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S37 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S38 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S39 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S40 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S41 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S42 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S43 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S44 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S45 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S46 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S47 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S48 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S49 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S50 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S51 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S52 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S53 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S54 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S55 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S56 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S57 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S58 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S59 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S60 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S61 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S62 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S63 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S64 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S65 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S66 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S67 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S68 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S69 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S70 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S71 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S72 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S73 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S74 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S75 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S76 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S77 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | O1 | REF1 | I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
66 | O2 | REF1 | I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
66 | I10 | REF1 | Newest Register | UINT32 | R | 0...12
66 | I11 | REF1 | Bias current | FLOAT | R | 0...250
66 | I12 | REF1 | Bias current | FLOAT | R | 0...250
66 | I13 | REF1 | Bias current | FLOAT | R | 0...250
66 | I14 | REF1 | Bias current | FLOAT | R | 0...250
66 | I15 | REF1 | Bias current | FLOAT | R | 0...250
66 | I16 | REF1 | Bias current | FLOAT | R | 0...250
66 | I17 | REF1 | Bias current | FLOAT | R | 0...250
66 | I18 | REF1 | Bias current | FLOAT | R | 0...250
66 | I19 | REF1 | Bias current | FLOAT | R | 0...250
66 | I20 | REF1 | Bias current | FLOAT | R | 0...250
66 | I21 | REF1 | Bias current | FLOAT | R | 0...250
66 | I22 | REF1 | Bias current | FLOAT | R | 0...250
66 | I23 | REF1 | Differential current | FLOAT | R | 0...250
66 | I24 | REF1 | Differential current | FLOAT | R | 0...250
66 | I25 | REF1 | Differential current | FLOAT | R | 0...250
66 | I26 | REF1 | Differential current | FLOAT | R | 0...250
66 | I27 | REF1 | Differential current | FLOAT | R | 0...250
66 | I28 | REF1 | Differential current | FLOAT | R | 0...250
66 | I29 | REF1 | Differential current | FLOAT | R | 0...250
66 | I30 | REF1 | Differential current | FLOAT | R | 0...250
66 | I31 | REF1 | Differential current | FLOAT | R | 0...250
66 | I32 | REF1 | Differential current | FLOAT | R | 0...250
66 | I33 | REF1 | Differential current | FLOAT | R | 0...250
66 | I34 | REF1 | Differential current | FLOAT | R | 0...250
66 | I35 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I36 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I37 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I38 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I39 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I40 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I41 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I42 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I43 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I44 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I45 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I46 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | S78 | REF1 | EventMaskLo | UINT32 | RW | 0...4294967295
66 | S79 | REF1 | EventMaskHi | UINT32 | RW | 0...4294967295
73 | S1 | TOLT1 | TT> [49T] mode | UINT32 | RW | 0=Disabled;1=Activated
73 | V1 | TOLT1 | TT> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
73 | V2 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
73 | V3 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
73 | V4 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
73 | V5 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
73 | V6 | TOLT1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
73 | I1 | TOLT1 | IN thermal cap current | FLOAT | RW | 0...40
73 | I2 | TOLT1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
73 | S2 | TOLT1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
73 | S3 | TOLT1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
73 | I3 | TOLT1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
73 | I4 | TOLT1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
73 | S4 | TOLT1 | tau1 (t const heating) | FLOAT | RW | 0...500
73 | S5 | TOLT1 | tau2 (t const cooling) | FLOAT | RW | 0...500
73 | S6 | TOLT1 | kSF (service factor) | FLOAT | RW | 0.01...5
73 | S7 | TOLT1 | Cold Reset default theta | FLOAT | RW | 0...150
73 | V7 | TOLT1 | TT> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
73 | I5 | TOLT1 | TT> Time to 100% Theta | UINT32 | R | 0...4294967295
73 | I6 | TOLT1 | TT> Reference T curr. | FLOAT | R | 0...50
73 | I7 | TOLT1 | TT> Active meas curr. | FLOAT | R | 0...50
73 | I8 | TOLT1 | TT> T est.with act. curr. | FLOAT | R | 0...500
73 | I9 | TOLT1 | TT> T at the moment | FLOAT | R | 0...500
73 | I10 | TOLT1 | TT> Max.Temp.Rise All. | FLOAT | R | 0...250
73 | I11 | TOLT1 | TT> Temp.Rise atm. | FLOAT | R | 0...250
73 | I12 | TOLT1 | TT> Hot Spot estimate | FLOAT | R | 0...250
73 | I13 | TOLT1 | TT> Hot Spot Max. All | FLOAT | R | 0...250
73 | I14 | TOLT1 | TT> Used k for amb. temp | FLOAT | R | 0...3
73 | I15 | TOLT1 | TT> Trip delay remaining | UINT32 | R | 0...4294967295
73 | I16 | TOLT1 | TT> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
73 | I17 | TOLT1 | TT> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
73 | I18 | TOLT1 | TT> Inhibit time to rel. | UINT32 | R | 0...4294967295
73 | I19 | TOLT1 | TT> Trip time to rel. | UINT32 | R | 0...4294967295
73 | I20 | TOLT1 | TT> Thermal cap used | FLOAT | R | 0...500
73 | I21 | TOLT1 | Alarm1 inits | UINT32 | R | 0...4294967295
73 | I22 | TOLT1 | Alarm2 inits | UINT32 | R | 0...4294967295
73 | I23 | TOLT1 | Restart Inhibits | UINT32 | R | 0...4294967295
73 | I24 | TOLT1 | Trips | UINT32 | R | 0...4294967295
73 | I25 | TOLT1 | Trips Blocked | UINT32 | R | 0...4294967295
73 | S8 | TOLT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
73 | S9 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S10 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S11 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S12 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S13 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S14 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S15 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S16 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S17 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S18 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S19 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S20 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S21 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S22 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S23 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S24 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S25 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S26 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S27 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S28 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S29 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S30 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S31 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S32 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S33 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S34 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S35 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S36 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S37 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S38 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S39 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S40 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S41 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S42 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S43 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S44 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S45 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S46 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S47 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S48 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S49 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S50 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S51 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S52 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S53 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S54 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S55 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S56 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S57 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S58 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S59 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S60 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S61 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S62 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S63 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S64 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S65 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S66 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S67 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S68 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S69 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S70 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S71 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S72 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | O1 | TOLT1 | TT> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
73 | O2 | TOLT1 | TT> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
73 | O3 | TOLT1 | TT> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
73 | O4 | TOLT1 | TT> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
73 | O5 | TOLT1 | TT> Trip | SIGNAL_OUT | RW | 0...4294967295
73 | I26 | TOLT1 | Newest Register | UINT32 | R | 0...12
73 | I27 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I28 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I29 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I30 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I31 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I32 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I33 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I34 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I35 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I36 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I37 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I38 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I39 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I40 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I41 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I42 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I43 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I44 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I45 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I46 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I47 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I48 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I49 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I50 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I51 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I52 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I53 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I54 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I55 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I56 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I57 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I58 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I59 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I60 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I61 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I62 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | S73 | TOLT1 | EventMaskLo | UINT32 | RW | 0...4294967295
73 | S74 | TOLT1 | EventMaskHi | UINT32 | RW | 0...4294967295
67 | S1 | TOLF1 | TF> [49F] mode | UINT32 | RW | 0=Disabled;1=Activated
67 | V1 | TOLF1 | TF> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
67 | V2 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
67 | V3 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
67 | V4 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
67 | V5 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
67 | V6 | TOLF1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
67 | I1 | TOLF1 | IN thermal cap current | FLOAT | RW | 0...40
67 | I2 | TOLF1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
67 | I3 | TOLF1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
67 | I4 | TOLF1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
67 | I5 | TOLF1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
67 | I6 | TOLF1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
67 | S2 | TOLF1 | tau (t const) | FLOAT | RW | 0...500
67 | S3 | TOLF1 | Nominal current | FLOAT | RW | 1...9999999
67 | S4 | TOLF1 | kSF (service factor) | FLOAT | RW | 0.01...5
67 | I7 | TOLF1 | TF> Time to 100% Theta | UINT32 | R | 0...4294967295
67 | I8 | TOLF1 | TF> Reference T curr. | FLOAT | R | 0...50
67 | I9 | TOLF1 | TF> Active meas curr. | FLOAT | R | 0...50
67 | I10 | TOLF1 | TF> T est.with act. curr. | FLOAT | R | 0...500
67 | I11 | TOLF1 | TF> T at the moment | FLOAT | R | 0...500
67 | I12 | TOLF1 | TF> Max.Temp.Rise All. | FLOAT | R | 0...250
67 | I13 | TOLF1 | TF> Temp.Rise atm. | FLOAT | R | 0...250
67 | I14 | TOLF1 | TF> Hot Spot estimate | FLOAT | R | 0...250
67 | I15 | TOLF1 | TF> Hot Spot Max. All | FLOAT | R | 0...250
67 | I16 | TOLF1 | TF> Used k for amb. temp | FLOAT | R | 0...3
67 | I17 | TOLF1 | TF> Trip delay remaining | UINT32 | R | 0...4294967295
67 | I18 | TOLF1 | TF> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
67 | I19 | TOLF1 | TF> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
67 | I20 | TOLF1 | TF> Inhibit time to rel. | UINT32 | R | 0...4294967295
67 | I21 | TOLF1 | TF> Trip time to rel. | UINT32 | R | 0...4294967295
67 | I22 | TOLF1 | TF> Thermal cap used | FLOAT | R | 0...500
67 | I23 | TOLF1 | Alarm1 inits | UINT32 | R | 0...4294967295
67 | I24 | TOLF1 | Alarm2 inits | UINT32 | R | 0...4294967295
67 | I25 | TOLF1 | Restart Inhibits | UINT32 | R | 0...4294967295
67 | I26 | TOLF1 | Trips | UINT32 | R | 0...4294967295
67 | I27 | TOLF1 | Trips Blocked | UINT32 | R | 0...4294967295
67 | S5 | TOLF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
67 | S6 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S7 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S8 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S9 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S10 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S11 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S12 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S13 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S14 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S15 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S16 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S17 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S18 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S19 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S20 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S21 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S22 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S23 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S24 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S25 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S26 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S27 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S28 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S29 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S30 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S31 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S32 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S33 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S34 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S35 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S36 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S37 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S38 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S39 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S40 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S41 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S42 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S43 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S44 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S45 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S46 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S47 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S48 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S49 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S50 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S51 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S52 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S53 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S54 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S55 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S56 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S57 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S58 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S59 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S60 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S61 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S62 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S63 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S64 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S65 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S66 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S67 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S68 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S69 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | O1 | TOLF1 | TF> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
67 | O2 | TOLF1 | TF> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
67 | O3 | TOLF1 | TF> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
67 | O4 | TOLF1 | TF> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
67 | O5 | TOLF1 | TF> Trip | SIGNAL_OUT | RW | 0...4294967295
67 | I28 | TOLF1 | Newest Register | UINT32 | R | 0...12
67 | I29 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I30 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I31 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I32 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I33 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I34 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I35 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I36 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I37 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I38 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I39 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I40 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I41 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I42 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I43 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I44 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I45 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I46 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I47 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I48 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I49 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I50 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I51 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I52 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I53 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I54 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I55 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I56 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I57 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I58 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I59 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I60 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I61 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I62 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I63 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I64 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I65 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I66 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I67 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I68 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I69 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I70 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I71 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I72 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I73 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I74 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I75 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I76 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | S70 | TOLF1 | EventMaskLo | UINT32 | RW | 0...4294967295
67 | S71 | TOLF1 | EventMaskHi | UINT32 | RW | 0...4294967295
68 | S1 | TOLM1 | TM> [49M] mode | UINT32 | RW | 0=Disabled; 1=Activated
68 | V1 | TOLM1 | TM> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
68 | V2 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
68 | V3 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
68 | V4 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
68 | V5 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
68 | V6 | TOLM1 | Motor status | UINT32 | R | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
68 | S2 | TOLM1 | Pick-up current (x In) | FLOAT | RW | 0...40
68 | S3 | TOLM1 | NPS Biasing in use | UINT32 | RW | 0=No NPS biasing;1=NPS Biasing in use
68 | S4 | TOLM1 | NPS Bias factor | FLOAT | RW | 0.1...10
68 | S5 | TOLM1 | Time constants | UINT32 | RW | 0=Single;1=Multiple
68 | S6 | TOLM1 | Long Heat T const (cold) | FLOAT | RW | 0...500
68 | S7 | TOLM1 | Long Heat T const (hot) | FLOAT | RW | 0...500
68 | S8 | TOLM1 | Long Cool T const Run | FLOAT | RW | 0...3000
68 | S9 | TOLM1 | Long Cool T const Stop | FLOAT | RW | 0...3000
68 | S10 | TOLM1 | Short Heat T const (cold) | FLOAT | RW | 0...500
68 | S11 | TOLM1 | Short Heat T const (hot) | FLOAT | RW | 0...500
68 | S12 | TOLM1 | Short Cool T const | FLOAT | RW | 0...3000
68 | S13 | TOLM1 | Wf factor for L/S T const | FLOAT | RW | 0...1
68 | S14 | TOLM1 | T const dyn. balancing | UINT32 | RW | 0=Fixed;1=Dynamic
68 | S15 | TOLM1 | Short Cool T used when stop | FLOAT | RW | 0...3000
68 | S16 | TOLM1 | Cold Reset Theta Default | FLOAT | RW | 0...150
68 | I1 | TOLM1 | Wf in use | FLOAT | R | 0...1
68 | I2 | TOLM1 | Long heat TC in use | FLOAT | R | 0...500
68 | I3 | TOLM1 | Short heat TC in use | FLOAT | R | 0...500
68 | I4 | TOLM1 | Long cool TC in use | FLOAT | R | 0...500
68 | I5 | TOLM1 | Short cool TC in use | FLOAT | R | 0...500
68 | I6 | TOLM1 | Cold stall time | FLOAT | R | 0...500
68 | I7 | TOLM1 | Hot stall time | FLOAT | R | 0...500
68 | S17 | TOLM1 | Dev.Temp (tmax) | UINT32 | RW | 0=A;1=B;2=F;3=H;4=Manual set
68 | S18 | TOLM1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
68 | S19 | TOLM1 | Amb. T Selection | UINT32 | RW | 0=Manual set;1=RTD
68 | S20 | TOLM1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
68 | V7 | TOLM1 | TM> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
68 | I8 | TOLM1 | TM> Time to 100% T | UINT32 | R | 0...4294967295
68 | I9 | TOLM1 | TM> Reference T curr. | FLOAT | R | 0...50
68 | I10 | TOLM1 | TM> Active meas curr. | FLOAT | R | 0...50
68 | I11 | TOLM1 | TM> T est.with act. curr. | FLOAT | R | 0...500
68 | I12 | TOLM1 | TM> T at the moment | FLOAT | R | 0...500
68 | I13 | TOLM1 | TM> Max.Temp.Rise All. | FLOAT | R | 0...250
68 | I14 | TOLM1 | TM> Temp.Rise atm. | FLOAT | R | 0...250
68 | I15 | TOLM1 | TM> Hot Spot estimate | FLOAT | R | 0...250
68 | I16 | TOLM1 | TM> Hot Spot Max. All | FLOAT | R | 0...250
68 | I17 | TOLM1 | TM> Used k for amb. temp | FLOAT | R | 0...5
68 | I18 | TOLM1 | TM> Trip delay remaining | UINT32 | R | 0...4294967295
68 | I19 | TOLM1 | TM> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
68 | I20 | TOLM1 | TM> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
68 | I21 | TOLM1 | TM> Inhibit time to rel. | UINT32 | R | 0...4294967295
68 | I22 | TOLM1 | TM> Trip time to rel. | UINT32 | R | 0...4294967295
68 | I23 | TOLM1 | TM> Thermal cap used | FLOAT | R | 0...500
68 | I24 | TOLM1 | Alarm1 inits | UINT32 | R | 0...4294967295
68 | I25 | TOLM1 | Alarm2 inits | UINT32 | R | 0...4294967295
68 | I26 | TOLM1 | Restart Inhibits | UINT32 | R | 0...4294967295
68 | I27 | TOLM1 | Trips | UINT32 | R | 0...4294967295
68 | I28 | TOLM1 | Trips Blocked | UINT32 | R | 0...4294967295
68 | S21 | TOLM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
68 | S22 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S23 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S24 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S25 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S26 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S27 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S28 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S29 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S30 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S31 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S32 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S33 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S34 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S35 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S36 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S37 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S38 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S39 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S40 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S41 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S42 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S43 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S44 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S45 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S46 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S47 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S48 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S49 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S50 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S51 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S52 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S53 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S54 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S55 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S56 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S57 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S58 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S59 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S60 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S61 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S62 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S63 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S64 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S65 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S66 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S67 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S68 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S69 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S70 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S71 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S72 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S73 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S74 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S75 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S76 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S77 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S78 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S79 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S80 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S81 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S82 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S83 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S84 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S85 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | O1 | TOLM1 | TM> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
68 | O2 | TOLM1 | TM> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
68 | O3 | TOLM1 | TM> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
68 | O4 | TOLM1 | TM> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
68 | O5 | TOLM1 | TM> Trip | SIGNAL_OUT | RW | 0...4294967295
68 | I29 | TOLM1 | Newest Register | UINT32 | R | 0...12
68 | I30 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I31 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I32 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I33 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I34 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I35 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I36 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I37 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I38 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I39 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I40 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I41 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I42 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I43 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I44 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I45 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I46 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I47 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I48 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I49 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I50 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I51 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I52 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I53 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I54 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I55 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I56 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I57 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I58 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I59 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I60 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I61 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I62 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I63 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I64 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I65 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I66 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I67 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I68 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I69 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I70 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I71 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I72 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I73 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I74 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I75 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I76 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I77 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I78 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I79 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I80 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I81 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I82 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I83 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I84 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I85 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I86 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I87 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I88 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I89 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I90 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I91 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I92 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I93 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I94 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I95 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I96 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I97 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I98 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I99 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I100 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I101 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I102 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I103 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I104 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I105 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I106 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I107 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I108 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I109 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I110 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I111 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I112 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I113 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I114 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I115 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I116 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I117 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I118 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I119 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I120 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I121 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I122 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I123 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I124 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I125 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I126 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I127 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I128 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I129 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I130 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I131 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I132 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I133 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I134 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I135 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I136 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I137 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | S86 | TOLM1 | EventMaskLo | UINT32 | RW | 0...4294967295
68 | S87 | TOLM1 | EventMaskHi | UINT32 | RW | 0...4294967295
57 | S1 | LCR1 | ISt> [48/14/50LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
57 | V1 | LCR1 | ISt> condition | UINT32 | R | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
57 | I1 | LCR1 | ISt> starts | UINT32 | R | 0...4294967295
57 | I2 | LCR1 | ISt> Set cap used in last start | FLOAT | R | 0...500
57 | I3 | LCR1 | ISt> Max cap used in last start | FLOAT | R | 0...500
57 | I4 | LCR1 | ISt> Set time trips | UINT32 | R | 0...4294967295
57 | I5 | LCR1 | ISt> Max cap trips | UINT32 | R | 0...4294967295
57 | I6 | LCR1 | ISt> blocks | UINT32 | R | 0...4294967295
57 | S2 | LCR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
57 | S3 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S4 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S5 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S6 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S7 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S8 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S9 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S10 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S11 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S12 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S13 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S14 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S15 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S16 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S17 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S18 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S19 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S20 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S21 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S22 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S23 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S24 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S25 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S26 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S27 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S28 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S29 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S30 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S31 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S32 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S33 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S34 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S35 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S36 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S37 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S38 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S39 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S40 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S41 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S42 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S43 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S44 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S45 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S46 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S47 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S48 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S49 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S50 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | O1 | LCR1 | ISt> START | SIGNAL_OUT | RW | 0...4294967295
57 | O2 | LCR1 | ISt> Set time TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O3 | LCR1 | ISt> Machine cap.TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O4 | LCR1 | ISt> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
57 | I7 | LCR1 | Newest Register | UINT32 | R | 0...12
57 | I8 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I9 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I10 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I11 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I12 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I13 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I14 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I15 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I16 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I17 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I18 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I19 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I20 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I21 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I22 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I23 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I24 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I25 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I26 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I27 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I28 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I29 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I30 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I31 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I32 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I33 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I34 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I35 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I36 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I37 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I38 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I39 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I40 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I41 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I42 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I43 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I44 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I45 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I46 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I47 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I48 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I49 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I50 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I51 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I52 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I53 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I54 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I55 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I56 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I57 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I58 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I59 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I60 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I61 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I62 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I63 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I64 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I65 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I66 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I67 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I68 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I69 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I70 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I71 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I72 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I73 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I74 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I75 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I76 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I77 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I78 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I79 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I80 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I81 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I82 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I83 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I84 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I85 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I86 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I87 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I88 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I89 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I90 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I91 | LCR1 | Phase C current | FLOAT | R | 0...250
56 | S1 | FSP1 | N> [66/86] mode | UINT32 | RW | 0=Disabled; 1=Activated
56 | V1 | FSP1 | N> condition | UINT32 | R | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
56 | I1 | FSP1 | N> alarms | UINT32 | R | 0...4294967295
56 | I2 | FSP1 | N> Inhibits | UINT32 | R | 0...4294967295
56 | I3 | FSP1 | N> blocks | UINT32 | R | 0...4294967295
56 | S2 | FSP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
56 | I4 | FSP1 | Start monitoring time left | UINT32 | R | 0...4294967295
56 | I5 | FSP1 | Inhibit time on | UINT32 | R | 0...4294967295
56 | I6 | FSP1 | Alarm time on | UINT32 | R | 0...4294967295
56 | I7 | FSP1 | Time since last start | UINT32 | R | 0...4294967295
56 | I8 | FSP1 | Start count atm. | UINT32 | R | 0...4294967295
56 | I9 | FSP1 | Starts left atm. | UINT32 | R | 0...4294967295
56 | S3 | FSP1 | Give one more start (Warning! Motor may overheat) | UINT32 | W | 0=-;1=Deduct one start
56 | O1 | FSP1 | N> One start remaining (Alarm) | SIGNAL_OUT | RW | 0...4294967295
56 | O2 | FSP1 | N> INHIBIT ON (General) | SIGNAL_OUT | RW | 0...4294967295
56 | O3 | FSP1 | N> INHIBIT ON Mot Running | SIGNAL_OUT | RW | 0...4294967295
56 | O4 | FSP1 | N> INHIBIT ON Mot Stopped | SIGNAL_OUT | RW | 0...4294967295
56 | O5 | FSP1 | N> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
56 | I10 | FSP1 | Newest Register | UINT32 | R | 0...12
56 | S4 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S5 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S6 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S7 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S8 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S9 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S10 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S11 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S12 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S13 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S14 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S15 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S16 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S17 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S18 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S19 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S20 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S21 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S22 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S23 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S24 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S25 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S26 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S27 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S28 | FSP1 | Start count | FLOAT | R | 0...250
56 | S29 | FSP1 | Start count | FLOAT | R | 0...250
56 | S30 | FSP1 | Start count | FLOAT | R | 0...250
56 | S31 | FSP1 | Start count | FLOAT | R | 0...250
56 | S32 | FSP1 | Start count | FLOAT | R | 0...250
56 | S33 | FSP1 | Start count | FLOAT | R | 0...250
56 | S34 | FSP1 | Start count | FLOAT | R | 0...250
56 | S35 | FSP1 | Start count | FLOAT | R | 0...250
56 | S36 | FSP1 | Start count | FLOAT | R | 0...250
56 | S37 | FSP1 | Start count | FLOAT | R | 0...250
56 | S38 | FSP1 | Start count | FLOAT | R | 0...250
56 | S39 | FSP1 | Start count | FLOAT | R | 0...250
56 | S40 | FSP1 | EventMaskLo | UINT32 | RW | 0...4294967295
60 | S1 | NUC1 | I< [37] mode | UINT32 | RW | 0=Disabled; 1=Activated
60 | V1 | NUC1 | I< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
60 | I1 | NUC1 | I< starts | UINT32 | R | 0...4294967295
60 | I2 | NUC1 | I< trips | UINT32 | R | 0...4294967295
60 | I3 | NUC1 | I< blocks | UINT32 | R | 0...4294967295
60 | S2 | NUC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
60 | S3 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S4 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S5 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S6 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S7 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S8 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S9 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S10 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S11 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S12 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S13 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S14 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S15 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S16 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S17 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S18 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S19 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S20 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S21 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S22 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S23 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S24 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S25 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S26 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | O1 | NUC1 | I< START | SIGNAL_OUT | RW | 0...4294967295
60 | O2 | NUC1 | I< TRIP | SIGNAL_OUT | RW | 0...4294967295
60 | O3 | NUC1 | I< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
60 | I4 | NUC1 | Newest Register | UINT32 | R | 0...12
60 | I5 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I6 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I7 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I8 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I9 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I10 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I11 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I12 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I13 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I14 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I15 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I16 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I17 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I18 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I19 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I20 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I21 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I22 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I23 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I24 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I25 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I26 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I27 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I28 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I29 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I30 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I31 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I32 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I33 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I34 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I35 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I36 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I37 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I38 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I39 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I40 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | S27 | NUC1 | EventMaskLo | UINT32 | RW | 0...4294967295
59 | S1 | MJP1 | Im> [51LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
59 | V1 | MJP1 | Im> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
59 | I1 | MJP1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
59 | I2 | MJP1 | Im> starts | UINT32 | R | 0...4294967295
59 | I3 | MJP1 | Im> trips | UINT32 | R | 0...4294967295
59 | I4 | MJP1 | Im> blocks | UINT32 | R | 0...4294967295
59 | S2 | MJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
59 | S3 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S4 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S5 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S6 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S7 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S8 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S9 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S10 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S11 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S12 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S13 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S14 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S15 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S16 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S17 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S18 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | O1 | MJP1 | Im> START | SIGNAL_OUT | RW | 0...4294967295
59 | O2 | MJP1 | Im> TRIP | SIGNAL_OUT | RW | 0...4294967295
59 | O3 | MJP1 | Im> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
59 | I5 | MJP1 | Newest Register | UINT32 | R | 0...12
59 | I6 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I7 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I8 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I9 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I10 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I11 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I12 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I13 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I14 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I15 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I16 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I17 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I18 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I19 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I20 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I21 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I22 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I23 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I24 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I25 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I26 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I27 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I28 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I29 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I30 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I31 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I32 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I33 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I34 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I35 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I36 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I37 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I38 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I39 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I40 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I41 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | S19 | MJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
85 | S1 | OV1 | U> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
85 | V1 | OV1 | U> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
85 | I1 | OV1 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
85 | I2 | OV1 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
85 | I3 | OV1 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
85 | I4 | OV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
85 | I5 | OV1 | U> starts | UINT32 | R | 0...4294967295
85 | I6 | OV1 | U> trips | UINT32 | R | 0...4294967295
85 | I7 | OV1 | U> blocks | UINT32 | R | 0...4294967295
85 | S2 | OV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
85 | S3 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S4 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S5 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S6 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S7 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S8 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S9 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S10 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S11 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S12 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S13 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S14 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S15 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S16 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S17 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S18 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S19 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S20 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S21 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S22 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S23 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S24 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S25 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S26 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | O1 | OV1 | U> START | SIGNAL_OUT | RW | 0...4294967295
85 | O2 | OV1 | U> TRIP | SIGNAL_OUT | RW | 0...4294967295
85 | O3 | OV1 | U> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
85 | I8 | OV1 | Newest Register | UINT32 | R | 0...12
85 | I9 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I10 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I11 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I12 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I13 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I14 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I15 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I16 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I17 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I18 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I19 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I20 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I21 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I22 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I23 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I24 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I25 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I26 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I27 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I28 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I29 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I30 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I31 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I32 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I33 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I34 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I35 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I36 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I37 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I38 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I39 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I40 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I41 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I42 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I43 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I44 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | S27 | OV1 | EventMaskLo | UINT32 | RW | 0...4294967295
86 | S1 | OV2 | U>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
86 | V1 | OV2 | U>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
86 | I1 | OV2 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
86 | I2 | OV2 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
86 | I3 | OV2 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
86 | I4 | OV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
86 | I5 | OV2 | U>> starts | UINT32 | R | 0...4294967295
86 | I6 | OV2 | U>> trips | UINT32 | R | 0...4294967295
86 | I7 | OV2 | U>> blocks | UINT32 | R | 0...4294967295
86 | S2 | OV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
86 | S3 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S4 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S5 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S6 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S7 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S8 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S9 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S10 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S11 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S12 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S13 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S14 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S15 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S16 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S17 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S18 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S19 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S20 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S21 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S22 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S23 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S24 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S25 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S26 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | O1 | OV2 | U>> START | SIGNAL_OUT | RW | 0...4294967295
86 | O2 | OV2 | U>> TRIP | SIGNAL_OUT | RW | 0...4294967295
86 | O3 | OV2 | U>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
86 | I8 | OV2 | Newest Register | UINT32 | R | 0...12
86 | I9 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I10 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I11 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I12 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I13 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I14 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I15 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I16 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I17 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I18 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I19 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I20 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I21 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I22 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I23 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I24 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I25 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I26 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I27 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I28 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I29 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I30 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I31 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I32 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I33 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I34 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I35 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I36 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I37 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I38 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I39 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I40 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I41 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I42 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I43 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I44 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | S27 | OV2 | EventMaskLo | UINT32 | RW | 0...4294967295
87 | S1 | OV3 | U>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
87 | V1 | OV3 | U>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
87 | I1 | OV3 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
87 | I2 | OV3 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
87 | I3 | OV3 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
87 | I4 | OV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
87 | I5 | OV3 | U>>> starts | UINT32 | R | 0...4294967295
87 | I6 | OV3 | U>>> trips | UINT32 | R | 0...4294967295
87 | I7 | OV3 | U>>> blocks | UINT32 | R | 0...4294967295
87 | S2 | OV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
87 | S3 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S4 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S5 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S6 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S7 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S8 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S9 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S10 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S11 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S12 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S13 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S14 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S15 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S16 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S17 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S18 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S19 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S20 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S21 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S22 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S23 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S24 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S25 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S26 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | O1 | OV3 | U>>> START | SIGNAL_OUT | RW | 0...4294967295
87 | O2 | OV3 | U>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
87 | O3 | OV3 | U>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
87 | I8 | OV3 | Newest Register | UINT32 | R | 0...12
87 | I9 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I10 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I11 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I12 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I13 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I14 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I15 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I16 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I17 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I18 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I19 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I20 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I21 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I22 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I23 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I24 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I25 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I26 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I27 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I28 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I29 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I30 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I31 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I32 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I33 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I34 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I35 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I36 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I37 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I38 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I39 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I40 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I41 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I42 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I43 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I44 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | S27 | OV3 | EventMaskLo | UINT32 | RW | 0...4294967295
88 | S1 | OV4 | U>>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
88 | V1 | OV4 | U>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
88 | I1 | OV4 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
88 | I2 | OV4 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
88 | I3 | OV4 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
88 | I4 | OV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
88 | I5 | OV4 | U>>>> starts | UINT32 | R | 0...4294967295
88 | I6 | OV4 | U>>>> trips | UINT32 | R | 0...4294967295
88 | I7 | OV4 | U>>>> blocks | UINT32 | R | 0...4294967295
88 | S2 | OV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
88 | S3 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S4 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S5 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S6 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S7 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S8 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S9 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S10 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S11 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S12 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S13 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S14 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S15 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S16 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S17 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S18 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S19 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S20 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S21 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S22 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S23 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S24 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S25 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S26 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | O1 | OV4 | U>>>> START | SIGNAL_OUT | RW | 0...4294967295
88 | O2 | OV4 | U>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
88 | O3 | OV4 | U>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
88 | I8 | OV4 | Newest Register | UINT32 | R | 0...12
88 | I9 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I10 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I11 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I12 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I13 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I14 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I15 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I16 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I17 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I18 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I19 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I20 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I21 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I22 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I23 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I24 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I25 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I26 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I27 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I28 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I29 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I30 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I31 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I32 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I33 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I34 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I35 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I36 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I37 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I38 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I39 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I40 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I41 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I42 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I43 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I44 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | S27 | OV4 | EventMaskLo | UINT32 | RW | 0...4294967295
89 | S1 | UV1 | U< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
89 | V1 | UV1 | U< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
89 | I1 | UV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
89 | I2 | UV1 | U< starts | UINT32 | R | 0...4294967295
89 | I3 | UV1 | U< trips | UINT32 | R | 0...4294967295
89 | I4 | UV1 | U< blocks | UINT32 | R | 0...4294967295
89 | S2 | UV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
89 | S3 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S4 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S5 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S6 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S7 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S8 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S9 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S10 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S11 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S12 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S13 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S14 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S15 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S16 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S17 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S18 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S19 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S20 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S21 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S22 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S23 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S24 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S25 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S26 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S27 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S28 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S29 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S30 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S31 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S32 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S33 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S34 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | O1 | UV1 | U< START | SIGNAL_OUT | RW | 0...4294967295
89 | O2 | UV1 | U< TRIP | SIGNAL_OUT | RW | 0...4294967295
89 | O3 | UV1 | U< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
89 | I5 | UV1 | Newest Register | UINT32 | R | 0...12
89 | I6 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I7 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I8 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I9 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I10 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I11 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I12 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I13 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I14 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I15 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I16 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I17 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I18 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I19 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I20 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I21 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I22 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I23 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I24 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I25 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I26 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I27 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I28 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I29 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I30 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I31 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I32 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I33 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I34 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I35 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I36 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I37 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I38 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I39 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I40 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I41 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | S35 | UV1 | EventMaskLo | UINT32 | RW | 0...4294967295
90 | S1 | UV2 | U<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
90 | V1 | UV2 | U<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
90 | I1 | UV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
90 | I2 | UV2 | U<< starts | UINT32 | R | 0...4294967295
90 | I3 | UV2 | U<< trips | UINT32 | R | 0...4294967295
90 | I4 | UV2 | U<< blocks | UINT32 | R | 0...4294967295
90 | S2 | UV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
90 | S3 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S4 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S5 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S6 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S7 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S8 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S9 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S10 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S11 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S12 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S13 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S14 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S15 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S16 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S17 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S18 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S19 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S20 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S21 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S22 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S23 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S24 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S25 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S26 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S27 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S28 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S29 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S30 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S31 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S32 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S33 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S34 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | O1 | UV2 | U<< START | SIGNAL_OUT | RW | 0...4294967295
90 | O2 | UV2 | U<< TRIP | SIGNAL_OUT | RW | 0...4294967295
90 | O3 | UV2 | U<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
90 | I5 | UV2 | Newest Register | UINT32 | R | 0...12
90 | I6 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I7 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I8 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I9 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I10 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I11 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I12 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I13 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I14 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I15 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I16 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I17 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I18 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I19 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I20 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I21 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I22 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I23 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I24 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I25 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I26 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I27 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I28 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I29 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I30 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I31 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I32 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I33 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I34 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I35 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I36 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I37 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I38 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I39 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I40 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I41 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | S35 | UV2 | EventMaskLo | UINT32 | RW | 0...4294967295
91 | S1 | UV3 | U<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
91 | V1 | UV3 | U<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
91 | I1 | UV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
91 | I2 | UV3 | U<<< starts | UINT32 | R | 0...4294967295
91 | I3 | UV3 | U<<< trips | UINT32 | R | 0...4294967295
91 | I4 | UV3 | U<<< blocks | UINT32 | R | 0...4294967295
91 | S2 | UV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
91 | S3 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S4 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S5 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S6 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S7 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S8 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S9 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S10 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S11 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S12 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S13 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S14 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S15 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S16 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S17 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S18 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S19 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S20 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S21 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S22 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S23 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S24 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S25 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S26 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S27 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S28 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S29 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S30 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S31 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S32 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S33 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S34 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | O1 | UV3 | U<<< START | SIGNAL_OUT | RW | 0...4294967295
91 | O2 | UV3 | U<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
91 | O3 | UV3 | U<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
91 | I5 | UV3 | Newest Register | UINT32 | R | 0...12
91 | I6 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I7 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I8 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I9 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I10 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I11 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I12 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I13 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I14 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I15 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I16 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I17 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I18 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I19 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I20 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I21 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I22 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I23 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I24 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I25 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I26 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I27 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I28 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I29 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I30 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I31 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I32 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I33 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I34 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I35 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I36 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I37 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I38 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I39 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I40 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I41 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | S35 | UV3 | EventMaskLo | UINT32 | RW | 0...4294967295
92 | S1 | UV4 | U<<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
92 | V1 | UV4 | U<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
92 | I1 | UV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
92 | I2 | UV4 | U<<<< starts | UINT32 | R | 0...4294967295
92 | I3 | UV4 | U<<<< trips | UINT32 | R | 0...4294967295
92 | I4 | UV4 | U<<<< blocks | UINT32 | R | 0...4294967295
92 | S2 | UV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
92 | S3 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S4 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S5 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S6 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S7 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S8 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S9 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S10 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S11 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S12 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S13 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S14 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S15 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S16 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S17 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S18 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S19 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S20 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S21 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S22 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S23 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S24 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S25 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S26 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S27 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S28 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S29 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S30 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S31 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S32 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S33 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S34 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | O1 | UV4 | U<<<< START | SIGNAL_OUT | RW | 0...4294967295
92 | O2 | UV4 | U<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
92 | O3 | UV4 | U<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
92 | I5 | UV4 | Newest Register | UINT32 | R | 0...12
92 | I6 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I7 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I8 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I9 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I10 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I11 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I12 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I13 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I14 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I15 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I16 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I17 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I18 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I19 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I20 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I21 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I22 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I23 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I24 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I25 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I26 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I27 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I28 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I29 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I30 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I31 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I32 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I33 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I34 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I35 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I36 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I37 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I38 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I39 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I40 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I41 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | S35 | UV4 | EventMaskLo | UINT32 | RW | 0...4294967295
93 | S1 | NOV1 | U0> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
93 | V1 | NOV1 | U0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
93 | I1 | NOV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
93 | I2 | NOV1 | U0> starts | UINT32 | R | 0...4294967295
93 | I3 | NOV1 | U0> trips | UINT32 | R | 0...4294967295
93 | I4 | NOV1 | U0> blocks | UINT32 | R | 0...4294967295
93 | S2 | NOV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
93 | S3 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S4 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S5 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S6 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S7 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S8 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S9 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S10 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S11 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S12 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S13 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S14 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S15 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S16 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S17 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S18 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | O1 | NOV1 | U0> START | SIGNAL_OUT | RW | 0...4294967295
93 | O2 | NOV1 | U0> TRIP | SIGNAL_OUT | RW | 0...4294967295
93 | O3 | NOV1 | U0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
93 | I5 | NOV1 | Newest Register | UINT32 | R | 0...12
93 | I6 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I7 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I8 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I9 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I10 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I11 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I12 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I13 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I14 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I15 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I16 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I17 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I18 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I19 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I20 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I21 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I22 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I23 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I24 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I25 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I26 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I27 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I28 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I29 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | S19 | NOV1 | EventMaskLo | UINT32 | RW | 0...4294967295
94 | S1 | NOV2 | U0>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
94 | V1 | NOV2 | U0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
94 | I1 | NOV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
94 | I2 | NOV2 | U0>> starts | UINT32 | R | 0...4294967295
94 | I3 | NOV2 | U0>> trips | UINT32 | R | 0...4294967295
94 | I4 | NOV2 | U0>> blocks | UINT32 | R | 0...4294967295
94 | S2 | NOV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
94 | S3 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S4 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S5 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S6 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S7 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S8 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S9 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S10 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S11 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S12 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S13 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S14 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S15 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S16 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S17 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S18 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | O1 | NOV2 | U0>> START | SIGNAL_OUT | RW | 0...4294967295
94 | O2 | NOV2 | U0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
94 | O3 | NOV2 | U0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
94 | I5 | NOV2 | Newest Register | UINT32 | R | 0...12
94 | I6 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I7 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I8 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I9 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I10 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I11 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I12 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I13 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I14 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I15 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I16 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I17 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I18 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I19 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I20 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I21 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I22 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I23 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I24 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I25 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I26 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I27 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I28 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I29 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | S19 | NOV2 | EventMaskLo | UINT32 | RW | 0...4294967295
95 | S1 | NOV3 | U0>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
95 | V1 | NOV3 | U0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
95 | I1 | NOV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
95 | I2 | NOV3 | U0>>> starts | UINT32 | R | 0...4294967295
95 | I3 | NOV3 | U0>>> trips | UINT32 | R | 0...4294967295
95 | I4 | NOV3 | U0>>> blocks | UINT32 | R | 0...4294967295
95 | S2 | NOV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
95 | S3 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S4 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S5 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S6 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S7 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S8 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S9 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S10 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S11 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S12 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S13 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S14 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S15 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S16 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S17 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S18 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | O1 | NOV3 | U0>>> START | SIGNAL_OUT | RW | 0...4294967295
95 | O2 | NOV3 | U0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
95 | O3 | NOV3 | U0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
95 | I5 | NOV3 | Newest Register | UINT32 | R | 0...12
95 | I6 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I7 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I8 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I9 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I10 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I11 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I12 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I13 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I14 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I15 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I16 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I17 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I18 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I19 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I20 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I21 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I22 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I23 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I24 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I25 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I26 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I27 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I28 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I29 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | S19 | NOV3 | EventMaskLo | UINT32 | RW | 0...4294967295
96 | S1 | NOV4 | U0>>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
96 | V1 | NOV4 | U0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
96 | I1 | NOV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
96 | I2 | NOV4 | U0>>>> starts | UINT32 | R | 0...4294967295
96 | I3 | NOV4 | U0>>>> trips | UINT32 | R | 0...4294967295
96 | I4 | NOV4 | U0>>>> blocks | UINT32 | R | 0...4294967295
96 | S2 | NOV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
96 | S3 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S4 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S5 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S6 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S7 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S8 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S9 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S10 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S11 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S12 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S13 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S14 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S15 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S16 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S17 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S18 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | O1 | NOV4 | U0>>>> START | SIGNAL_OUT | RW | 0...4294967295
96 | O2 | NOV4 | U0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
96 | O3 | NOV4 | U0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
96 | I5 | NOV4 | Newest Register | UINT32 | R | 0...12
96 | I6 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I7 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I8 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I9 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I10 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I11 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I12 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I13 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I14 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I15 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I16 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I17 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I18 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I19 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I20 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I21 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I22 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I23 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I24 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I25 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I26 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I27 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I28 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I29 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | S19 | NOV4 | EventMaskLo | UINT32 | RW | 0...4294967295
130 | S1 | VUB1 | U1/2 >/< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
130 | V1 | VUB1 | U1/2 >/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
130 | I1 | VUB1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
130 | I2 | VUB1 | U1/2 >/< starts | UINT32 | R | 0...4294967295
130 | I3 | VUB1 | U1/2 >/< trips | UINT32 | R | 0...4294967295
130 | I4 | VUB1 | U1/2 >/< blocks | UINT32 | R | 0...4294967295
130 | S2 | VUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
130 | S3 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S4 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S5 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S6 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S7 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S8 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S9 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S10 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S11 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S12 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S13 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S14 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S15 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S16 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S17 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S18 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S19 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S20 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S21 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S22 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S23 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S24 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S25 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S26 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S27 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S28 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S29 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S30 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S31 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S32 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S33 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S34 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | O1 | VUB1 | U1/2 >/< START | SIGNAL_OUT | RW | 0...4294967295
130 | O2 | VUB1 | U1/2 >/< TRIP | SIGNAL_OUT | RW | 0...4294967295
130 | O3 | VUB1 | U1/2 >/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
130 | I5 | VUB1 | Newest Register | UINT32 | R | 0...12
130 | I6 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I7 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I8 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I9 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I10 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I11 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I12 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I13 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I14 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I15 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I16 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I17 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I18 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I19 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I20 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I21 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I22 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I23 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I24 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I25 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I26 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I27 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I28 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I29 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | S35 | VUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
131 | S1 | VUB2 | U1/2 >>/<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
131 | V1 | VUB2 | U1/2 >>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
131 | I1 | VUB2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
131 | I2 | VUB2 | U1/2 >>/<< starts | UINT32 | R | 0...4294967295
131 | I3 | VUB2 | U1/2 >>/<< trips | UINT32 | R | 0...4294967295
131 | I4 | VUB2 | U1/2 >>/<< blocks | UINT32 | R | 0...4294967295
131 | S2 | VUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
131 | S3 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S4 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S5 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S6 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S7 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S8 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S9 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S10 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S11 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S12 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S13 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S14 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S15 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S16 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S17 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S18 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S19 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S20 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S21 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S22 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S23 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S24 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S25 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S26 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S27 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S28 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S29 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S30 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S31 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S32 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S33 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S34 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | O1 | VUB2 | U1/2 >>/<< START | SIGNAL_OUT | RW | 0...4294967295
131 | O2 | VUB2 | U1/2 >>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
131 | O3 | VUB2 | U1/2 >>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
131 | I5 | VUB2 | Newest Register | UINT32 | R | 0...12
131 | I6 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I7 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I8 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I9 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I10 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I11 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I12 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I13 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I14 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I15 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I16 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I17 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I18 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I19 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I20 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I21 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I22 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I23 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I24 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I25 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I26 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I27 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I28 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I29 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | S35 | VUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
132 | S1 | VUB3 | U1/2 >>>/<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
132 | V1 | VUB3 | U1/2 >>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
132 | I1 | VUB3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
132 | I2 | VUB3 | U1/2 >>>/<<< starts | UINT32 | R | 0...4294967295
132 | I3 | VUB3 | U1/2 >>>/<<< trips | UINT32 | R | 0...4294967295
132 | I4 | VUB3 | U1/2 >>>/<<< blocks | UINT32 | R | 0...4294967295
132 | S2 | VUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
132 | S3 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S4 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S5 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S6 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S7 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S8 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S9 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S10 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S11 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S12 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S13 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S14 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S15 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S16 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S17 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S18 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S19 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S20 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S21 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S22 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S23 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S24 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S25 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S26 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S27 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S28 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S29 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S30 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S31 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S32 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S33 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S34 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | O1 | VUB3 | U1/2 >>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
132 | O2 | VUB3 | U1/2 >>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
132 | O3 | VUB3 | U1/2 >>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
132 | I5 | VUB3 | Newest Register | UINT32 | R | 0...12
132 | I6 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I7 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I8 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I9 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I10 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I11 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I12 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I13 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I14 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I15 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I16 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I17 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I18 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I19 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I20 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I21 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I22 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I23 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I24 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I25 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I26 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I27 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I28 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I29 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | S35 | VUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
133 | S1 | VUB4 | U1/2 >>>>/<<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
133 | V1 | VUB4 | U1/2 >>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
133 | I1 | VUB4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
133 | I2 | VUB4 | U1/2 >>>>/<<<< starts | UINT32 | R | 0...4294967295
133 | I3 | VUB4 | U1/2 >>>>/<<<< trips | UINT32 | R | 0...4294967295
133 | I4 | VUB4 | U1/2 >>>>/<<<< blocks | UINT32 | R | 0...4294967295
133 | S2 | VUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
133 | S3 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S4 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S5 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S6 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S7 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S8 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S9 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S10 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S11 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S12 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S13 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S14 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S15 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S16 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S17 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S18 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S19 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S20 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S21 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S22 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S23 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S24 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S25 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S26 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S27 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S28 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S29 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S30 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S31 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S32 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S33 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S34 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | O1 | VUB4 | U1/2 >>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
133 | O2 | VUB4 | U1/2 >>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
133 | O3 | VUB4 | U1/2 >>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
133 | I5 | VUB4 | Newest Register | UINT32 | R | 0...12
133 | I6 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I7 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I8 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I9 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I10 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I11 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I12 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I13 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I14 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I15 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I16 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I17 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I18 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I19 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I20 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I21 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I22 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I23 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I24 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I25 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I26 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I27 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I28 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I29 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | S35 | VUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
99 | S1 | FRQV1 | f</> [81O/81U] mode | UINT32 | RW | 0=Disabled;1=Activated
99 | V1 | FRQV1 | f> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I1 | FRQV1 | f> fmeas / fset | FLOAT | R | 0...20
99 | S2 | FRQV1 | f>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V2 | FRQV1 | f>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I2 | FRQV1 | f>> fmeas / fset | FLOAT | R | 0...20
99 | S3 | FRQV1 | f>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V3 | FRQV1 | f>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I3 | FRQV1 | f>>> fmeas / fset | FLOAT | R | 0...20
99 | S4 | FRQV1 | f>>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V4 | FRQV1 | f>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I4 | FRQV1 | f>>>> fmeas / fset | FLOAT | R | 0...20
99 | S5 | FRQV1 | f< Enable | UINT32 | RW | 0=No;1=Yes
99 | V5 | FRQV1 | f< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I5 | FRQV1 | f< fmeas / fset | FLOAT | R | 0...20
99 | S6 | FRQV1 | f<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V6 | FRQV1 | f<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I6 | FRQV1 | f<< fmeas / fset | FLOAT | R | 0...20
99 | S7 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V7 | FRQV1 | f<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I7 | FRQV1 | f<<< fmeas / fset | FLOAT | R | 0...20
99 | S8 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V8 | FRQV1 | f<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I8 | FRQV1 | f<<<< fmeas / fset | FLOAT | R | 0...20
99 | I9 | FRQV1 | f> starts | UINT32 | R | 0...4294967295
99 | I10 | FRQV1 | f> trips | UINT32 | R | 0...4294967295
99 | I11 | FRQV1 | f> blocks | UINT32 | R | 0...4294967295
99 | I12 | FRQV1 | f>> starts | UINT32 | R | 0...4294967295
99 | I13 | FRQV1 | f>> trips | UINT32 | R | 0...4294967295
99 | I14 | FRQV1 | f>> blocks | UINT32 | R | 0...4294967295
99 | I15 | FRQV1 | f>>> starts | UINT32 | R | 0...4294967295
99 | I16 | FRQV1 | f>>> trips | UINT32 | R | 0...4294967295
99 | I17 | FRQV1 | f>>> blocks | UINT32 | R | 0...4294967295
99 | I18 | FRQV1 | f>>>> starts | UINT32 | R | 0...4294967295
99 | I19 | FRQV1 | f>>>> trips | UINT32 | R | 0...4294967295
99 | I20 | FRQV1 | f>>>> blocks | UINT32 | R | 0...4294967295
99 | I21 | FRQV1 | f< starts | UINT32 | R | 0...4294967295
99 | I22 | FRQV1 | f< trips | UINT32 | R | 0...4294967295
99 | I23 | FRQV1 | f< blocks | UINT32 | R | 0...4294967295
99 | I24 | FRQV1 | f<< starts | UINT32 | R | 0...4294967295
99 | I25 | FRQV1 | f<< trips | UINT32 | R | 0...4294967295
99 | I26 | FRQV1 | f<< blocks | UINT32 | R | 0...4294967295
99 | I27 | FRQV1 | f<<< starts | UINT32 | R | 0...4294967295
99 | I28 | FRQV1 | f<<< trips | UINT32 | R | 0...4294967295
99 | I29 | FRQV1 | f<<< blocks | UINT32 | R | 0...4294967295
99 | I30 | FRQV1 | f<<<< starts | UINT32 | R | 0...4294967295
99 | I31 | FRQV1 | f<<<< trips | UINT32 | R | 0...4294967295
99 | I32 | FRQV1 | f<<<< blocks | UINT32 | R | 0...4294967295
99 | S9 | FRQV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
99 | S10 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S11 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S12 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S13 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S14 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S15 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S16 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S17 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S18 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S19 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S20 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S21 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S22 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S23 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S24 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S25 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S26 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S27 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S28 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S29 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S30 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S31 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S32 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S33 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S34 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S35 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S36 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S37 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S38 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S39 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S40 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S41 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S42 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S43 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S44 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S45 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S46 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S47 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S48 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S49 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S50 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S51 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S52 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S53 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S54 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S55 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S56 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S57 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S58 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S59 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S60 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S61 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S62 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S63 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S64 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S65 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S66 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S67 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S68 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S69 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S70 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S71 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S72 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S73 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S74 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S75 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S76 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S77 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S78 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S79 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S80 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S81 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S82 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S83 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S84 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S85 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S86 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S87 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S88 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S89 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S90 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S91 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S92 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S93 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S94 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S95 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S96 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S97 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S98 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S99 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S100 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S101 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S102 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S103 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S104 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S105 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S106 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S107 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S108 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S109 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S110 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S111 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S112 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S113 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S114 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S115 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S116 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S117 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S118 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S119 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S120 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S121 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S122 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S123 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S124 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S125 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S126 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S127 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S128 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S129 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S130 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S131 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S132 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S133 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S134 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S135 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S136 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S137 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S138 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S139 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S140 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S141 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S142 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S143 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S144 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S145 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S146 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S147 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S148 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S149 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S150 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S151 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S152 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S153 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S154 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S155 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S156 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S157 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S158 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S159 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S160 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S161 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S162 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S163 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S164 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S165 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S166 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S167 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S168 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S169 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S170 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S171 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S172 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S173 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S174 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S175 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S176 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S177 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S178 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S179 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S180 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S181 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S182 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S183 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S184 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S185 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S186 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S187 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S188 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S189 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S190 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S191 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S192 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S193 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S194 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S195 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S196 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S197 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S198 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S199 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S200 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S201 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | O1 | FRQV1 | f> START | SIGNAL_OUT | RW | 0...4294967295
99 | O2 | FRQV1 | f> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O3 | FRQV1 | f> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O4 | FRQV1 | f>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O5 | FRQV1 | f>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O6 | FRQV1 | f>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O7 | FRQV1 | f>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O8 | FRQV1 | f>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O9 | FRQV1 | f>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O10 | FRQV1 | f>>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O11 | FRQV1 | f>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O12 | FRQV1 | f>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O13 | FRQV1 | f< START | SIGNAL_OUT | RW | 0...4294967295
99 | O14 | FRQV1 | f< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O15 | FRQV1 | f< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O16 | FRQV1 | f<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O17 | FRQV1 | f<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O18 | FRQV1 | f<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O19 | FRQV1 | f<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O20 | FRQV1 | f<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O21 | FRQV1 | f<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O22 | FRQV1 | f<<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O23 | FRQV1 | f<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O24 | FRQV1 | f<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | I33 | FRQV1 | Newest Register | UINT32 | R | 0...12
99 | I34 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I35 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I36 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I37 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I38 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I39 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I40 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I41 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I42 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I43 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I44 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I45 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | S202 | FRQV1 | EventMaskLo | UINT32 | RW | 0...4294967295
103 | S1 | DFT1 | df/dt >/< [81] mode | UINT32 | RW | 0=Disabled;1=Activated
103 | S2 | DFT1 | Max allowed df/dt rate | FLOAT | RW | 0.1...50
103 | I1 | DFT1 | Measured df/dt | FLOAT | R | 0...20
103 | S3 | DFT1 | df/dt >/< (1) Enable | UINT32 | RW | 0=No;1=Yes
103 | V1 | DFT1 | df/dt >/< (1) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I2 | DFT1 | df/dt >/< (1) fmeas / fset | FLOAT | R | 0...20
103 | S4 | DFT1 | df/dt >/< (2) Enable | UINT32 | RW | 0=No;1=Yes
103 | V2 | DFT1 | df/dt >/< (2) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I3 | DFT1 | df/dt >/< (2) fmeas / fset | FLOAT | R | 0...20
103 | S5 | DFT1 | df/dt >/< (3) Enable | UINT32 | RW | 0=No;1=Yes
103 | V3 | DFT1 | df/dt >/< (3) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I4 | DFT1 | df/dt >/< (3) fmeas / fset | FLOAT | R | 0...20
103 | S6 | DFT1 | df/dt >/< (4) Enable | UINT32 | RW | 0=No;1=Yes
103 | V4 | DFT1 | df/dt >/< (4) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I5 | DFT1 | df/dt >/< (4) fmeas / fset | FLOAT | R | 0...20
103 | S7 | DFT1 | df/dt >/< (5) Enable | UINT32 | RW | 0=No;1=Yes
103 | V5 | DFT1 | df/dt >/< (5) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I6 | DFT1 | df/dt >/< (5) fmeas / fset | FLOAT | R | 0...20
103 | S8 | DFT1 | df/dt >/< (6) Enable | UINT32 | RW | 0=No;1=Yes
103 | V6 | DFT1 | df/dt >/< (6) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I7 | DFT1 | df/dt >/< (6) fmeas / fset | FLOAT | R | 0...20
103 | S9 | DFT1 | df/dt >/< (7) Enable | UINT32 | RW | 0=No;1=Yes
103 | V7 | DFT1 | df/dt >/< (7) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I8 | DFT1 | df/dt >/< (7) fmeas / fset | FLOAT | R | 0...20
103 | S10 | DFT1 | df/dt >/< (8) Enable | UINT32 | RW | 0=No;1=Yes
103 | V8 | DFT1 | df/dt >/< (8) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I9 | DFT1 | df/dt >/< (8) fmeas / fset | FLOAT | R | 0...20
103 | I10 | DFT1 | df/dt >/< (1) starts | UINT32 | R | 0...4294967295
103 | I11 | DFT1 | df/dt >/< (1) trips | UINT32 | R | 0...4294967295
103 | I12 | DFT1 | df/dt >/< (1) blocks | UINT32 | R | 0...4294967295
103 | I13 | DFT1 | df/dt >/< (2) starts | UINT32 | R | 0...4294967295
103 | I14 | DFT1 | df/dt >/< (2) trips | UINT32 | R | 0...4294967295
103 | I15 | DFT1 | df/dt >/< (2) blocks | UINT32 | R | 0...4294967295
103 | I16 | DFT1 | df/dt >/< (3) starts | UINT32 | R | 0...4294967295
103 | I17 | DFT1 | df/dt >/< (3) trips | UINT32 | R | 0...4294967295
103 | I18 | DFT1 | df/dt >/< (3) blocks | UINT32 | R | 0...4294967295
103 | I19 | DFT1 | df/dt >/< (4) starts | UINT32 | R | 0...4294967295
103 | I20 | DFT1 | df/dt >/< (4) trips | UINT32 | R | 0...4294967295
103 | I21 | DFT1 | df/dt >/< (4) blocks | UINT32 | R | 0...4294967295
103 | I22 | DFT1 | df/dt >/< (5) starts | UINT32 | R | 0...4294967295
103 | I23 | DFT1 | df/dt >/< (5) trips | UINT32 | R | 0...4294967295
103 | I24 | DFT1 | df/dt >/< (5) blocks | UINT32 | R | 0...4294967295
103 | I25 | DFT1 | df/dt >/< (6) starts | UINT32 | R | 0...4294967295
103 | I26 | DFT1 | df/dt >/< (6) trips | UINT32 | R | 0...4294967295
103 | I27 | DFT1 | df/dt >/< (6) blocks | UINT32 | R | 0...4294967295
103 | I28 | DFT1 | df/dt >/< (7) starts | UINT32 | R | 0...4294967295
103 | I29 | DFT1 | df/dt >/< (7) trips | UINT32 | R | 0...4294967295
103 | I30 | DFT1 | df/dt >/< (7) blocks | UINT32 | R | 0...4294967295
103 | I31 | DFT1 | df/dt >/< (8) starts | UINT32 | R | 0...4294967295
103 | I32 | DFT1 | df/dt >/< (8) trips | UINT32 | R | 0...4294967295
103 | I33 | DFT1 | df/dt >/< (8) blocks | UINT32 | R | 0...4294967295
103 | S11 | DFT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
103 | S12 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S13 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S14 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S15 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S16 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S17 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S18 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S19 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S20 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S21 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S22 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S23 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S24 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S25 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S26 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S27 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S28 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S29 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S30 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S31 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S32 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S33 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S34 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S35 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S36 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S37 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S38 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S39 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S40 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S41 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S42 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S43 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S44 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S45 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S46 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S47 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S48 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S49 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S50 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S51 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S52 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S53 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S54 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S55 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S56 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S57 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S58 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S59 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S60 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S61 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S62 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S63 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S64 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S65 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S66 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S67 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S68 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S69 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S70 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S71 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S72 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S73 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S74 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S75 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S76 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S77 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S78 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S79 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S80 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S81 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S82 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S83 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S84 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S85 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S86 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S87 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S88 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S89 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S90 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S91 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S92 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S93 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S94 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S95 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S96 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S97 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S98 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S99 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S100 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S101 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S102 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S103 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S104 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S105 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S106 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S107 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S108 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S109 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S110 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S111 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S112 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S113 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S114 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S115 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S116 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S117 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S118 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S119 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S120 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S121 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S122 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S123 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S124 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S125 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S126 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S127 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S128 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S129 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S130 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S131 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S132 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S133 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S134 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S135 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S136 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S137 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S138 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S139 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S140 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S141 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S142 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S143 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S144 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S145 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S146 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S147 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S148 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S149 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S150 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S151 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S152 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S153 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S154 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S155 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S156 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S157 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S158 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S159 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S160 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S161 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S162 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S163 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S164 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S165 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S166 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S167 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S168 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S169 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S170 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S171 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S172 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S173 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S174 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S175 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S176 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S177 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S178 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S179 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S180 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S181 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S182 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S183 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S184 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S185 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S186 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S187 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S188 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S189 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S190 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S191 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S192 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S193 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S194 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S195 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S196 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S197 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S198 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S199 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S200 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S201 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S202 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S203 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S204 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S205 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S206 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S207 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S208 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S209 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S210 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S211 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S212 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S213 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S214 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S215 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S216 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S217 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S218 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S219 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S220 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S221 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S222 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S223 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S224 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S225 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S226 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S227 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S228 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S229 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S230 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S231 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S232 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S233 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S234 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S235 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S236 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S237 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S238 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S239 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S240 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S241 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S242 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S243 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S244 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S245 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S246 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S247 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S248 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S249 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S250 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S251 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S252 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S253 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S254 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S255 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S256 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S257 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S258 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S259 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S260 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S261 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S262 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S263 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S264 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S265 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S266 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S267 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S268 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S269 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S270 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S271 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S272 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S273 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S274 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S275 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S276 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S277 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S278 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S279 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S280 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S281 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S282 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S283 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S284 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S285 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S286 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S287 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S288 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S289 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S290 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S291 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S292 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S293 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S294 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S295 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S296 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S297 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S298 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S299 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S300 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S301 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S302 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S303 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S304 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S305 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S306 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S307 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S308 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S309 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S310 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S311 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S312 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S313 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S314 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S315 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S316 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S317 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S318 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S319 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S320 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S321 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S322 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S323 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S324 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S325 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S326 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S327 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S328 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S329 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S330 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S331 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S332 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S333 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S334 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S335 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S336 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S337 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S338 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S339 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S340 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S341 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S342 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S343 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S344 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S345 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S346 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S347 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S348 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S349 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S350 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S351 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S352 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S353 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S354 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S355 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S356 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S357 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S358 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S359 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S360 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S361 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S362 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S363 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S364 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S365 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S366 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S367 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S368 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S369 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S370 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S371 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S372 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S373 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S374 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S375 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S376 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S377 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S378 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S379 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S380 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S381 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S382 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S383 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S384 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S385 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S386 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S387 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S388 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S389 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S390 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S391 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S392 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S393 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S394 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S395 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S396 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S397 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S398 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S399 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S400 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S401 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S402 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S403 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S404 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S405 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S406 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S407 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S408 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S409 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S410 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S411 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S412 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S413 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S414 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S415 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S416 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S417 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S418 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S419 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S420 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S421 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S422 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S423 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S424 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S425 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S426 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S427 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S428 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S429 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S430 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S431 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S432 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S433 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S434 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S435 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S436 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S437 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S438 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S439 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S440 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S441 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S442 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S443 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S444 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S445 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S446 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S447 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S448 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S449 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S450 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S451 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S452 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S453 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S454 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S455 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S456 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S457 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S458 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S459 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | O1 | DFT1 | df/dt >/< (1) START | SIGNAL_OUT | RW | 0...4294967295
103 | O2 | DFT1 | df/dt >/< (1) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O3 | DFT1 | df/dt >/< (1) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O4 | DFT1 | df/dt >/< (2) START | SIGNAL_OUT | RW | 0...4294967295
103 | O5 | DFT1 | df/dt >/< (2) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O6 | DFT1 | df/dt >/< (2) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O7 | DFT1 | df/dt >/< (3) START | SIGNAL_OUT | RW | 0...4294967295
103 | O8 | DFT1 | df/dt >/< (3) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O9 | DFT1 | df/dt >/< (3) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O10 | DFT1 | df/dt >/< (4) START | SIGNAL_OUT | RW | 0...4294967295
103 | O11 | DFT1 | df/dt >/< (4) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O12 | DFT1 | df/dt >/< (4) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O13 | DFT1 | df/dt >/< (5) START | SIGNAL_OUT | RW | 0...4294967295
103 | O14 | DFT1 | df/dt >/< (5) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O15 | DFT1 | df/dt >/< (5) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O16 | DFT1 | df/dt >/< (6) START | SIGNAL_OUT | RW | 0...4294967295
103 | O17 | DFT1 | df/dt >/< (6) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O18 | DFT1 | df/dt >/< (6) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O19 | DFT1 | df/dt >/< (7) START | SIGNAL_OUT | RW | 0...4294967295
103 | O20 | DFT1 | df/dt >/< (7) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O21 | DFT1 | df/dt >/< (7) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O22 | DFT1 | df/dt >/< (8) START | SIGNAL_OUT | RW | 0...4294967295
103 | O23 | DFT1 | df/dt >/< (8) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O24 | DFT1 | df/dt >/< (8) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | I34 | DFT1 | Newest Register | UINT32 | R | 0...12
103 | I35 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I36 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I37 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I38 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I39 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I40 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I41 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I42 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I43 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I44 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I45 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I46 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I47 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I48 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I49 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I50 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I51 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I52 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I53 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I54 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I55 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I56 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I57 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I58 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | S460 | DFT1 | EventMaskLo | UINT32 | RW | 0...4294967295
183 | V1 | RHC1 | Counter is now | UINT32 | R | 0=Idle;1=Counting
183 | I1 | RHC1 | Running hours | UINT32 | RW | 0...4294967295
183 | I2 | RHC1 | Start count | UINT32 | RW | 0...4294967295
183 | I3 | RHC1 | Clear Hours | UINT32 | W | 0=-;1=Clear
183 | S1 | RHC1 | EventMaskLo | UINT32 | RW | 0...4294967295
113 | V1 | GST1 | Generator is now | UINT32 | R | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
113 | I1 | GST1 | Times Overloaded | UINT32 | R | 0...4294967295
113 | I2 | GST1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
113 | I3 | GST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
113 | I4 | GST1 | Generating time | UINT32 | R | 0...4294967295
113 | I5 | GST1 | Overloading cumulative | UINT32 | R | 0...4294967295
113 | I6 | GST1 | Last overload duration | UINT32 | R | 0...4294967295
113 | I7 | GST1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
113 | I8 | GST1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
113 | S1 | GST1 | Clear total times | UINT32 | W | 0=-;1=Clear
113 | S2 | GST1 | Generator nominal MVA (S) | FLOAT | RW | 0.1...500
113 | S3 | GST1 | Generator nominal Voltage (Vt) | FLOAT | RW | 0.1...25
113 | S4 | GST1 | Prime mover max power output (Pmax) | FLOAT | RW | 0.1...500
113 | S5 | GST1 | Block trafo in protection area | UINT32 | RW | 0=No;1=Yes
113 | S6 | GST1 | Generator voltage measurement | UINT32 | RW | 0=LV side VT (no corrections);1=HV side VT(Reduce to LV);2=HV side VT(HV measurements)
113 | S7 | GST1 | Ratio for generator nominal voltage scaling (1 p.u.) | UINT32 | RW | 0=Generator nominal voltage;1=Transformer LV nominal voltage;2=Set Un ratio by hand
113 | I9 | GST1 | Transformer ratio HV -> LV Trafo. | FLOAT | R | 0.01...100
113 | I10 | GST1 | Transformer ratio HV -> LV Gen. | FLOAT | R | 0.01...100
113 | I11 | GST1 | Voltage ratio | FLOAT | RW | 0.001...100
113 | I12 | GST1 | Voltage scaling | FLOAT | R | 0.01...100
113 | S8 | GST1 | Transformer nominal MVA | FLOAT | RW | 0.001...500
113 | S9 | GST1 | HV side nominal voltage | FLOAT | RW | 0.001...500
113 | S10 | GST1 | LV side nominal voltage | FLOAT | RW | 0.001...500
113 | S11 | GST1 | Transformer Zk % | FLOAT | RW | 0.001...25
113 | S12 | GST1 | Transformer nom freq. | FLOAT | RW | 10...75
113 | S13 | GST1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
113 | I13 | GST1 | HV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I14 | GST1 | HV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I15 | GST1 | HV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I16 | GST1 | LV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I17 | GST1 | LV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I18 | GST1 | LV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I19 | GST1 | Transformer nom impedance | FLOAT | R | 0.01...250
113 | I20 | GST1 | Transformer nom Zk ohm | FLOAT | R | 0.01...250
113 | I21 | GST1 | Transformer nom SC inductance | FLOAT | R | 0.001...100
113 | I22 | GST1 | LV side max 3ph SC curr | FLOAT | R | 0.001...500
113 | I23 | GST1 | LV side 3ph SC to HV side | FLOAT | R | 0.001...500
113 | I24 | GST1 | LV side max 2ph SC curr | FLOAT | R | 0.001...500
113 | I25 | GST1 | LV side 2ph SC to HV side | FLOAT | R | 0.001...500
113 | I26 | GST1 | Trafo HV nominal current | FLOAT | R | 0.01...50000
113 | I27 | GST1 | Trafo LV nominal current | FLOAT | R | 0.01...50000
113 | O1 | GST1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
113 | O2 | GST1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O3 | GST1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O4 | GST1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
113 | O5 | GST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | O6 | GST1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | I28 | GST1 | Newest Register | UINT32 | R | 0...12
113 | I29 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I30 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I31 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I32 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I33 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I34 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I35 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I36 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I37 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I38 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I39 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I40 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I41 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I42 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I43 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I44 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I45 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I46 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I47 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I48 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I49 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I50 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I51 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I52 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I53 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I54 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I55 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I56 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I57 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I58 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I59 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I60 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I61 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I62 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I63 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I64 | GST1 | L3 Current | FLOAT | R | 0...250
113 | S14 | GST1 | EventMaskLo | UINT32 | RW | 0...4294967295
164 | S1 | PWR1 | PQS>/< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
164 | V1 | PWR1 | PQS>/< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
164 | I1 | PWR1 | Meas/Set at the moment | FLOAT | R | -1250...1250
164 | I2 | PWR1 | Meas/Nom at the moment | FLOAT | R | -1250...1250
164 | I3 | PWR1 | PQS>/< starts | UINT32 | R | 0...4294967295
164 | I4 | PWR1 | PQS>/< trips | UINT32 | R | 0...4294967295
164 | I5 | PWR1 | PQS>/< blocks | UINT32 | R | 0...4294967295
164 | S2 | PWR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
164 | S3 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S4 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S5 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S6 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S7 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S8 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S9 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S10 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S11 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S12 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S13 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S14 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S15 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S16 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S17 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S18 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | O1 | PWR1 | PQS>/< START | SIGNAL_OUT | RW | 0...4294967295
164 | O2 | PWR1 | PQS>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
164 | O3 | PWR1 | PQS>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
164 | I6 | PWR1 | Newest Register | UINT32 | R | 0...12
164 | I7 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I8 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I9 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I10 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I11 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I12 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I13 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I14 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I15 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I16 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I17 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I18 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | S19 | PWR1 | EventMaskLo | UINT32 | RW | 0...4294967295
165 | S1 | PWR2 | PQS>>/<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
165 | V1 | PWR2 | PQS>>/<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
165 | I1 | PWR2 | Meas/Set at the moment | FLOAT | R | -1250...1250
165 | I2 | PWR2 | Meas/Nom at the moment | FLOAT | R | -1250...1250
165 | I3 | PWR2 | PQS>>/<< starts | UINT32 | R | 0...4294967295
165 | I4 | PWR2 | PQS>>/<< trips | UINT32 | R | 0...4294967295
165 | I5 | PWR2 | PQS>>/<< blocks | UINT32 | R | 0...4294967295
165 | S2 | PWR2 | Clear statistics | UINT32 | W | 0=-;1=Clear
165 | S3 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S4 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S5 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S6 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S7 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S8 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S9 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S10 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S11 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S12 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S13 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S14 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S15 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S16 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S17 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S18 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | O1 | PWR2 | PQS>>/<< START | SIGNAL_OUT | RW | 0...4294967295
165 | O2 | PWR2 | PQS>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
165 | O3 | PWR2 | PQS>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
165 | I6 | PWR2 | Newest Register | UINT32 | R | 0...12
165 | I7 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I8 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I9 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I10 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I11 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I12 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I13 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I14 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I15 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I16 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I17 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I18 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | S19 | PWR2 | EventMaskLo | UINT32 | RW | 0...4294967295
166 | S1 | PWR3 | PQS>>>/<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
166 | V1 | PWR3 | PQS>>>/<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
166 | I1 | PWR3 | Meas/Set at the moment | FLOAT | R | -1250...1250
166 | I2 | PWR3 | Meas/Nom at the moment | FLOAT | R | -1250...1250
166 | I3 | PWR3 | PQS>>>/<<< starts | UINT32 | R | 0...4294967295
166 | I4 | PWR3 | PQS>>>/<<< trips | UINT32 | R | 0...4294967295
166 | I5 | PWR3 | PQS>>>/<<< blocks | UINT32 | R | 0...4294967295
166 | S2 | PWR3 | Clear statistics | UINT32 | W | 0=-;1=Clear
166 | S3 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S4 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S5 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S6 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S7 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S8 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S9 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S10 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S11 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S12 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S13 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S14 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S15 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S16 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S17 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S18 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | O1 | PWR3 | PQS>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
166 | O2 | PWR3 | PQS>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
166 | O3 | PWR3 | PQS>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
166 | I6 | PWR3 | Newest Register | UINT32 | R | 0...12
166 | I7 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I8 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I9 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I10 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I11 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I12 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I13 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I14 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I15 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I16 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I17 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I18 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | S19 | PWR3 | EventMaskLo | UINT32 | RW | 0...4294967295
167 | S1 | PWR4 | PQS>>>>/<<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
167 | V1 | PWR4 | PQS>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
167 | I1 | PWR4 | Meas/Set at the moment | FLOAT | R | -1250...1250
167 | I2 | PWR4 | Meas/Nom at the moment | FLOAT | R | -1250...1250
167 | I3 | PWR4 | PQS>>>>/<<<< starts | UINT32 | R | 0...4294967295
167 | I4 | PWR4 | PQS>>>>/<<<< trips | UINT32 | R | 0...4294967295
167 | I5 | PWR4 | PQS>>>>/<<<< blocks | UINT32 | R | 0...4294967295
167 | S2 | PWR4 | Clear statistics | UINT32 | W | 0=-;1=Clear
167 | S3 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S4 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S5 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S6 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S7 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S8 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S9 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S10 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S11 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S12 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S13 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S14 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S15 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S16 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S17 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S18 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | O1 | PWR4 | PQS>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
167 | O2 | PWR4 | PQS>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
167 | O3 | PWR4 | PQS>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
167 | I6 | PWR4 | Newest Register | UINT32 | R | 0...12
167 | I7 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I8 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I9 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I10 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I11 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I12 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I13 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I14 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I15 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I16 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I17 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I18 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | S19 | PWR4 | EventMaskLo | UINT32 | RW | 0...4294967295
100 | S1 | OPW1 | P> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
100 | V1 | OPW1 | P> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
100 | I1 | OPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
100 | I2 | OPW1 | P> starts | UINT32 | R | 0...4294967295
100 | I3 | OPW1 | P> trips | UINT32 | R | 0...4294967295
100 | I4 | OPW1 | P> blocks | UINT32 | R | 0...4294967295
100 | S2 | OPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
100 | S3 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S4 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S5 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S6 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S7 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S8 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S9 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S10 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S11 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S12 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S13 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S14 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S15 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S16 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S17 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S18 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | O1 | OPW1 | P> START | SIGNAL_OUT | RW | 0...4294967295
100 | O2 | OPW1 | P> TRIP | SIGNAL_OUT | RW | 0...4294967295
100 | O3 | OPW1 | P> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
100 | I5 | OPW1 | Newest Register | UINT32 | R | 0...12
100 | I6 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I7 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I8 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I9 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I10 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I11 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I12 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I13 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I14 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I15 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I16 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I17 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | S19 | OPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
101 | S1 | UPW1 | P< [37] mode | UINT32 | RW | 0=Disabled;1=Activated
101 | V1 | UPW1 | P< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
101 | I1 | UPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
101 | I2 | UPW1 | P< starts | UINT32 | R | 0...4294967295
101 | I3 | UPW1 | P< trips | UINT32 | R | 0...4294967295
101 | I4 | UPW1 | P< blocks | UINT32 | R | 0...4294967295
101 | S2 | UPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
101 | S3 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S4 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S5 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S6 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S7 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S8 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S9 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S10 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S11 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S12 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S13 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S14 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S15 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S16 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S17 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S18 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S19 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S20 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S21 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S22 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S23 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S24 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S25 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S26 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | O1 | UPW1 | P< START | SIGNAL_OUT | RW | 0...4294967295
101 | O2 | UPW1 | P< TRIP | SIGNAL_OUT | RW | 0...4294967295
101 | O3 | UPW1 | P< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
101 | I5 | UPW1 | Newest Register | UINT32 | R | 0...12
101 | I6 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I7 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I8 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I9 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I10 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I11 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I12 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I13 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I14 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I15 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I16 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I17 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | S27 | UPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
102 | S1 | RPW1 | Prev> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
102 | V1 | RPW1 | Prev> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
102 | I1 | RPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
102 | I2 | RPW1 | Prev> starts | UINT32 | R | 0...4294967295
102 | I3 | RPW1 | Prev> trips | UINT32 | R | 0...4294967295
102 | I4 | RPW1 | Prev> blocks | UINT32 | R | 0...4294967295
102 | S2 | RPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
102 | S3 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S4 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S5 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S6 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S7 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S8 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S9 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S10 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S11 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S12 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S13 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S14 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S15 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S16 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S17 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S18 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | O1 | RPW1 | Prev> START | SIGNAL_OUT | RW | 0...4294967295
102 | O2 | RPW1 | Prev> TRIP | SIGNAL_OUT | RW | 0...4294967295
102 | O3 | RPW1 | Prev> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
102 | I5 | RPW1 | Newest Register | UINT32 | R | 0...12
102 | I6 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I7 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I8 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I9 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I10 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I11 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I12 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I13 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I14 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I15 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I16 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I17 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | S19 | RPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
110 | S1 | SEF1 | U03rd< [64S] mode | UINT32 | RW | 0=Disabled; 1=Activated
110 | V1 | SEF1 | U03rd< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
110 | I1 | SEF1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
110 | I2 | SEF1 | Measured U0 3rd harm (%) | FLOAT | R | 0...1250
110 | I3 | SEF1 | Measured U0 3rd harm (Pri) | FLOAT | R | 0...1250
110 | I4 | SEF1 | U03rd< starts | UINT32 | R | 0...4294967295
110 | I5 | SEF1 | U03rd< trips | UINT32 | R | 0...4294967295
110 | I6 | SEF1 | U03rd< blocks | UINT32 | R | 0...4294967295
110 | S2 | SEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
110 | S3 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S4 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S5 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S6 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S7 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S8 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S9 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S10 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S11 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S12 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S13 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S14 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S15 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S16 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S17 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S18 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S19 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S20 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S21 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S22 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S23 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S24 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S25 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S26 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | O1 | SEF1 | U03rd< START | SIGNAL_OUT | RW | 0...4294967295
110 | O2 | SEF1 | U03rd< TRIP | SIGNAL_OUT | RW | 0...4294967295
110 | O3 | SEF1 | U03rd< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
110 | I7 | SEF1 | Newest Register | UINT32 | R | 0...12
110 | I8 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I9 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I10 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I11 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I12 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I13 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I14 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I15 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I16 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I17 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I18 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I19 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I20 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I21 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I22 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I23 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I24 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I25 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I26 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I27 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I28 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I29 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I30 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I31 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | S27 | SEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
109 | S1 | UEX1 | Q< [40] mode | UINT32 | RW | 0=Disabled; 1=Activated
109 | V1 | UEX1 | Q< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
109 | I1 | UEX1 | Qmeas/Qset at the moment | FLOAT | R | -1250...1250
109 | I2 | UEX1 | Q< starts | UINT32 | R | 0...4294967295
109 | I3 | UEX1 | Q< trips | UINT32 | R | 0...4294967295
109 | I4 | UEX1 | Q< blocks | UINT32 | R | 0...4294967295
109 | S2 | UEX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
109 | S3 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S4 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S5 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S6 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S7 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S8 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S9 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S10 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S11 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S12 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S13 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S14 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S15 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S16 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S17 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S18 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S19 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S20 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S21 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S22 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S23 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S24 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S25 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S26 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S27 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S28 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S29 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S30 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S31 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S32 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S33 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S34 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S35 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S36 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S37 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S38 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S39 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S40 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S41 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S42 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S43 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S44 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S45 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S46 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S47 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S48 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S49 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S50 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | O1 | UEX1 | Q< START | SIGNAL_OUT | RW | 0...4294967295
109 | O2 | UEX1 | Q< TRIP | SIGNAL_OUT | RW | 0...4294967295
109 | O3 | UEX1 | Q< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
109 | I5 | UEX1 | Newest Register | UINT32 | R | 0...12
109 | I6 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I7 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I8 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I9 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I10 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I11 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I12 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I13 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I14 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I15 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I16 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I17 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I18 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I19 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I20 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I21 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I22 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I23 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I24 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I25 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I26 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I27 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I28 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I29 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | S51 | UEX1 | EventMaskLo | UINT32 | RW | 0...4294967295
111 | S1 | UIM1 | Z< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
111 | V1 | UIM1 | Z< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
111 | I1 | UIM1 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
111 | I2 | UIM1 | Z< starts | UINT32 | R | 0...4294967295
111 | I3 | UIM1 | Z< trips | UINT32 | R | 0...4294967295
111 | I4 | UIM1 | Z< blocks | UINT32 | R | 0...4294967295
111 | S2 | UIM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
111 | S3 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S4 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S5 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S6 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S7 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S8 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S9 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S10 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S11 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S12 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S13 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S14 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S15 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S16 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S17 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S18 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | O1 | UIM1 | Z< START | SIGNAL_OUT | RW | 0...4294967295
111 | O2 | UIM1 | Z< TRIP | SIGNAL_OUT | RW | 0...4294967295
111 | O3 | UIM1 | Z< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
111 | I5 | UIM1 | Newest Register | UINT32 | R | 0...12
111 | I6 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I7 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I8 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I9 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I10 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I11 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I12 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I13 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I14 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I15 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I16 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I17 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I18 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I19 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I20 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I21 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I22 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I23 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I24 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I25 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I26 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I27 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I28 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I29 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I30 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I31 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I32 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I33 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I34 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I35 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I36 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I37 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I38 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I39 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I40 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I41 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | S19 | UIM1 | EventMaskLo | UINT32 | RW | 0...4294967295
149 | S1 | UIM2 | Z<< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
149 | V1 | UIM2 | Z<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
149 | I1 | UIM2 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
149 | I2 | UIM2 | Z<< starts | UINT32 | R | 0...4294967295
149 | I3 | UIM2 | Z<< trips | UINT32 | R | 0...4294967295
149 | I4 | UIM2 | Z<< blocks | UINT32 | R | 0...4294967295
149 | S2 | UIM2 | Clear statistics | UINT32 | W | 0=-;1=Clear
149 | S3 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S4 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S5 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S6 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S7 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S8 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S9 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S10 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S11 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S12 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S13 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S14 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S15 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S16 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S17 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S18 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | O1 | UIM2 | Z<< START | SIGNAL_OUT | RW | 0...4294967295
149 | O2 | UIM2 | Z<< TRIP | SIGNAL_OUT | RW | 0...4294967295
149 | O3 | UIM2 | Z<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
149 | I5 | UIM2 | Newest Register | UINT32 | R | 0...12
149 | I6 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I7 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I8 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I9 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I10 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I11 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I12 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I13 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I14 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I15 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I16 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I17 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I18 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I19 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I20 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I21 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I22 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I23 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I24 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I25 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I26 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I27 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I28 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I29 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I30 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I31 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I32 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I33 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I34 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I35 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I36 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I37 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I38 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I39 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I40 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I41 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | S19 | UIM2 | EventMaskLo | UINT32 | RW | 0...4294967295
112 | S1 | VOC1 | Iv> [51V] mode | UINT32 | RW | 0=Disabled; 1=Activated
112 | V1 | VOC1 | Iv> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
112 | I1 | VOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
112 | I2 | VOC1 | Iv> starts | UINT32 | R | 0...4294967295
112 | I3 | VOC1 | Iv> trips | UINT32 | R | 0...4294967295
112 | I4 | VOC1 | Iv> blocks | UINT32 | R | 0...4294967295
112 | S2 | VOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
112 | S3 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S4 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S5 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S6 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S7 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S8 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S9 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S10 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S11 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S12 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S13 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S14 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S15 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S16 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S17 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S18 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S19 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S20 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S21 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S22 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S23 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S24 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S25 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S26 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S27 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S28 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S29 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S30 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S31 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S32 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S33 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S34 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S35 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S36 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S37 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S38 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S39 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S40 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S41 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S42 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | O1 | VOC1 | Iv> START | SIGNAL_OUT | RW | 0...4294967295
112 | O2 | VOC1 | Iv> TRIP | SIGNAL_OUT | RW | 0...4294967295
112 | O3 | VOC1 | Iv> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
112 | I5 | VOC1 | Newest Register | UINT32 | R | 0...12
112 | I6 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I7 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I8 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I9 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I10 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I11 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I12 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I13 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I14 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I15 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I16 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I17 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I18 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I19 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I20 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I21 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I22 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I23 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I24 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I25 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I26 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I27 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I28 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I29 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I30 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I31 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I32 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I33 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I34 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I35 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I36 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I37 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I38 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I39 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I40 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I41 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I42 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I43 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I44 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I45 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I46 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I47 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I48 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I49 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I50 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I51 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I52 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I53 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I54 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I55 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I56 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I57 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I58 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I59 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I60 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I61 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I62 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I63 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I64 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I65 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | S43 | VOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
128 | S1 | VHZ1 | V/Hz > [24] mode | UINT32 | RW | 0=Disabled;1=Activated
128 | S2 | VHZ1 | V/Hz(1) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V1 | VHZ1 | V/Hz(1) > condition | UINT32 | R | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
128 | I1 | VHZ1 | V/Hz(1) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | S3 | VHZ1 | V/Hz(2) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V2 | VHZ1 | V/Hz(2) > condition | UINT32 | R | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
128 | I2 | VHZ1 | V/Hz(2) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | I3 | VHZ1 | U/f at the moment | FLOAT | R | -100...100
128 | I4 | VHZ1 | U/f atm to nominal U/f ratio | FLOAT | R | -100...100
128 | I5 | VHZ1 | V/Hz(1) > Starts | UINT32 | R | 0...4294967295
128 | I6 | VHZ1 | V/Hz(1) > Alarms | UINT32 | R | 0...4294967295
128 | I7 | VHZ1 | V/Hz(1) > Trips | UINT32 | R | 0...4294967295
128 | I8 | VHZ1 | V/Hz(1) > Blocks | UINT32 | R | 0...4294967295
128 | I9 | VHZ1 | V/Hz(2) > Starts | UINT32 | R | 0...4294967295
128 | I10 | VHZ1 | V/Hz(2) > Alarms | UINT32 | R | 0...4294967295
128 | I11 | VHZ1 | V/Hz(2) > Trips | UINT32 | R | 0...4294967295
128 | I12 | VHZ1 | V/Hz(2) > Blocks | UINT32 | R | 0...4294967295
128 | S4 | VHZ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
128 | S5 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S6 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S7 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S8 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S9 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S10 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S11 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S12 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S13 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S14 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S15 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S16 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S17 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S18 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S19 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S20 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S21 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S22 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S23 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S24 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S25 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S26 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S27 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S28 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S29 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S30 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S31 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S32 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S33 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S34 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S35 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S36 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S37 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S38 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S39 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S40 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S41 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S42 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S43 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S44 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S45 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S46 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S47 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S48 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S49 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S50 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S51 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S52 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | O1 | VHZ1 | V/Hz(1) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O2 | VHZ1 | V/Hz(1) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O3 | VHZ1 | V/Hz(1) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O4 | VHZ1 | V/Hz(1) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | O5 | VHZ1 | V/Hz(2) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O6 | VHZ1 | V/Hz(2) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O7 | VHZ1 | V/Hz(2) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O8 | VHZ1 | V/Hz(2) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | I13 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I14 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I15 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I16 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I17 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I18 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I19 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I20 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I21 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I22 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I23 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I24 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I25 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I26 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I27 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I28 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I29 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I30 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I31 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I32 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I33 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I34 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I35 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I36 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I37 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I38 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I39 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I40 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I41 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I42 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I43 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I44 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I45 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I46 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I47 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I48 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I49 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I50 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I51 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I52 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I53 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I54 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I55 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I56 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I57 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I58 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I59 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I60 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I61 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I62 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I63 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I64 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I65 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I66 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I67 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I68 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I69 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I70 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I71 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I72 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I73 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I74 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I75 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I76 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I77 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I78 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I79 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I80 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I81 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I82 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I83 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I84 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I85 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I86 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I87 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I88 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I89 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I90 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I91 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I92 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I93 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I94 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I95 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I96 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I97 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I98 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I99 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I100 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I101 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I102 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I103 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I104 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I105 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I106 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I107 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I108 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I109 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I110 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | S53 | VHZ1 | EventMaskLo | UINT32 | RW | 0...4294967295
129 | S1 | UPF1 | PF< [55] mode | UINT32 | RW | 0=Disabled; 1=Activated
129 | V1 | UPF1 | PF< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
129 | S2 | UPF1 | Available modes | UINT32 | RW | 0=Trip;1=Trip and Alarm
129 | I1 | UPF1 | PFmeas/PFalarm at the moment | FLOAT | R | 0...1250
129 | I2 | UPF1 | PFmeas/PFtrip at the moment | FLOAT | R | 0...1250
129 | I3 | UPF1 | PF< Alarm Starts | UINT32 | R | 0...4294967295
129 | I4 | UPF1 | PF< Alarms | UINT32 | R | 0...4294967295
129 | I5 | UPF1 | PF< Starts | UINT32 | R | 0...4294967295
129 | I6 | UPF1 | PF< Trips | UINT32 | R | 0...4294967295
129 | I7 | UPF1 | PF< Blocks | UINT32 | R | 0...4294967295
129 | S3 | UPF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
129 | S4 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S5 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S6 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S7 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S8 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S9 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S10 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S11 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S12 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S13 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S14 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S15 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S16 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S17 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S18 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S19 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S20 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S21 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S22 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S23 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S24 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S25 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S26 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S27 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S28 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S29 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S30 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S31 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S32 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S33 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S34 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S35 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | O1 | UPF1 | PF< START | SIGNAL_OUT | RW | 0...4294967295
129 | O2 | UPF1 | PF< TRIP | SIGNAL_OUT | RW | 0...4294967295
129 | O3 | UPF1 | PF< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
129 | I8 | UPF1 | Newest Register | UINT32 | R | 0...12
129 | I9 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I10 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I11 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I12 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I13 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I14 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I15 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I16 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I17 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I18 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I19 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I20 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | S36 | UPF1 | EventMaskLo | UINT32 | RW | 0...4294967295
141 | I1 | RTDIN | S1 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I2 | RTDIN | S1 Resistance | FLOAT | R | 0...4000.000
141 | I3 | RTDIN | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I4 | RTDIN | S1 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I5 | RTDIN | S2 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I6 | RTDIN | S2 Resistance | FLOAT | R | 0...4000.000
141 | I7 | RTDIN | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I8 | RTDIN | S2 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I9 | RTDIN | S3 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I10 | RTDIN | S3 Resistance | FLOAT | R | 0...4000.000
141 | I11 | RTDIN | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I12 | RTDIN | S3 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I13 | RTDIN | S4 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I14 | RTDIN | S4 Resistance | FLOAT | R | 0...4000.000
141 | I15 | RTDIN | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I16 | RTDIN | S4 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I17 | RTDIN | S5 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I18 | RTDIN | S5 Resistance | FLOAT | R | 0...4000.000
141 | I19 | RTDIN | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I20 | RTDIN | S5 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I21 | RTDIN | S6 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I22 | RTDIN | S6 Resistance | FLOAT | R | 0...4000.000
141 | I23 | RTDIN | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I24 | RTDIN | S6 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I25 | RTDIN | S7 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I26 | RTDIN | S7 Resistance | FLOAT | R | 0...4000.000
141 | I27 | RTDIN | S7 Measurement mA | FLOAT | R | 0.000...20.000
141 | I28 | RTDIN | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I29 | RTDIN | S7 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I30 | RTDIN | S8 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I31 | RTDIN | S8 Resistance | FLOAT | R | 0...4000.000
141 | I32 | RTDIN | S8 Measurement mA | FLOAT | R | 0.000...20.000
141 | I33 | RTDIN | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I34 | RTDIN | S8 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I35 | RTDIN | S9 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I36 | RTDIN | S9 Resistance | FLOAT | R | 0...4000.000
141 | I37 | RTDIN | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I38 | RTDIN | S9 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I39 | RTDIN | S10 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I40 | RTDIN | S10 Resistance | FLOAT | R | 0...4000.000
141 | I41 | RTDIN | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I42 | RTDIN | S10 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I43 | RTDIN | S11 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I44 | RTDIN | S11 Resistance | FLOAT | R | 0...4000.000
141 | I45 | RTDIN | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I46 | RTDIN | S11 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I47 | RTDIN | S12 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I48 | RTDIN | S12 Resistance | FLOAT | R | 0...4000.000
141 | I49 | RTDIN | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I50 | RTDIN | S12 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I51 | RTDIN | S13 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I52 | RTDIN | S13 Resistance | FLOAT | R | 0...4000.000
141 | I53 | RTDIN | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I54 | RTDIN | S13 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I55 | RTDIN | S14 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I56 | RTDIN | S14 Resistance | FLOAT | R | 0...4000.000
141 | I57 | RTDIN | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I58 | RTDIN | S14 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I59 | RTDIN | S15 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I60 | RTDIN | S15 Resistance | FLOAT | R | 0...4000.000
141 | I61 | RTDIN | S15 Measurement mA | FLOAT | R | 0.000...20.000
141 | I62 | RTDIN | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I63 | RTDIN | S15 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I64 | RTDIN | S16 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I65 | RTDIN | S16 Resistance | FLOAT | R | 0...4000.000
141 | I66 | RTDIN | S16 Measurement mA | FLOAT | R | 0.000...20.000
141 | I67 | RTDIN | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I68 | RTDIN | S16 Filtered measurement | FLOAT | R | -200.0...2000.0
69 | S1 | RTD1 | RTD mode | UINT32 | RW | 0=Disabled;1=Activated
69 | S2 | RTD1 | S1 enable | UINT32 | RW | 0=No;1=Yes
69 | I1 | RTD1 | S1 Measurement (Protection) | FLOAT | R | -200...2000
69 | V1 | RTD1 | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S3 | RTD1 | S1 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I2 | RTD1 | S1 Alarm1 act | UINT32 | R | 0...4294967295
69 | S4 | RTD1 | S1 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S5 | RTD1 | S1 Alarm1 | FLOAT | RW | -200...2000
69 | S6 | RTD1 | S1 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I3 | RTD1 | S1 Alarm2 act | UINT32 | R | 0...4294967295
69 | S7 | RTD1 | S1 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S8 | RTD1 | S1 Alarm2 | FLOAT | RW | -200...2000
69 | I4 | RTD1 | S2 Measurement (Protection) | FLOAT | R | -200...2000
69 | V2 | RTD1 | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S9 | RTD1 | S2 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I5 | RTD1 | S2 Alarm1 act | UINT32 | R | 0...4294967295
69 | S10 | RTD1 | S2 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S11 | RTD1 | S2 Alarm1 | FLOAT | RW | -200...2000
69 | S12 | RTD1 | S2 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I6 | RTD1 | S2 Alarm2 act | UINT32 | R | 0...4294967295
69 | S13 | RTD1 | S2 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S14 | RTD1 | S2 Alarm2 | FLOAT | RW | -200...2000
69 | I7 | RTD1 | S3 Measurement (Protection) | FLOAT | R | -200...2000
69 | V3 | RTD1 | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S15 | RTD1 | S3 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I8 | RTD1 | S3 Alarm1 act | UINT32 | R | 0...4294967295
69 | S16 | RTD1 | S3 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S17 | RTD1 | S3 Alarm1 | FLOAT | RW | -200...2000
69 | S18 | RTD1 | S3 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I9 | RTD1 | S3 Alarm2 act | UINT32 | R | 0...4294967295
69 | S19 | RTD1 | S3 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S20 | RTD1 | S3 Alarm2 | FLOAT | RW | -200...2000
69 | I10 | RTD1 | S4 Measurement (Protection) | FLOAT | R | -200...2000
69 | V4 | RTD1 | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S21 | RTD1 | S4 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I11 | RTD1 | S4 Alarm1 act | UINT32 | R | 0...4294967295
69 | S22 | RTD1 | S4 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S23 | RTD1 | S4 Alarm1 | FLOAT | RW | -200...2000
69 | S24 | RTD1 | S4 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I12 | RTD1 | S4 Alarm2 act | UINT32 | R | 0...4294967295
69 | S25 | RTD1 | S4 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S26 | RTD1 | S4 Alarm2 | FLOAT | RW | -200...2000
69 | I13 | RTD1 | S5 Measurement (Protection) | FLOAT | R | -200...2000
69 | V5 | RTD1 | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S27 | RTD1 | S5 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I14 | RTD1 | S5 Alarm1 act | UINT32 | R | 0...4294967295
69 | S28 | RTD1 | S5 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S29 | RTD1 | S5 Alarm1 | FLOAT | RW | -200...2000
69 | S30 | RTD1 | S5 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I15 | RTD1 | S5 Alarm2 act | UINT32 | R | 0...4294967295
69 | S31 | RTD1 | S5 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S32 | RTD1 | S5 Alarm2 | FLOAT | RW | -200...2000
69 | I16 | RTD1 | S6 Measurement (Protection) | FLOAT | R | -200...2000
69 | V6 | RTD1 | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S33 | RTD1 | S6 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I17 | RTD1 | S6 Alarm1 act | UINT32 | R | 0...4294967295
69 | S34 | RTD1 | S6 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S35 | RTD1 | S6 Alarm1 | FLOAT | RW | -200...2000
69 | S36 | RTD1 | S6 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I18 | RTD1 | S6 Alarm2 act | UINT32 | R | 0...4294967295
69 | S37 | RTD1 | S6 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S38 | RTD1 | S6 Alarm2 | FLOAT | RW | -200...2000
69 | I19 | RTD1 | S7 Measurement (Protection) | FLOAT | R | -200...2000
69 | V7 | RTD1 | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S39 | RTD1 | S7 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I20 | RTD1 | S7 Alarm1 act | UINT32 | R | 0...4294967295
69 | S40 | RTD1 | S7 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S41 | RTD1 | S7 Alarm1 | FLOAT | RW | -200...2000
69 | S42 | RTD1 | S7 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I21 | RTD1 | S7 Alarm2 act | UINT32 | R | 0...4294967295
69 | S43 | RTD1 | S7 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S44 | RTD1 | S7 Alarm2 | FLOAT | RW | -200...2000
69 | I22 | RTD1 | S8 Measurement (Protection) | FLOAT | R | -200...2000
69 | V8 | RTD1 | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S45 | RTD1 | S8 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I23 | RTD1 | S8 Alarm1 act | UINT32 | R | 0...4294967295
69 | S46 | RTD1 | S8 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S47 | RTD1 | S8 Alarm1 | FLOAT | RW | -200...2000
69 | S48 | RTD1 | S8 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I24 | RTD1 | S8 Alarm2 act | UINT32 | R | 0...4294967295
69 | S49 | RTD1 | S8 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S50 | RTD1 | S8 Alarm2 | FLOAT | RW | -200...2000
69 | I25 | RTD1 | S9 Measurement (Protection) | FLOAT | R | -200...2000
69 | V9 | RTD1 | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S51 | RTD1 | S9 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I26 | RTD1 | S9 Alarm1 act | UINT32 | R | 0...4294967295
69 | S52 | RTD1 | S9 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S53 | RTD1 | S9 Alarm1 | FLOAT | RW | -200...2000
69 | S54 | RTD1 | S9 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I27 | RTD1 | S9 Alarm2 act | UINT32 | R | 0...4294967295
69 | S55 | RTD1 | S9 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S56 | RTD1 | S9 Alarm2 | FLOAT | RW | -200...2000
69 | I28 | RTD1 | S10 Measurement (Protection) | FLOAT | R | -200...2000
69 | V10 | RTD1 | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S57 | RTD1 | S10 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I29 | RTD1 | S10 Alarm1 act | UINT32 | R | 0...4294967295
69 | S58 | RTD1 | S10 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S59 | RTD1 | S10 Alarm1 | FLOAT | RW | -200...2000
69 | S60 | RTD1 | S10 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I30 | RTD1 | S10 Alarm2 act | UINT32 | R | 0...4294967295
69 | S61 | RTD1 | S10 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S62 | RTD1 | S10 Alarm2 | FLOAT | RW | -200...2000
69 | I31 | RTD1 | S11 Measurement (Protection) | FLOAT | R | -200...2000
69 | V11 | RTD1 | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S63 | RTD1 | S11 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I32 | RTD1 | S11 Alarm1 act | UINT32 | R | 0...4294967295
69 | S64 | RTD1 | S11 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S65 | RTD1 | S11 Alarm1 | FLOAT | RW | -200...2000
69 | S66 | RTD1 | S11 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I33 | RTD1 | S11 Alarm2 act | UINT32 | R | 0...4294967295
69 | S67 | RTD1 | S11 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S68 | RTD1 | S11 Alarm2 | FLOAT | RW | -200...2000
69 | I34 | RTD1 | S12 Measurement (Protection) | FLOAT | R | -200...2000
69 | V12 | RTD1 | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S69 | RTD1 | S12 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I35 | RTD1 | S12 Alarm1 act | UINT32 | R | 0...4294967295
69 | S70 | RTD1 | S12 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S71 | RTD1 | S12 Alarm1 | FLOAT | RW | -200...2000
69 | S72 | RTD1 | S12 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I36 | RTD1 | S12 Alarm2 act | UINT32 | R | 0...4294967295
69 | S73 | RTD1 | S12 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S74 | RTD1 | S12 Alarm2 | FLOAT | RW | -200...2000
69 | I37 | RTD1 | S13 Measurement (Protection) | FLOAT | R | -200...2000
69 | V13 | RTD1 | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S75 | RTD1 | S13 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I38 | RTD1 | S13 Alarm1 act | UINT32 | R | 0...4294967295
69 | S76 | RTD1 | S13 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S77 | RTD1 | S13 Alarm1 | FLOAT | RW | -200...2000
69 | S78 | RTD1 | S13 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I39 | RTD1 | S13 Alarm2 act | UINT32 | R | 0...4294967295
69 | S79 | RTD1 | S13 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S80 | RTD1 | S13 Alarm2 | FLOAT | RW | -200...2000
69 | I40 | RTD1 | S14 Measurement (Protection) | FLOAT | R | -200...2000
69 | V14 | RTD1 | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S81 | RTD1 | S14 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I41 | RTD1 | S14 Alarm1 act | UINT32 | R | 0...4294967295
69 | S82 | RTD1 | S14 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S83 | RTD1 | S14 Alarm1 | FLOAT | RW | -200...2000
69 | S84 | RTD1 | S14 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I42 | RTD1 | S14 Alarm2 act | UINT32 | R | 0...4294967295
69 | S85 | RTD1 | S14 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S86 | RTD1 | S14 Alarm2 | FLOAT | RW | -200...2000
69 | I43 | RTD1 | S15 Measurement (Protection) | FLOAT | R | -200...2000
69 | V15 | RTD1 | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S87 | RTD1 | S15 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I44 | RTD1 | S15 Alarm1 act | UINT32 | R | 0...4294967295
69 | S88 | RTD1 | S15 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S89 | RTD1 | S15 Alarm1 | FLOAT | RW | -200...2000
69 | S90 | RTD1 | S15 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I45 | RTD1 | S15 Alarm2 act | UINT32 | R | 0...4294967295
69 | S91 | RTD1 | S15 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S92 | RTD1 | S15 Alarm2 | FLOAT | RW | -200...2000
69 | I46 | RTD1 | S16 Measurement (Protection) | FLOAT | R | -200...2000
69 | V16 | RTD1 | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S93 | RTD1 | S16 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I47 | RTD1 | S16 Alarm1 act | UINT32 | R | 0...4294967295
69 | S94 | RTD1 | S16 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S95 | RTD1 | S16 Alarm1 | FLOAT | RW | -200...2000
69 | S96 | RTD1 | S16 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I48 | RTD1 | S16 Alarm2 act | UINT32 | R | 0...4294967295
69 | S97 | RTD1 | S16 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S98 | RTD1 | S16 Alarm2 | FLOAT | RW | -200...2000
69 | O1 | RTD1 | S1 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O2 | RTD1 | S1 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O3 | RTD1 | S1 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O4 | RTD1 | S2 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O5 | RTD1 | S2 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O6 | RTD1 | S2 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O7 | RTD1 | S3 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O8 | RTD1 | S3 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O9 | RTD1 | S3 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O10 | RTD1 | S4 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O11 | RTD1 | S4 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O12 | RTD1 | S4 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O13 | RTD1 | S5 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O14 | RTD1 | S5 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O15 | RTD1 | S5 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O16 | RTD1 | S6 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O17 | RTD1 | S6 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O18 | RTD1 | S6 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O19 | RTD1 | S7 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O20 | RTD1 | S7 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O21 | RTD1 | S7 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O22 | RTD1 | S8 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O23 | RTD1 | S8 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O24 | RTD1 | S8 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O25 | RTD1 | S9 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O26 | RTD1 | S9 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O27 | RTD1 | S9 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O28 | RTD1 | S10 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O29 | RTD1 | S10 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O30 | RTD1 | S10 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O31 | RTD1 | S11 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O32 | RTD1 | S11 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O33 | RTD1 | S11 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O34 | RTD1 | S12 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O35 | RTD1 | S12 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O36 | RTD1 | S12 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O37 | RTD1 | S13 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O38 | RTD1 | S13 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O39 | RTD1 | S13 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O40 | RTD1 | S14 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O41 | RTD1 | S14 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O42 | RTD1 | S14 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O43 | RTD1 | S15 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O44 | RTD1 | S15 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O45 | RTD1 | S15 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O46 | RTD1 | S16 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O47 | RTD1 | S16 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O48 | RTD1 | S16 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | S99 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
69 | S100 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
70 | S1 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
70 | S2 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
74 | S1 | ARC1 | I/I0 Arc> [50ARC/50NARC] mode | UINT32 | RW | 0=Disabled;1=Activated
74 | S2 | ARC1 | I/I0 Arc> Self supervision test pulse | UINT32 | RW | 0=Disabled;1=On
74 | V1 | ARC1 | I/I0 Arc> condition | UINT32 | R | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
74 | V2 | ARC1 | Sensor status | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I1 | ARC1 | I/I0 Arc> Zone1 Trips | UINT32 | R | 0...4294967295
74 | I2 | ARC1 | I/I0 Arc> Zone1 Blocks | UINT32 | R | 0...4294967295
74 | I3 | ARC1 | I/I0 Arc> Zone2 Trips | UINT32 | R | 0...4294967295
74 | I4 | ARC1 | I/I0 Arc> Zone2 Blocks | UINT32 | R | 0...4294967295
74 | I5 | ARC1 | I/I0 Arc> Zone3 Trips | UINT32 | R | 0...4294967295
74 | I6 | ARC1 | I/I0 Arc> Zone3 Blocks | UINT32 | R | 0...4294967295
74 | I7 | ARC1 | I/I0 Arc> Zone4 Trips | UINT32 | R | 0...4294967295
74 | I8 | ARC1 | I/I0 Arc> Zone4 Blocks | UINT32 | R | 0...4294967295
74 | S3 | ARC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
74 | I9 | ARC1 | Channel 1 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I10 | ARC1 | Channel 1 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I11 | ARC1 | Channel 2 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I12 | ARC1 | Channel 2 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I13 | ARC1 | Channel 3 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I14 | ARC1 | Channel 3 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I15 | ARC1 | Channel 4 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I16 | ARC1 | Channel 4 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | S4 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S5 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S6 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S7 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S8 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S9 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S10 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S11 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S12 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S13 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S14 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S15 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S16 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S17 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S18 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S19 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S20 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S21 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S22 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S23 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S24 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S25 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S26 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S27 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S28 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S29 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S30 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S31 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S32 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S33 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S34 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S35 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S36 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S37 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S38 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S39 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S40 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S41 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S42 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S43 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S44 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S45 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S46 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S47 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S48 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S49 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S50 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S51 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S52 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S53 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S54 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S55 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S56 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S57 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S58 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S59 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S60 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S61 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S62 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S63 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S64 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S65 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S66 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S67 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S68 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S69 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S70 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S71 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S72 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S73 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S74 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S75 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S76 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S77 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S78 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S79 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S80 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S81 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S82 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S83 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S84 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S85 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S86 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S87 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S88 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S89 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S90 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S91 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S92 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S93 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S94 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S95 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S96 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S97 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S98 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S99 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S100 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S101 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S102 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S103 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S104 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S105 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S106 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S107 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S108 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S109 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S110 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S111 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S112 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S113 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S114 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S115 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S116 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S117 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S118 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S119 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S120 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S121 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S122 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S123 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S124 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S125 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S126 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S127 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S128 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S129 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S130 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S131 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S132 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S133 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S134 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S135 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S136 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S137 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S138 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S139 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S140 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S141 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S142 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S143 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S144 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S145 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S146 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S147 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S148 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S149 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S150 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S151 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S152 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S153 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S154 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S155 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S156 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S157 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S158 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S159 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S160 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S161 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S162 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S163 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S164 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S165 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S166 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S167 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S168 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S169 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S170 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S171 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S172 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S173 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S174 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S175 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S176 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S177 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S178 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S179 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S180 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S181 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S182 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S183 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S184 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S185 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S186 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S187 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S188 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S189 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S190 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S191 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S192 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S193 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S194 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S195 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S196 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S197 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S198 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S199 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S200 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S201 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S202 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S203 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S204 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S205 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S206 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S207 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S208 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S209 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S210 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S211 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S212 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S213 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S214 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S215 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S216 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S217 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S218 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S219 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S220 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S221 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S222 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S223 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S224 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S225 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S226 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S227 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S228 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S229 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S230 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S231 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S232 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S233 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S234 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S235 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S236 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S237 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S238 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S239 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S240 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S241 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S242 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S243 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S244 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S245 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S246 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S247 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S248 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S249 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S250 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S251 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S252 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S253 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S254 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S255 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S256 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S257 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S258 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S259 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S260 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S261 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S262 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S263 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S264 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S265 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S266 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S267 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S268 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S269 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S270 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S271 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S272 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S273 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S274 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S275 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S276 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S277 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S278 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S279 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S280 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S281 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S282 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S283 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S284 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S285 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S286 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S287 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S288 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S289 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S290 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S291 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S292 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S293 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S294 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S295 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S296 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S297 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S298 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S299 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S300 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S301 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S302 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S303 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S304 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S305 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S306 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S307 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S308 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S309 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S310 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S311 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S312 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S313 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S314 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S315 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S316 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S317 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S318 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S319 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S320 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S321 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S322 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S323 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S324 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S325 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S326 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S327 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S328 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S329 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S330 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S331 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S332 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S333 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S334 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S335 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S336 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S337 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S338 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S339 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S340 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S341 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S342 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S343 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S344 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S345 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S346 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S347 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S348 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S349 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S350 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S351 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S352 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S353 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S354 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S355 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S356 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S357 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S358 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S359 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S360 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S361 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S362 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S363 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S364 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S365 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S366 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S367 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S368 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S369 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S370 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S371 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S372 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S373 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S374 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S375 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S376 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S377 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S378 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S379 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S380 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S381 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S382 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S383 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S384 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S385 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S386 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S387 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S388 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S389 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S390 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S391 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S392 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S393 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S394 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S395 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S396 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S397 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S398 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S399 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S400 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S401 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S402 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S403 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S404 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S405 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S406 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S407 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S408 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S409 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S410 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S411 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | O1 | ARC1 | I/I0 Arc> Ph.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O2 | ARC1 | I/I0 Arc> Res.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O3 | ARC1 | I/I0 Arc> Zone1.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O4 | ARC1 | I/I0 Arc> Zone2.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O5 | ARC1 | I/I0 Arc> Zone3.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O6 | ARC1 | I/I0 Arc> Zone4.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O7 | ARC1 | I/I0 Arc> Ph.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O8 | ARC1 | I/I0 Arc> Res.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O9 | ARC1 | I/I0 Arc> Ph.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O10 | ARC1 | I/I0 Arc> Res.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O11 | ARC1 | I/I0 Arc> Zone1 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O12 | ARC1 | I/I0 Arc> Zone1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O13 | ARC1 | I/I0 Arc> Zone2 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O14 | ARC1 | I/I0 Arc> Zone2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O15 | ARC1 | I/I0 Arc> Zone3 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O16 | ARC1 | I/I0 Arc> Zone3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O17 | ARC1 | I/I0 Arc> Zone4 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O18 | ARC1 | I/I0 Arc> Zone4 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O19 | ARC1 | I/I0 Arc> S1 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O20 | ARC1 | I/I0 Arc> S2 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O21 | ARC1 | I/I0 Arc> S3 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O22 | ARC1 | I/I0 Arc> S4 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O23 | ARC1 | I/I0 Arc> IO unit fault | SIGNAL_OUT | RW | 0...4294967295
74 | I17 | ARC1 | Newest Register | UINT32 | R | 0...12
74 | I18 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I19 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I20 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I21 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I22 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I23 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I24 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I25 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I26 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I27 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I28 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I29 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I30 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I31 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I32 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I33 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I34 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I35 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I36 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I37 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I38 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I39 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I40 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I41 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I42 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I43 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I44 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I45 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I46 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I47 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I48 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I49 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I50 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I51 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I52 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I53 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I54 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I55 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I56 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I57 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I58 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I59 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I60 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I61 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I62 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I63 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I64 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I65 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I66 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I67 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I68 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I69 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I70 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I71 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I72 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I73 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I74 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I75 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I76 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I77 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | S412 | ARC1 | EventMaskLo | UINT32 | RW | 0...4294967295
74 | S413 | ARC1 | EventMaskHi | UINT32 | RW | 0...4294967295
52 | S1 | CTS1 | CTS1 mode | UINT32 | RW | 0=Disabled;1=Activated
52 | V1 | CTS1 | CTS1 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
52 | I1 | CTS1 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
52 | I2 | CTS1 | Natural unbalance ang | FLOAT | R | -360...360
52 | I3 | CTS1 | Measured current difference Isum, I0 | FLOAT | R | 0...50
52 | I4 | CTS1 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
52 | I5 | CTS1 | CTS1 alarms | UINT32 | R | 0...4294967295
52 | I6 | CTS1 | CTS1 blocks | UINT32 | R | 0...4294967295
52 | S2 | CTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
52 | S3 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S4 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S5 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S6 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S7 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S8 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S9 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S10 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S11 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S12 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S13 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S14 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S15 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S16 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S17 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S18 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S19 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S20 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S21 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S22 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S23 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S24 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S25 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S26 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S27 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S28 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S29 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S30 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S31 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S32 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S33 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S34 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S35 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S36 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S37 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S38 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S39 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S40 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S41 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S42 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S43 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S44 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S45 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S46 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S47 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S48 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S49 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S50 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | O1 | CTS1 | CTS1 ALARM | SIGNAL_OUT | RW | 0...4294967295
52 | O2 | CTS1 | CTS1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
52 | I7 | CTS1 | Newest Register | UINT32 | R | 0...12
52 | I8 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I9 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I10 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I11 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I12 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I13 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I14 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I15 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I16 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I17 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I18 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I19 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I20 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I21 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I22 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I23 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I24 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I25 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I26 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I27 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I28 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I29 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I30 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I31 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I32 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I33 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I34 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I35 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I36 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I37 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I38 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I39 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I40 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I41 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I42 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I43 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I44 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I45 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I46 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I47 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I48 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I49 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I50 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I51 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I52 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I53 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I54 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I55 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I56 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I57 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I58 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I59 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I60 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I61 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I62 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I63 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I64 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I65 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I66 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I67 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I68 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I69 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I70 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I71 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I72 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I73 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I74 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I75 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I76 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I77 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I78 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I79 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | S51 | CTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
52 | S52 | CTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
54 | S1 | CTS2 | CTS2 mode | UINT32 | RW | 0=Disabled;1=Activated
54 | V1 | CTS2 | CTS2 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
54 | I1 | CTS2 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
54 | I2 | CTS2 | Natural unbalance ang | FLOAT | R | -360...360
54 | I3 | CTS2 | Measured current difference Isum, I0 | FLOAT | R | 0...50
54 | I4 | CTS2 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
54 | I5 | CTS2 | CTS2 alarms | UINT32 | R | 0...4294967295
54 | I6 | CTS2 | CTS2 blocks | UINT32 | R | 0...4294967295
54 | S2 | CTS2 | Clear statistics | UINT32 | W | 0=-;1=Clear
54 | S3 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S4 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S5 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S6 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S7 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S8 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S9 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S10 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S11 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S12 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S13 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S14 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S15 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S16 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S17 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S18 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S19 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S20 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S21 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S22 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S23 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S24 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S25 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S26 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S27 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S28 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S29 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S30 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S31 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S32 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S33 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S34 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S35 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S36 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S37 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S38 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S39 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S40 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S41 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S42 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S43 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S44 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S45 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S46 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S47 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S48 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S49 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S50 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | O1 | CTS2 | CTS2 ALARM | SIGNAL_OUT | RW | 0...4294967295
54 | O2 | CTS2 | CTS2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
54 | I7 | CTS2 | Newest Register | UINT32 | R | 0...12
54 | I8 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I9 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I10 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I11 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I12 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I13 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I14 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I15 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I16 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I17 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I18 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I19 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I20 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I21 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I22 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I23 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I24 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I25 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I26 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I27 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I28 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I29 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I30 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I31 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I32 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I33 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I34 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I35 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I36 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I37 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I38 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I39 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I40 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I41 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I42 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I43 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I44 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I45 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I46 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I47 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I48 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I49 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I50 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I51 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I52 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I53 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I54 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I55 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I56 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I57 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I58 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I59 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I60 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I61 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I62 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I63 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I64 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I65 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I66 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I67 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I68 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I69 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I70 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I71 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I72 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I73 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I74 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I75 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I76 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I77 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I78 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I79 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | S51 | CTS2 | EventMaskLo | UINT32 | RW | 0...4294967295
54 | S52 | CTS2 | EventMaskHi | UINT32 | RW | 0...4294967295
53 | S1 | VTS1 | VTS [60] mode | UINT32 | RW | 0=Disabled;1=Activated
53 | V1 | VTS1 | VTS condition | UINT32 | R | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
53 | V2 | VTS1 | Bus voltages | UINT32 | R | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
53 | I1 | VTS1 | VTS Starts | UINT32 | R | 0...4294967295
53 | I2 | VTS1 | Line fuse fails | UINT32 | R | 0...4294967295
53 | I3 | VTS1 | Bus fuse fails | UINT32 | R | 0...4294967295
53 | I4 | VTS1 | VTS Blocks | UINT32 | R | 0...4294967295
53 | S2 | VTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
53 | S3 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S4 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S5 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S6 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S7 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S8 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S9 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S10 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S11 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S12 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S13 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S14 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S15 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S16 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S17 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S18 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S19 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S20 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S21 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S22 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S23 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S24 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S25 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S26 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S27 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S28 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S29 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S30 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S31 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S32 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S33 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S34 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S35 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S36 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S37 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S38 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S39 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S40 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S41 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S42 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S43 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S44 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S45 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S46 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S47 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S48 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S49 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S50 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | O1 | VTS1 | VTS Start | SIGNAL_OUT | RW | 0...4294967295
53 | O2 | VTS1 | VTS Fail Alarm Bus | SIGNAL_OUT | RW | 0...4294967295
53 | O3 | VTS1 | VTS Fail Alarm Line | SIGNAL_OUT | RW | 0...4294967295
53 | O4 | VTS1 | VTS Blocked(time delay) | SIGNAL_OUT | RW | 0...4294967295
53 | I5 | VTS1 | Newest Register | UINT32 | R | 0...12
53 | I6 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I7 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I8 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I9 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I10 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I11 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I12 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I13 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I14 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I15 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I16 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I17 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I18 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I19 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I20 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I21 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I22 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I23 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I24 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I25 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I26 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I27 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I28 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I29 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I30 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I31 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I32 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I33 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I34 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I35 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I36 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I37 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I38 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I39 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I40 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I41 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I42 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I43 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I44 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I45 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I46 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I47 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I48 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I49 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I50 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I51 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I52 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I53 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I54 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I55 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I56 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I57 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I58 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I59 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I60 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I61 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I62 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I63 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I64 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I65 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | S51 | VTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
53 | S52 | VTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
43 | S1 | FLX1 | Fault locator mode | UINT32 | RW | 0=Disabled;1=Activated
43 | V1 | FLX1 | Fault locator condition | UINT32 | R | 0=Idle;1=Triggered;2=Calc ready
43 | I1 | FLX1 | Times Flocator triggered | UINT32 | R | 0...4294967295
43 | I2 | FLX1 | Last fault reactance | FLOAT | R | -1800...1800
43 | I3 | FLX1 | Last fault distance | FLOAT | R | -1800...1800
43 | V2 | FLX1 | Last fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I4 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I5 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I6 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | I7 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I8 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I9 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | V3 | FLX1 | Last fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | S2 | FLX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
43 | S3 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S4 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S5 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S6 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S7 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S8 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S9 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S10 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S11 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S12 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S13 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S14 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S15 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S16 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S17 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S18 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | I10 | FLX1 | Newest Register | UINT32 | R | 0...12
43 | I11 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I12 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I13 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I14 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I15 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I16 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I17 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I18 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I19 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I20 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I21 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I22 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I23 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I24 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I25 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I26 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I27 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I28 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I29 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I30 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I31 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I32 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I33 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I34 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I35 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I36 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I37 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I38 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I39 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I40 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I41 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I42 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I43 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I44 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I45 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I46 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I47 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I48 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I49 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I50 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I51 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I52 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I53 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I54 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I55 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I56 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I57 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I58 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I59 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I60 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I61 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I62 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I63 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I64 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I65 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I66 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I67 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I68 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I69 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I70 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I71 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I72 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I73 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I74 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I75 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I76 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I77 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I78 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I79 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I80 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I81 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I82 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I83 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I84 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I85 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I86 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I87 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I88 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I89 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I90 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I91 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I92 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I93 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I94 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I95 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I96 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I97 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I98 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I99 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I100 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I101 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I102 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I103 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I104 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I105 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I106 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I107 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I108 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I109 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I110 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I111 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I112 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I113 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I114 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I115 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I116 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I117 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I118 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I119 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I120 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I121 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I122 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I123 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I124 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I125 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I126 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I127 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I128 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I129 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I130 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | S19 | FLX1 | EventMaskLo | UINT32 | RW | 0...4294967295
55 | S1 | THD1 | THD mode | UINT32 | RW | 0=Disabled;1=Activated
55 | V1 | THD1 | THD condition | UINT32 | R | 0=Normal;1=Start;2=Alarm;3=Blocked
55 | S2 | THD1 | Measurement magnitude | UINT32 | RW | 0=Amplitude;1=Power
55 | I1 | THD1 | THD starts | UINT32 | R | 0...4294967295
55 | I2 | THD1 | THD alarms | UINT32 | R | 0...4294967295
55 | I3 | THD1 | THD blocks | UINT32 | R | 0...4294967295
55 | S3 | THD1 | Clear statistics | UINT32 | W | 0=-;1=Clear
55 | S4 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S5 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S6 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S7 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S8 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S9 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S10 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S11 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S12 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S13 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S14 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S15 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S16 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S17 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S18 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S19 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S20 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S21 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S22 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S23 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S24 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S25 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S26 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S27 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S28 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S29 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S30 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S31 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S32 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S33 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S34 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S35 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S36 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S37 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S38 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S39 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S40 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S41 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S42 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S43 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S44 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S45 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S46 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S47 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S48 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S49 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S50 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S51 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S52 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S53 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S54 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S55 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S56 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S57 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S58 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S59 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S60 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S61 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S62 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S63 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S64 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S65 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S66 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S67 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S68 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S69 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S70 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S71 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S72 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S73 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S74 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S75 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | O1 | THD1 | THDPH> START | SIGNAL_OUT | RW | 0...4294967295
55 | O2 | THD1 | THDPH> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O3 | THD1 | THDI01> START | SIGNAL_OUT | RW | 0...4294967295
55 | O4 | THD1 | THDI01> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O5 | THD1 | THDI02> START | SIGNAL_OUT | RW | 0...4294967295
55 | O6 | THD1 | THDI02> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O7 | THD1 | THD> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
55 | I4 | THD1 | Newest Register | UINT32 | R | 0...12
55 | I5 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I6 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I7 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I8 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I9 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I10 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I11 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I12 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I13 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I14 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I15 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I16 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I17 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I18 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I19 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I20 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I21 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I22 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I23 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I24 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I25 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I26 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I27 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I28 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I29 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I30 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I31 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I32 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I33 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I34 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I35 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I36 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I37 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I38 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I39 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I40 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | S76 | THD1 | EventMaskLo | UINT32 | RW | 0...4294967295
58 | S1 | CBW1 | CBW mode | UINT32 | RW | 0=Disabled;1=Activated
58 | V1 | CBW1 | CBW condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On
58 | I1 | CBW1 | Breaker operations | UINT32 | R | 0...4294967295
58 | I2 | CBW1 | Alarm 1 counter | UINT32 | R | 0...4294967295
58 | I3 | CBW1 | Alarm 2 counter | UINT32 | R | 0...4294967295
58 | I4 | CBW1 | L1 Operations Left | FLOAT | R | 0...4294967295
58 | I5 | CBW1 | L2 Operations Left | FLOAT | R | 0...4294967295
58 | I6 | CBW1 | L3 Operations Left | FLOAT | R | 0...4294967295
58 | S2 | CBW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
58 | S3 | CBW1 | Alarm 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S4 | CBW1 | Alarm 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S5 | CBW1 | Alarm 1 Set | UINT32 | RW | 0...200000
58 | S6 | CBW1 | Alarm 2 Set | UINT32 | RW | 0...200000
58 | S7 | CBW1 | Operations 1 | FLOAT | RW | 0...200000
58 | S8 | CBW1 | Operations 2 | FLOAT | RW | 0...200000
58 | S9 | CBW1 | Current 1 | FLOAT | RW | 0...100
58 | S10 | CBW1 | Current 2 | FLOAT | RW | 0...100
58 | O1 | CBW1 | CBW Alarm 1 act | SIGNAL_OUT | RW | 0...4294967295
58 | I7 | CBW1 | Newest Register | UINT32 | R | 0...12
58 | I8 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I9 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I10 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I11 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I12 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I13 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I14 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I15 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I16 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I17 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I18 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I19 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I20 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I21 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I22 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I23 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I24 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I25 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I26 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I27 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I28 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I29 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I30 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I31 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I32 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I33 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I34 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I35 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I36 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I37 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I38 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I39 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I40 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I41 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I42 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I43 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | S11 | CBW1 | EventMaskLo | UINT32 | RW | 0...4294967295
97 | S1 | NJK1 | U0> RECL [79] mode | UINT32 | RW | 0=Disabled;1=Activated
97 | V1 | NJK1 | U0> RECL condition | UINT32 | R | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
97 | I1 | NJK1 | Requests | UINT32 | R | 0...4294967295
97 | I2 | NJK1 | Blocks | UINT32 | R | 0...4294967295
97 | I3 | NJK1 | Starts | UINT32 | R | 0...4294967295
97 | I4 | NJK1 | Breaker closes | UINT32 | R | 0...4294967295
97 | S2 | NJK1 | Clear statistics | UINT32 | W | 0=-;1=Clear
97 | S3 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S4 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S5 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S6 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S7 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S8 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S9 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S10 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | O1 | NJK1 | U0> RECL Blocked | SIGNAL_OUT | RW | 0...4294967295
97 | O2 | NJK1 | U0> RECL Active | SIGNAL_OUT | RW | 0...4294967295
97 | O3 | NJK1 | U0> RECL CLOSE | SIGNAL_OUT | RW | 0...4294967295
97 | O4 | NJK1 | U0> RECL BLKU0 | SIGNAL_OUT | RW | 0...4294967295
97 | I5 | NJK1 | Newest Register | UINT32 | R | 0...12
97 | I6 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I7 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I8 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I9 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I10 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I11 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I12 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I13 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I14 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I15 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I16 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I17 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I18 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I19 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I20 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I21 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I22 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I23 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I24 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I25 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I26 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I27 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I28 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I29 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | S11 | NJK1 | EventMaskLo | UINT32 | RW | 0...4294967295
61 | S1 | SOF1 | SOTF mode | UINT32 | RW | 0=Disabled;1=Activated
61 | V1 | SOF1 | SOTF condition | UINT32 | R | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
61 | I1 | SOF1 | Inits | UINT32 | R | 0...4294967295
61 | I2 | SOF1 | Starts | UINT32 | R | 0...4294967295
61 | I3 | SOF1 | Trips | UINT32 | R | 0...4294967295
61 | I4 | SOF1 | Blocks | UINT32 | R | 0...4294967295
61 | S2 | SOF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
61 | S3 | SOF1 | SG in use | UINT32 | RW | 0...255
61 | S4 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S5 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S6 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S7 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S8 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S9 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S10 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S11 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | O1 | SOF1 | SOTF Blocked | SIGNAL_OUT | RW | 0...4294967295
61 | O2 | SOF1 | SOTF Active | SIGNAL_OUT | RW | 0...4294967295
61 | O3 | SOF1 | SOTF Trip | SIGNAL_OUT | RW | 0...4294967295
61 | I5 | SOF1 | Newest Register | UINT32 | R | 0...12
61 | I6 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I7 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I8 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I9 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I10 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I11 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I12 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I13 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I14 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I15 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I16 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I17 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I18 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I19 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I20 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I21 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I22 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I23 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I24 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I25 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I26 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I27 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I28 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I29 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | S12 | SOF1 | EventMaskLo | UINT32 | RW | 0...4294967295
142 | S1 | DOS1 | Energy dose counter mode | UINT32 | RW | 0=Disabled;1=Activated
142 | S2 | DOS1 | Clear pulsecounters | UINT32 | W | 0=-;1=Clear
142 | S3 | DOS1 | DC 1 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S4 | DOS1 | DC 1 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I1 | DOS1 | DC 1 Input signal | FLOAT | R | -1000000...1000000
142 | S5 | DOS1 | DC 1 Pulse magnitude | FLOAT | RW | 0...1800
142 | S6 | DOS1 | DC 1 Pulse Lenght | FLOAT | RW | 0...1800
142 | I2 | DOS1 | DC 1 Pulses sent | UINT32 | R | 0...4294967295
142 | S7 | DOS1 | DC 2 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S8 | DOS1 | DC 2 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I3 | DOS1 | DC 2 Input signal | FLOAT | R | -1000000...1000000
142 | S9 | DOS1 | DC 2 Pulse magnitude | FLOAT | RW | 0...1800
142 | S10 | DOS1 | DC 2 Pulse Lenght | FLOAT | RW | 0...1800
142 | I4 | DOS1 | DC 2 Pulses sent | UINT32 | R | 0...4294967295
142 | S11 | DOS1 | DC 3 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S12 | DOS1 | DC 3 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I5 | DOS1 | DC 3 Input signal | FLOAT | R | -1000000...1000000
142 | S13 | DOS1 | DC 3 Pulse magnitude | FLOAT | RW | 0...1800
142 | S14 | DOS1 | DC 3 Pulse Lenght | FLOAT | RW | 0...1800
142 | I6 | DOS1 | DC 3 Pulses sent | UINT32 | R | 0...4294967295
142 | S15 | DOS1 | DC 4 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S16 | DOS1 | DC 4 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I7 | DOS1 | DC 4 Input signal | FLOAT | R | -1000000...1000000
142 | S17 | DOS1 | DC 4 Pulse magnitude | FLOAT | RW | 0...1800
142 | S18 | DOS1 | DC 4 Pulse Lenght | FLOAT | RW | 0...1800
142 | I8 | DOS1 | DC 4 Pulses sent | UINT32 | R | 0...4294967295
142 | O1 | DOS1 | DC 1 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O2 | DOS1 | DC 2 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O3 | DOS1 | DC 3 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O4 | DOS1 | DC 4 Pulse out | SIGNAL_OUT | RW | 0...4294967295
144 | V1 | PCS1 | PCS1 Switch Status | SIGNAL_OUT | RW | 0...4294967295
145 | V1 | PCS2 | PCS2 Switch Status | SIGNAL_OUT | RW | 0...4294967295
146 | V1 | PCS3 | PCS3 Switch Status | SIGNAL_OUT | RW | 0...4294967295
147 | V1 | PCS4 | PCS4 Switch Status | SIGNAL_OUT | RW | 0...4294967295
148 | V1 | PCS5 | PCS5 Switch Status | SIGNAL_OUT | RW | 0...4294967295
45 | S1 | SYN1 | Synchrocheck (SYN1,2,3) [25] mode | UINT32 | RW | 0=Disabled;1=Activated
45 | V1 | SYN1 | SYN1 Condition | UINT32 | R | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok
45 | V2 | SYN1 | SYN2 Condition | UINT32 | R | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok
45 | V3 | SYN1 | SYN3 Condition | UINT32 | R | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok
45 | I1 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I2 | SYN1 | SYN1 Mag diff | FLOAT | R | -120...120
45 | I3 | SYN1 | SYN1 Ang diff | FLOAT | R | -360...360
45 | I4 | SYN1 | SYN1 freq diff | FLOAT | R | -75...75
45 | I5 | SYN1 | SYN1 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S2 | SYN1 | Estimated BRK Closing time | FLOAT | R | 0...360
45 | S3 | SYN1 | Networks rotating time | FLOAT | R | 0...360
45 | S4 | SYN1 | Networks placement atm | FLOAT | R | -360...360
45 | I6 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I7 | SYN1 | SYN2 Mag diff | FLOAT | R | -120...120
45 | I8 | SYN1 | SYN2 Ang diff | FLOAT | R | -360...360
45 | I9 | SYN1 | SYN2 freq diff | FLOAT | R | -75...75
45 | I10 | SYN1 | SYN2 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S5 | SYN1 | SYN2 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S6 | SYN1 | SYN2 Networks rotating time | FLOAT | R | 0...360.000
45 | S7 | SYN1 | SYN2 Networks placement atm | FLOAT | R | -360.000...360.000
45 | I11 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I12 | SYN1 | SYN3 Mag diff | FLOAT | R | -120...120
45 | I13 | SYN1 | SYN3 Ang diff | FLOAT | R | -360...360
45 | I14 | SYN1 | SYN3 freq diff | FLOAT | R | -75...75
45 | I15 | SYN1 | SYN3 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S8 | SYN1 | SYN3 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S9 | SYN1 | SYN3 Networks rotating time | FLOAT | R | 0...360.000
45 | S10 | SYN1 | SYN3 Networks placement atm | FLOAT | R | -360.000...360.000
45 | S11 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S12 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S13 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S14 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S15 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S16 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S17 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S18 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S19 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S20 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S21 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S22 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S23 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S24 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S25 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S26 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S27 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S28 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S29 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S30 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S31 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S32 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S33 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S34 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S35 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S36 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S37 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S38 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S39 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S40 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S41 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S42 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S43 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S44 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S45 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S46 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S47 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S48 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S49 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S50 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S51 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S52 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S53 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S54 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S55 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S56 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S57 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S58 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S59 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S60 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S61 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S62 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S63 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S64 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S65 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S66 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S67 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S68 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S69 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S70 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S71 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S72 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S73 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S74 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S75 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S76 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S77 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S78 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S79 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S80 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S81 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S82 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S83 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S84 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S85 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S86 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S87 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S88 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S89 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S90 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S91 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S92 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S93 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S94 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S95 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S96 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S97 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S98 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S99 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S100 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S101 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S102 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S103 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S104 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S105 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S106 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S107 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S108 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S109 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S110 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S111 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S112 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S113 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S114 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S115 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S116 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S117 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S118 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S119 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S120 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S121 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S122 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S123 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S124 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S125 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S126 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S127 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S128 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S129 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S130 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S131 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S132 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S133 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S134 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S135 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S136 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S137 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S138 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S139 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S140 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S141 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S142 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S143 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S144 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S145 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S146 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S147 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S148 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S149 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S150 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S151 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S152 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S153 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S154 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S155 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S156 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S157 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S158 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S159 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S160 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S161 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S162 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S163 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S164 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S165 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S166 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S167 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S168 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S169 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S170 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S171 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S172 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S173 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S174 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S175 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S176 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S177 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S178 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S179 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S180 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S181 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S182 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S183 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S184 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S185 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S186 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S187 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S188 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S189 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S190 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S191 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S192 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S193 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S194 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S195 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S196 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S197 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S198 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S199 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S200 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S201 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S202 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S203 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S204 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S205 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S206 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S207 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S208 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S209 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S210 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S211 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S212 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S213 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S214 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S215 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S216 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S217 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S218 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S219 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S220 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S221 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S222 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S223 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S224 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S225 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S226 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S227 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S228 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S229 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S230 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S231 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S232 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S233 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S234 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S235 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S236 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S237 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S238 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S239 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S240 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S241 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S242 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S243 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S244 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S245 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S246 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S247 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S248 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S249 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S250 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S251 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S252 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S253 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S254 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S255 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S256 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S257 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S258 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S259 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S260 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S261 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S262 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S263 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S264 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S265 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S266 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S267 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S268 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S269 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S270 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S271 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S272 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S273 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S274 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | O1 | SYN1 | SYN1 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O2 | SYN1 | SYN1 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O3 | SYN1 | SYN1 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O4 | SYN1 | SYN1 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O5 | SYN1 | SYN1 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O6 | SYN1 | SYN1 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O7 | SYN1 | SYN1 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O8 | SYN1 | SYN1 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O9 | SYN1 | SYN1 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O10 | SYN1 | SYN1 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O11 | SYN1 | SYN1 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O12 | SYN1 | SYN1 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O13 | SYN1 | SYN1 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O14 | SYN1 | SYN1 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O15 | SYN1 | SYN1 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O16 | SYN1 | SYN1 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O17 | SYN1 | SYN1 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O18 | SYN1 | SYN1 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O19 | SYN1 | SYN1 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O20 | SYN1 | SYN1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O21 | SYN1 | SYN2 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O22 | SYN1 | SYN2 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O23 | SYN1 | SYN2 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O24 | SYN1 | SYN2 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O25 | SYN1 | SYN2 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O26 | SYN1 | SYN2 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O27 | SYN1 | SYN2 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O28 | SYN1 | SYN2 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O29 | SYN1 | SYN2 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O30 | SYN1 | SYN2 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O31 | SYN1 | SYN2 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O32 | SYN1 | SYN2 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O33 | SYN1 | SYN2 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O34 | SYN1 | SYN2 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O35 | SYN1 | SYN2 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O36 | SYN1 | SYN2 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O37 | SYN1 | SYN2 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O38 | SYN1 | SYN2 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O39 | SYN1 | SYN2 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O40 | SYN1 | SYN2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O41 | SYN1 | SYN3 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O42 | SYN1 | SYN3 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O43 | SYN1 | SYN3 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O44 | SYN1 | SYN3 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O45 | SYN1 | SYN3 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O46 | SYN1 | SYN3 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O47 | SYN1 | SYN3 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O48 | SYN1 | SYN3 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O49 | SYN1 | SYN3 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O50 | SYN1 | SYN3 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O51 | SYN1 | SYN3 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O52 | SYN1 | SYN3 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O53 | SYN1 | SYN3 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O54 | SYN1 | SYN3 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O55 | SYN1 | SYN3 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O56 | SYN1 | SYN3 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O57 | SYN1 | SYN3 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O58 | SYN1 | SYN3 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O59 | SYN1 | SYN3 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O60 | SYN1 | SYN3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | I16 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I17 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I18 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I19 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I20 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I21 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I22 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I23 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I24 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I25 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I26 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I27 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I28 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I29 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I30 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I31 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I32 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I33 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I34 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I35 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I36 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I37 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I38 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I39 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I40 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I41 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I42 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I43 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I44 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I45 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I46 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I47 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I48 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I49 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I50 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I51 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I52 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I53 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I54 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I55 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I56 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I57 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I58 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I59 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I60 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I61 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I62 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I63 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I64 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I65 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I66 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I67 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I68 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I69 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I70 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I71 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I72 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I73 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I74 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I75 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I76 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I77 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I78 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I79 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I80 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I81 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I82 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I83 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I84 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I85 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I86 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I87 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I88 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I89 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I90 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I91 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I92 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I93 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I94 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I95 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I96 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I97 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I98 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I99 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I100 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I101 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I102 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I103 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I104 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I105 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I106 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I107 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I108 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I109 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I110 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I111 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I112 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I113 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I114 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I115 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I116 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I117 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I118 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I119 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I120 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I121 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I122 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I123 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I124 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I125 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I126 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I127 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I128 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I129 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I130 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I131 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I132 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I133 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I134 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I135 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I136 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I137 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I138 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I139 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I140 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I141 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I142 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I143 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I144 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I145 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I146 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I147 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I148 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I149 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I150 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I151 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I152 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I153 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I154 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I155 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I156 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I157 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I158 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I159 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I160 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I161 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I162 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I163 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I164 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I165 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I166 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I167 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I168 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I169 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I170 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I171 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I172 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I173 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I174 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I175 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I176 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I177 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I178 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I179 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I180 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I181 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I182 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I183 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I184 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I185 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I186 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I187 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I188 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I189 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I190 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I191 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I192 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I193 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I194 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I195 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I196 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I197 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I198 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I199 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I200 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I201 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I202 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I203 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I204 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I205 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I206 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I207 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I208 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I209 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I210 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I211 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I212 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I213 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I214 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I215 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I216 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I217 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I218 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I219 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I220 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I221 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I222 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I223 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I224 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I225 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I226 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I227 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I228 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I229 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I230 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I231 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I232 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I233 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I234 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I235 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I236 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I237 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I238 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I239 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I240 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I241 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I242 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I243 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I244 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I245 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I246 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I247 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I248 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I249 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I250 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I251 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I252 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I253 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I254 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I255 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I256 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I257 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I258 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I259 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I260 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I261 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I262 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I263 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I264 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I265 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I266 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I267 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I268 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I269 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I270 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I271 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I272 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I273 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I274 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I275 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I276 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I277 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I278 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I279 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I280 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I281 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I282 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I283 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I284 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I285 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I286 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I287 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I288 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I289 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I290 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I291 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I292 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I293 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I294 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I295 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I296 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I297 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I298 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I299 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I300 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I301 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I302 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I303 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I304 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I305 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I306 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I307 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I308 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I309 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I310 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I311 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I312 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I313 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I314 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I315 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I316 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I317 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I318 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I319 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I320 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I321 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I322 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I323 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I324 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I325 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I326 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I327 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I328 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I329 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I330 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I331 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I332 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I333 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I334 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I335 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I336 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I337 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I338 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I339 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I340 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I341 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I342 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I343 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I344 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I345 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I346 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I347 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I348 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I349 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I350 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I351 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I352 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I353 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I354 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I355 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I356 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I357 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I358 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I359 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I360 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I361 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I362 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I363 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I364 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I365 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I366 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I367 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I368 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I369 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I370 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I371 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I372 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I373 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I374 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I375 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I376 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I377 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I378 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | S275 | SYN1 | EventMaskLo | UINT32 | RW | 0...4294967295
45 | S276 | SYN1 | EventMaskHi | UINT32 | RW | 0...4294967295
219 | S1 | SYNX1 | SYN1 Extra EventMaskLo | UINT32 | RW | 0...4294967295
219 | S2 | SYNX1 | SYN1 Extra EventMaskHi | UINT32 | RW | 0...4294967295
220 | S1 | SYNX2 | SYN2 Extra EventMaskLo | UINT32 | RW | 0...4294967295
220 | S2 | SYNX2 | SYN2 Extra EventMaskHi | UINT32 | RW | 0...4294967295
221 | S1 | SYNX3 | SYN3 Extra EventMaskLo | UINT32 | RW | 0...4294967295
221 | S2 | SYNX3 | SYN3 Extra EventMaskHi | UINT32 | RW | 0...4294967295
155 | S1 | VJP1 | <DELTA><alpha> > mode | UINT32 | RW | 0=Disabled;1=Activated
155 | V1 | VJP1 | <DELTA><alpha> > condition | UINT32 | R | 0=Normal;1=Blocked:2=Trip;3=Alarm
155 | S2 | VJP1 | Available stages | UINT32 | RW | 0=Trip;1=Trip and Alarm
155 | S3 | VJP1 | Monitored voltages | UINT32 | RW | 0=System all P-P Voltages;1=System any P-P Voltage;2=System L12 Voltage;3=System L23 Voltage;4=System L31 Voltage;5=System all P-E voltages;6=System any P-E voltage;7=System L1 Voltage;8=System L2 Voltage;9=System L3 Voltage;10=U3 Voltage;11=U4 Voltage
155 | V2 | VJP1 | Voltage meas selected | UINT32 | R | 0=Selection Ok;1=Selection not available
155 | I1 | VJP1 | <DELTA><alpha> > U1 Angle difference | FLOAT | R | -360...360
155 | I2 | VJP1 | <DELTA><alpha> U1meas/Set | FLOAT | R | -360...360
155 | I3 | VJP1 | <DELTA><alpha> U2 Angle difference | FLOAT | R | -360...360
155 | I4 | VJP1 | <DELTA><alpha> U2meas/Set | FLOAT | R | -360...360
155 | I5 | VJP1 | <DELTA><alpha> U3 Angle difference | FLOAT | R | -360...360
155 | I6 | VJP1 | <DELTA><alpha> U3meas/Set | FLOAT | R | -360...360
155 | I7 | VJP1 | <DELTA><alpha> > Alarms | UINT32 | R | 0...4294967295
155 | I8 | VJP1 | <DELTA><alpha> > Trips | UINT32 | R | 0...4294967295
155 | I9 | VJP1 | <DELTA><alpha> > Blocks | UINT32 | R | 0...4294967295
155 | S4 | VJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
155 | S5 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S6 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S7 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S8 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S9 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S10 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S11 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S12 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S13 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S14 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S15 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S16 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S17 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S18 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S19 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S20 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S21 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S22 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S23 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S24 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S25 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S26 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S27 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S28 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | O1 | VJP1 | <DELTA><alpha> > TRIP | SIGNAL_OUT | RW | 0...4294967295
155 | O2 | VJP1 | <DELTA><alpha> > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
155 | I10 | VJP1 | Newest Register | UINT32 | R | 0...12
155 | I11 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I12 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I13 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I14 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I15 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I16 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I17 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I18 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I19 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I20 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I21 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I22 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I23 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I24 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I25 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I26 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I27 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I28 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I29 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I30 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I31 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I32 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I33 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I34 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I35 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I36 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I37 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I38 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I39 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I40 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I41 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I42 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I43 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I44 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I45 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I46 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | S29 | VJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S1 | OBJ1 | Object1 mode | UINT32 | RW | 0=Disabled;1=Activated
46 | I1 | OBJ1 | Object1 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I2 | OBJ1 | Object1 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
46 | I3 | OBJ1 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | S2 | OBJ1 | Breaker traverse time | FLOAT | RW | 0.02...500
46 | S3 | OBJ1 | WD Cart traverse time | FLOAT | RW | 0.02...500
46 | S4 | OBJ1 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
46 | S5 | OBJ1 | Sync wait timeout | FLOAT | RW | 0.02...500
46 | S6 | OBJ1 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
46 | S7 | OBJ1 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
46 | S8 | OBJ1 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
46 | S9 | OBJ1 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
46 | S10 | OBJ1 | Control Termination Timeout | FLOAT | RW | 0.02...500
46 | O1 | OBJ1 | Object1 Status Open | SIGNAL_OUT | RW | 0...4294967295
46 | O2 | OBJ1 | Object1 Status Closed | SIGNAL_OUT | RW | 0...4294967295
46 | O3 | OBJ1 | Object1 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
46 | O4 | OBJ1 | Object1 Status Bad | SIGNAL_OUT | RW | 0...4294967295
46 | O5 | OBJ1 | Object1 Open Command | SIGNAL_OUT | RW | 0...4294967295
46 | O6 | OBJ1 | Object1 Close Command | SIGNAL_OUT | RW | 0...4294967295
46 | O7 | OBJ1 | Object1 Open Request | SIGNAL_OUT | RW | 0...4294967295
46 | O8 | OBJ1 | Object1 Close Request | SIGNAL_OUT | RW | 0...4294967295
46 | O9 | OBJ1 | Object1 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
46 | O10 | OBJ1 | Object1 No sync wait | SIGNAL_OUT | RW | 0...4294967295
46 | O11 | OBJ1 | Object1 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
46 | O12 | OBJ1 | Object1 No sync fail | SIGNAL_OUT | RW | 0...4294967295
46 | O13 | OBJ1 | Object1 Open timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O14 | OBJ1 | Object1 Close timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O15 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O16 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O17 | OBJ1 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
46 | S11 | OBJ1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S12 | OBJ1 | EventMaskHi | UINT32 | RW | 0...4294967295
46 | I4 | OBJ1 | Newest Register | UINT32 | R | 0...12
46 | I5 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I6 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I7 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I8 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I9 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I10 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I11 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I12 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I13 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I14 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I15 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I16 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I17 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I18 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I19 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I20 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I21 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I22 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I23 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I24 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I25 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I26 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I27 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I28 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I29 | OBJ1 | Open requests | UINT32 | R | 0...4294967295
46 | I30 | OBJ1 | Close requests | UINT32 | R | 0...4294967295
46 | I31 | OBJ1 | Open requests failed | UINT32 | R | 0...4294967295
46 | I32 | OBJ1 | Close requests failed | UINT32 | R | 0...4294967295
46 | S13 | OBJ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
47 | S1 | OBJ2 | Object2 mode | UINT32 | RW | 0=Disabled;1=Activated
47 | I1 | OBJ2 | Object2 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I2 | OBJ2 | Object2 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
47 | I3 | OBJ2 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | S2 | OBJ2 | Breaker traverse time | FLOAT | RW | 0.02...500
47 | S3 | OBJ2 | WD Cart traverse time | FLOAT | RW | 0.02...500
47 | S4 | OBJ2 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
47 | S5 | OBJ2 | Sync wait timeout | FLOAT | RW | 0.02...500
47 | S6 | OBJ2 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
47 | S7 | OBJ2 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
47 | S8 | OBJ2 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
47 | S9 | OBJ2 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
47 | S10 | OBJ2 | Control Termination Timeout | FLOAT | RW | 0.02...500
47 | O1 | OBJ2 | Object2 Status Open | SIGNAL_OUT | RW | 0...4294967295
47 | O2 | OBJ2 | Object2 Status Closed | SIGNAL_OUT | RW | 0...4294967295
47 | O3 | OBJ2 | Object2 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
47 | O4 | OBJ2 | Object2 Status Bad | SIGNAL_OUT | RW | 0...4294967295
47 | O5 | OBJ2 | Object2 Open Command | SIGNAL_OUT | RW | 0...4294967295
47 | O6 | OBJ2 | Object2 Close Command | SIGNAL_OUT | RW | 0...4294967295
47 | O7 | OBJ2 | Object2 Open Request | SIGNAL_OUT | RW | 0...4294967295
47 | O8 | OBJ2 | Object2 Close Request | SIGNAL_OUT | RW | 0...4294967295
47 | O9 | OBJ2 | Object2 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
47 | O10 | OBJ2 | Object2 No sync wait | SIGNAL_OUT | RW | 0...4294967295
47 | O11 | OBJ2 | Object2 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
47 | O12 | OBJ2 | Object2 No sync fail | SIGNAL_OUT | RW | 0...4294967295
47 | O13 | OBJ2 | Object2 Open timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O14 | OBJ2 | Object2 Close timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O15 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O16 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O17 | OBJ2 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
47 | S11 | OBJ2 | EventMaskLo | UINT32 | RW | 0...4294967295
47 | S12 | OBJ2 | EventMaskHi | UINT32 | RW | 0...4294967295
47 | I4 | OBJ2 | Newest Register | UINT32 | R | 0...12
47 | I5 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I6 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I7 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I8 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I9 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I10 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I11 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I12 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I13 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I14 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I15 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I16 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I17 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I18 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I19 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I20 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I21 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I22 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I23 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I24 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I25 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I26 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I27 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I28 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I29 | OBJ2 | Open requests | UINT32 | R | 0...4294967295
47 | I30 | OBJ2 | Close requests | UINT32 | R | 0...4294967295
47 | I31 | OBJ2 | Open requests failed | UINT32 | R | 0...4294967295
47 | I32 | OBJ2 | Close requests failed | UINT32 | R | 0...4294967295
47 | S13 | OBJ2 | Clear statistics | UINT32 | W | 0=-;1=Clear
48 | S1 | OBJ3 | Object3 mode | UINT32 | RW | 0=Disabled;1=Activated
48 | I1 | OBJ3 | Object3 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I2 | OBJ3 | Object3 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
48 | I3 | OBJ3 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | S2 | OBJ3 | Breaker traverse time | FLOAT | RW | 0.02...500
48 | S3 | OBJ3 | WD Cart traverse time | FLOAT | RW | 0.02...500
48 | S4 | OBJ3 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
48 | S5 | OBJ3 | Sync wait timeout | FLOAT | RW | 0.02...500
48 | S6 | OBJ3 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
48 | S7 | OBJ3 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
48 | S8 | OBJ3 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
48 | S9 | OBJ3 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
48 | S10 | OBJ3 | Control Termination Timeout | FLOAT | RW | 0.02...500
48 | O1 | OBJ3 | Object3 Status Open | SIGNAL_OUT | RW | 0...4294967295
48 | O2 | OBJ3 | Object3 Status Closed | SIGNAL_OUT | RW | 0...4294967295
48 | O3 | OBJ3 | Object3 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
48 | O4 | OBJ3 | Object3 Status Bad | SIGNAL_OUT | RW | 0...4294967295
48 | O5 | OBJ3 | Object3 Open Command | SIGNAL_OUT | RW | 0...4294967295
48 | O6 | OBJ3 | Object3 Close Command | SIGNAL_OUT | RW | 0...4294967295
48 | O7 | OBJ3 | Object3 Open Request | SIGNAL_OUT | RW | 0...4294967295
48 | O8 | OBJ3 | Object3 Close Request | SIGNAL_OUT | RW | 0...4294967295
48 | O9 | OBJ3 | Object3 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
48 | O10 | OBJ3 | Object3 No sync wait | SIGNAL_OUT | RW | 0...4294967295
48 | O11 | OBJ3 | Object3 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
48 | O12 | OBJ3 | Object3 No sync fail | SIGNAL_OUT | RW | 0...4294967295
48 | O13 | OBJ3 | Object3 Open timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O14 | OBJ3 | Object3 Close timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O15 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O16 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O17 | OBJ3 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
48 | S11 | OBJ3 | EventMaskLo | UINT32 | RW | 0...4294967295
48 | S12 | OBJ3 | EventMaskHi | UINT32 | RW | 0...4294967295
48 | I4 | OBJ3 | Newest Register | UINT32 | R | 0...12
48 | I5 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I6 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I7 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I8 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I9 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I10 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I11 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I12 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I13 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I14 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I15 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I16 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I17 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I18 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I19 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I20 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I21 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I22 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I23 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I24 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I25 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I26 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I27 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I28 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I29 | OBJ3 | Open requests | UINT32 | R | 0...4294967295
48 | I30 | OBJ3 | Close requests | UINT32 | R | 0...4294967295
48 | I31 | OBJ3 | Open requests failed | UINT32 | R | 0...4294967295
48 | I32 | OBJ3 | Close requests failed | UINT32 | R | 0...4294967295
48 | S13 | OBJ3 | Clear statistics | UINT32 | W | 0=-;1=Clear
49 | S1 | OBJ4 | Object4 mode | UINT32 | RW | 0=Disabled;1=Activated
49 | I1 | OBJ4 | Object4 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I2 | OBJ4 | Object4 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
49 | I3 | OBJ4 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | S2 | OBJ4 | Breaker traverse time | FLOAT | RW | 0.02...500
49 | S3 | OBJ4 | WD Cart traverse time | FLOAT | RW | 0.02...500
49 | S4 | OBJ4 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
49 | S5 | OBJ4 | Sync wait timeout | FLOAT | RW | 0.02...500
49 | S6 | OBJ4 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
49 | S7 | OBJ4 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
49 | S8 | OBJ4 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
49 | S9 | OBJ4 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
49 | S10 | OBJ4 | Control Termination Timeout | FLOAT | RW | 0.02...500
49 | O1 | OBJ4 | Object4 Status Open | SIGNAL_OUT | RW | 0...4294967295
49 | O2 | OBJ4 | Object4 Status Closed | SIGNAL_OUT | RW | 0...4294967295
49 | O3 | OBJ4 | Object4 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
49 | O4 | OBJ4 | Object4 Status Bad | SIGNAL_OUT | RW | 0...4294967295
49 | O5 | OBJ4 | Object4 Open Command | SIGNAL_OUT | RW | 0...4294967295
49 | O6 | OBJ4 | Object4 Close Command | SIGNAL_OUT | RW | 0...4294967295
49 | O7 | OBJ4 | Object4 Open Request | SIGNAL_OUT | RW | 0...4294967295
49 | O8 | OBJ4 | Object4 Close Request | SIGNAL_OUT | RW | 0...4294967295
49 | O9 | OBJ4 | Object4 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
49 | O10 | OBJ4 | Object4 No sync wait | SIGNAL_OUT | RW | 0...4294967295
49 | O11 | OBJ4 | Object4 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
49 | O12 | OBJ4 | Object4 No sync fail | SIGNAL_OUT | RW | 0...4294967295
49 | O13 | OBJ4 | Object4 Open timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O14 | OBJ4 | Object4 Close timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O15 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O16 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O17 | OBJ4 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
49 | S11 | OBJ4 | EventMaskLo | UINT32 | RW | 0...4294967295
49 | S12 | OBJ4 | EventMaskHi | UINT32 | RW | 0...4294967295
49 | I4 | OBJ4 | Newest Register | UINT32 | R | 0...12
49 | I5 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I6 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I7 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I8 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I9 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I10 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I11 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I12 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I13 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I14 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I15 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I16 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I17 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I18 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I19 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I20 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I21 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I22 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I23 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I24 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I25 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I26 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I27 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I28 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I29 | OBJ4 | Open requests | UINT32 | R | 0...4294967295
49 | I30 | OBJ4 | Close requests | UINT32 | R | 0...4294967295
49 | I31 | OBJ4 | Open requests failed | UINT32 | R | 0...4294967295
49 | I32 | OBJ4 | Close requests failed | UINT32 | R | 0...4294967295
49 | S13 | OBJ4 | Clear statistics | UINT32 | W | 0=-;1=Clear
50 | S1 | OBJ5 | Object5 mode | UINT32 | RW | 0=Disabled;1=Activated
50 | I1 | OBJ5 | Object5 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I2 | OBJ5 | Object5 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
50 | I3 | OBJ5 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | S2 | OBJ5 | Breaker traverse time | FLOAT | RW | 0.02...500
50 | S3 | OBJ5 | WD Cart traverse time | FLOAT | RW | 0.02...500
50 | S4 | OBJ5 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
50 | S5 | OBJ5 | Sync wait timeout | FLOAT | RW | 0.02...500
50 | S6 | OBJ5 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
50 | S7 | OBJ5 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
50 | S8 | OBJ5 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
50 | S9 | OBJ5 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
50 | S10 | OBJ5 | Control Termination Timeout | FLOAT | RW | 0.02...500
50 | O1 | OBJ5 | Object5 Status Open | SIGNAL_OUT | RW | 0...4294967295
50 | O2 | OBJ5 | Object5 Status Closed | SIGNAL_OUT | RW | 0...4294967295
50 | O3 | OBJ5 | Object5 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
50 | O4 | OBJ5 | Object5 Status Bad | SIGNAL_OUT | RW | 0...4294967295
50 | O5 | OBJ5 | Object5 Open Command | SIGNAL_OUT | RW | 0...4294967295
50 | O6 | OBJ5 | Object5 Close Command | SIGNAL_OUT | RW | 0...4294967295
50 | O7 | OBJ5 | Object5 Open Request | SIGNAL_OUT | RW | 0...4294967295
50 | O8 | OBJ5 | Object5 Close Request | SIGNAL_OUT | RW | 0...4294967295
50 | O9 | OBJ5 | Object5 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
50 | O10 | OBJ5 | Object5 No sync wait | SIGNAL_OUT | RW | 0...4294967295
50 | O11 | OBJ5 | Object5 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
50 | O12 | OBJ5 | Object5 No sync fail | SIGNAL_OUT | RW | 0...4294967295
50 | O13 | OBJ5 | Object5 Open timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O14 | OBJ5 | Object5 Close timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O15 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O16 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O17 | OBJ5 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
50 | S11 | OBJ5 | EventMaskLo | UINT32 | RW | 0...4294967295
50 | S12 | OBJ5 | EventMaskHi | UINT32 | RW | 0...4294967295
50 | I4 | OBJ5 | Newest Register | UINT32 | R | 0...12
50 | I5 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I6 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I7 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I8 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I9 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I10 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I11 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I12 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I13 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I14 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I15 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I16 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I17 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I18 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I19 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I20 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I21 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I22 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I23 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I24 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I25 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I26 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I27 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I28 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I29 | OBJ5 | Open requests | UINT32 | R | 0...4294967295
50 | I30 | OBJ5 | Close requests | UINT32 | R | 0...4294967295
50 | I31 | OBJ5 | Open requests failed | UINT32 | R | 0...4294967295
50 | I32 | OBJ5 | Close requests failed | UINT32 | R | 0...4294967295
50 | S13 | OBJ5 | Clear statistics | UINT32 | W | 0=-;1=Clear
150 | S1 | OBJ6 | Object6 mode | UINT32 | RW | 0=Disabled;1=Activated
150 | I1 | OBJ6 | Object6 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I2 | OBJ6 | Object6 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
150 | I3 | OBJ6 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | S2 | OBJ6 | Breaker traverse time | FLOAT | RW | 0.02...500
150 | S3 | OBJ6 | WD Cart traverse time | FLOAT | RW | 0.02...500
150 | S4 | OBJ6 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
150 | S5 | OBJ6 | Sync wait timeout | FLOAT | RW | 0.02...500
150 | S6 | OBJ6 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
150 | S7 | OBJ6 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
150 | S8 | OBJ6 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
150 | S9 | OBJ6 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
150 | S10 | OBJ6 | Control Termination Timeout | FLOAT | RW | 0.02...500
150 | O1 | OBJ6 | Object6 Status Open | SIGNAL_OUT | RW | 0...4294967295
150 | O2 | OBJ6 | Object6 Status Closed | SIGNAL_OUT | RW | 0...4294967295
150 | O3 | OBJ6 | Object6 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
150 | O4 | OBJ6 | Object6 Status Bad | SIGNAL_OUT | RW | 0...4294967295
150 | O5 | OBJ6 | Object6 Open Command | SIGNAL_OUT | RW | 0...4294967295
150 | O6 | OBJ6 | Object6 Close Command | SIGNAL_OUT | RW | 0...4294967295
150 | O7 | OBJ6 | Object6 Open Request | SIGNAL_OUT | RW | 0...4294967295
150 | O8 | OBJ6 | Object6 Close Request | SIGNAL_OUT | RW | 0...4294967295
150 | O9 | OBJ6 | Object6 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
150 | O10 | OBJ6 | Object6 No sync wait | SIGNAL_OUT | RW | 0...4294967295
150 | O11 | OBJ6 | Object6 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
150 | O12 | OBJ6 | Object6 No sync fail | SIGNAL_OUT | RW | 0...4294967295
150 | O13 | OBJ6 | Object6 Open timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O14 | OBJ6 | Object6 Close timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O15 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O16 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O17 | OBJ6 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
150 | S11 | OBJ6 | EventMaskLo | UINT32 | RW | 0...4294967295
150 | S12 | OBJ6 | EventMaskHi | UINT32 | RW | 0...4294967295
150 | I4 | OBJ6 | Newest Register | UINT32 | R | 0...12
150 | I5 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I6 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I7 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I8 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I9 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I10 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I11 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I12 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I13 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I14 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I15 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I16 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I17 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I18 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I19 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I20 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I21 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I22 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I23 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I24 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I25 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I26 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I27 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I28 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I29 | OBJ6 | Open requests | UINT32 | R | 0...4294967295
150 | I30 | OBJ6 | Close requests | UINT32 | R | 0...4294967295
150 | I31 | OBJ6 | Open requests failed | UINT32 | R | 0...4294967295
150 | I32 | OBJ6 | Close requests failed | UINT32 | R | 0...4294967295
150 | S13 | OBJ6 | Clear statistics | UINT32 | W | 0=-;1=Clear
151 | S1 | OBJ7 | Object7 mode | UINT32 | RW | 0=Disabled;1=Activated
151 | I1 | OBJ7 | Object7 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I2 | OBJ7 | Object7 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
151 | I3 | OBJ7 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | S2 | OBJ7 | Breaker traverse time | FLOAT | RW | 0.02...500
151 | S3 | OBJ7 | WD Cart traverse time | FLOAT | RW | 0.02...500
151 | S4 | OBJ7 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
151 | S5 | OBJ7 | Sync wait timeout | FLOAT | RW | 0.02...500
151 | S6 | OBJ7 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
151 | S7 | OBJ7 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
151 | S8 | OBJ7 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
151 | S9 | OBJ7 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
151 | S10 | OBJ7 | Control Termination Timeout | FLOAT | RW | 0.02...500
151 | O1 | OBJ7 | Object7 Status Open | SIGNAL_OUT | RW | 0...4294967295
151 | O2 | OBJ7 | Object7 Status Closed | SIGNAL_OUT | RW | 0...4294967295
151 | O3 | OBJ7 | Object7 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
151 | O4 | OBJ7 | Object7 Status Bad | SIGNAL_OUT | RW | 0...4294967295
151 | O5 | OBJ7 | Object7 Open Command | SIGNAL_OUT | RW | 0...4294967295
151 | O6 | OBJ7 | Object7 Close Command | SIGNAL_OUT | RW | 0...4294967295
151 | O7 | OBJ7 | Object7 Open Request | SIGNAL_OUT | RW | 0...4294967295
151 | O8 | OBJ7 | Object7 Close Request | SIGNAL_OUT | RW | 0...4294967295
151 | O9 | OBJ7 | Object7 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
151 | O10 | OBJ7 | Object7 No sync wait | SIGNAL_OUT | RW | 0...4294967295
151 | O11 | OBJ7 | Object7 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
151 | O12 | OBJ7 | Object7 No sync fail | SIGNAL_OUT | RW | 0...4294967295
151 | O13 | OBJ7 | Object7 Open timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O14 | OBJ7 | Object7 Close timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O15 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O16 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O17 | OBJ7 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
151 | S11 | OBJ7 | EventMaskLo | UINT32 | RW | 0...4294967295
151 | S12 | OBJ7 | EventMaskHi | UINT32 | RW | 0...4294967295
151 | I4 | OBJ7 | Newest Register | UINT32 | R | 0...12
151 | I5 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I6 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I7 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I8 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I9 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I10 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I11 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I12 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I13 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I14 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I15 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I16 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I17 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I18 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I19 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I20 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I21 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I22 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I23 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I24 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I25 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I26 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I27 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I28 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I29 | OBJ7 | Open requests | UINT32 | R | 0...4294967295
151 | I30 | OBJ7 | Close requests | UINT32 | R | 0...4294967295
151 | I31 | OBJ7 | Open requests failed | UINT32 | R | 0...4294967295
151 | I32 | OBJ7 | Close requests failed | UINT32 | R | 0...4294967295
151 | S13 | OBJ7 | Clear statistics | UINT32 | W | 0=-;1=Clear
152 | S1 | OBJ8 | Object8 mode | UINT32 | RW | 0=Disabled;1=Activated
152 | I1 | OBJ8 | Object8 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I2 | OBJ8 | Object8 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
152 | I3 | OBJ8 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | S2 | OBJ8 | Breaker traverse time | FLOAT | RW | 0.02...500
152 | S3 | OBJ8 | WD Cart traverse time | FLOAT | RW | 0.02...500
152 | S4 | OBJ8 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
152 | S5 | OBJ8 | Sync wait timeout | FLOAT | RW | 0.02...500
152 | S6 | OBJ8 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
152 | S7 | OBJ8 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
152 | S8 | OBJ8 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
152 | S9 | OBJ8 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
152 | S10 | OBJ8 | Control Termination Timeout | FLOAT | RW | 0.02...500
152 | O1 | OBJ8 | Object8 Status Open | SIGNAL_OUT | RW | 0...4294967295
152 | O2 | OBJ8 | Object8 Status Closed | SIGNAL_OUT | RW | 0...4294967295
152 | O3 | OBJ8 | Object8 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
152 | O4 | OBJ8 | Object8 Status Bad | SIGNAL_OUT | RW | 0...4294967295
152 | O5 | OBJ8 | Object8 Open Command | SIGNAL_OUT | RW | 0...4294967295
152 | O6 | OBJ8 | Object8 Close Command | SIGNAL_OUT | RW | 0...4294967295
152 | O7 | OBJ8 | Object8 Open Request | SIGNAL_OUT | RW | 0...4294967295
152 | O8 | OBJ8 | Object8 Close Request | SIGNAL_OUT | RW | 0...4294967295
152 | O9 | OBJ8 | Object8 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
152 | O10 | OBJ8 | Object8 No sync wait | SIGNAL_OUT | RW | 0...4294967295
152 | O11 | OBJ8 | Object8 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
152 | O12 | OBJ8 | Object8 No sync fail | SIGNAL_OUT | RW | 0...4294967295
152 | O13 | OBJ8 | Object8 Open timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O14 | OBJ8 | Object8 Close timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O15 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O16 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O17 | OBJ8 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
152 | S11 | OBJ8 | EventMaskLo | UINT32 | RW | 0...4294967295
152 | S12 | OBJ8 | EventMaskHi | UINT32 | RW | 0...4294967295
152 | I4 | OBJ8 | Newest Register | UINT32 | R | 0...12
152 | I5 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I6 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I7 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I8 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I9 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I10 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I11 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I12 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I13 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I14 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I15 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I16 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I17 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I18 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I19 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I20 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I21 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I22 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I23 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I24 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I25 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I26 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I27 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I28 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I29 | OBJ8 | Open requests | UINT32 | R | 0...4294967295
152 | I30 | OBJ8 | Close requests | UINT32 | R | 0...4294967295
152 | I31 | OBJ8 | Open requests failed | UINT32 | R | 0...4294967295
152 | I32 | OBJ8 | Close requests failed | UINT32 | R | 0...4294967295
152 | S13 | OBJ8 | Clear statistics | UINT32 | W | 0=-;1=Clear
153 | S1 | OBJ9 | Object9 mode | UINT32 | RW | 0=Disabled;1=Activated
153 | I1 | OBJ9 | Object9 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I2 | OBJ9 | Object9 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
153 | I3 | OBJ9 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | S2 | OBJ9 | Breaker traverse time | FLOAT | RW | 0.02...500
153 | S3 | OBJ9 | WD Cart traverse time | FLOAT | RW | 0.02...500
153 | S4 | OBJ9 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
153 | S5 | OBJ9 | Sync wait timeout | FLOAT | RW | 0.02...500
153 | S6 | OBJ9 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
153 | S7 | OBJ9 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
153 | S8 | OBJ9 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
153 | S9 | OBJ9 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
153 | S10 | OBJ9 | Control Termination Timeout | FLOAT | RW | 0.02...500
153 | O1 | OBJ9 | Object9 Status Open | SIGNAL_OUT | RW | 0...4294967295
153 | O2 | OBJ9 | Object9 Status Closed | SIGNAL_OUT | RW | 0...4294967295
153 | O3 | OBJ9 | Object9 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
153 | O4 | OBJ9 | Object9 Status Bad | SIGNAL_OUT | RW | 0...4294967295
153 | O5 | OBJ9 | Object9 Open Command | SIGNAL_OUT | RW | 0...4294967295
153 | O6 | OBJ9 | Object9 Close Command | SIGNAL_OUT | RW | 0...4294967295
153 | O7 | OBJ9 | Object9 Open Request | SIGNAL_OUT | RW | 0...4294967295
153 | O8 | OBJ9 | Object9 Close Request | SIGNAL_OUT | RW | 0...4294967295
153 | O9 | OBJ9 | Object9 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
153 | O10 | OBJ9 | Object9 No sync wait | SIGNAL_OUT | RW | 0...4294967295
153 | O11 | OBJ9 | Object9 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
153 | O12 | OBJ9 | Object9 No sync fail | SIGNAL_OUT | RW | 0...4294967295
153 | O13 | OBJ9 | Object9 Open timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O14 | OBJ9 | Object9 Close timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O15 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O16 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O17 | OBJ9 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
153 | S11 | OBJ9 | EventMaskLo | UINT32 | RW | 0...4294967295
153 | S12 | OBJ9 | EventMaskHi | UINT32 | RW | 0...4294967295
153 | I4 | OBJ9 | Newest Register | UINT32 | R | 0...12
153 | I5 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I6 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I7 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I8 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I9 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I10 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I11 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I12 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I13 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I14 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I15 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I16 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I17 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I18 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I19 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I20 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I21 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I22 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I23 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I24 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I25 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I26 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I27 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I28 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I29 | OBJ9 | Open requests | UINT32 | R | 0...4294967295
153 | I30 | OBJ9 | Close requests | UINT32 | R | 0...4294967295
153 | I31 | OBJ9 | Open requests failed | UINT32 | R | 0...4294967295
153 | I32 | OBJ9 | Close requests failed | UINT32 | R | 0...4294967295
153 | S13 | OBJ9 | Clear statistics | UINT32 | W | 0=-;1=Clear
154 | S1 | OBJ10 | Object10 mode | UINT32 | RW | 0=Disabled;1=Activated
154 | I1 | OBJ10 | Object10 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I2 | OBJ10 | Object10 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
154 | I3 | OBJ10 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | S2 | OBJ10 | Breaker traverse time | FLOAT | RW | 0.02...500
154 | S3 | OBJ10 | WD Cart traverse time | FLOAT | RW | 0.02...500
154 | S4 | OBJ10 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
154 | S5 | OBJ10 | Sync wait timeout | FLOAT | RW | 0.02...500
154 | S6 | OBJ10 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
154 | S7 | OBJ10 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
154 | S8 | OBJ10 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
154 | S9 | OBJ10 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
154 | S10 | OBJ10 | Control Termination Timeout | FLOAT | RW | 0.02...500
154 | O1 | OBJ10 | Object10 Status Open | SIGNAL_OUT | RW | 0...4294967295
154 | O2 | OBJ10 | Object10 Status Closed | SIGNAL_OUT | RW | 0...4294967295
154 | O3 | OBJ10 | Object10 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
154 | O4 | OBJ10 | Object10 Status Bad | SIGNAL_OUT | RW | 0...4294967295
154 | O5 | OBJ10 | Object10 Open Command | SIGNAL_OUT | RW | 0...4294967295
154 | O6 | OBJ10 | Object10 Close Command | SIGNAL_OUT | RW | 0...4294967295
154 | O7 | OBJ10 | Object10 Open Request | SIGNAL_OUT | RW | 0...4294967295
154 | O8 | OBJ10 | Object10 Close Request | SIGNAL_OUT | RW | 0...4294967295
154 | O9 | OBJ10 | Object10 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
154 | O10 | OBJ10 | Object10 No sync wait | SIGNAL_OUT | RW | 0...4294967295
154 | O11 | OBJ10 | Object10 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
154 | O12 | OBJ10 | Object10 No sync fail | SIGNAL_OUT | RW | 0...4294967295
154 | O13 | OBJ10 | Object10 Open timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O14 | OBJ10 | Object10 Close timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O15 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O16 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O17 | OBJ10 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
154 | S11 | OBJ10 | EventMaskLo | UINT32 | RW | 0...4294967295
154 | S12 | OBJ10 | EventMaskHi | UINT32 | RW | 0...4294967295
154 | I4 | OBJ10 | Newest Register | UINT32 | R | 0...12
154 | I5 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I6 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I7 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I8 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I9 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I10 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I11 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I12 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I13 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I14 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I15 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I16 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I17 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I18 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I19 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I20 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I21 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I22 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I23 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I24 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I25 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I26 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I27 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I28 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I29 | OBJ10 | Open requests | UINT32 | R | 0...4294967295
154 | I30 | OBJ10 | Close requests | UINT32 | R | 0...4294967295
154 | I31 | OBJ10 | Open requests failed | UINT32 | R | 0...4294967295
154 | I32 | OBJ10 | Close requests failed | UINT32 | R | 0...4294967295
154 | S13 | OBJ10 | Clear statistics | UINT32 | W | 0=-;1=Clear
104 | S1 | CIN1 | Indicator 1 mode | UINT32 | RW | 0=Disabled;1=Activated
104 | S2 | CIN1 | Ind.1 traverse time | FLOAT | RW | 0.02...500
104 | I1 | CIN1 | Ind.1 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
105 | S1 | CIN2 | Indicator 2 mode | UINT32 | RW | 0=Disabled;1=Activated
105 | S2 | CIN2 | Ind.2 traverse time | FLOAT | RW | 0.02...500
105 | I1 | CIN2 | Ind.2 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
106 | S1 | CIN3 | Indicator 3 mode | UINT32 | RW | 0=Disabled;1=Activated
106 | S2 | CIN3 | Ind.3 traverse time | FLOAT | RW | 0.02...500
106 | I1 | CIN3 | Ind.3 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
107 | S1 | CIN4 | Indicator 4 mode | UINT32 | RW | 0=Disabled;1=Activated
107 | S2 | CIN4 | Ind.4 traverse time | FLOAT | RW | 0.02...500
107 | I1 | CIN4 | Ind.4 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
108 | S1 | CIN5 | Indicator 5 mode | UINT32 | RW | 0=Disabled;1=Activated
108 | S2 | CIN5 | Ind.5 traverse time | FLOAT | RW | 0.02...500
108 | I1 | CIN5 | Ind.5 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
63 | S1 | AR1 | Auto-recloser [79] Mode | UINT32 | RW | 0=Disabled;1=Activated
63 | V1 | AR1 | AR Status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear
63 | V2 | AR1 | Timer active | UINT32 | R | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
63 | I1 | AR1 | AR Timer value | FLOAT | R | 0...1800
63 | I2 | AR1 | AR Started | UINT32 | R | 0...4294967295
63 | I3 | AR1 | Shot 1 Started | UINT32 | R | 0...4294967295
63 | I4 | AR1 | Shot 2 Started | UINT32 | R | 0...4294967295
63 | I5 | AR1 | Shot 3 Started | UINT32 | R | 0...4294967295
63 | I6 | AR1 | Shot 4 Started | UINT32 | R | 0...4294967295
63 | I7 | AR1 | Shot 5 Started | UINT32 | R | 0...4294967295
63 | I8 | AR1 | Shot 1 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I9 | AR1 | Shot 2 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I10 | AR1 | Shot 3 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I11 | AR1 | Shot 4 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I12 | AR1 | Shot 5 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I13 | AR1 | Shot 1 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I14 | AR1 | Shot 2 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I15 | AR1 | Shot 3 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I16 | AR1 | Shot 4 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I17 | AR1 | Shot 5 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I18 | AR1 | Shot 1 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I19 | AR1 | Shot 2 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I20 | AR1 | Shot 3 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I21 | AR1 | Shot 4 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I22 | AR1 | Shot 5 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I23 | AR1 | Shot 1 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I24 | AR1 | Shot 2 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I25 | AR1 | Shot 3 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I26 | AR1 | Shot 4 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I27 | AR1 | Shot 5 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I28 | AR1 | Shot 1 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I29 | AR1 | Shot 2 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I30 | AR1 | Shot 3 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I31 | AR1 | Shot 4 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I32 | AR1 | Shot 5 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I33 | AR1 | Shots failed | UINT32 | R | 0...4294967295
63 | I34 | AR1 | Shots cleared | UINT32 | R | 0...4294967295
63 | I35 | AR1 | Final trips | UINT32 | R | 0...4294967295
63 | S2 | AR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
63 | S3 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S4 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S5 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S6 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S7 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S8 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S9 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S10 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S11 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S12 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S13 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S14 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S15 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S16 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S17 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S18 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S19 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S20 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S21 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S22 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S23 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S24 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S25 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S26 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S27 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S28 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S29 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S30 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S31 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S32 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S33 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S34 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S35 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S36 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S37 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S38 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S39 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S40 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S41 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S42 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S43 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S44 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S45 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S46 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S47 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S48 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S49 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S50 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S51 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S52 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S53 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S54 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S55 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S56 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S57 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S58 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S59 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S60 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S61 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S62 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S63 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S64 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S65 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S66 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S67 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S68 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S69 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S70 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S71 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S72 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S73 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S74 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S75 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S76 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S77 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S78 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S79 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S80 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S81 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S82 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S83 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S84 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S85 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S86 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S87 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S88 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S89 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S90 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S91 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S92 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S93 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S94 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S95 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S96 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S97 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S98 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S99 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S100 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S101 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S102 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S103 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S104 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S105 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S106 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S107 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S108 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S109 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S110 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S111 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S112 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S113 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S114 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S115 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S116 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S117 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S118 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S119 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S120 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled