63 | S121 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S122 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S123 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S124 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S125 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S126 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S127 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S128 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S129 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S130 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S131 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S132 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S133 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S134 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S135 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S136 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S137 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S138 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S139 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S140 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S141 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S142 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S143 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S144 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S145 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S146 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S147 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S148 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S149 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S150 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S151 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S152 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S153 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S154 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S155 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S156 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S157 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S158 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S159 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S160 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S161 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S162 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S163 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S164 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S165 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S166 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S167 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S168 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S169 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S170 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S171 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S172 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S173 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S174 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S175 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S176 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S177 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S178 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S179 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S180 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S181 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S182 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S183 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S184 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S185 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S186 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S187 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S188 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S189 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S190 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S191 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S192 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S193 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S194 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S195 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S196 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S197 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S198 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S199 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S200 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S201 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S202 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S203 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S204 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S205 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S206 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S207 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S208 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S209 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S210 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S211 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S212 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S213 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S214 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S215 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S216 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S217 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S218 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S219 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S220 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S221 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S222 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S223 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S224 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S225 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S226 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S227 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S228 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S229 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S230 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S231 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S232 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S233 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S234 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S235 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S236 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S237 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S238 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S239 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S240 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S241 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S242 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S243 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S244 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S245 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S246 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S247 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S248 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S249 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S250 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S251 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S252 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S253 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S254 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S255 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S256 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S257 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S258 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S259 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S260 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S261 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S262 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S263 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S264 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S265 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S266 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S267 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S268 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S269 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S270 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S271 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S272 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S273 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S274 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S275 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S276 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S277 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S278 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S279 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S280 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S281 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S282 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S283 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S284 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S285 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S286 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S287 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S288 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S289 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S290 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S291 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S292 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S293 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S294 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S295 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S296 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S297 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S298 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S299 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S300 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S301 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S302 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S303 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S304 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S305 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S306 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S307 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S308 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S309 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S310 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S311 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S312 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S313 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S314 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S315 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S316 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S317 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S318 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S319 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S320 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S321 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S322 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S323 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S324 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S325 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S326 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S327 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S328 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S329 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S330 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S331 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S332 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S333 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S334 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S335 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S336 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S337 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S338 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S339 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S340 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S341 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S342 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S343 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S344 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S345 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S346 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S347 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S348 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S349 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S350 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S351 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S352 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S353 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S354 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S355 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S356 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S357 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S358 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S359 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S360 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S361 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S362 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S363 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S364 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S365 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S366 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S367 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S368 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S369 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S370 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S371 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S372 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S373 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S374 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S375 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S376 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S377 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S378 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S379 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S380 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S381 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S382 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S383 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S384 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S385 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S386 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S387 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S388 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S389 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S390 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S391 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S392 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S393 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S394 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S395 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S396 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S397 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S398 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S399 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S400 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S401 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S402 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S403 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S404 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S405 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S406 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S407 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S408 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S409 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S410 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S411 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S412 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S413 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S414 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S415 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S416 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S417 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S418 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S419 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S420 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S421 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S422 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S423 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S424 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S425 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S426 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S427 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S428 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S429 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S430 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S431 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S432 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S433 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S434 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S435 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S436 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S437 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S438 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S439 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S440 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S441 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S442 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S443 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S444 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S445 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S446 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S447 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S448 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S449 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S450 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S451 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S452 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S453 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S454 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S455 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S456 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S457 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S458 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S459 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S460 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S461 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S462 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S463 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S464 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S465 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S466 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S467 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S468 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S469 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S470 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S471 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S472 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S473 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S474 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S475 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S476 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S477 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S478 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S479 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S480 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S481 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S482 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S483 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S484 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S485 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S486 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S487 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S488 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S489 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S490 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S491 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S492 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S493 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S494 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S495 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S496 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S497 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S498 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S499 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S500 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S501 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S502 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S503 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S504 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S505 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S506 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S507 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S508 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S509 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S510 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S511 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S512 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S513 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S514 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S515 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S516 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S517 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S518 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S519 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S520 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S521 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S522 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S523 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S524 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S525 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S526 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S527 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S528 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S529 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S530 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S531 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S532 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S533 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S534 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S535 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S536 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S537 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S538 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S539 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S540 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S541 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S542 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S543 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S544 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S545 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S546 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S547 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S548 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S549 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S550 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S551 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S552 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S553 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S554 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S555 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S556 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S557 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S558 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S559 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S560 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S561 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S562 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S563 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S564 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S565 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S566 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S567 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S568 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S569 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S570 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S571 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S572 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S573 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S574 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S575 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S576 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S577 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S578 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S579 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S580 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S581 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S582 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S583 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S584 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S585 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S586 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S587 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S588 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S589 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S590 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S591 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S592 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S593 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S594 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S595 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S596 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S597 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S598 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S599 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S600 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S601 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S602 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S603 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S604 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S605 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S606 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S607 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S608 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S609 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S610 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S611 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S612 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S613 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S614 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S615 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S616 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S617 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S618 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S619 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S620 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S621 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S622 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S623 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S624 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S625 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S626 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S627 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S628 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S629 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S630 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S631 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S632 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S633 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S634 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S635 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S636 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S637 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S638 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S639 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S640 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S641 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S642 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S643 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S644 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S645 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S646 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S647 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S648 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S649 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S650 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S651 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S652 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S653 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S654 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S655 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S656 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S657 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S658 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S659 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S660 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S661 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S662 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S663 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S664 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S665 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S666 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S667 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S668 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S669 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S670 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S671 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S672 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S673 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S674 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S675 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S676 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S677 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S678 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S679 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S680 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S681 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S682 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S683 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S684 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S685 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S686 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S687 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S688 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S689 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S690 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S691 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S692 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S693 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S694 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S695 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S696 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S697 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S698 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S699 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S700 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S701 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S702 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S703 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S704 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S705 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S706 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S707 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S708 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S709 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S710 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S711 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S712 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S713 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S714 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S715 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S716 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S717 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S718 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S719 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S720 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S721 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S722 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S723 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S724 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S725 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S726 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S727 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S728 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S729 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S730 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S731 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S732 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S733 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S734 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S735 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S736 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S737 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S738 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S739 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S740 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S741 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S742 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S743 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S744 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S745 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S746 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S747 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S748 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S749 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S750 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S751 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S752 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S753 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S754 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S755 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S756 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S757 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S758 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S759 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S760 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S761 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S762 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S763 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S764 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S765 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S766 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S767 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S768 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S769 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S770 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S771 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S772 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S773 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S774 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S775 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S776 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S777 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S778 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S779 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S780 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S781 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S782 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S783 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S784 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S785 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S786 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S787 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S788 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S789 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S790 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S791 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S792 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S793 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S794 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S795 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S796 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S797 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S798 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S799 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S800 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S801 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S802 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S803 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S804 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S805 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S806 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S807 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S808 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S809 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S810 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S811 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S812 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S813 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S814 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S815 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S816 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S817 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S818 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S819 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S820 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S821 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S822 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S823 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S824 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S825 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S826 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S827 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S828 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S829 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S830 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S831 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S832 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S833 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S834 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S835 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S836 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S837 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S838 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S839 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S840 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S841 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S842 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S843 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S844 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S845 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S846 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S847 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S848 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S849 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S850 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S851 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S852 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S853 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S854 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S855 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S856 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S857 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S858 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S859 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S860 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S861 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S862 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S863 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S864 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S865 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S866 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S867 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S868 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S869 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S870 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S871 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S872 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S873 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S874 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S875 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S876 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S877 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S878 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S879 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S880 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S881 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S882 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S883 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S884 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S885 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S886 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S887 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S888 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S889 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S890 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S891 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S892 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S893 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S894 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S895 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S896 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S897 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S898 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S899 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S900 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S901 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S902 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S903 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S904 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S905 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S906 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S907 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S908 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S909 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S910 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S911 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S912 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S913 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S914 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S915 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S916 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S917 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S918 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S919 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S920 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S921 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S922 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S923 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S924 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S925 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S926 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S927 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S928 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S929 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S930 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S931 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S932 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S933 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S934 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S935 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S936 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S937 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S938 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S939 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S940 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S941 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S942 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S943 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S944 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S945 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S946 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S947 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S948 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S949 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S950 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S951 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S952 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S953 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S954 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S955 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S956 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S957 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S958 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S959 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S960 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S961 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S962 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S963 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S964 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S965 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S966 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S967 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S968 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S969 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S970 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S971 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S972 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S973 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S974 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S975 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S976 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S977 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S978 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S979 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S980 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S981 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S982 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S983 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S984 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S985 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S986 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S987 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S988 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S989 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S990 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S991 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S992 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S993 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S994 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S995 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S996 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S997 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S998 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S999 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1000 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1001 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1002 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1003 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1004 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1005 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1006 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1007 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1008 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1009 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1010 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1011 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1012 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1013 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1014 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1015 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1016 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1017 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1018 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1019 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1020 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1021 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1022 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1023 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1024 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1025 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1026 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1027 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1028 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1029 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1030 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1031 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1032 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1033 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1034 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1035 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1036 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1037 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1038 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1039 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1040 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1041 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1042 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1043 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1044 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1045 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1046 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1047 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1048 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1049 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1050 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1051 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1052 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1053 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1054 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1055 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1056 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1057 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1058 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1059 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1060 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1061 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1062 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1063 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1064 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1065 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1066 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1067 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1068 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1069 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1070 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1071 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1072 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1073 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1074 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1075 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1076 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1077 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1078 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1079 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1080 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1081 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1082 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1083 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1084 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1085 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1086 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1087 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1088 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1089 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1090 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1091 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1092 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1093 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1094 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1095 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1096 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1097 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1098 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1099 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1100 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1101 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1102 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1103 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1104 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1105 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1106 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1107 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1108 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1109 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1110 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1111 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1112 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1113 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1114 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1115 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1116 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1117 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1118 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1119 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1120 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1121 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1122 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1123 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1124 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1125 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1126 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1127 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1128 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1129 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1130 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1131 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1132 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1133 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1134 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1135 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1136 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1137 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1138 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1139 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1140 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1141 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1142 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1143 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1144 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1145 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1146 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1147 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1148 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1149 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1150 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1151 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1152 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1153 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1154 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1155 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1156 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1157 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1158 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1159 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1160 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1161 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1162 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1163 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1164 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1165 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1166 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1167 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1168 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1169 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1170 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1171 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1172 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1173 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1174 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1175 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1176 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1177 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1178 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1179 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1180 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1181 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1182 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1183 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1184 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1185 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1186 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1187 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1188 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1189 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1190 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1191 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1192 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1193 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1194 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1195 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1196 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1197 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1198 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1199 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1200 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1201 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1202 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1203 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1204 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1205 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1206 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1207 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1208 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1209 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1210 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1211 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1212 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1213 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1214 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1215 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1216 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1217 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1218 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1219 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1220 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1221 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1222 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1223 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1224 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1225 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1226 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1227 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1228 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1229 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1230 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1231 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1232 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1233 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1234 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1235 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1236 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1237 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1238 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1239 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1240 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1241 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1242 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1243 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1244 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1245 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1246 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1247 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1248 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1249 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1250 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | O1 | AR1 | AR On | SIGNAL_OUT | RW | 0...4294967295
63 | O2 | AR1 | AR Off | SIGNAL_OUT | RW | 0...4294967295
63 | O3 | AR1 | AR In Progress | SIGNAL_OUT | RW | 0...4294967295
63 | O4 | AR1 | AR1 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O5 | AR1 | AR2 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O6 | AR1 | AR3 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O7 | AR1 | AR4 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O8 | AR1 | AR5 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O9 | AR1 | AR Running | SIGNAL_OUT | RW | 0...4294967295
63 | O10 | AR1 | AR Shot 1 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O11 | AR1 | AR Shot 2 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O12 | AR1 | AR Shot 3 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O13 | AR1 | AR Shot 4 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O14 | AR1 | AR Shot 5 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O15 | AR1 | AR Sequence finished | SIGNAL_OUT | RW | 0...4294967295
63 | O16 | AR1 | AR Final Trip | SIGNAL_OUT | RW | 0...4294967295
63 | O17 | AR1 | Dead time on | SIGNAL_OUT | RW | 0...4294967295
63 | O18 | AR1 | ARC time on | SIGNAL_OUT | RW | 0...4294967295
63 | O19 | AR1 | Reclaim time on | SIGNAL_OUT | RW | 0...4294967295
63 | O20 | AR1 | AR Ready | SIGNAL_OUT | RW | 0...4294967295
63 | O21 | AR1 | AR Lockout after successfull sequence | SIGNAL_OUT | RW | 0...4294967295
63 | O22 | AR1 | AR Operation Inhibit | SIGNAL_OUT | RW | 0...4294967295
63 | O23 | AR1 | AR Locked | SIGNAL_OUT | RW | 0...4294967295
63 | I36 | AR1 | Newest Register | UINT32 | R | 0...12
63 | I37 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I38 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I39 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I40 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I41 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I42 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I43 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I44 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I45 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I46 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I47 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I48 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I49 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I50 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I51 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I52 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I53 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I54 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I55 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I56 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I57 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I58 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I59 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I60 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I61 | AR1 | Active time | FLOAT | R | 0...1800
63 | I62 | AR1 | Active time | FLOAT | R | 0...1800
63 | I63 | AR1 | Active time | FLOAT | R | 0...1800
63 | I64 | AR1 | Active time | FLOAT | R | 0...1800
63 | I65 | AR1 | Active time | FLOAT | R | 0...1800
63 | I66 | AR1 | Active time | FLOAT | R | 0...1800
63 | I67 | AR1 | Active time | FLOAT | R | 0...1800
63 | I68 | AR1 | Active time | FLOAT | R | 0...1800
63 | I69 | AR1 | Active time | FLOAT | R | 0...1800
63 | I70 | AR1 | Active time | FLOAT | R | 0...1800
63 | I71 | AR1 | Active time | FLOAT | R | 0...1800
63 | I72 | AR1 | Active time | FLOAT | R | 0...1800
63 | S1251 | AR1 | EventMaskLo | UINT32 | RW | 0...4294967295
63 | S1252 | AR1 | EventMaskHi | UINT32 | RW | 0...4294967295
115 | S1 | VRG1 | Vreg [AVR/90] mode | UINT32 | RW | 0=Disabled;1=Activated
115 | V1 | VRG1 | Vreg settings condition | UINT32 | R | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok
115 | V2 | VRG1 | Vreg condition | UINT32 | R | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on
115 | V3 | VRG1 | Vreg timer active | UINT32 | R | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
115 | I1 | VRG1 | Time left to operation | FLOAT | R | 0...1800
115 | I2 | VRG1 | Voltage now | FLOAT | R | 0...140
115 | I3 | VRG1 | Voltage difference to set target | FLOAT | R | -140...140
115 | I4 | VRG1 | Voltage set now to | FLOAT | R | -50000...50000
115 | I5 | VRG1 | Tap location now (- 0 +) | FLOAT | R | -30...30
115 | I6 | VRG1 | Absolute tap location | FLOAT | R | 0...50
115 | V4 | VRG1 | Tap changer on high border | UINT32 | R | 0=No;1=Yes
115 | V5 | VRG1 | Tap changer on low border | UINT32 | R | 0=No;1=Yes
115 | I7 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual (loc&rem)
115 | V6 | VRG1 | Remote tap control input | UINT32 | RW | 0=Stop;1=Lower;2=Higher
115 | S2 | VRG1 | Control pulselength max | FLOAT | RW | 0...1800
115 | S3 | VRG1 | Control pulselength min | FLOAT | RW | 0...1800
115 | S4 | VRG1 | Min time between pulses | FLOAT | RW | 0...1800
115 | V7 | VRG1 | Tap position ind. Setting | UINT32 | R | 0=Not selected;1=Set Ok;2=Wrong setting;3=Meas.Quality Fault.
115 | I8 | VRG1 | AVR rised voltage | UINT32 | R | 0...4294967295
115 | I9 | VRG1 | AVR reduced voltage | UINT32 | R | 0...4294967295
115 | I10 | VRG1 | AVR control blocked | UINT32 | R | 0...4294967295
115 | I11 | VRG1 | AVR Undervoltage blocked | UINT32 | R | 0...4294967295
115 | I12 | VRG1 | AVR Overcurrent blocked | UINT32 | R | 0...4294967295
115 | S5 | VRG1 | Clear statistics | UINT32 | W | 0=-;1=Clear
115 | S6 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S7 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S8 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S9 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S10 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S11 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S12 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S13 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S14 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S15 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S16 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S17 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S18 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S19 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S20 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S21 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S22 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S23 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S24 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S25 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S26 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S27 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S28 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S29 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S30 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S31 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S32 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S33 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S34 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S35 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S36 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S37 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S38 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S39 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S40 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S41 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S42 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S43 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S44 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S45 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S46 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S47 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S48 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S49 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S50 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S51 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S52 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S53 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S54 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S55 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S56 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S57 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S58 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S59 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S60 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S61 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S62 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S63 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S64 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S65 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S66 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S67 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S68 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S69 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S70 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S71 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S72 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S73 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S74 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S75 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S76 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S77 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S78 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S79 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S80 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S81 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S82 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S83 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S84 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S85 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S86 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S87 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S88 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S89 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S90 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S91 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S92 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S93 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S94 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S95 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S96 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S97 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S98 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S99 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S100 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S101 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S102 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S103 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S104 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S105 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S106 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S107 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S108 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S109 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S110 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S111 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S112 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S113 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S114 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S115 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S116 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S117 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S118 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S119 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S120 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S121 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S122 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S123 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S124 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S125 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S126 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S127 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S128 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S129 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S130 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S131 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S132 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S133 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | I13 | VRG1 | AVR to Manual control | SIGNAL_IN | RW | 0...4294967295
115 | O1 | VRG1 | AVR Raise Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O2 | VRG1 | AVR Lower Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O3 | VRG1 | AVR In manual control | SIGNAL_OUT | RW | 0...4294967295
115 | O4 | VRG1 | AVR U>/< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O5 | VRG1 | AVR U>>/<< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O6 | VRG1 | AVR Outputs blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O7 | VRG1 | AVR Operation blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O8 | VRG1 | AVR Control wait on | SIGNAL_OUT | RW | 0...4294967295
115 | O9 | VRG1 | AVR U< block active | SIGNAL_OUT | RW | 0...4294967295
115 | O10 | VRG1 | AVR I> block active | SIGNAL_OUT | RW | 0...4294967295
115 | O11 | VRG1 | AVR Tap in highlimit | SIGNAL_OUT | RW | 0...4294967295
115 | O12 | VRG1 | AVR Tap in lowlimit | SIGNAL_OUT | RW | 0...4294967295
115 | I14 | VRG1 | Newest Register | UINT32 | R | 0...12
115 | I15 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I16 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I17 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I18 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I19 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I20 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I21 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I22 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I23 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I24 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I25 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I26 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I27 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I28 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I29 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I30 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I31 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I32 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I33 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I34 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I35 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I36 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I37 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I38 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I39 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I40 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I41 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I42 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I43 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I44 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I45 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I46 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I47 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I48 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I49 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I50 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I51 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I52 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I53 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I54 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I55 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I56 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I57 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I58 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I59 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I60 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I61 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I62 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | S134 | VRG1 | EventMaskLo | UINT32 | RW | 0...4294967295
115 | S135 | VRG1 | EventMaskHi | UINT32 | RW | 0...4294967295
135 | S1 | EMON1 | Monitor mode | UINT32 | RW | 0=Disabled;1=Activated
135 | S2 | EMON1 | I> (50) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V1 | EMON1 | I> (50) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S3 | EMON1 | I0> (50N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S4 | EMON1 | I0> (50N) I0input | UINT32 | RW | 0=I01;1=I02;2=I0Calc
135 | V2 | EMON1 | I0> (50N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S5 | EMON1 | Idir> (67) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V3 | EMON1 | Idir> (67) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S6 | EMON1 | I0dir> (67N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S7 | EMON1 | I0dir> (67N) I0input | UINT32 | RW | 0=I01;1=I02
135 | S8 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=select
135 | S9 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V4 | EMON1 | I0dir> (67N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S10 | EMON1 | I0Int> (67NT) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S11 | EMON1 | I0Int> (67NT) I0input | UINT32 | RW | 0=I01;1=I02
135 | V5 | EMON1 | I0Int> (67NT) Monitor condition | UINT32 | R | 0=Normal;1=FLT FW;2=FLT REV
135 | S12 | EMON1 | U< (27) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S13 | EMON1 | U< (27) Measured magnitude | UINT32 | RW | 0=P-P Voltages;1=P-E Voltages
135 | S14 | EMON1 | U< (27) Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
135 | V6 | EMON1 | U< (27) Monitor condition | UINT32 | R | 0=Normal;1=Undervoltage;2=No voltage
135 | S15 | EMON1 | U0> (59N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S16 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=Select
135 | S17 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V7 | EMON1 | U0> (59N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S18 | EMON1 | FL (21FL) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V8 | EMON1 | FL (21FL) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | I1 | EMON1 | I> (50) Alarms | UINT32 | R | 0...4294967295
135 | I2 | EMON1 | I0> (50N) Alarms | UINT32 | R | 0...4294967295
135 | I3 | EMON1 | Idir> (67) Alarms | UINT32 | R | 0...4294967295
135 | I4 | EMON1 | I0dir> (67N) Alarms | UINT32 | R | 0...4294967295
135 | I5 | EMON1 | I0Int> (67) Alarms FWD | UINT32 | R | 0...4294967295
135 | I6 | EMON1 | I0Int> (67) Alarms REV | UINT32 | R | 0...4294967295
135 | I7 | EMON1 | U< (27) Undervoltage Alarms | UINT32 | R | 0...4294967295
135 | I8 | EMON1 | U< (27) No voltage Alarms | UINT32 | R | 0...4294967295
135 | I9 | EMON1 | U0> (59N) Alarms | UINT32 | R | 0...4294967295
135 | I10 | EMON1 | FL (21FL) Triggered | UINT32 | R | 0...4294967295
135 | S19 | EMON1 | Clear statistics | UINT32 | W | 0=-;1=Clear
135 | S20 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S21 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S22 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S23 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S24 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S25 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S26 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S27 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S28 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S29 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S30 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S31 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S32 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S33 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S34 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S35 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S36 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S37 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S38 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S39 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S40 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S41 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S42 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S43 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S44 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S45 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S46 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S47 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S48 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S49 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S50 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S51 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S52 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S53 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S54 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S55 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S56 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S57 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S58 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S59 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S60 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S61 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S62 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S63 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S64 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S65 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S66 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S67 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S68 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S69 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S70 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S71 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S72 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S73 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S74 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S75 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S76 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S77 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S78 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S79 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S80 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S81 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S82 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S83 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S84 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S85 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S86 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S87 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S88 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S89 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S90 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S91 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S92 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S93 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S94 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S95 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S96 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S97 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S98 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S99 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S100 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S101 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S102 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S103 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S104 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S105 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S106 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S107 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S108 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S109 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S110 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S111 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S112 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S113 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S114 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S115 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S116 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S117 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S118 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S119 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S120 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S121 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S122 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S123 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S124 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S125 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S126 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S127 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S128 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S129 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S130 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S131 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S132 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S133 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S134 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S135 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S136 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S137 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S138 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S139 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S140 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S141 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S142 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S143 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S144 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S145 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S146 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S147 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S148 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S149 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S150 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S151 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S152 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S153 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S154 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S155 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S156 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S157 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S158 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S159 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S160 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S161 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S162 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S163 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S164 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S165 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S166 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S167 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S168 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S169 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S170 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S171 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S172 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S173 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S174 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S175 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S176 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S177 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S178 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S179 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S180 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S181 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S182 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S183 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S184 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S185 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S186 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S187 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S188 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S189 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S190 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S191 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S192 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S193 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S194 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S195 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S196 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S197 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S198 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S199 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S200 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S201 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S202 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S203 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S204 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S205 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S206 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S207 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S208 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S209 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S210 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S211 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S212 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S213 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S214 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S215 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S216 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S217 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S218 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S219 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S220 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S221 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S222 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S223 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S224 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S225 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S226 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S227 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | O1 | EMON1 | I> (50) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O2 | EMON1 | I0> (50N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O3 | EMON1 | Idir> (67) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O4 | EMON1 | I0dir> (67N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O5 | EMON1 | I0int> (67NT) Alarm FWD | SIGNAL_OUT | RW | 0...4294967295
135 | O6 | EMON1 | I0int> (67NT) Alarm REV | SIGNAL_OUT | RW | 0...4294967295
135 | O7 | EMON1 | U< (27) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O8 | EMON1 | U< (27) No voltage | SIGNAL_OUT | RW | 0...4294967295
135 | O9 | EMON1 | U0> (59N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O10 | EMON1 | FL (21FL) Triggered | SIGNAL_OUT | RW | 0...4294967295
135 | I11 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I12 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I13 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I14 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I15 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I16 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I17 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I18 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I19 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I20 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I21 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I22 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I23 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I24 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I25 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I26 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I27 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I28 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I29 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I30 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I31 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I32 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I33 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I34 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I35 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I36 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I37 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I38 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I39 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I40 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I41 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I42 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I43 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I44 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I45 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I46 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I47 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I48 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I49 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I50 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I51 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I52 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I53 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I54 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I55 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I56 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I57 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I58 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I59 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I60 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I61 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I62 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I63 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I64 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I65 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I66 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I67 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I68 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I69 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I70 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I71 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I72 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I73 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I74 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I75 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I76 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I77 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I78 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I79 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I80 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I81 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I82 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I83 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I84 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I85 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I86 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I87 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I88 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I89 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I90 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I91 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I92 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I93 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I94 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I95 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I96 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I97 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I98 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I99 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I100 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I101 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I102 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I103 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I104 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I105 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I106 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I107 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I108 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I109 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I110 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I111 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I112 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I113 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I114 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I115 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I116 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I117 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I118 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I119 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I120 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I121 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I122 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I123 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I124 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I125 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I126 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I127 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I128 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I129 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I130 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I131 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I132 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I133 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I134 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I135 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I136 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I137 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I138 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I139 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I140 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I141 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I142 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I143 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I144 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I145 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I146 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I147 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I148 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I149 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I150 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I151 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I152 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I153 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I154 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I155 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I156 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I157 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I158 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I159 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I160 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I161 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I162 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I163 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I164 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I165 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I166 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I167 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I168 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I169 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I170 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I171 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I172 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I173 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I174 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I175 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I176 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I177 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I178 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I179 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I180 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I181 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I182 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I183 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I184 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I185 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I186 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I187 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I188 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I189 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I190 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I191 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I192 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I193 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I194 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I195 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I196 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I197 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I198 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I199 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I200 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I201 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I202 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I203 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I204 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I205 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I206 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I207 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I208 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I209 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I210 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I211 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I212 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I213 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I214 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I215 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I216 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I217 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I218 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I219 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I220 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I221 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I222 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I223 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I224 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I225 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I226 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I227 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I228 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I229 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I230 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I231 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I232 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I233 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I234 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I235 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I236 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I237 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I238 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I239 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I240 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I241 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I242 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I243 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I244 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I245 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I246 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I247 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I248 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I249 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I250 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I251 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I252 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I253 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I254 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I255 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I256 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I257 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I258 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | S228 | EMON1 | EventMaskLo | UINT32 | RW | 0...4294967295
135 | S229 | EMON1 | EventMaskHi | UINT32 | RW | 0...4294967295
143 | O1 | ALARM | ALARM 1 | SIGNAL_IN | RW | 0...4294967295
143 | O2 | ALARM | ALARM 2 | SIGNAL_IN | RW | 0...4294967295
143 | O3 | ALARM | ALARM 3 | SIGNAL_IN | RW | 0...4294967295
143 | O4 | ALARM | ALARM 4 | SIGNAL_IN | RW | 0...4294967295
143 | O5 | ALARM | ALARM 5 | SIGNAL_IN | RW | 0...4294967295
143 | O6 | ALARM | ALARM 6 | SIGNAL_IN | RW | 0...4294967295
143 | O7 | ALARM | ALARM 7 | SIGNAL_IN | RW | 0...4294967295
143 | O8 | ALARM | ALARM 8 | SIGNAL_IN | RW | 0...4294967295
143 | O9 | ALARM | ALARM 9 | SIGNAL_IN | RW | 0...4294967295
143 | O10 | ALARM | ALARM 10 | SIGNAL_IN | RW | 0...4294967295
143 | O11 | ALARM | ALARM 11 | SIGNAL_IN | RW | 0...4294967295
143 | O12 | ALARM | ALARM 12 | SIGNAL_IN | RW | 0...4294967295
143 | O13 | ALARM | ALARM 13 | SIGNAL_IN | RW | 0...4294967295
143 | O14 | ALARM | ALARM 14 | SIGNAL_IN | RW | 0...4294967295
143 | O15 | ALARM | ALARM 15 | SIGNAL_IN | RW | 0...4294967295
143 | O16 | ALARM | ALARM 16 | SIGNAL_IN | RW | 0...4294967295
143 | O17 | ALARM | ALARM 17 | SIGNAL_IN | RW | 0...4294967295
143 | O18 | ALARM | ALARM 18 | SIGNAL_IN | RW | 0...4294967295
143 | O19 | ALARM | ALARM 19 | SIGNAL_IN | RW | 0...4294967295
143 | O20 | ALARM | ALARM 20 | SIGNAL_IN | RW | 0...4294967295
143 | O21 | ALARM | ALARM 21 | SIGNAL_IN | RW | 0...4294967295
143 | O22 | ALARM | ALARM 22 | SIGNAL_IN | RW | 0...4294967295
143 | O23 | ALARM | ALARM 23 | SIGNAL_IN | RW | 0...4294967295
143 | O24 | ALARM | ALARM 24 | SIGNAL_IN | RW | 0...4294967295
143 | O25 | ALARM | ALARM 25 | SIGNAL_IN | RW | 0...4294967295
143 | O26 | ALARM | ALARM 26 | SIGNAL_IN | RW | 0...4294967295
143 | O27 | ALARM | ALARM 27 | SIGNAL_IN | RW | 0...4294967295
143 | O28 | ALARM | ALARM 28 | SIGNAL_IN | RW | 0...4294967295
143 | O29 | ALARM | ALARM 29 | SIGNAL_IN | RW | 0...4294967295
143 | O30 | ALARM | ALARM 30 | SIGNAL_IN | RW | 0...4294967295
143 | O31 | ALARM | ALARM 31 | SIGNAL_IN | RW | 0...4294967295
143 | O32 | ALARM | ALARM 32 | SIGNAL_IN | RW | 0...4294967295
143 | O33 | ALARM | ALARM 33 | SIGNAL_IN | RW | 0...4294967295
143 | O34 | ALARM | ALARM 34 | SIGNAL_IN | RW | 0...4294967295
143 | O35 | ALARM | ALARM 35 | SIGNAL_IN | RW | 0...4294967295
143 | O36 | ALARM | ALARM 36 | SIGNAL_IN | RW | 0...4294967295
143 | O37 | ALARM | ALARM 37 | SIGNAL_IN | RW | 0...4294967295
143 | O38 | ALARM | ALARM 38 | SIGNAL_IN | RW | 0...4294967295
143 | O39 | ALARM | ALARM 39 | SIGNAL_IN | RW | 0...4294967295
143 | O40 | ALARM | ALARM 40 | SIGNAL_IN | RW | 0...4294967295
143 | O41 | ALARM | ALARM 41 | SIGNAL_IN | RW | 0...4294967295
143 | O42 | ALARM | ALARM 42 | SIGNAL_IN | RW | 0...4294967295
143 | O43 | ALARM | ALARM 43 | SIGNAL_IN | RW | 0...4294967295
143 | O44 | ALARM | ALARM 44 | SIGNAL_IN | RW | 0...4294967295
143 | O45 | ALARM | ALARM 45 | SIGNAL_IN | RW | 0...4294967295
143 | O46 | ALARM | ALARM 46 | SIGNAL_IN | RW | 0...4294967295
143 | O47 | ALARM | ALARM 47 | SIGNAL_IN | RW | 0...4294967295
143 | O48 | ALARM | ALARM 48 | SIGNAL_IN | RW | 0...4294967295
143 | O49 | ALARM | ALARM 49 | SIGNAL_IN | RW | 0...4294967295
143 | O50 | ALARM | ALARM 50 | SIGNAL_IN | RW | 0...4294967295
143 | O51 | ALARM | ALARM 51 | SIGNAL_IN | RW | 0...4294967295
143 | O52 | ALARM | ALARM 52 | SIGNAL_IN | RW | 0...4294967295
143 | O53 | ALARM | ALARM 53 | SIGNAL_IN | RW | 0...4294967295
143 | O54 | ALARM | ALARM 54 | SIGNAL_IN | RW | 0...4294967295
143 | O55 | ALARM | ALARM 55 | SIGNAL_IN | RW | 0...4294967295
143 | O56 | ALARM | ALARM 56 | SIGNAL_IN | RW | 0...4294967295
143 | O57 | ALARM | ALARM 57 | SIGNAL_IN | RW | 0...4294967295
143 | O58 | ALARM | ALARM 58 | SIGNAL_IN | RW | 0...4294967295
143 | O59 | ALARM | ALARM 59 | SIGNAL_IN | RW | 0...4294967295
143 | O60 | ALARM | ALARM 60 | SIGNAL_IN | RW | 0...4294967295
143 | O61 | ALARM | ALARM 61 | SIGNAL_IN | RW | 0...4294967295
143 | O62 | ALARM | ALARM 62 | SIGNAL_IN | RW | 0...4294967295
143 | O63 | ALARM | ALARM 63 | SIGNAL_IN | RW | 0...4294967295
143 | O64 | ALARM | ALARM 64 | SIGNAL_IN | RW | 0...4294967295
159 | S1 | ALARM1 | EventMaskLo | UINT32 | RW | 0...4294967295
159 | S2 | ALARM1 | EventMaskHi | UINT32 | RW | 0...4294967295
160 | S1 | ALARM2 | EventMaskLo | UINT32 | RW | 0...4294967295
160 | S2 | ALARM2 | EventMaskHi | UINT32 | RW | 0...4294967295
162 | S1 | GSYN | Synchronizer mode | UINT32 | RW | 0=Disabled;1=Activated
162 | S2 | GSYN | Synchronizer reference voltage input | UINT32 | RW | 0=U4 Input;1=U3 Input
162 | S3 | GSYN | Voltage difference calculation mode | UINT32 | RW | 0=System is reference;1=U3/U4 Input is reference
162 | S4 | GSYN | Synchronizer voltage reference | UINT32 | RW | 0=UL12;1=UL23;2=UL31;3=UL1;4=UL2;5=UL3
162 | S5 | GSYN | Synchronizer measurement settings | UINT32 | R | 0=Meas.Conf.Incorrect;1=PP and PE voltages;2=PP Voltages;
162 | S6 | GSYN | Synchronizer status | UINT32 | R | 0=Conf.Error;1=Idle Ready;2=Synchronizing;3=Blocked
162 | S7 | GSYN | Force control signals on | UINT32 | RW | 0=None;1=Blocked On;2=Running On;3=Increase U On;4=Decrease U On;5=Increase F On;6=Decrease F On;7=CB Close On;8=LongSyncTime On
162 | S8 | GSYN | Synchronizing by | UINT32 | RW | 0=Autosynchronizer;1=Manual commands
162 | S9 | GSYN | Manual switching mode | UINT32 | RW | 0=Assisted synchroswitch;1=I know what I am doing
162 | S10 | GSYN | Synchroswitch status | UINT32 | R | 0=Standstill;1=Departing;2=Enclosing
162 | S11 | GSYN | Magnitude side A | FLOAT | R | 0.000...200.000
162 | S12 | GSYN | Magnitude side B | FLOAT | R | 0.000...200.000
162 | S13 | GSYN | Frequency side A | FLOAT | R | 0.000...75.000
162 | S14 | GSYN | Frequency side B | FLOAT | R | 0.000...75.000
162 | S15 | GSYN | Magnitude difference | FLOAT | R | -200...200
162 | S16 | GSYN | Frequency difference | FLOAT | R | -100...100
162 | S17 | GSYN | Angle difference | FLOAT | R | -360...360
162 | S18 | GSYN | Magnitude difference on closing BRK | FLOAT | R | -200...200
162 | S19 | GSYN | Frequency difference on closing BRK | FLOAT | R | -100...100
162 | S20 | GSYN | Angle difference on closing BRK | FLOAT | R | -360...360
162 | S21 | GSYN | Estimated BRK Closing time | FLOAT | R | 0...360
162 | S22 | GSYN | Networks rotating time | FLOAT | R | 0...360
162 | S23 | GSYN | Networks placement atm | FLOAT | R | -360...360
162 | S24 | GSYN | Synchronizing time left | FLOAT | R | 0...1800
162 | S25 | GSYN | Get measurement errors for fine tuning | UINT32 | RW | 0=-;1=Get errors
162 | S26 | GSYN | Magnitude difference fine tune | FLOAT | RW | -200...200
162 | S27 | GSYN | Frequency difference fine tune | FLOAT | RW | -100...100
162 | S28 | GSYN | Angle difference fine tune | FLOAT | RW | -360...360
162 | S29 | GSYN | Minimum voltage allowed for synchronizing | FLOAT | RW | 0...105
162 | S30 | GSYN | Maximum voltage allowed for synchronizing | FLOAT | RW | 0...200
162 | S31 | GSYN | Maximum zero voltage allowed for synchronizing (100% disabled) | FLOAT | RW | 0...100
162 | S32 | GSYN | Maximum allowed voltage difference | FLOAT | RW | 0.1...50
162 | S33 | GSYN | Maximum allowed overfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S34 | GSYN | Maximum allowed underfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S35 | GSYN | Max.Time for synchronizing | FLOAT | RW | 0...1800
162 | S36 | GSYN | Maximum allowed angular disposition to allow synchronizing | FLOAT | RW | 0.01...25
162 | S37 | GSYN | Adjustment for measurement inaccuracy or set of desired volt. offset | FLOAT | RW | -95...95
162 | S38 | GSYN | Adjustment for measurement inaccuracy or set of desired angular offset | FLOAT | RW | -60...60
162 | S39 | GSYN | Adjustment for measurement inaccuracy or set of desired freq. offset | FLOAT | RW | -0.5...2
162 | S40 | GSYN | Voltage adjustment slope | FLOAT | RW | 0...25
162 | S41 | GSYN | Volt. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S42 | GSYN | Volt. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S43 | GSYN | Volt. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S44 | GSYN | Freq. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S45 | GSYN | Freq. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S46 | GSYN | Freq. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S47 | GSYN | Maximum allowed voltage difference to start synchronizing | FLOAT | RW | 0...50
162 | S48 | GSYN | Integrator sum when voltage adjustment pulse is generated | FLOAT | RW | 0...50
162 | S49 | GSYN | Voltage adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S50 | GSYN | Frequency adjustment slope when increasing | FLOAT | RW | 0...10
162 | S51 | GSYN | Frequency adjustment slope when decreasing | FLOAT | RW | -10...0
162 | S52 | GSYN | Maximum allowed frequency difference to start synchronizing | FLOAT | RW | 0...25
162 | S53 | GSYN | Integrator sum when frequency adjustment pulse is generated | FLOAT | RW | 0...50
162 | S54 | GSYN | Frequency adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S55 | GSYN | Filter time for angle derivative | FLOAT | RW | 0...1800
162 | S56 | GSYN | Circuit breaker pre-closing adjustment constant | FLOAT | RW | 0...10
162 | S57 | GSYN | Circuit breaker pre-closing time incl auxiliary relays | FLOAT | RW | 0...1800
162 | S58 | GSYN | Lenght of circuit breaker closing pulse | FLOAT | RW | 0...1800
162 | I1 | GSYN | Start Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I2 | GSYN | Stop Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I3 | GSYN | Block and Interrupt Synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I4 | GSYN | Breaker Closed | SIGNAL_IN | RW | 0...4294967295
162 | I5 | GSYN | Manual increase voltage | SIGNAL_IN | RW | 0...4294967295
162 | I6 | GSYN | Manual decrease voltage | SIGNAL_IN | RW | 0...4294967295
162 | I7 | GSYN | Manual increase frequency | SIGNAL_IN | RW | 0...4294967295
162 | I8 | GSYN | Manual decrease frequency | SIGNAL_IN | RW | 0...4294967295
162 | I9 | GSYN | Manual Close Breaker | SIGNAL_IN | RW | 0...4294967295
162 | O1 | GSYN | GSYN Voltage Mag.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O2 | GSYN | GSYN Voltage Freq.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O3 | GSYN | GSYN Voltage Ang.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O4 | GSYN | GSYN Blocked | SIGNAL_OUT | RW | 0...4294967295
162 | O5 | GSYN | GSYN Running | SIGNAL_OUT | RW | 0...4294967295
162 | O6 | GSYN | GSYN Increase Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O7 | GSYN | GSYN Decrease Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O8 | GSYN | GSYN Increase Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O9 | GSYN | GSYN Decrease Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O10 | GSYN | GSYN Breaker Close Pulse | SIGNAL_OUT | RW | 0...4294967295
162 | O11 | GSYN | GSYN Long Sync Time | SIGNAL_OUT | RW | 0...4294967295
162 | O12 | GSYN | GSYN Nets Standstill | SIGNAL_OUT | RW | 0...4294967295
162 | O13 | GSYN | GSYN Nets Departing | SIGNAL_OUT | RW | 0...4294967295
162 | O14 | GSYN | GSYN Nets Enclosing | SIGNAL_OUT | RW | 0...4294967295
162 | S59 | GSYN | Control EventMaskLo | UINT32 | RW | 0...4294967295
162 | S60 | GSYN | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | S1 | VREC | Measurement value recorder mode | UINT32 | RW | 0=Disabled;1=Activated
163 | S2 | VREC | Scale current values to primary | UINT32 | RW | 0=No;1=Yes
163 | S3 | VREC | Record fault types (Overcurrrent & Voltage Over/Under) faults | UINT32 | RW | 0=No;1=Yes
163 | I1 | VREC | Trigger register to memory | SIGNAL_IN | RW | 0...4294967295
163 | I2 | VREC | Tripped stage | UINT32 | R | 0=-;1=I> Trip;2=I>> Trip;3=I>>> Trip;4=I>>>> Trip;5=IDir> Trip;6=IDir>> Trip;7=IDir>>> Trip;8=IDir>>>> Trip;9=U> Trip;10=U>> Trip;11=U>>> Trip;12=U>>>> Trip;13=U< Trip;14=U<< Trip;15=U<<< Trip;16=U<<<< Trip;17=I0> TRIP;18=I0>> Trip;19=I0>>> Trip;20=I0>>>> Trip;21=I0Dir> Trip;22=I0Dir>> Trip;23=I0Dir>>> Trip;24=I0Dir>>>> Trip;25=f> Trip;26=f>> Trip;27=f>>> Trip;28=f>>>> Trip;29=f< Trip;30=f<< Trip;31=f<<< Trip;32=f<<<< Trip;33=P> Trip;34=P< Trip;35=Prev> Trip;36=T> Trip;37=I2> Trip;38=I2>> Trip;39=I2>>> Trip;40=I2>>>> Trip;41=U1/2 > Trip;42=U1/2 >> Trip;43=U1/2 >>> Trip;44=U1/2 >>>> Trip;45=U0> Trip;46=U0>> Trip;47=U0>>> Trip;48=U0>>>> Trip
163 | I3 | VREC | Overcurrent fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;
163 | I4 | VREC | Voltage fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C;8=-;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I5 | VREC | VREC Magnitude 1 | FLOAT | R | 0...1800
163 | I6 | VREC | VREC Magnitude 2 | FLOAT | R | 0...1800
163 | I7 | VREC | VREC Magnitude 3 | FLOAT | R | 0...1800
163 | I8 | VREC | VREC Magnitude 4 | FLOAT | R | 0...1800
163 | I9 | VREC | VREC Magnitude 5 | FLOAT | R | 0...1800
163 | I10 | VREC | VREC Magnitude 6 | FLOAT | R | 0...1800
163 | I11 | VREC | VREC Magnitude 7 | FLOAT | R | 0...1800
163 | I12 | VREC | VREC Magnitude 8 | FLOAT | R | 0...1800
163 | I13 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I14 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I15 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I16 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I17 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I18 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I19 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I20 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I21 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I22 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I23 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I24 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295

## M SPA map AQ-210 v2.1.1.3-233
SPA Ch | SPA Data | Ch Name | Description | Type | Access | Range
46 | V1 | OBJ1 | Open Select | UINT32 | W | 1=Select
46 | V2 | OBJ1 | Close Select | UINT32 | W | 1=Select
46 | V3 | OBJ1 | Execute | UINT32 | W | 1=Execute
46 | V4 | OBJ1 | Cancel | UINT32 | W | 1=Cancel
46 | V5 | OBJ1 | Direct Open | UINT32 | W | 1=Open
46 | V6 | OBJ1 | Direct Close | UINT32 | W | 1=Close
47 | V1 | OBJ2 | Open Select | UINT32 | W | 1=Select
47 | V2 | OBJ2 | Close Select | UINT32 | W | 1=Select
47 | V3 | OBJ2 | Execute | UINT32 | W | 1=Execute
47 | V4 | OBJ2 | Cancel | UINT32 | W | 1=Cancel
47 | V5 | OBJ2 | Direct Open | UINT32 | W | 1=Open
47 | V6 | OBJ2 | Direct Close | UINT32 | W | 1=Close
48 | V1 | OBJ3 | Open Select | UINT32 | W | 1=Select
48 | V2 | OBJ3 | Close Select | UINT32 | W | 1=Select
48 | V3 | OBJ3 | Execute | UINT32 | W | 1=Execute
48 | V4 | OBJ3 | Cancel | UINT32 | W | 1=Cancel
48 | V5 | OBJ3 | Direct Open | UINT32 | W | 1=Open
48 | V6 | OBJ3 | Direct Close | UINT32 | W | 1=Close
49 | V1 | OBJ4 | Open Select | UINT32 | W | 1=Select
49 | V2 | OBJ4 | Close Select | UINT32 | W | 1=Select
49 | V3 | OBJ4 | Execute | UINT32 | W | 1=Execute
49 | V4 | OBJ4 | Cancel | UINT32 | W | 1=Cancel
49 | V5 | OBJ4 | Direct Open | UINT32 | W | 1=Open
49 | V6 | OBJ4 | Direct Close | UINT32 | W | 1=Close
50 | V1 | OBJ5 | Open Select | UINT32 | W | 1=Select
50 | V2 | OBJ5 | Close Select | UINT32 | W | 1=Select
50 | V3 | OBJ5 | Execute | UINT32 | W | 1=Execute
50 | V4 | OBJ5 | Cancel | UINT32 | W | 1=Cancel
50 | V5 | OBJ5 | Direct Open | UINT32 | W | 1=Open
50 | V6 | OBJ5 | Direct Close | UINT32 | W | 1=Close
150 | V1 | OBJ6 | Open Select | UINT32 | W | 1=Select
150 | V2 | OBJ6 | Close Select | UINT32 | W | 1=Select
150 | V3 | OBJ6 | Execute | UINT32 | W | 1=Execute
150 | V4 | OBJ6 | Cancel | UINT32 | W | 1=Cancel
150 | V5 | OBJ6 | Direct Open | UINT32 | W | 1=Open
150 | V6 | OBJ6 | Direct Close | UINT32 | W | 1=Close
151 | V1 | OBJ7 | Open Select | UINT32 | W | 1=Select
151 | V2 | OBJ7 | Close Select | UINT32 | W | 1=Select
151 | V3 | OBJ7 | Execute | UINT32 | W | 1=Execute
151 | V4 | OBJ7 | Cancel | UINT32 | W | 1=Cancel
151 | V5 | OBJ7 | Direct Open | UINT32 | W | 1=Open
151 | V6 | OBJ7 | Direct Close | UINT32 | W | 1=Close
152 | V1 | OBJ8 | Open Select | UINT32 | W | 1=Select
152 | V2 | OBJ8 | Close Select | UINT32 | W | 1=Select
152 | V3 | OBJ8 | Execute | UINT32 | W | 1=Execute
152 | V4 | OBJ8 | Cancel | UINT32 | W | 1=Cancel
152 | V5 | OBJ8 | Direct Open | UINT32 | W | 1=Open
152 | V6 | OBJ8 | Direct Close | UINT32 | W | 1=Close
153 | V1 | OBJ9 | Open Select | UINT32 | W | 1=Select
153 | V2 | OBJ9 | Close Select | UINT32 | W | 1=Select
153 | V3 | OBJ9 | Execute | UINT32 | W | 1=Execute
153 | V4 | OBJ9 | Cancel | UINT32 | W | 1=Cancel
153 | V5 | OBJ9 | Direct Open | UINT32 | W | 1=Open
153 | V6 | OBJ9 | Direct Close | UINT32 | W | 1=Close
154 | V1 | OBJ10 | Open Select | UINT32 | W | 1=Select
154 | V2 | OBJ10 | Close Select | UINT32 | W | 1=Select
154 | V3 | OBJ10 | Execute | UINT32 | W | 1=Execute
154 | V4 | OBJ10 | Cancel | UINT32 | W | 1=Cancel
154 | V5 | OBJ10 | Direct Open | UINT32 | W | 1=Open
154 | V6 | OBJ10 | Direct Close | UINT32 | W | 1=Close
116 | S1 | MEAS1 | Side 1 Current meas update interval | UINT32 | RW | 5...10000
116 | I1 | MEAS1 | Pri.Pha.curr.IL1 | FLOAT | R | 0...100000
116 | I2 | MEAS1 | Pri.Pha.curr.IL2 | FLOAT | R | 0...100000
116 | I3 | MEAS1 | Pri.Pha.curr.IL3 | FLOAT | R | 0...100000
116 | I4 | MEAS1 | Pri.Res.curr.I01 | FLOAT | R | 0...100000
116 | I5 | MEAS1 | Pri.Res.curr.I02 | FLOAT | R | 0...100000
116 | I6 | MEAS1 | Pha.angle IL1 | FLOAT | R | -360...360
116 | I7 | MEAS1 | Pha.angle IL2 | FLOAT | R | -360...360
116 | I8 | MEAS1 | Pha.angle IL3 | FLOAT | R | -360...360
116 | I9 | MEAS1 | Res.curr.angle I01 | FLOAT | R | -360...360
116 | I10 | MEAS1 | Res.curr.angle I02 | FLOAT | R | -360...360
116 | I11 | MEAS1 | Pri.calc.I0 | FLOAT | R | 0...100000
116 | I12 | MEAS1 | calc.I0 Pha.angle | FLOAT | R | -360...360
116 | I13 | MEAS1 | Pha.curr.IL1 TRMS Pri | FLOAT | R | 0...100000
116 | I14 | MEAS1 | Pha.curr.IL2 TRMS Pri | FLOAT | R | 0...100000
116 | I15 | MEAS1 | Pha.curr.IL3 TRMS Pri | FLOAT | R | 0...100000
116 | I16 | MEAS1 | Pri.Pos.seq.curr. | FLOAT | R | 0...100000
116 | I17 | MEAS1 | Pri.Neg.seq.curr. | FLOAT | R | 0...100000
116 | I18 | MEAS1 | Pri.Zero seq.curr. | FLOAT | R | 0...100000
116 | I19 | MEAS1 | Pos.seq.curr.angle | FLOAT | R | -360...360
116 | I20 | MEAS1 | Neg.seq.curr.angle | FLOAT | R | -360...360
116 | I21 | MEAS1 | Zero seq.curr.angle | FLOAT | R | -360...360
116 | I22 | MEAS1 | Res.curr.I01 TRMS Pri | FLOAT | R | 0...100000
116 | I23 | MEAS1 | Res.curr.I02 TRMS Pri | FLOAT | R | 0...100000
116 | I24 | MEAS1 | Pha.L1 ampl. THD | FLOAT | R | 0...100
116 | I25 | MEAS1 | Pha.L1 pow. THD | FLOAT | R | 0...100
116 | I26 | MEAS1 | Pha.L2 ampl. THD | FLOAT | R | 0...100
116 | I27 | MEAS1 | Pha.L2 pow. THD | FLOAT | R | 0...100
116 | I28 | MEAS1 | Pha.L3 ampl. THD | FLOAT | R | 0...100
116 | I29 | MEAS1 | Pha.L3 pow. THD | FLOAT | R | 0...100
116 | I30 | MEAS1 | Res.I01 ampl. THD | FLOAT | R | 0...100
116 | I31 | MEAS1 | Res.I01 pow. THD | FLOAT | R | 0...100
116 | I32 | MEAS1 | Res.I02 ampl. THD | FLOAT | R | 0...100
116 | I33 | MEAS1 | Res.I02 pow. THD | FLOAT | R | 0...100
116 | I34 | MEAS1 | Meas1 IL ang. Ref | FLOAT | R | -360...360
117 | S1 | MEAS2 | Side 2 Current meas update interval | UINT32 | RW | 5...10000
117 | I1 | MEAS2 | Pri.Pha.curr.I''L1 | FLOAT | R | 0...100000
117 | I2 | MEAS2 | Pri.Pha.curr.I''L2 | FLOAT | R | 0...100000
117 | I3 | MEAS2 | Pri.Pha.curr.I''L3 | FLOAT | R | 0...100000
117 | I4 | MEAS2 | Pha.angle I''L1 | FLOAT | R | -360...360
117 | I5 | MEAS2 | Pha.angle I''L2 | FLOAT | R | -360...360
117 | I6 | MEAS2 | Pha.angle I''L3 | FLOAT | R | -360...360
117 | I7 | MEAS2 | Pri.Res.curr.I''01 | FLOAT | R | 0...100000
117 | I8 | MEAS2 | Res.curr.angle I''01 | FLOAT | R | -360...360
117 | I9 | MEAS2 | Pri.Res.curr.I''02 | FLOAT | R | 0...100000
117 | I10 | MEAS2 | Res.curr.angle I''02 | FLOAT | R | -360...360
117 | I11 | MEAS2 | Pri.calc.I''0 | FLOAT | R | 0...100000
117 | I12 | MEAS2 | calc.I''0 Pha.angle | FLOAT | R | -360...360
117 | I13 | MEAS2 | Pha.curr.I''L1 TRMS Pri | FLOAT | R | 0...100000
117 | I14 | MEAS2 | Pha.curr.I''L2 TRMS Pri | FLOAT | R | 0...100000
117 | I15 | MEAS2 | Pha.curr.I''L3 TRMS Pri | FLOAT | R | 0...100000
117 | I16 | MEAS2 | I'' Pri.Pos.seq.curr. | FLOAT | R | 0...100000
117 | I17 | MEAS2 | I'' Pri.Neg.seq.curr. | FLOAT | R | 0...100000
117 | I18 | MEAS2 | I'' Pri.Zero seq.curr. | FLOAT | R | 0...100000
117 | I19 | MEAS2 | I'' Pos.seq.curr.angle | FLOAT | R | -360...360
117 | I20 | MEAS2 | I'' Neg.seq.curr.angle | FLOAT | R | -360...360
117 | I21 | MEAS2 | I'' Zero seq.curr.angle | FLOAT | R | -360...360
117 | I22 | MEAS2 | Res.curr.I''01 TRMS Pri | FLOAT | R | 0...100000
117 | I23 | MEAS2 | Res.curr.I''02 TRMS Pri | FLOAT | R | 0...100000
117 | I24 | MEAS2 | Pha.I''L1 ampl. THD | FLOAT | R | 0...100
117 | I25 | MEAS2 | Pha.I''L1 pow. THD | FLOAT | R | 0...100
117 | I26 | MEAS2 | Pha.I''L2 ampl. THD | FLOAT | R | 0...100
117 | I27 | MEAS2 | Pha.I''L2 pow. THD | FLOAT | R | 0...100
117 | I28 | MEAS2 | Pha.I''L3 ampl. THD | FLOAT | R | 0...100
117 | I29 | MEAS2 | Pha.I''L3 pow. THD | FLOAT | R | 0...100
117 | I30 | MEAS2 | Res.I''01 ampl. THD | FLOAT | R | 0...100
117 | I31 | MEAS2 | Res.I''01 pow. THD | FLOAT | R | 0...100
117 | I32 | MEAS2 | Res.I''02 ampl. THD | FLOAT | R | 0...100
117 | I33 | MEAS2 | Res.I''02 pow. THD | FLOAT | R | 0...100
117 | I34 | MEAS2 | MEAS2 IL ang. Ref | FLOAT | R | -360...360
118 | S1 | MEAS3 | Voltage meas update interval | UINT32 | RW | 5...10000
118 | I1 | MEAS3 | Pos.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I2 | MEAS3 | Neg.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I3 | MEAS3 | Zero.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I4 | MEAS3 | Pos.Seq volt.Angle | FLOAT | R | -360...360
118 | I5 | MEAS3 | Neg.Seq.volt.Angle | FLOAT | R | -360...360
118 | I6 | MEAS3 | Zero.Seq.volt.Angle | FLOAT | R | -360...360
118 | I7 | MEAS3 | System volt UL12 mag | FLOAT | R | 0...1000000
118 | I8 | MEAS3 | System volt UL12 mag(kV) | FLOAT | R | 0...1000
118 | I9 | MEAS3 | System volt UL12 ang | FLOAT | R | -360...360
118 | I10 | MEAS3 | System volt UL23 mag | FLOAT | R | 0...1000000
118 | I11 | MEAS3 | System volt UL23 mag(kV) | FLOAT | R | 0...1000
118 | I12 | MEAS3 | System volt UL23 ang | FLOAT | R | -360...360
118 | I13 | MEAS3 | System volt UL31 mag | FLOAT | R | 0...1000000
118 | I14 | MEAS3 | System volt UL31 mag(kV) | FLOAT | R | 0...1000
118 | I15 | MEAS3 | System volt UL31 ang | FLOAT | R | -360...360
118 | I16 | MEAS3 | System volt UL1 mag | FLOAT | R | 0...1000000
118 | I17 | MEAS3 | System volt UL1 mag(kV) | FLOAT | R | 0...1000
118 | I18 | MEAS3 | System volt UL1 ang | FLOAT | R | -360...360
118 | I19 | MEAS3 | System volt UL2 mag | FLOAT | R | 0...1000000
118 | I20 | MEAS3 | System volt UL2 mag(kV) | FLOAT | R | 0...1000
118 | I21 | MEAS3 | System volt UL2 ang | FLOAT | R | -360...360
118 | I22 | MEAS3 | System volt UL3 mag | FLOAT | R | 0...1000000
118 | I23 | MEAS3 | System volt UL3 mag(kV) | FLOAT | R | 0...1000
118 | I24 | MEAS3 | System volt UL3 ang | FLOAT | R | -360...360
118 | I25 | MEAS3 | System volt U0 mag | FLOAT | R | 0...1000000
118 | I26 | MEAS3 | System volt U0 mag(kV) | FLOAT | R | 0...1000
118 | I27 | MEAS3 | System volt U0 mag(%) | FLOAT | R | 0...120
118 | I28 | MEAS3 | System volt U0 ang | FLOAT | R | -360...360
118 | I29 | MEAS3 | System volt U3 mag | FLOAT | R | 0...1000000
118 | I30 | MEAS3 | System volt U3 mag(kV) | FLOAT | R | 0...1000
118 | I31 | MEAS3 | System volt U3 ang | FLOAT | R | -360...360
118 | I32 | MEAS3 | System volt U4 mag | FLOAT | R | 0...1000000
118 | I33 | MEAS3 | System volt U4 mag(kV) | FLOAT | R | 0...1000
118 | I34 | MEAS3 | System volt U4 ang | FLOAT | R | -360...360
188 | I1 | IMERX | IL1 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I2 | IMERX | IL1 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I3 | IMERX | IL2 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I4 | IMERX | IL2 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I5 | IMERX | IL3 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I6 | IMERX | IL3 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I7 | IMERX | Pos.seq. Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I8 | IMERX | Pos.Seq. Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I9 | IMERX | I01 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I10 | IMERX | I01 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I11 | IMERX | I02 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I12 | IMERX | I02 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I13 | IMERX | I01 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I14 | IMERX | I01 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
188 | I15 | IMERX | I02 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I16 | IMERX | I02 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
119 | S1 | POW1 | Power meas update interval | UINT32 | RW | 5...10000
119 | S2 | POW1 | Nominal Power kVA | FLOAT | RW | 0.1...500000
119 | I1 | POW1 | PQ Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Ind;2=Q2 Rev Cap;3=Q3 Rev Ind;4=Q4 Fwd Cap
119 | I2 | POW1 | VA Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Cap, AV;2=Q2 Rev Ind AV;3=Q3 Rev Cap VA;4=Q4 Fwd Ind VA
119 | I3 | POW1 | Export Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I4 | POW1 | Export Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I5 | POW1 | Import Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I6 | POW1 | Import Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I7 | POW1 | Active Energy (P) Export/Import balance MWh | INT32 | R | -2147483647...2147483647
119 | I8 | POW1 | Active Energy (P) Export/Import balance kWh | INT32 | R | -2147483647...2147483647
119 | I9 | POW1 | Exported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I10 | POW1 | Exported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I11 | POW1 | Imported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I12 | POW1 | Imported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I13 | POW1 | Reactive Energy (Q) balance while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I14 | POW1 | Reactive Energy (Q) balance while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I15 | POW1 | Exported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I16 | POW1 | Exported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I17 | POW1 | Imported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I18 | POW1 | Imported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I19 | POW1 | Reactive Energy (Q) balance while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I20 | POW1 | Reactive Energy (Q) balance while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I21 | POW1 | Apparent Energy (S) while Export (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I22 | POW1 | Apparent Energy (S) while Export (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I23 | POW1 | Apparent Energy (S) while Import (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I24 | POW1 | Apparent Energy (S) while Import (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I25 | POW1 | Apparent Energy (S) Net | INT32 | R | -2147483647...2147483647
119 | I26 | POW1 | Real Energy (P) Net | INT32 | RW | -2147483647...2147483647
119 | I27 | POW1 | Reactive Energy (Q) Net | INT32 | RW | -2147483647...2147483647
119 | I28 | POW1 | Real Energy (P) Supply (Default supply direction towards busbar) | INT32 | RW | -2147483647...2147483647
119 | I29 | POW1 | Reactive Energy (Q) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
119 | I30 | POW1 | Real Energy (P) Demand (Default demand direction from busbar) | INT32 | RW | -2147483647...2147483647
119 | I31 | POW1 | Reactive Energy (Q) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
119 | S3 | POW1 | Reset 3ph Energies | UINT32 | RW | 0=-;1=Reset
119 | I32 | POW1 | POW1 L1 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I33 | POW1 | POW1 L1 Active power (P) | FLOAT | R | -1000000...1000000
119 | I34 | POW1 | POW1 L1 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I35 | POW1 | POW1 L1 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I36 | POW1 | POW1 L1 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I37 | POW1 | L1 PF | FLOAT | R | -1000000...1000000
119 | I38 | POW1 | POW1 L2 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I39 | POW1 | POW1 L2 Active power (P) | FLOAT | R | -1000000...1000000
119 | I40 | POW1 | POW1 L2 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I41 | POW1 | POW1 L2 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I42 | POW1 | POW1 L2 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I43 | POW1 | L2 PF | FLOAT | R | -1000000...1000000
119 | I44 | POW1 | POW1 L3 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I45 | POW1 | POW1 L3 Active power (P) | FLOAT | R | -1000000...1000000
119 | I46 | POW1 | POW1 L3 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I47 | POW1 | POW1 L3 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I48 | POW1 | POW1 L3 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I49 | POW1 | L3 PF | FLOAT | R | -1000000...1000000
119 | I50 | POW1 | POW1 3PH Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I51 | POW1 | POW1 3PH Apparent power (S MVA) | FLOAT | R | -1000000...1000000
119 | I52 | POW1 | POW1 3PH Active power (P) | FLOAT | R | -1000000...1000000
119 | I53 | POW1 | POW1 3PH Active power (P MW) | FLOAT | R | -1000000...1000000
119 | I54 | POW1 | POW1 3PH Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I55 | POW1 | POW1 3PH Reactive power (QMVar) | FLOAT | R | -1000000...1000000
119 | I56 | POW1 | POW1 3PH Tan(phi) | FLOAT | R | -1000000...1000000
119 | I57 | POW1 | POW1 3PH Cos(phi) | FLOAT | R | -1000000...1000000
119 | I58 | POW1 | 3PH PF | FLOAT | R | -1000000...1000000
136 | S1 | IMP1 | Impedance meas. update interval | UINT32 | RW | 500...10000
136 | I1 | IMP1 | Primary L12 R | FLOAT | R | -1000000...1000000
136 | I2 | IMP1 | Primary L12 X | FLOAT | R | -1000000...1000000
136 | I3 | IMP1 | Primary L23 R | FLOAT | R | -1000000...1000000
136 | I4 | IMP1 | Primary L23 X | FLOAT | R | -1000000...1000000
136 | I5 | IMP1 | Primary L31 R | FLOAT | R | -1000000...1000000
136 | I6 | IMP1 | Primary L31 X | FLOAT | R | -1000000...1000000
136 | I7 | IMP1 | Primary Z12 | FLOAT | R | -1000000...1000000
136 | I8 | IMP1 | Primary Z23 | FLOAT | R | -1000000...1000000
136 | I9 | IMP1 | Primary Z31 | FLOAT | R | -1000000...1000000
136 | I10 | IMP1 | Angle Z12 | FLOAT | R | -360...360
136 | I11 | IMP1 | Angle Z23 | FLOAT | R | -360...360
136 | I12 | IMP1 | Angle Z31 | FLOAT | R | -360...360
136 | I13 | IMP1 | Primary L1 R | FLOAT | R | -1000000...1000000
136 | I14 | IMP1 | Primary L1 X | FLOAT | R | -1000000...1000000
136 | I15 | IMP1 | Primary L2 R | FLOAT | R | -1000000...1000000
136 | I16 | IMP1 | Primary L2 X | FLOAT | R | -1000000...1000000
136 | I17 | IMP1 | Primary L3 R | FLOAT | R | -1000000...1000000
136 | I18 | IMP1 | Primary L3 X | FLOAT | R | -1000000...1000000
136 | I19 | IMP1 | Primary Z1 | FLOAT | R | -1000000...1000000
136 | I20 | IMP1 | Primary Z2 | FLOAT | R | -1000000...1000000
136 | I21 | IMP1 | Primary Z3 | FLOAT | R | -1000000...1000000
136 | I22 | IMP1 | Angle Z1 | FLOAT | R | -360...360
136 | I23 | IMP1 | Angle Z2 | FLOAT | R | -360...360
136 | I24 | IMP1 | Angle Z3 | FLOAT | R | -360...360
137 | I1 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I2 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I3 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I4 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I5 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I6 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I7 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I8 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I9 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I10 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I11 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I12 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
120 | S1 | FREQS | Smpl mode | UINT32 | RW | 0=Fixed;1=Tracking
120 | S2 | FREQS | Max. Tracking freq. allowed (+Nom f) | FLOAT | RW | 0.001...75
120 | S3 | FREQS | Sys.nom.f | FLOAT | RW | 7...75
120 | S4 | FREQS | Min. Tracking freq. allowed (- Nom f) | FLOAT | RW | 0.001...75
120 | I1 | FREQS | Track.sys.f | FLOAT | R | 0...75
120 | I2 | FREQS | f atm. Protections (when not measurable returns to nominal) | FLOAT | R | 0...75
120 | I3 | FREQS | f atm. Display (when not measurable is 0Hz) | FLOAT | R | 0...75
10 | I1 | DIGI | Dis 1-32 | UINT32 | R | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32
10 | I2 | DIGI | Dis 33-64 | UINT32 | R | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51
10 | I3 | DIGI | DI1 | SIGNAL_OUT | R | 0...4294967295
10 | V1 | DIGI | DI1 Counter | UINT32 | R | 0...4294967295
10 | V2 | DIGI | DI1 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I4 | DIGI | DI2 | SIGNAL_OUT | R | 0...4294967295
10 | V3 | DIGI | DI2 Counter | UINT32 | R | 0...4294967295
10 | V4 | DIGI | DI2 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I5 | DIGI | DI3 | SIGNAL_OUT | R | 0...4294967295
10 | V5 | DIGI | DI3 Counter | UINT32 | R | 0...4294967295
10 | V6 | DIGI | DI3 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I6 | DIGI | DI4 | SIGNAL_OUT | R | 0...4294967295
10 | V7 | DIGI | DI4 Counter | UINT32 | R | 0...4294967295
10 | V8 | DIGI | DI4 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I7 | DIGI | DI5 | SIGNAL_OUT | R | 0...4294967295
10 | V9 | DIGI | DI5 Counter | UINT32 | R | 0...4294967295
10 | V10 | DIGI | DI5 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I8 | DIGI | DI6 | SIGNAL_OUT | R | 0...4294967295
10 | V11 | DIGI | DI6 Counter | UINT32 | R | 0...4294967295
10 | V12 | DIGI | DI6 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I9 | DIGI | DI7 | SIGNAL_OUT | R | 0...4294967295
10 | V13 | DIGI | DI7 Counter | UINT32 | R | 0...4294967295
10 | V14 | DIGI | DI7 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I10 | DIGI | DI8 | SIGNAL_OUT | R | 0...4294967295
10 | V15 | DIGI | DI8 Counter | UINT32 | R | 0...4294967295
10 | V16 | DIGI | DI8 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I11 | DIGI | DI9 | SIGNAL_OUT | R | 0...4294967295
10 | V17 | DIGI | DI9 Counter | UINT32 | R | 0...4294967295
10 | V18 | DIGI | DI9 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I12 | DIGI | DI10 | SIGNAL_OUT | R | 0...4294967295
10 | V19 | DIGI | DI10 Counter | UINT32 | R | 0...4294967295
10 | V20 | DIGI | DI10 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I13 | DIGI | DI11 | SIGNAL_OUT | R | 0...4294967295
10 | V21 | DIGI | DI11 Counter | UINT32 | R | 0...4294967295
10 | V22 | DIGI | DI11 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I14 | DIGI | DI12 | SIGNAL_OUT | R | 0...4294967295
10 | V23 | DIGI | DI12 Counter | UINT32 | R | 0...4294967295
10 | V24 | DIGI | DI12 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I15 | DIGI | DI13 | SIGNAL_OUT | R | 0...4294967295
10 | V25 | DIGI | DI13 Counter | UINT32 | R | 0...4294967295
10 | V26 | DIGI | DI13 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I16 | DIGI | DI14 | SIGNAL_OUT | R | 0...4294967295
10 | V27 | DIGI | DI14 Counter | UINT32 | R | 0...4294967295
10 | V28 | DIGI | DI14 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I17 | DIGI | DI15 | SIGNAL_OUT | R | 0...4294967295
10 | V29 | DIGI | DI15 Counter | UINT32 | R | 0...4294967295
10 | V30 | DIGI | DI15 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I18 | DIGI | DI16 | SIGNAL_OUT | R | 0...4294967295
10 | V31 | DIGI | DI16 Counter | UINT32 | R | 0...4294967295
10 | V32 | DIGI | DI16 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I19 | DIGI | DI17 | SIGNAL_OUT | R | 0...4294967295
10 | V33 | DIGI | DI17 Counter | UINT32 | R | 0...4294967295
10 | V34 | DIGI | DI17 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I20 | DIGI | DI18 | SIGNAL_OUT | R | 0...4294967295
10 | V35 | DIGI | DI18 Counter | UINT32 | R | 0...4294967295
10 | V36 | DIGI | DI18 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I21 | DIGI | DI19 | SIGNAL_OUT | R | 0...4294967295
10 | V37 | DIGI | DI19 Counter | UINT32 | R | 0...4294967295
10 | V38 | DIGI | DI19 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I22 | DIGI | DI20 | SIGNAL_OUT | R | 0...4294967295
10 | V39 | DIGI | DI20 Counter | UINT32 | R | 0...4294967295
10 | V40 | DIGI | DI20 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I23 | DIGI | DI21 | SIGNAL_OUT | R | 0...4294967295
10 | V41 | DIGI | DI21 Counter | UINT32 | R | 0...4294967295
10 | V42 | DIGI | DI21 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I24 | DIGI | DI22 | SIGNAL_OUT | R | 0...4294967295
10 | V43 | DIGI | DI22 Counter | UINT32 | R | 0...4294967295
10 | V44 | DIGI | DI22 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I25 | DIGI | DI23 | SIGNAL_OUT | R | 0...4294967295
10 | V45 | DIGI | DI23 Counter | UINT32 | R | 0...4294967295
10 | V46 | DIGI | DI23 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I26 | DIGI | DI24 | SIGNAL_OUT | R | 0...4294967295
10 | V47 | DIGI | DI24 Counter | UINT32 | R | 0...4294967295
10 | V48 | DIGI | DI24 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I27 | DIGI | DI25 | SIGNAL_OUT | R | 0...4294967295
10 | V49 | DIGI | DI25 Counter | UINT32 | R | 0...4294967295
10 | V50 | DIGI | DI25 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I28 | DIGI | DI26 | SIGNAL_OUT | R | 0...4294967295
10 | V51 | DIGI | DI26 Counter | UINT32 | R | 0...4294967295
10 | V52 | DIGI | DI26 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I29 | DIGI | DI27 | SIGNAL_OUT | R | 0...4294967295
10 | V53 | DIGI | DI27 Counter | UINT32 | R | 0...4294967295
10 | V54 | DIGI | DI27 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I30 | DIGI | DI28 | SIGNAL_OUT | R | 0...4294967295
10 | V55 | DIGI | DI28 Counter | UINT32 | R | 0...4294967295
10 | V56 | DIGI | DI28 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I31 | DIGI | DI29 | SIGNAL_OUT | R | 0...4294967295
10 | V57 | DIGI | DI29 Counter | UINT32 | R | 0...4294967295
10 | V58 | DIGI | DI29 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I32 | DIGI | DI30 | SIGNAL_OUT | R | 0...4294967295
10 | V59 | DIGI | DI30 Counter | UINT32 | R | 0...4294967295
10 | V60 | DIGI | DI30 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I33 | DIGI | DI31 | SIGNAL_OUT | R | 0...4294967295
10 | V61 | DIGI | DI31 Counter | UINT32 | R | 0...4294967295
10 | V62 | DIGI | DI31 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I34 | DIGI | DI32 | SIGNAL_OUT | R | 0...4294967295
10 | V63 | DIGI | DI32 Counter | UINT32 | R | 0...4294967295
10 | V64 | DIGI | DI32 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I35 | DIGI | DI33 | SIGNAL_OUT | R | 0...4294967295
10 | V65 | DIGI | DI33 Counter | UINT32 | R | 0...4294967295
10 | V66 | DIGI | DI33 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I36 | DIGI | DI34 | SIGNAL_OUT | R | 0...4294967295
10 | V67 | DIGI | DI34 Counter | UINT32 | R | 0...4294967295
10 | V68 | DIGI | DI34 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I37 | DIGI | DI35 | SIGNAL_OUT | R | 0...4294967295
10 | V69 | DIGI | DI35 Counter | UINT32 | R | 0...4294967295
10 | V70 | DIGI | DI35 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I38 | DIGI | DI36 | SIGNAL_OUT | R | 0...4294967295
10 | V71 | DIGI | DI36 Counter | UINT32 | R | 0...4294967295
10 | V72 | DIGI | DI36 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I39 | DIGI | DI37 | SIGNAL_OUT | R | 0...4294967295
10 | V73 | DIGI | DI37 Counter | UINT32 | R | 0...4294967295
10 | V74 | DIGI | DI37 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I40 | DIGI | DI38 | SIGNAL_OUT | R | 0...4294967295
10 | V75 | DIGI | DI38 Counter | UINT32 | R | 0...4294967295
10 | V76 | DIGI | DI38 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I41 | DIGI | DI39 | SIGNAL_OUT | R | 0...4294967295
10 | V77 | DIGI | DI39 Counter | UINT32 | R | 0...4294967295
10 | V78 | DIGI | DI39 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I42 | DIGI | DI40 | SIGNAL_OUT | R | 0...4294967295
10 | V79 | DIGI | DI40 Counter | UINT32 | R | 0...4294967295
10 | V80 | DIGI | DI40 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I43 | DIGI | DI41 | SIGNAL_OUT | R | 0...4294967295
10 | V81 | DIGI | DI41 Counter | UINT32 | R | 0...4294967295
10 | V82 | DIGI | DI41 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I44 | DIGI | DI42 | SIGNAL_OUT | R | 0...4294967295
10 | V83 | DIGI | DI42 Counter | UINT32 | R | 0...4294967295
10 | V84 | DIGI | DI42 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I45 | DIGI | DI43 | SIGNAL_OUT | R | 0...4294967295
10 | V85 | DIGI | DI43 Counter | UINT32 | R | 0...4294967295
10 | V86 | DIGI | DI43 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I46 | DIGI | DI44 | SIGNAL_OUT | R | 0...4294967295
10 | V87 | DIGI | DI44 Counter | UINT32 | R | 0...4294967295
10 | V88 | DIGI | DI44 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I47 | DIGI | DI45 | SIGNAL_OUT | R | 0...4294967295
10 | V89 | DIGI | DI45 Counter | UINT32 | R | 0...4294967295
10 | V90 | DIGI | DI45 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I48 | DIGI | DI46 | SIGNAL_OUT | R | 0...4294967295
10 | V91 | DIGI | DI46 Counter | UINT32 | R | 0...4294967295
10 | V92 | DIGI | DI46 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I49 | DIGI | DI47 | SIGNAL_OUT | R | 0...4294967295
10 | V93 | DIGI | DI47 Counter | UINT32 | R | 0...4294967295
10 | V94 | DIGI | DI47 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I50 | DIGI | DI48 | SIGNAL_OUT | R | 0...4294967295
10 | V95 | DIGI | DI48 Counter | UINT32 | R | 0...4294967295
10 | V96 | DIGI | DI48 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I51 | DIGI | DI49 | SIGNAL_OUT | R | 0...4294967295
10 | V97 | DIGI | DI49 Counter | UINT32 | R | 0...4294967295
10 | V98 | DIGI | DI49 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I52 | DIGI | DI50 | SIGNAL_OUT | R | 0...4294967295
10 | V99 | DIGI | DI50 Counter | UINT32 | R | 0...4294967295
10 | V100 | DIGI | DI50 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I53 | DIGI | DI51 | SIGNAL_OUT | R | 0...4294967295
10 | V101 | DIGI | DI51 Counter | UINT32 | R | 0...4294967295
10 | V102 | DIGI | DI51 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | S1 | DIGI | EventMaskLo | UINT32 | RW | 0...4294967295
10 | S2 | DIGI | EventMaskHi | UINT32 | RW | 0...4294967295
11 | S1 | DIGI2 | EventMaskLo | UINT32 | RW | 0...4294967295
11 | S2 | DIGI2 | EventMaskHi | UINT32 | RW | 0...4294967295
15 | O1 | RELE | Outputs status | UINT32 | R | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15
15 | O2 | RELE | OUT1 | SIGNAL_IN | RW | 0...4294967295
15 | O3 | RELE | OUT2 | SIGNAL_IN | RW | 0...4294967295
15 | O4 | RELE | OUT3 | SIGNAL_IN | RW | 0...4294967295
15 | O5 | RELE | OUT4 | SIGNAL_IN | RW | 0...4294967295
15 | O6 | RELE | OUT5 | SIGNAL_IN | RW | 0...4294967295
15 | O7 | RELE | OUT6 | SIGNAL_IN | RW | 0...4294967295
15 | O8 | RELE | OUT7 | SIGNAL_IN | RW | 0...4294967295
15 | O9 | RELE | OUT8 | SIGNAL_IN | RW | 0...4294967295
15 | O10 | RELE | OUT9 | SIGNAL_IN | RW | 0...4294967295
15 | O11 | RELE | OUT10 | SIGNAL_IN | RW | 0...4294967295
15 | O12 | RELE | OUT11 | SIGNAL_IN | RW | 0...4294967295
15 | O13 | RELE | OUT12 | SIGNAL_IN | RW | 0...4294967295
15 | O14 | RELE | OUT13 | SIGNAL_IN | RW | 0...4294967295
15 | O15 | RELE | OUT14 | SIGNAL_IN | RW | 0...4294967295
15 | O16 | RELE | OUT15 | SIGNAL_IN | RW | 0...4294967295
121 | O1 | LED | LED START | SIGNAL_IN | RW | 0...4294967295
121 | O2 | LED | LED TRIP | SIGNAL_IN | RW | 0...4294967295
121 | O3 | LED | User LED 1 | SIGNAL_IN | RW | 0...4294967295
121 | O4 | LED | User LED 2 | SIGNAL_IN | RW | 0...4294967295
121 | O5 | LED | User LED 3 | SIGNAL_IN | RW | 0...4294967295
121 | O6 | LED | User LED 4 | SIGNAL_IN | RW | 0...4294967295
121 | O7 | LED | User LED 5 | SIGNAL_IN | RW | 0...4294967295
121 | O8 | LED | User LED 6 | SIGNAL_IN | RW | 0...4294967295
121 | O9 | LED | User LED 7 | SIGNAL_IN | RW | 0...4294967295
121 | O10 | LED | User LED 8 | SIGNAL_IN | RW | 0...4294967295
121 | O11 | LED | User LED 9 | SIGNAL_IN | RW | 0...4294967295
121 | O12 | LED | User LED 10 | SIGNAL_IN | RW | 0...4294967295
121 | O13 | LED | User LED 11 | SIGNAL_IN | RW | 0...4294967295
121 | O14 | LED | User LED 12 | SIGNAL_IN | RW | 0...4294967295
121 | O15 | LED | User LED 13 | SIGNAL_IN | RW | 0...4294967295
121 | O16 | LED | User LED 14 | SIGNAL_IN | RW | 0...4294967295
121 | O17 | LED | User LED 15 | SIGNAL_IN | RW | 0...4294967295
121 | O18 | LED | User LED 16 | SIGNAL_IN | RW | 0...4294967295
122 | O1 | LEDX | User LED 17 | SIGNAL_IN | RW | 0...4294967295
122 | O2 | LEDX | User LED 18 | SIGNAL_IN | RW | 0...4294967295
122 | O3 | LEDX | User LED 19 | SIGNAL_IN | RW | 0...4294967295
122 | O4 | LEDX | User LED 20 | SIGNAL_IN | RW | 0...4294967295
122 | O5 | LEDX | User LED 21 | SIGNAL_IN | RW | 0...4294967295
122 | O6 | LEDX | User LED 22 | SIGNAL_IN | RW | 0...4294967295
122 | O7 | LEDX | User LED 23 | SIGNAL_IN | RW | 0...4294967295
122 | O8 | LEDX | User LED 24 | SIGNAL_IN | RW | 0...4294967295
122 | O9 | LEDX | User LED 25 | SIGNAL_IN | RW | 0...4294967295
122 | O10 | LEDX | User LED 26 | SIGNAL_IN | RW | 0...4294967295
122 | O11 | LEDX | User LED 27 | SIGNAL_IN | RW | 0...4294967295
122 | O12 | LEDX | User LED 28 | SIGNAL_IN | RW | 0...4294967295
122 | O13 | LEDX | User LED 29 | SIGNAL_IN | RW | 0...4294967295
122 | O14 | LEDX | User LED 30 | SIGNAL_IN | RW | 0...4294967295
122 | O15 | LEDX | User LED 31 | SIGNAL_IN | RW | 0...4294967295
122 | O16 | LEDX | User LED 32 | SIGNAL_IN | RW | 0...4294967295
122 | O17 | LEDX | User LED 33 | SIGNAL_IN | RW | 0...4294967295
122 | O18 | LEDX | User LED 34 | SIGNAL_IN | RW | 0...4294967295
122 | O19 | LEDX | User LED 35 | SIGNAL_IN | RW | 0...4294967295
122 | O20 | LEDX | User LED 36 | SIGNAL_IN | RW | 0...4294967295
122 | O21 | LEDX | User LED 37 | SIGNAL_IN | RW | 0...4294967295
122 | O22 | LEDX | User LED 38 | SIGNAL_IN | RW | 0...4294967295
122 | O23 | LEDX | User LED 39 | SIGNAL_IN | RW | 0...4294967295
122 | O24 | LEDX | User LED 40 | SIGNAL_IN | RW | 0...4294967295
122 | O25 | LEDX | User LED 41 | SIGNAL_IN | RW | 0...4294967295
122 | O26 | LEDX | User LED 42 | SIGNAL_IN | RW | 0...4294967295
122 | O27 | LEDX | User LED 43 | SIGNAL_IN | RW | 0...4294967295
122 | O28 | LEDX | User LED 44 | SIGNAL_IN | RW | 0...4294967295
122 | O29 | LEDX | User LED 45 | SIGNAL_IN | RW | 0...4294967295
122 | O30 | LEDX | User LED 46 | SIGNAL_IN | RW | 0...4294967295
122 | O31 | LEDX | User LED 47 | SIGNAL_IN | RW | 0...4294967295
122 | O32 | LEDX | User LED 48 | SIGNAL_IN | RW | 0...4294967295
65 | V1 | SGS | Active setting group | UINT32 | R | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
65 | S1 | SGS | Force SG | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | S2 | SGS | Force SG change | UINT32 | RW | 0=Disabled;1=Enabled
65 | S3 | SGS | Used setting groups | UINT32 | RW | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
65 | S4 | SGS | Remote SG change | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | O1 | SGS | Forced SG in use | SIGNAL_OUT | RW | 0...4294967295
65 | O2 | SGS | SG1 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O3 | SGS | SG2 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O4 | SGS | SG3 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O5 | SGS | SG4 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O6 | SGS | SG5 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O7 | SGS | SG6 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O8 | SGS | SG7 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O9 | SGS | SG8 Active | SIGNAL_OUT | RW | 0...4294967295
7 | I1 | CTRL | Local/Remote status | UINT32 | R | 0=Remote;1=Local
123 | V1 | DEV | Serial number | UINT32 | R | 0...4294967295
123 | V2 | DEV | SW version | STRING | R | ...32
124 | S1 | EVENT | Clear Events | UINT32 | RW | 0=-;1=Clear
125 | I1 | DIAG | Diagnostic alarm status | UINT32 | R | 0b=Temp. out of range;1b=Voltage out of range;2b=HW configuration invalid;3b=Relay output failure;4b=Option card A alarm;5b=Option card B alarm;6b=Option card C alarm;7b=Option card D alarm;8b=Option card E alarm;9b=Option card F alarm;10b=GOOSE invalid;
125 | S1 | DIAG | Clear diagnostic alarm | UINT32 | W | 0=-;1=Clear
125 | I2 | DIAG | Internal temperature | FLOAT | R | 0...200
125 | I3 | DIAG | Internal voltage 24V | FLOAT | R | 0...50
125 | I4 | DIAG | Internal voltage 24V max | FLOAT | R | 0...50
125 | I5 | DIAG | Internal voltage 24V min | FLOAT | R | 0...50
125 | I6 | DIAG | Internal voltage 24V deviation | FLOAT | R | 0...50
138 | I1 | MBIO | Input value | FLOAT | R | -101...2000
138 | I2 | MBIO | Input value | FLOAT | R | -101...2000
138 | I3 | MBIO | Input value | FLOAT | R | -101...2000
138 | I4 | MBIO | Input value | FLOAT | R | -101...2000
138 | I5 | MBIO | Input value | FLOAT | R | -101...2000
138 | I6 | MBIO | Input value | FLOAT | R | -101...2000
138 | I7 | MBIO | Input value | FLOAT | R | -101...2000
138 | I8 | MBIO | Input value | FLOAT | R | -101...2000
138 | I9 | MBIO | Input value | FLOAT | R | -101...2000
138 | I10 | MBIO | Input value | FLOAT | R | -101...2000
138 | I11 | MBIO | Input value | FLOAT | R | -101...2000
138 | I12 | MBIO | Input value | FLOAT | R | -101...2000
138 | I13 | MBIO | Input value | FLOAT | R | -101...2000
138 | I14 | MBIO | Input value | FLOAT | R | -101...2000
138 | I15 | MBIO | Input value | FLOAT | R | -101...2000
138 | I16 | MBIO | Input value | FLOAT | R | -101...2000
138 | I17 | MBIO | Input value | FLOAT | R | -101...2000
138 | I18 | MBIO | Input value | FLOAT | R | -101...2000
138 | I19 | MBIO | Input value | FLOAT | R | -101...2000
138 | I20 | MBIO | Input value | FLOAT | R | -101...2000
138 | I21 | MBIO | Input value | FLOAT | R | -101...2000
138 | I22 | MBIO | Input value | FLOAT | R | -101...2000
138 | I23 | MBIO | Input value | FLOAT | R | -101...2000
138 | I24 | MBIO | Input value | FLOAT | R | -101...2000
138 | I25 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I26 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I27 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I28 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I29 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I30 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I31 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I32 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I33 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I34 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I35 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I36 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I37 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I38 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I39 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I40 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I41 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I42 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I43 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I44 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I45 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I46 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I47 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I48 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | O1 | MBIO | MBIO ModA Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O2 | MBIO | MBIO ModA Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O3 | MBIO | MBIO ModA Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O4 | MBIO | MBIO ModA Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O5 | MBIO | MBIO ModA Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O6 | MBIO | MBIO ModA Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O7 | MBIO | MBIO ModA Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O8 | MBIO | MBIO ModA Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O9 | MBIO | MBIO ModB Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O10 | MBIO | MBIO ModB Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O11 | MBIO | MBIO ModB Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O12 | MBIO | MBIO ModB Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O13 | MBIO | MBIO ModB Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O14 | MBIO | MBIO ModB Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O15 | MBIO | MBIO ModB Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O16 | MBIO | MBIO ModB Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O17 | MBIO | MBIO ModC Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O18 | MBIO | MBIO ModC Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O19 | MBIO | MBIO ModC Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O20 | MBIO | MBIO ModC Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O21 | MBIO | MBIO ModC Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O22 | MBIO | MBIO ModC Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O23 | MBIO | MBIO ModC Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O24 | MBIO | MBIO ModC Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
139 | V1 | LOGIC | Reset Latches | UINT32 | RW | 0=-;1=Reset
8 | O1 | LOGIC1 | Logic out 1-32 | UINT32 | RW | 0...4294967295
139 | O1 | LOGIC | Logical Output 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O2 | LOGIC | Logical Output 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O3 | LOGIC | Logical Output 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O4 | LOGIC | Logical Output 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O5 | LOGIC | Logical Output 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O6 | LOGIC | Logical Output 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O7 | LOGIC | Logical Output 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O8 | LOGIC | Logical Output 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O9 | LOGIC | Logical Output 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O10 | LOGIC | Logical Output 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O11 | LOGIC | Logical Output 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O12 | LOGIC | Logical Output 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O13 | LOGIC | Logical Output 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O14 | LOGIC | Logical Output 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O15 | LOGIC | Logical Output 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O16 | LOGIC | Logical Output 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O17 | LOGIC | Logical Output 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O18 | LOGIC | Logical Output 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O19 | LOGIC | Logical Output 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O20 | LOGIC | Logical Output 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O21 | LOGIC | Logical Output 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O22 | LOGIC | Logical Output 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O23 | LOGIC | Logical Output 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O24 | LOGIC | Logical Output 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O25 | LOGIC | Logical Output 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O26 | LOGIC | Logical Output 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O27 | LOGIC | Logical Output 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O28 | LOGIC | Logical Output 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O29 | LOGIC | Logical Output 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O30 | LOGIC | Logical Output 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O31 | LOGIC | Logical Output 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O32 | LOGIC | Logical Output 32 | SIGNAL_OUT | RW | 0...4294967295
139 | O33 | LOGIC | Logical Input 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O34 | LOGIC | Logical Input 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O35 | LOGIC | Logical Input 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O36 | LOGIC | Logical Input 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O37 | LOGIC | Logical Input 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O38 | LOGIC | Logical Input 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O39 | LOGIC | Logical Input 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O40 | LOGIC | Logical Input 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O41 | LOGIC | Logical Input 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O42 | LOGIC | Logical Input 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O43 | LOGIC | Logical Input 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O44 | LOGIC | Logical Input 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O45 | LOGIC | Logical Input 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O46 | LOGIC | Logical Input 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O47 | LOGIC | Logical Input 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O48 | LOGIC | Logical Input 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O49 | LOGIC | Logical Input 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O50 | LOGIC | Logical Input 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O51 | LOGIC | Logical Input 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O52 | LOGIC | Logical Input 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O53 | LOGIC | Logical Input 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O54 | LOGIC | Logical Input 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O55 | LOGIC | Logical Input 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O56 | LOGIC | Logical Input 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O57 | LOGIC | Logical Input 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O58 | LOGIC | Logical Input 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O59 | LOGIC | Logical Input 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O60 | LOGIC | Logical Input 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O61 | LOGIC | Logical Input 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O62 | LOGIC | Logical Input 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O63 | LOGIC | Logical Input 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O64 | LOGIC | Logical Input 32 | SIGNAL_OUT | RW | 0...4294967295
8 | S1 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
8 | S2 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
9 | S1 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
9 | S2 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
140 | O1 | TIMER | Timer1 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O2 | TIMER | Timer2 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O3 | TIMER | Timer3 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O4 | TIMER | Timer4 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O5 | TIMER | Timer5 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O6 | TIMER | Timer6 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O7 | TIMER | Timer7 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O8 | TIMER | Timer8 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O9 | TIMER | Timer9 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O10 | TIMER | Timer10 Output | SIGNAL_OUT | RW | 0...4294967295
2 | I1 | IRF | Internal Relay Fault status | UINT32 | R | 0b=Storage error;1b=Logic file missing;2b=Aquisition unit error;3b=Measurement config error;4b=Relay hardware setup error;5b=System overload error;6b=Not configured yet;7b=Firmware upgrade done;8b=Slot supervision error;9b=Software inconsistency error;10b=Safe setting mode active;
2 | S1 | IRF | Clear Fault status | UINT32 | W | 0=-;1=Clear
2 | I2 | IRF | Option card health status | UINT32 | R | 0b=Baseboard fault;1b=Card slot A fault;2b=Card slot B fault;3b=Card slot C fault;4b=Card slot D fault;5b=Card slot E fault;6b=Card slot F fault;
20 | S1 | NOC1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
20 | V1 | NOC1 | I> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
20 | V2 | NOC1 | I> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
20 | I1 | NOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
20 | I2 | NOC1 | I> starts | UINT32 | R | 0...4294967295
20 | I3 | NOC1 | I> trips | UINT32 | R | 0...4294967295
20 | I4 | NOC1 | I> blocks | UINT32 | R | 0...4294967295
20 | S2 | NOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
20 | S3 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S4 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S5 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S6 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S7 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S8 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S9 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S10 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S11 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S12 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S13 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S14 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S15 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S16 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S17 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S18 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S19 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S20 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S21 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S22 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S23 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S24 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S25 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S26 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S27 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S28 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S29 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S30 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S31 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S32 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S33 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S34 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | O1 | NOC1 | I> START (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O2 | NOC1 | I> START(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O3 | NOC1 | I> START(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O4 | NOC1 | I> START(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O5 | NOC1 | I> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O6 | NOC1 | I> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O7 | NOC1 | I> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O8 | NOC1 | I> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O9 | NOC1 | I> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
20 | V3 | NOC1 | Newest Register | UINT32 | R | 0...12
20 | V4 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V5 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V6 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V7 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V8 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V9 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V10 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V11 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V12 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V13 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V14 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V15 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V16 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V17 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V18 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V19 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V20 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V21 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V22 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V23 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V24 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V25 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V26 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V27 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V28 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V29 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V30 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V31 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V32 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V33 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V34 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V35 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V36 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V37 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V38 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V39 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | S35 | NOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
21 | S1 | NOC2 | I>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
21 | S2 | NOC2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
21 | V1 | NOC2 | I>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
21 | V2 | NOC2 | I>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
21 | I1 | NOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
21 | I2 | NOC2 | I>> starts | UINT32 | R | 0...4294967295
21 | I3 | NOC2 | I>> trips | UINT32 | R | 0...4294967295
21 | I4 | NOC2 | I>> blocks | UINT32 | R | 0...4294967295
21 | S3 | NOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
21 | S4 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S5 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S6 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S7 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S8 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S9 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S10 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S11 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S12 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S13 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S14 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S15 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S16 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S17 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S18 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S19 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S20 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S21 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S22 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S23 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S24 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S25 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S26 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S27 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S28 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S29 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S30 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S31 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S32 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S33 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S34 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S35 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | O1 | NOC2 | I>> START (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O2 | NOC2 | I>> START(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O3 | NOC2 | I>> START(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O4 | NOC2 | I>> START(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O5 | NOC2 | I>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O6 | NOC2 | I>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O7 | NOC2 | I>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O8 | NOC2 | I>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O9 | NOC2 | I>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
21 | V3 | NOC2 | Newest Register | UINT32 | R | 0...12
21 | V4 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V5 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V6 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V7 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V8 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V9 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V10 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V11 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V12 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V13 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V14 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V15 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V16 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V17 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V18 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V19 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V20 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V21 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V22 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V23 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V24 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V25 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V26 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V27 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V28 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V29 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V30 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V31 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V32 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V33 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V34 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V35 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V36 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V37 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V38 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V39 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | S36 | NOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
22 | S1 | NOC3 | I>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
22 | S2 | NOC3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
22 | V1 | NOC3 | I>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
22 | V2 | NOC3 | I>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
22 | I1 | NOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
22 | I2 | NOC3 | I>>> starts | UINT32 | R | 0...4294967295
22 | I3 | NOC3 | I>>> trips | UINT32 | R | 0...4294967295
22 | I4 | NOC3 | I>>> blocks | UINT32 | R | 0...4294967295
22 | S3 | NOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
22 | S4 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S5 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S6 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S7 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S8 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S9 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S10 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S11 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S12 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S13 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S14 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S15 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S16 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S17 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S18 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S19 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S20 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S21 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S22 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S23 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S24 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S25 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S26 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S27 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S28 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S29 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S30 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S31 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S32 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S33 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S34 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S35 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | O1 | NOC3 | I>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O2 | NOC3 | I>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O3 | NOC3 | I>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O4 | NOC3 | I>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O5 | NOC3 | I>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O6 | NOC3 | I>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O7 | NOC3 | I>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O8 | NOC3 | I>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O9 | NOC3 | I>>>BLOCKED | SIGNAL_OUT | RW | 0...4294967295
22 | V3 | NOC3 | Newest Register | UINT32 | R | 0...12
22 | V4 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V5 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V6 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V7 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V8 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V9 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V10 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V11 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V12 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V13 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V14 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V15 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V16 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V17 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V18 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V19 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V20 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V21 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V22 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V23 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V24 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V25 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V26 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V27 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V28 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V29 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V30 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V31 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V32 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V33 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V34 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V35 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V36 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V37 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V38 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V39 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | S36 | NOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
23 | S1 | NOC4 | I>>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
23 | S2 | NOC4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
23 | V1 | NOC4 | I>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
23 | V2 | NOC4 | I>>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
23 | I1 | NOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
23 | I2 | NOC4 | I>>>> starts | UINT32 | R | 0...4294967295
23 | I3 | NOC4 | I>>>> trips | UINT32 | R | 0...4294967295
23 | I4 | NOC4 | I>>>> blocks | UINT32 | R | 0...4294967295
23 | S3 | NOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
23 | S4 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S5 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S6 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S7 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S8 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S9 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S10 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S11 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S12 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S13 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S14 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S15 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S16 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S17 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S18 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S19 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S20 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S21 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S22 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S23 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S24 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S25 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S26 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S27 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S28 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S29 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S30 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S31 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S32 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S33 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S34 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S35 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | O1 | NOC4 | I>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O2 | NOC4 | I>>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O3 | NOC4 | I>>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O4 | NOC4 | I>>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O5 | NOC4 | I>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O6 | NOC4 | I>>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O7 | NOC4 | I>>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O8 | NOC4 | I>>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O9 | NOC4 | I>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
23 | V3 | NOC4 | Newest Register | UINT32 | R | 0...12
23 | V4 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V5 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V6 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V7 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V8 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V9 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V10 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V11 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V12 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V13 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V14 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V15 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V16 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V17 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V18 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V19 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V20 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V21 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V22 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V23 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V24 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V25 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V26 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V27 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V28 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V29 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V30 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V31 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V32 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V33 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V34 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V35 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V36 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V37 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V38 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V39 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | S36 | NOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
205 | V1 | ROC1 | Idrw> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
205 | I1 | ROC1 | Idrw> Imeas/Iset at the moment | FLOAT | R | -1250...1250
205 | I2 | ROC1 | Idrw> I/U Angle atm. | FLOAT | R | -360...360
205 | I3 | ROC1 | Idrw> I measured p.u. | FLOAT | R | 0...1250
205 | I4 | ROC1 | Idrw> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
205 | I5 | ROC1 | Idrw> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
205 | I6 | ROC1 | Idrw> U measured p.u. | FLOAT | R | 0...1250
205 | I7 | ROC1 | Idrw> starts | UINT32 | R | 0...4294967295
205 | I8 | ROC1 | Idrw> trips | UINT32 | R | 0...4294967295
205 | I9 | ROC1 | Idrw> blocks | UINT32 | R | 0...4294967295
205 | S1 | ROC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
205 | S2 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S3 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S4 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S5 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S6 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S7 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S8 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S9 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S10 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S11 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S12 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S13 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S14 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S15 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S16 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S17 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S18 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S19 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S20 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S21 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S22 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S23 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S24 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S25 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S26 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S27 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S28 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S29 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S30 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S31 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S32 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S33 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S34 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S35 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S36 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S37 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S38 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S39 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S40 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S41 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S42 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S43 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S44 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S45 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S46 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S47 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S48 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S49 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S50 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S51 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S52 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S53 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S54 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S55 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S56 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S57 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S58 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S59 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S60 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S61 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S62 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S63 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S64 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S65 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | O1 | ROC1 | Idrw> START | SIGNAL_OUT | RW | 0...4294967295
205 | O2 | ROC1 | Idrw> TRIP | SIGNAL_OUT | RW | 0...4294967295
205 | O3 | ROC1 | Idrw> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
205 | V2 | ROC1 | Newest Register | UINT32 | R | 0...12
205 | V3 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V4 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V5 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V6 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V7 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V8 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V9 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V10 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V11 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V12 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V13 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V14 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V15 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V16 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V17 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V18 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V19 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V20 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V21 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V22 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V23 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V24 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V25 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V26 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | S66 | ROC1 | EventMaskLo | UINT32 | RW | 0...4294967295
206 | V1 | ROC2 | Idrw>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
206 | I1 | ROC2 | Idrw>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
206 | I2 | ROC2 | Idrw>> I/U Angle atm. | FLOAT | R | -360...360
206 | I3 | ROC2 | Idrw>> I measured p.u. | FLOAT | R | 0...1250
206 | I4 | ROC2 | Idrw>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
206 | I5 | ROC2 | Idrw>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
206 | I6 | ROC2 | Idrw>> U measured p.u. | FLOAT | R | 0...1250
206 | I7 | ROC2 | Idrw>> starts | UINT32 | R | 0...4294967295
206 | I8 | ROC2 | Idrw>> trips | UINT32 | R | 0...4294967295
206 | I9 | ROC2 | Idrw>> blocks | UINT32 | R | 0...4294967295
206 | S1 | ROC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
206 | S2 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S3 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S4 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S5 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S6 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S7 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S8 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S9 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S10 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S11 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S12 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S13 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S14 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S15 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S16 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S17 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S18 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S19 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S20 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S21 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S22 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S23 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S24 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S25 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S26 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S27 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S28 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S29 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S30 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S31 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S32 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S33 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S34 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S35 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S36 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S37 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S38 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S39 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S40 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S41 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S42 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S43 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S44 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S45 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S46 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S47 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S48 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S49 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S50 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S51 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S52 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S53 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S54 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S55 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S56 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S57 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S58 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S59 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S60 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S61 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S62 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S63 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S64 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S65 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | O1 | ROC2 | Idrw>> START | SIGNAL_OUT | RW | 0...4294967295
206 | O2 | ROC2 | Idrw>> TRIP | SIGNAL_OUT | RW | 0...4294967295
206 | O3 | ROC2 | Idrw>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
206 | V2 | ROC2 | Newest Register | UINT32 | R | 0...12
206 | V3 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V4 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V5 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V6 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V7 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V8 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V9 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V10 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V11 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V12 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V13 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V14 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V15 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V16 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V17 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V18 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V19 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V20 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V21 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V22 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V23 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V24 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V25 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V26 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | S66 | ROC2 | EventMaskLo | UINT32 | RW | 0...4294967295
207 | V1 | ROC3 | Idrw>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
207 | I1 | ROC3 | Idrw>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
207 | I2 | ROC3 | Idrw>>> I/U Angle atm. | FLOAT | R | -360...360
207 | I3 | ROC3 | Idrw>>> I measured p.u. | FLOAT | R | 0...1250
207 | I4 | ROC3 | Idrw>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
207 | I5 | ROC3 | Idrw>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
207 | I6 | ROC3 | Idrw>>> U measured p.u. | FLOAT | R | 0...1250
207 | I7 | ROC3 | Idrw>>> starts | UINT32 | R | 0...4294967295
207 | I8 | ROC3 | Idrw>>> trips | UINT32 | R | 0...4294967295
207 | I9 | ROC3 | Idrw>>> blocks | UINT32 | R | 0...4294967295
207 | S1 | ROC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
207 | S2 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S3 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S4 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S5 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S6 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S7 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S8 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S9 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S10 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S11 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S12 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S13 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S14 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S15 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S16 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S17 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S18 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S19 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S20 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S21 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S22 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S23 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S24 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S25 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S26 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S27 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S28 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S29 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S30 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S31 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S32 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S33 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S34 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S35 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S36 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S37 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S38 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S39 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S40 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S41 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S42 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S43 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S44 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S45 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S46 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S47 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S48 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S49 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S50 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S51 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S52 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S53 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S54 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S55 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S56 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S57 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S58 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S59 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S60 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S61 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S62 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S63 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S64 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S65 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | O1 | ROC3 | Idrw>>> START | SIGNAL_OUT | RW | 0...4294967295
207 | O2 | ROC3 | Idrw>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
207 | O3 | ROC3 | Idrw>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
207 | V2 | ROC3 | Newest Register | UINT32 | R | 0...12
207 | V3 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V4 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V5 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V6 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V7 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V8 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V9 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V10 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V11 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V12 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V13 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V14 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V15 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V16 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V17 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V18 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V19 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V20 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V21 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V22 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V23 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V24 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V25 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V26 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | S66 | ROC3 | EventMaskLo | UINT32 | RW | 0...4294967295
208 | V1 | ROC4 | Idrw>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
208 | I1 | ROC4 | Idrw>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
208 | I2 | ROC4 | Idrw>>>> I/U Angle atm. | FLOAT | R | -360...360
208 | I3 | ROC4 | Idrw>>>> I measured p.u. | FLOAT | R | 0...1250
208 | I4 | ROC4 | Idrw>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
208 | I5 | ROC4 | Idrw>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
208 | I6 | ROC4 | Idrw>>>> U measured p.u. | FLOAT | R | 0...1250
208 | I7 | ROC4 | Idrw>>>> starts | UINT32 | R | 0...4294967295
208 | I8 | ROC4 | Idrw>>>> trips | UINT32 | R | 0...4294967295
208 | I9 | ROC4 | Idrw>>>> blocks | UINT32 | R | 0...4294967295
208 | S1 | ROC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
208 | S2 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S3 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S4 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S5 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S6 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S7 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S8 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S9 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S10 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S11 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S12 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S13 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S14 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S15 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S16 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S17 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S18 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S19 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S20 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S21 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S22 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S23 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S24 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S25 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S26 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S27 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S28 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S29 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S30 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S31 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S32 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S33 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S34 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S35 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S36 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S37 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S38 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S39 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S40 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S41 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S42 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S43 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S44 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S45 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S46 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S47 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S48 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S49 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S50 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S51 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S52 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S53 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S54 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S55 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S56 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S57 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S58 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S59 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S60 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S61 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S62 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S63 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S64 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S65 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | O1 | ROC4 | Idrw>>>> START | SIGNAL_OUT | RW | 0...4294967295
208 | O2 | ROC4 | Idrw>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
208 | O3 | ROC4 | Idrw>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
208 | V2 | ROC4 | Newest Register | UINT32 | R | 0...12
208 | V3 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V4 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V5 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V6 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V7 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V8 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V9 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V10 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V11 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V12 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V13 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V14 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V15 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V16 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V17 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V18 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V19 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V20 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V21 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V22 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V23 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V24 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V25 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V26 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | S66 | ROC4 | EventMaskLo | UINT32 | RW | 0...4294967295
209 | V1 | ROC5 | Idrw>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
209 | I1 | ROC5 | Idrw>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
209 | I2 | ROC5 | Idrw>>>>> I/U Angle atm. | FLOAT | R | -360...360
209 | I3 | ROC5 | Idrw>>>>> I measured p.u. | FLOAT | R | 0...1250
209 | I4 | ROC5 | Idrw>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
209 | I5 | ROC5 | Idrw>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
209 | I6 | ROC5 | Idrw>>>>> U measured p.u. | FLOAT | R | 0...1250
209 | I7 | ROC5 | Idrw>>>>> starts | UINT32 | R | 0...4294967295
209 | I8 | ROC5 | Idrw>>>>> trips | UINT32 | R | 0...4294967295
209 | I9 | ROC5 | Idrw>>>>> blocks | UINT32 | R | 0...4294967295
209 | S1 | ROC5 | Clear statistics | UINT32 | W | 0=-;1=Clear
209 | S2 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S3 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S4 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S5 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S6 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S7 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S8 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S9 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S10 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S11 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S12 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S13 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S14 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S15 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S16 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S17 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S18 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S19 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S20 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S21 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S22 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S23 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S24 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S25 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S26 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S27 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S28 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S29 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S30 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S31 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S32 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S33 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S34 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S35 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S36 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S37 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S38 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S39 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S40 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S41 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S42 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S43 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S44 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S45 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S46 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S47 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S48 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S49 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S50 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S51 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S52 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S53 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S54 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S55 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S56 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S57 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S58 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S59 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S60 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S61 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S62 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S63 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S64 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S65 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | O1 | ROC5 | Idrw>>>>> START | SIGNAL_OUT | RW | 0...4294967295
209 | O2 | ROC5 | Idrw>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
209 | O3 | ROC5 | Idrw>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
209 | V2 | ROC5 | Newest Register | UINT32 | R | 0...12
209 | V3 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V4 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V5 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V6 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V7 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V8 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V9 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V10 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V11 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V12 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V13 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V14 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V15 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V16 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V17 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V18 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V19 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V20 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V21 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V22 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V23 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V24 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V25 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V26 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | S66 | ROC5 | EventMaskLo | UINT32 | RW | 0...4294967295
210 | V1 | ROC6 | Idrw>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
210 | I1 | ROC6 | Idrw>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
210 | I2 | ROC6 | Idrw>>>>>> I/U Angle atm. | FLOAT | R | -360...360
210 | I3 | ROC6 | Idrw>>>>>> I measured p.u. | FLOAT | R | 0...1250
210 | I4 | ROC6 | Idrw>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
210 | I5 | ROC6 | Idrw>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
210 | I6 | ROC6 | Idrw>>>>>> U measured p.u. | FLOAT | R | 0...1250
210 | I7 | ROC6 | Idrw>>>>>> starts | UINT32 | R | 0...4294967295
210 | I8 | ROC6 | Idrw>>>>>> trips | UINT32 | R | 0...4294967295
210 | I9 | ROC6 | Idrw>>>>>> blocks | UINT32 | R | 0...4294967295
210 | S1 | ROC6 | Clear statistics | UINT32 | W | 0=-;1=Clear
210 | S2 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S3 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S4 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S5 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S6 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S7 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S8 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S9 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S10 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S11 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S12 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S13 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S14 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S15 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S16 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S17 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S18 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S19 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S20 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S21 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S22 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S23 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S24 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S25 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S26 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S27 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S28 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S29 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S30 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S31 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S32 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S33 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S34 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S35 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S36 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S37 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S38 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S39 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S40 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S41 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S42 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S43 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S44 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S45 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S46 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S47 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S48 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S49 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S50 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S51 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S52 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S53 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S54 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S55 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S56 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S57 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S58 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S59 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S60 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S61 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S62 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S63 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S64 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S65 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | O1 | ROC6 | Idrw>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
210 | O2 | ROC6 | Idrw>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
210 | O3 | ROC6 | Idrw>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
210 | V2 | ROC6 | Newest Register | UINT32 | R | 0...12
210 | V3 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V4 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V5 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V6 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V7 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V8 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V9 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V10 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V11 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V12 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V13 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V14 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V15 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V16 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V17 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V18 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V19 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V20 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V21 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V22 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V23 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V24 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V25 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V26 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | S66 | ROC6 | EventMaskLo | UINT32 | RW | 0...4294967295
211 | V1 | ROC7 | Idrw>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
211 | I1 | ROC7 | Idrw>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
211 | I2 | ROC7 | Idrw>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
211 | I3 | ROC7 | Idrw>>>>>>> I measured p.u. | FLOAT | R | 0...1250
211 | I4 | ROC7 | Idrw>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
211 | I5 | ROC7 | Idrw>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
211 | I6 | ROC7 | Idrw>>>>>>> U measured p.u. | FLOAT | R | 0...1250
211 | I7 | ROC7 | Idrw>>>>>>> starts | UINT32 | R | 0...4294967295
211 | I8 | ROC7 | Idrw>>>>>>> trips | UINT32 | R | 0...4294967295
211 | I9 | ROC7 | Idrw>>>>>>> blocks | UINT32 | R | 0...4294967295
211 | S1 | ROC7 | Clear statistics | UINT32 | W | 0=-;1=Clear
211 | S2 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S3 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S4 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S5 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S6 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S7 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S8 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S9 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S10 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S11 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S12 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S13 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S14 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S15 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S16 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S17 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S18 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S19 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S20 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S21 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S22 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S23 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S24 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S25 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S26 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S27 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S28 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S29 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S30 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S31 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S32 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S33 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S34 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S35 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S36 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S37 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S38 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S39 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S40 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S41 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S42 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S43 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S44 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S45 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S46 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S47 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S48 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S49 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S50 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S51 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S52 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S53 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S54 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S55 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S56 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S57 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S58 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S59 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S60 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S61 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S62 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S63 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S64 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S65 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | O1 | ROC7 | Idrw>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
211 | O2 | ROC7 | Idrw>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
211 | O3 | ROC7 | Idrw>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
211 | V2 | ROC7 | Newest Register | UINT32 | R | 0...12
211 | V3 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V4 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V5 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V6 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V7 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V8 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V9 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V10 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V11 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V12 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V13 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V14 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V15 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V16 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V17 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V18 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V19 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V20 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V21 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V22 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V23 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V24 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V25 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V26 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | S66 | ROC7 | EventMaskLo | UINT32 | RW | 0...4294967295
212 | V1 | ROC8 | Idrw>>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
212 | I1 | ROC8 | Idrw>>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
212 | I2 | ROC8 | Idrw>>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
212 | I3 | ROC8 | Idrw>>>>>>>> I measured p.u. | FLOAT | R | 0...1250
212 | I4 | ROC8 | Idrw>>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
212 | I5 | ROC8 | Idrw>>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
212 | I6 | ROC8 | Idrw>>>>>>>> U measured p.u. | FLOAT | R | 0...1250
212 | I7 | ROC8 | Idrw>>>>>>>> starts | UINT32 | R | 0...4294967295
212 | I8 | ROC8 | Idrw>>>>>>>> trips | UINT32 | R | 0...4294967295
212 | I9 | ROC8 | Idrw>>>>>>>> blocks | UINT32 | R | 0...4294967295
212 | S1 | ROC8 | Clear statistics | UINT32 | W | 0=-;1=Clear
212 | S2 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S3 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S4 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S5 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S6 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S7 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S8 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S9 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S10 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S11 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S12 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S13 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S14 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S15 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S16 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S17 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S18 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S19 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S20 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S21 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S22 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S23 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S24 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S25 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S26 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S27 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S28 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S29 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S30 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S31 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S32 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S33 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S34 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S35 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S36 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S37 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S38 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S39 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S40 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S41 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S42 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S43 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S44 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S45 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S46 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S47 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S48 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S49 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S50 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S51 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S52 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S53 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S54 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S55 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S56 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S57 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S58 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S59 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S60 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S61 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S62 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S63 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S64 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S65 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | O1 | ROC8 | Idrw>>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
212 | O2 | ROC8 | Idrw>>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
212 | O3 | ROC8 | Idrw>>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
212 | V2 | ROC8 | Newest Register | UINT32 | R | 0...12
212 | V3 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V4 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V5 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V6 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V7 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V8 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V9 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V10 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V11 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V12 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V13 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V14 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V15 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V16 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V17 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V18 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V19 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V20 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V21 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V22 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V23 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V24 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V25 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V26 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | S66 | ROC8 | EventMaskLo | UINT32 | RW | 0...4294967295
213 | V1 | ROV1 | Urw>/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
213 | I1 | ROV1 | Urw>/< Umeas/Uset at the moment | FLOAT | R | 0...1250
213 | I2 | ROV1 | Urw>/< U measured p.u. | FLOAT | R | 0...1250
213 | I3 | ROV1 | Urw>/< starts | UINT32 | R | 0...4294967295
213 | I4 | ROV1 | Urw>/< trips | UINT32 | R | 0...4294967295
213 | I5 | ROV1 | Urw>/< blocks | UINT32 | R | 0...4294967295
213 | S1 | ROV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
213 | S2 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S3 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S4 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S5 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S6 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S7 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S8 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S9 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S10 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S11 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S12 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S13 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S14 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S15 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S16 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S17 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S18 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S19 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S20 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S21 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S22 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S23 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S24 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S25 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S26 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S27 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S28 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S29 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S30 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S31 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S32 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S33 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S34 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S35 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S36 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S37 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S38 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S39 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S40 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S41 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S42 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S43 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S44 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S45 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S46 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S47 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S48 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S49 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | O1 | ROV1 | Urw>/< START | SIGNAL_OUT | RW | 0...4294967295
213 | O2 | ROV1 | Urw>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
213 | O3 | ROV1 | Urw>/< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
213 | O4 | ROV1 | Urw>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
213 | V2 | ROV1 | Newest Register | UINT32 | R | 0...12
213 | V3 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V4 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V5 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V6 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V7 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V8 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V9 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V10 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V11 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V12 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V13 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V14 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V15 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V16 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V17 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V18 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V19 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V20 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V21 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V22 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V23 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V24 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V25 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V26 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | S50 | ROV1 | EventMaskLo | UINT32 | RW | 0...4294967295
214 | V1 | ROV2 | Urw>>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
214 | I1 | ROV2 | Urw>>/<< Umeas/Uset at the moment | FLOAT | R | 0...1250
214 | I2 | ROV2 | Urw>>/<< U measured p.u. | FLOAT | R | 0...1250
214 | I3 | ROV2 | Urw>>/<< starts | UINT32 | R | 0...4294967295
214 | I4 | ROV2 | Urw>>/<< trips | UINT32 | R | 0...4294967295
214 | I5 | ROV2 | Urw>>/<< blocks | UINT32 | R | 0...4294967295
214 | S1 | ROV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
214 | S2 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S3 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S4 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S5 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S6 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S7 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S8 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S9 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S10 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S11 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S12 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S13 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S14 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S15 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S16 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S17 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S18 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S19 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S20 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S21 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S22 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S23 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S24 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S25 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S26 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S27 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S28 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S29 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S30 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S31 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S32 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S33 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S34 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S35 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S36 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S37 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S38 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S39 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S40 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S41 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S42 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S43 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S44 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S45 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S46 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S47 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S48 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S49 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | O1 | ROV2 | Urw>>/<< START | SIGNAL_OUT | RW | 0...4294967295
214 | O2 | ROV2 | Urw>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
214 | O3 | ROV2 | Urw>>/<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
214 | O4 | ROV2 | Urw>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
214 | V2 | ROV2 | Newest Register | UINT32 | R | 0...12
214 | V3 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V4 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V5 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V6 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V7 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V8 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V9 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V10 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V11 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V12 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V13 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V14 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V15 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V16 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V17 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V18 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V19 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V20 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V21 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V22 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V23 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V24 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V25 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V26 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | S50 | ROV2 | EventMaskLo | UINT32 | RW | 0...4294967295
215 | V1 | ROV3 | Urw>>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
215 | I1 | ROV3 | Urw>>>/<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
215 | I2 | ROV3 | Urw>>>/<<< U measured p.u. | FLOAT | R | 0...1250
215 | I3 | ROV3 | Urw>>>/<<< starts | UINT32 | R | 0...4294967295
215 | I4 | ROV3 | Urw>>>/<<< trips | UINT32 | R | 0...4294967295
215 | I5 | ROV3 | Urw>>>/<<< blocks | UINT32 | R | 0...4294967295
215 | S1 | ROV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
215 | S2 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S3 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S4 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S5 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S6 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S7 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S8 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S9 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S10 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S11 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S12 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S13 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S14 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S15 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S16 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S17 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S18 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S19 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S20 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S21 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S22 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S23 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S24 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S25 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S26 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S27 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S28 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S29 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S30 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S31 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S32 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S33 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S34 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S35 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S36 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S37 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S38 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S39 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S40 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S41 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S42 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S43 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S44 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S45 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S46 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S47 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S48 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S49 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | O1 | ROV3 | Urw>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
215 | O2 | ROV3 | Urw>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
215 | O3 | ROV3 | Urw>>>/<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
215 | O4 | ROV3 | Urw>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
215 | V2 | ROV3 | Newest Register | UINT32 | R | 0...12
215 | V3 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V4 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V5 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V6 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V7 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V8 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V9 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V10 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V11 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V12 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V13 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V14 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V15 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V16 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V17 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V18 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V19 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V20 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V21 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V22 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V23 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V24 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V25 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V26 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | S50 | ROV3 | EventMaskLo | UINT32 | RW | 0...4294967295
216 | V1 | ROV4 | Urw>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
216 | I1 | ROV4 | Urw>>>>/<<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
216 | I2 | ROV4 | Urw>>>>/<<<< U measured p.u. | FLOAT | R | 0...1250
216 | I3 | ROV4 | Urw>>>>/<<<< starts | UINT32 | R | 0...4294967295
216 | I4 | ROV4 | Urw>>>>/<<<< trips | UINT32 | R | 0...4294967295
216 | I5 | ROV4 | Urw>>>>/<<<< blocks | UINT32 | R | 0...4294967295
216 | S1 | ROV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
216 | S2 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S3 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S4 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S5 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S6 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S7 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S8 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S9 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S10 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S11 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S12 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S13 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S14 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S15 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S16 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S17 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S18 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S19 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S20 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S21 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S22 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S23 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S24 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S25 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S26 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S27 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S28 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S29 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S30 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S31 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S32 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S33 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S34 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S35 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S36 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S37 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S38 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S39 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S40 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S41 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S42 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S43 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S44 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S45 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S46 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S47 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S48 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S49 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | O1 | ROV4 | Urw>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
216 | O2 | ROV4 | Urw>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
216 | O3 | ROV4 | Urw>>>>/<<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
216 | O4 | ROV4 | Urw>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
216 | V2 | ROV4 | Newest Register | UINT32 | R | 0...12
216 | V3 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V4 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V5 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V6 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V7 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V8 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V9 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V10 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V11 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V12 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V13 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V14 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V15 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V16 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V17 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V18 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V19 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V20 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V21 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V22 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V23 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V24 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V25 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V26 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | S50 | ROV4 | EventMaskLo | UINT32 | RW | 0...4294967295
224 | I1 | CNU1 | Measured unbalance current | FLOAT | R | 0...50.00
224 | I2 | CNU1 | Unbalance current angle | FLOAT | R | -360.00...360.00
224 | S1 | CNU1 | Natural unbalance compensation | UINT32 | RW | 0=Not used;1=In use
224 | S2 | CNU1 | Compensate natural unbal. | UINT32 | RW | 0=-;1=Comp
224 | I3 | CNU1 | Natural unbalance | FLOAT | R | -50.00...50.00
224 | I4 | CNU1 | Natural unbalance ang | FLOAT | R | -360.00...360.00
224 | I5 | CNU1 | Compensated magnitude | FLOAT | R | -50.00...50.00
224 | I6 | CNU1 | Compensated angle | FLOAT | R | -360.00...360.00
217 | V1 | UCP1 | IUC> condition | UINT32 | R | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
217 | I1 | UCP1 | Unbalance current atm. | FLOAT | R | 0...1250
217 | I2 | UCP1 | Imeas/Iset (ALARM) atm. | FLOAT | R | 0...1250
217 | I3 | UCP1 | Imeas/Iset (TRIP) atm. | FLOAT | R | 0...1250
217 | I4 | UCP1 | IUC> Alarm Starts | UINT32 | R | 0...4294967295
217 | I5 | UCP1 | IUC> Alarms | UINT32 | R | 0...4294967295
217 | I6 | UCP1 | IUC> Starts | UINT32 | R | 0...4294967295
217 | I7 | UCP1 | IUC> Trips | UINT32 | R | 0...4294967295
217 | I8 | UCP1 | IUC> Blocks | UINT32 | R | 0...4294967295
217 | S1 | UCP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
217 | S2 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S3 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S4 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S5 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S6 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S7 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S8 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S9 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S10 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S11 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S12 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S13 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S14 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S15 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S16 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S17 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S18 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S19 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S20 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S21 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S22 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S23 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S24 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S25 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S26 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S27 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S28 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S29 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S30 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S31 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S32 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S33 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S34 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S35 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S36 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S37 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S38 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S39 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S40 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S41 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | O1 | UCP1 | IUC> ALARM START | SIGNAL_OUT | RW | 0...4294967295
217 | O2 | UCP1 | IUC> ALARM | SIGNAL_OUT | RW | 0...4294967295
217 | O3 | UCP1 | IUC> START | SIGNAL_OUT | RW | 0...4294967295
217 | O4 | UCP1 | IUC> TRIP | SIGNAL_OUT | RW | 0...4294967295
217 | O5 | UCP1 | IUC> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
217 | V2 | UCP1 | Newest Register | UINT32 | R | 0...12
217 | V3 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V4 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V5 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V6 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V7 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V8 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V9 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V10 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V11 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V12 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V13 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V14 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | S42 | UCP1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S1 | DOC1 | Idir> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
75 | V1 | DOC1 | Idir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
75 | I1 | DOC1 | Operating angle now | FLOAT | R | -360...360
75 | I2 | DOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
75 | I3 | DOC1 | Idir> starts | UINT32 | R | 0...4294967295
75 | I4 | DOC1 | Idir> trips | UINT32 | R | 0...4294967295
75 | I5 | DOC1 | Idir> blocks | UINT32 | R | 0...4294967295
75 | S2 | DOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
75 | S3 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S4 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S5 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S6 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S7 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S8 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S9 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S10 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S11 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S12 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S13 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S14 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S15 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S16 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S17 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S18 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S19 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S20 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S21 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S22 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S23 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S24 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S25 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S26 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S27 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S28 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S29 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S30 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S31 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S32 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S33 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S34 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S35 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S36 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S37 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S38 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S39 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S40 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S41 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S42 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S43 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S44 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S45 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S46 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S47 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S48 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S49 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S50 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S51 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S52 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S53 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S54 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S55 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S56 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S57 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S58 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | O1 | DOC1 | Idir> START | SIGNAL_OUT | RW | 0...4294967295
75 | O2 | DOC1 | Idir> TRIP | SIGNAL_OUT | RW | 0...4294967295
75 | O3 | DOC1 | Idir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
75 | S59 | DOC1 | Clear registers | UINT32 | W | 0=-;1=Clear
75 | I6 | DOC1 | Newest Register | UINT32 | R | 0...12
75 | I7 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I8 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I9 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I10 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I11 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I12 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I13 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I14 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I15 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I16 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I17 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I18 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I19 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I20 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I21 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I22 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I23 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I24 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I25 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I26 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I27 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I28 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I29 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I30 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I31 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I32 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I33 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I34 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I35 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I36 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I37 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I38 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I39 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I40 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I41 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I42 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I43 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I44 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I45 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I46 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I47 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I48 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I49 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I50 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I51 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I52 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I53 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I54 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | S60 | DOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S61 | DOC1 | EventMaskHi | UINT32 | RW | 0...4294967295
76 | S1 | DOC2 | Idir>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
76 | V1 | DOC2 | Idir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
76 | I1 | DOC2 | Operating angle now | FLOAT | R | -360.00...360.00
76 | I2 | DOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
76 | I3 | DOC2 | Idir>> starts | UINT32 | R | 0...4294967295
76 | I4 | DOC2 | Idir>> trips | UINT32 | R | 0...4294967295
76 | I5 | DOC2 | Idir>> blocks | UINT32 | R | 0...4294967295
76 | S2 | DOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
76 | S3 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S4 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S5 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S6 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S7 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S8 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S9 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S10 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S11 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S12 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S13 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S14 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S15 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S16 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S17 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S18 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S19 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S20 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S21 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S22 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S23 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S24 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S25 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S26 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S27 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S28 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S29 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S30 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S31 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S32 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S33 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S34 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S35 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S36 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S37 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S38 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S39 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S40 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S41 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S42 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S43 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S44 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S45 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S46 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S47 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S48 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S49 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S50 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S51 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S52 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S53 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S54 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S55 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S56 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S57 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S58 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | O1 | DOC2 | Idir>> START | SIGNAL_OUT | RW | 0...4294967295
76 | O2 | DOC2 | Idir>> TRIP | SIGNAL_OUT | RW | 0...4294967295
76 | O3 | DOC2 | Idir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
76 | S59 | DOC2 | Clear registers | UINT32 | W | 0=-;1=Clear
76 | I6 | DOC2 | Newest Register | UINT32 | R | 0...12
76 | I7 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I8 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I9 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I10 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I11 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I12 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I13 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I14 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I15 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I16 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I17 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I18 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I19 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I20 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I21 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I22 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I23 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I24 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I25 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I26 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I27 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I28 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I29 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I30 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I31 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I32 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I33 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I34 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I35 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I36 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I37 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I38 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I39 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I40 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I41 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I42 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I43 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I44 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I45 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I46 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I47 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I48 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I49 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I50 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I51 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I52 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I53 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I54 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | S60 | DOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
76 | S61 | DOC2 | EventMaskHi | UINT32 | RW | 0...4294967295
77 | S1 | DOC3 | Idir>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
77 | V1 | DOC3 | Idir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
77 | I1 | DOC3 | Operating angle now | FLOAT | R | -360...360
77 | I2 | DOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
77 | I3 | DOC3 | Idir>>> starts | UINT32 | R | 0...4294967295
77 | I4 | DOC3 | Idir>>> trips | UINT32 | R | 0...4294967295
77 | I5 | DOC3 | Idir>>> blocks | UINT32 | R | 0...4294967295
77 | S2 | DOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
77 | S3 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S4 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S5 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S6 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S7 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S8 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S9 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S10 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S11 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S12 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S13 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S14 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S15 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S16 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S17 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S18 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S19 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S20 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S21 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S22 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S23 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S24 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S25 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S26 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S27 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S28 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S29 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S30 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S31 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S32 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S33 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S34 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S35 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S36 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S37 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S38 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S39 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S40 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S41 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S42 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S43 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S44 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S45 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S46 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S47 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S48 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S49 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S50 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S51 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S52 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S53 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S54 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S55 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S56 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S57 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S58 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | O1 | DOC3 | Idir>>> START | SIGNAL_OUT | RW | 0...4294967295
77 | O2 | DOC3 | Idir>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
77 | O3 | DOC3 | Idir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
77 | S59 | DOC3 | Clear registers | UINT32 | W | 0=-;1=Clear
77 | I6 | DOC3 | Newest Register | UINT32 | R | 0...12
77 | I7 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I8 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I9 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I10 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I11 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I12 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I13 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I14 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I15 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I16 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I17 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I18 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I19 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I20 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I21 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I22 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I23 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I24 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I25 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I26 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I27 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I28 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I29 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I30 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I31 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I32 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I33 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I34 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I35 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I36 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I37 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I38 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I39 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I40 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I41 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I42 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I43 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I44 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I45 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I46 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I47 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I48 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I49 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I50 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I51 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I52 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I53 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I54 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | S60 | DOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
77 | S61 | DOC3 | EventMaskHi | UINT32 | RW | 0...4294967295
78 | S1 | DOC4 | Idir>>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
78 | V1 | DOC4 | Idir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
78 | I1 | DOC4 | Operating angle now | FLOAT | R | -360.00...360.00
78 | I2 | DOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
78 | I3 | DOC4 | Idir>>>> starts | UINT32 | R | 0...4294967295
78 | I4 | DOC4 | Idir>>>> trips | UINT32 | R | 0...4294967295
78 | I5 | DOC4 | Idir>>>> blocks | UINT32 | R | 0...4294967295
78 | S2 | DOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
78 | S3 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S4 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S5 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S6 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S7 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S8 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S9 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S10 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S11 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S12 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S13 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S14 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S15 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S16 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S17 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S18 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S19 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S20 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S21 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S22 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S23 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S24 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S25 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S26 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S27 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S28 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S29 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S30 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S31 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S32 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S33 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S34 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S35 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S36 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S37 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S38 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S39 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S40 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S41 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S42 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S43 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S44 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S45 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S46 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S47 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S48 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S49 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S50 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S51 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S52 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S53 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S54 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S55 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S56 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S57 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S58 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | O1 | DOC4 | Idir>>>> START | SIGNAL_OUT | RW | 0...4294967295
78 | O2 | DOC4 | Idir>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
78 | O3 | DOC4 | Idir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
78 | S59 | DOC4 | Clear registers | UINT32 | W | 0=-;1=Clear
78 | I6 | DOC4 | Newest Register | UINT32 | R | 0...12
78 | I7 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I8 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I9 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I10 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I11 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I12 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I13 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I14 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I15 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I16 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I17 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I18 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I19 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I20 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I21 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I22 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I23 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I24 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I25 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I26 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I27 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I28 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I29 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I30 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I31 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I32 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I33 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I34 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I35 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I36 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I37 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I38 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I39 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I40 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I41 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I42 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I43 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I44 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I45 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I46 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I47 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I48 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I49 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I50 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I51 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I52 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I53 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I54 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | S60 | DOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
78 | S61 | DOC4 | EventMaskHi | UINT32 | RW | 0...4294967295
26 | S1 | NEF1 | I0> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
26 | S2 | NEF1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
26 | V1 | NEF1 | I0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
26 | I1 | NEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
26 | I2 | NEF1 | I0> starts | UINT32 | R | 0...4294967295
26 | I3 | NEF1 | I0> trips | UINT32 | R | 0...4294967295
26 | I4 | NEF1 | I0> blocks | UINT32 | R | 0...4294967295
26 | S3 | NEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
26 | S4 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S5 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S6 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S7 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S8 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S9 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S10 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S11 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S12 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S13 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S14 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S15 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S16 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S17 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S18 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S19 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S20 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S21 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S22 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S23 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S24 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S25 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S26 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S27 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S28 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S29 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S30 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S31 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S32 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S33 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S34 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S35 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | O1 | NEF1 | I0> START | SIGNAL_OUT | RW | 0...4294967295
26 | O2 | NEF1 | I0> TRIP | SIGNAL_OUT | RW | 0...4294967295
26 | O3 | NEF1 | I0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
26 | I5 | NEF1 | Newest Register | UINT32 | R | 0...12
26 | I6 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I7 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I8 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I9 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I10 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I11 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I12 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I13 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I14 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I15 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I16 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I17 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | S36 | NEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
27 | S1 | NEF2 | I0>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
27 | S2 | NEF2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
27 | V1 | NEF2 | I0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
27 | I1 | NEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
27 | I2 | NEF2 | I0>> starts | UINT32 | R | 0...4294967295
27 | I3 | NEF2 | I0>> trips | UINT32 | R | 0...4294967295
27 | I4 | NEF2 | I0>> blocks | UINT32 | R | 0...4294967295
27 | S3 | NEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
27 | S4 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S5 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S6 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S7 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S8 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S9 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S10 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S11 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S12 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S13 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S14 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S15 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S16 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S17 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S18 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S19 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S20 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S21 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S22 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S23 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S24 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S25 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S26 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S27 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S28 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S29 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S30 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S31 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S32 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S33 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S34 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S35 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | O1 | NEF2 | I0>> START | SIGNAL_OUT | RW | 0...4294967295
27 | O2 | NEF2 | I0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
27 | O3 | NEF2 | I0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
27 | I5 | NEF2 | Newest Register | UINT32 | R | 0...12
27 | I6 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I7 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I8 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I9 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I10 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I11 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I12 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I13 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I14 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I15 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I16 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I17 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | S36 | NEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
28 | S1 | NEF3 | I0>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
28 | S2 | NEF3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
28 | V1 | NEF3 | I0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
28 | I1 | NEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
28 | I2 | NEF3 | I0>>> starts | UINT32 | R | 0...4294967295
28 | I3 | NEF3 | I0>>> trips | UINT32 | R | 0...4294967295
28 | I4 | NEF3 | I0>>> blocks | UINT32 | R | 0...4294967295
28 | S3 | NEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
28 | S4 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S5 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S6 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S7 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S8 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S9 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S10 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S11 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S12 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S13 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S14 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S15 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S16 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S17 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S18 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S19 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S20 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S21 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S22 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S23 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S24 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S25 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S26 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S27 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S28 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S29 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S30 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S31 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S32 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S33 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S34 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S35 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | O1 | NEF3 | I0>>> START | SIGNAL_OUT | RW | 0...4294967295
28 | O2 | NEF3 | I0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
28 | O3 | NEF3 | I0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
28 | I5 | NEF3 | Newest Register | UINT32 | R | 0...12
28 | I6 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I7 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I8 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I9 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I10 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I11 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I12 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I13 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I14 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I15 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I16 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I17 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | S36 | NEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
29 | S1 | NEF4 | I0>>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
29 | S2 | NEF4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
29 | V1 | NEF4 | I0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
29 | I1 | NEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
29 | I2 | NEF4 | I0>>>> starts | UINT32 | R | 0...4294967295
29 | I3 | NEF4 | I0>>>> trips | UINT32 | R | 0...4294967295
29 | I4 | NEF4 | I0>>>> blocks | UINT32 | R | 0...4294967295
29 | S3 | NEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
29 | S4 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S5 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S6 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S7 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S8 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S9 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S10 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S11 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S12 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S13 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S14 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S15 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S16 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S17 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S18 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S19 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S20 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S21 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S22 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S23 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S24 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S25 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S26 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S27 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S28 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S29 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S30 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S31 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S32 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S33 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S34 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S35 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | O1 | NEF4 | I0>>>> START | SIGNAL_OUT | RW | 0...4294967295
29 | O2 | NEF4 | I0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
29 | O3 | NEF4 | I0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
29 | I5 | NEF4 | Newest Register | UINT32 | R | 0...12
29 | I6 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I7 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I8 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I9 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I10 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I11 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I12 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I13 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I14 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I15 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I16 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I17 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | S36 | NEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | S1 | DEF1 | I0dir> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
81 | V1 | DEF1 | I0dir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
81 | I1 | DEF1 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
81 | I2 | DEF1 | I0 Magnitude | FLOAT | R | 0...250
81 | I3 | DEF1 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
81 | I4 | DEF1 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
81 | I5 | DEF1 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
81 | I6 | DEF1 | DEF(1) Measured residual current change | FLOAT | R | 0...250
81 | I7 | DEF1 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
81 | I8 | DEF1 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
81 | I9 | DEF1 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
81 | I10 | DEF1 | I0 meas / I0 set now | FLOAT | R | -250...250
81 | I11 | DEF1 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
81 | I12 | DEF1 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
81 | I13 | DEF1 | U0 meas now | FLOAT | R | 0...500
81 | I14 | DEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
81 | I15 | DEF1 | I0dir> starts | UINT32 | R | 0...4294967295
81 | I16 | DEF1 | I0dir> trips | UINT32 | R | 0...4294967295
81 | I17 | DEF1 | I0dir> blocks | UINT32 | R | 0...4294967295
81 | S2 | DEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
81 | S3 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S4 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S5 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S6 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S7 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S8 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S9 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S10 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S11 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S12 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S13 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S14 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S15 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S16 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S17 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S18 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S19 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S20 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S21 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S22 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S23 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S24 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S25 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S26 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S27 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S28 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S29 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S30 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S31 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S32 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S33 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S34 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S35 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S36 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S37 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S38 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S39 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S40 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S41 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S42 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S43 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S44 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S45 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S46 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S47 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S48 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S49 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S50 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S51 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S52 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S53 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S54 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S55 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S56 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S57 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S58 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S59 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S60 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S61 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S62 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S63 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S64 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S65 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S66 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S67 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S68 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S69 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S70 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S71 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S72 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S73 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S74 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S75 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S76 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S77 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S78 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S79 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S80 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S81 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S82 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S83 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S84 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S85 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S86 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S87 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S88 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S89 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S90 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S91 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S92 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S93 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S94 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S95 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S96 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S97 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S98 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S99 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S100 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S101 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S102 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S103 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S104 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S105 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S106 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S107 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S108 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S109 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S110 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S111 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S112 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S113 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S114 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S115 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S116 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S117 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S118 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S119 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S120 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S121 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S122 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | O1 | DEF1 | I0dir> START (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O2 | DEF1 | I0dir> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O3 | DEF1 | I0dir> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O4 | DEF1 | I0dir> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O5 | DEF1 | I0dir> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O6 | DEF1 | I0dir> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O7 | DEF1 | I0dir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
81 | I18 | DEF1 | Newest Register | UINT32 | R | 0...12
81 | I19 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I20 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I21 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I22 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I23 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I24 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I25 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I26 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I27 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I28 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I29 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I30 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I31 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I32 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I33 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I34 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I35 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I36 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I37 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I38 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I39 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I40 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I41 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I42 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I43 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I44 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I45 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I46 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I47 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I48 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I49 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I50 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I51 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I52 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I53 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I54 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I55 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I56 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I57 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I58 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I59 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I60 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I61 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I62 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I63 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I64 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I65 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I66 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I67 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I68 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I69 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I70 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I71 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I72 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I73 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I74 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I75 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I76 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I77 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I78 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I79 | DEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | I80 | DEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
82 | S1 | DEF2 | I0dir>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
82 | V1 | DEF2 | I0dir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
82 | I1 | DEF2 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
82 | I2 | DEF2 | I0 Magnitude | FLOAT | R | 0...250
82 | I3 | DEF2 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
82 | I4 | DEF2 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
82 | I5 | DEF2 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
82 | I6 | DEF2 | DEF(1) Measured residual current change | FLOAT | R | 0...250
82 | I7 | DEF2 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
82 | I8 | DEF2 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
82 | I9 | DEF2 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
82 | I10 | DEF2 | I0 meas / I0 set now | FLOAT | R | -250...250
82 | I11 | DEF2 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
82 | I12 | DEF2 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
82 | I13 | DEF2 | U0 meas now | FLOAT | R | 0...500
82 | I14 | DEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
82 | I15 | DEF2 | I0dir>> starts | UINT32 | R | 0...4294967295
82 | I16 | DEF2 | I0dir>> trips | UINT32 | R | 0...4294967295
82 | I17 | DEF2 | I0dir>> blocks | UINT32 | R | 0...4294967295
82 | S2 | DEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
82 | S3 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S4 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S5 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S6 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S7 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S8 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S9 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S10 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S11 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S12 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S13 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S14 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S15 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S16 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S17 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S18 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S19 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S20 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S21 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S22 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S23 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S24 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S25 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S26 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S27 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S28 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S29 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S30 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S31 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S32 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S33 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S34 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S35 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S36 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S37 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S38 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S39 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S40 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S41 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S42 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S43 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S44 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S45 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S46 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S47 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S48 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S49 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S50 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S51 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S52 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S53 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S54 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S55 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S56 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S57 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S58 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S59 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S60 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S61 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S62 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S63 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S64 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S65 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S66 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S67 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S68 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S69 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S70 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S71 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S72 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S73 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S74 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S75 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S76 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S77 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S78 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S79 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S80 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S81 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S82 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S83 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S84 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S85 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S86 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S87 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S88 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S89 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S90 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S91 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S92 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S93 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S94 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S95 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S96 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S97 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S98 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S99 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S100 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S101 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S102 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S103 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S104 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S105 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S106 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S107 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S108 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S109 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S110 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S111 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S112 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S113 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S114 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S115 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S116 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S117 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S118 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S119 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S120 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S121 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S122 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | O1 | DEF2 | I0dir>> START (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O2 | DEF2 | I0dir>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O3 | DEF2 | I0dir>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O4 | DEF2 | I0dir>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O5 | DEF2 | I0dir>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O6 | DEF2 | I0dir>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O7 | DEF2 | I0dir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
82 | I18 | DEF2 | Newest Register | UINT32 | R | 0...12
82 | I19 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I20 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I21 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I22 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I23 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I24 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I25 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I26 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I27 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I28 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I29 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I30 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I31 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I32 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I33 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I34 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I35 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I36 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I37 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I38 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I39 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I40 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I41 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I42 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I43 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I44 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I45 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I46 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I47 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I48 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I49 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I50 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I51 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I52 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I53 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I54 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I55 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I56 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I57 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I58 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I59 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I60 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I61 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I62 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I63 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I64 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I65 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I66 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I67 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I68 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I69 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I70 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I71 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I72 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I73 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I74 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I75 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I76 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I77 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I78 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I79 | DEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
82 | I80 | DEF2 | EventMaskHi | UINT32 | RW | 0...4294967295
83 | S1 | DEF3 | I0dir>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
83 | V1 | DEF3 | I0dir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
83 | I1 | DEF3 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
83 | I2 | DEF3 | I0 Magnitude | FLOAT | R | 0...250
83 | I3 | DEF3 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
83 | I4 | DEF3 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
83 | I5 | DEF3 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
83 | I6 | DEF3 | DEF(1) Measured residual current change | FLOAT | R | 0...250
83 | I7 | DEF3 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
83 | I8 | DEF3 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
83 | I9 | DEF3 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
83 | I10 | DEF3 | I0 meas / I0 set now | FLOAT | R | -250...250
83 | I11 | DEF3 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
83 | I12 | DEF3 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
83 | I13 | DEF3 | U0 meas now | FLOAT | R | 0...500
83 | I14 | DEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
83 | I15 | DEF3 | I0dir>>> starts | UINT32 | R | 0...4294967295
83 | I16 | DEF3 | I0dir>>> trips | UINT32 | R | 0...4294967295
83 | I17 | DEF3 | I0dir>>> blocks | UINT32 | R | 0...4294967295
83 | S2 | DEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
83 | S3 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S4 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S5 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S6 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S7 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S8 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S9 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S10 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S11 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S12 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S13 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S14 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S15 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S16 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S17 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S18 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S19 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S20 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S21 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S22 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S23 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S24 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S25 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S26 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S27 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S28 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S29 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S30 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S31 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S32 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S33 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S34 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S35 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S36 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S37 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S38 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S39 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S40 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S41 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S42 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S43 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S44 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S45 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S46 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S47 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S48 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S49 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S50 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S51 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S52 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S53 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S54 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S55 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S56 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S57 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S58 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S59 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S60 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S61 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S62 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S63 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S64 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S65 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S66 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S67 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S68 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S69 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S70 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S71 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S72 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S73 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S74 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S75 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S76 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S77 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S78 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S79 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S80 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S81 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S82 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S83 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S84 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S85 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S86 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S87 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S88 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S89 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S90 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S91 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S92 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S93 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S94 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S95 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S96 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S97 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S98 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S99 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S100 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S101 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S102 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S103 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S104 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S105 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S106 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S107 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S108 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S109 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S110 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S111 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S112 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S113 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S114 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S115 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S116 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S117 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S118 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S119 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S120 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S121 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S122 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | O1 | DEF3 | I0dir>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O2 | DEF3 | I0dir>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O3 | DEF3 | I0dir>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O4 | DEF3 | I0dir>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O5 | DEF3 | I0dir>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O6 | DEF3 | I0dir>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O7 | DEF3 | I0dir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
83 | I18 | DEF3 | Newest Register | UINT32 | R | 0...12
83 | I19 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I20 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I21 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I22 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I23 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I24 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I25 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I26 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I27 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I28 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I29 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I30 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I31 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I32 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I33 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I34 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I35 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I36 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I37 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I38 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I39 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I40 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I41 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I42 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I43 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I44 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I45 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I46 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I47 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I48 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I49 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I50 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I51 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I52 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I53 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I54 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I55 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I56 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I57 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I58 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I59 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I60 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I61 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I62 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I63 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I64 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I65 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I66 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I67 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I68 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I69 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I70 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I71 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I72 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I73 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I74 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I75 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I76 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I77 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I78 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I79 | DEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
83 | I80 | DEF3 | EventMaskHi | UINT32 | RW | 0...4294967295
84 | S1 | DEF4 | I0dir>>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
84 | V1 | DEF4 | I0dir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
84 | I1 | DEF4 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
84 | I2 | DEF4 | I0 Magnitude | FLOAT | R | 0...250
84 | I3 | DEF4 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
84 | I4 | DEF4 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
84 | I5 | DEF4 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
84 | I6 | DEF4 | DEF(1) Measured residual current change | FLOAT | R | 0...250
84 | I7 | DEF4 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
84 | I8 | DEF4 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
84 | I9 | DEF4 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
84 | I10 | DEF4 | I0 meas / I0 set now | FLOAT | R | -250...250
84 | I11 | DEF4 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
84 | I12 | DEF4 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
84 | I13 | DEF4 | U0 meas now | FLOAT | R | 0...500
84 | I14 | DEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
84 | I15 | DEF4 | I0dir>>>> starts | UINT32 | R | 0...4294967295
84 | I16 | DEF4 | I0dir>>>> trips | UINT32 | R | 0...4294967295
84 | I17 | DEF4 | I0dir>>>> blocks | UINT32 | R | 0...4294967295
84 | S2 | DEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
84 | S3 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S4 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S5 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S6 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S7 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S8 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S9 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S10 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S11 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S12 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S13 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S14 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S15 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S16 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S17 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S18 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S19 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S20 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S21 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S22 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S23 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S24 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S25 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S26 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S27 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S28 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S29 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S30 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S31 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S32 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S33 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S34 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S35 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S36 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S37 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S38 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S39 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S40 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S41 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S42 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S43 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S44 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S45 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S46 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S47 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S48 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S49 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S50 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S51 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S52 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S53 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S54 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S55 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S56 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S57 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S58 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S59 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S60 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S61 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S62 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S63 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S64 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S65 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S66 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S67 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S68 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S69 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S70 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S71 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S72 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S73 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S74 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S75 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S76 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S77 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S78 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S79 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S80 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S81 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S82 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S83 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S84 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S85 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S86 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S87 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S88 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S89 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S90 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S91 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S92 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S93 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S94 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S95 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S96 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S97 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S98 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S99 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S100 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S101 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S102 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S103 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S104 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S105 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S106 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S107 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S108 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S109 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S110 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S111 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S112 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S113 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S114 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S115 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S116 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S117 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S118 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S119 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S120 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S121 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S122 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | O1 | DEF4 | I0dir>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O2 | DEF4 | I0dir>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O3 | DEF4 | I0dir>>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O4 | DEF4 | I0dir>>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O5 | DEF4 | I0dir>>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O6 | DEF4 | I0dir>>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O7 | DEF4 | I0dir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
84 | I18 | DEF4 | Newest Register | UINT32 | R | 0...12
84 | I19 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I20 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I21 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I22 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I23 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I24 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I25 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I26 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I27 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I28 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I29 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I30 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I31 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I32 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I33 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I34 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I35 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I36 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I37 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I38 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I39 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I40 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I41 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I42 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I43 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I44 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I45 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I46 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I47 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I48 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I49 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I50 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I51 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I52 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I53 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I54 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I55 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I56 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I57 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I58 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I59 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I60 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I61 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I62 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I63 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I64 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I65 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I66 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I67 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I68 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I69 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I70 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I71 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I72 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I73 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I74 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I75 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I76 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I77 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I78 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I79 | DEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
84 | I80 | DEF4 | EventMaskHi | UINT32 | RW | 0...4294967295
114 | S1 | IEF1 | I0Int> [67NT] mode | UINT32 | RW | 0=Disabled;1=Activated
114 | V1 | IEF1 | I0Int> condition | UINT32 | R | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
114 | I1 | IEF1 | Spikes needed for trip > | UINT32 | R | 0...4294967295
114 | I2 | IEF1 | I0Int> starts FWD | UINT32 | R | 0...4294967295
114 | I3 | IEF1 | I0Int> starts REV | UINT32 | R | 0...4294967295
114 | I4 | IEF1 | I0Int> trips | UINT32 | R | 0...4294967295
114 | I5 | IEF1 | I0Int> blocks | UINT32 | R | 0...4294967295
114 | S2 | IEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
114 | S3 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S4 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S5 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S6 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S7 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S8 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S9 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S10 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S11 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S12 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S13 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S14 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S15 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S16 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S17 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S18 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S19 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S20 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S21 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S22 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S23 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S24 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S25 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S26 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S27 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S28 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S29 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S30 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S31 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S32 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S33 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S34 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S35 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S36 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S37 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S38 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S39 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S40 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S41 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S42 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S43 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S44 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S45 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S46 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S47 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S48 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S49 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S50 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | O1 | IEF1 | I0Int> IEF DETECTED | SIGNAL_OUT | RW | 0...4294967295
114 | O2 | IEF1 | I0Int> STARTFWD | SIGNAL_OUT | RW | 0...4294967295
114 | O3 | IEF1 | I0Int> STARTREV | SIGNAL_OUT | RW | 0...4294967295
114 | O4 | IEF1 | I0Int> TRIP | SIGNAL_OUT | RW | 0...4294967295
114 | O5 | IEF1 | I0Int> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
114 | I6 | IEF1 | Newest Register | UINT32 | R | 0...12
114 | I7 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I8 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I9 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I10 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I11 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I12 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I13 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I14 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I15 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I16 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I17 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I18 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I19 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I20 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I21 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I22 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I23 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I24 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I25 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I26 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I27 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I28 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I29 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I30 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I31 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I32 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I33 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I34 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I35 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I36 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I37 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I38 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I39 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I40 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I41 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I42 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I43 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I44 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I45 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I46 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I47 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I48 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I49 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I50 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I51 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I52 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I53 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I54 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I55 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I56 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I57 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I58 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I59 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I60 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I61 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I62 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I63 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I64 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I65 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I66 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | S51 | IEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
114 | S52 | IEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
32 | S1 | CUB1 | I2> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
32 | V1 | CUB1 | I2> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
32 | I1 | CUB1 | I2> starts | UINT32 | R | 0...4294967295
32 | I2 | CUB1 | I2> trips | UINT32 | R | 0...4294967295
32 | I3 | CUB1 | I2> blocks | UINT32 | R | 0...4294967295
32 | S2 | CUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
32 | I4 | CUB1 | I2> I2I1 relation | FLOAT | R | 0...100000
32 | I5 | CUB1 | I2 meas/I2 set | FLOAT | R | 0...100000
32 | S3 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S4 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S5 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S6 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S7 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S8 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S9 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S10 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S11 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S12 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S13 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S14 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S15 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S16 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S17 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S18 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S19 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S20 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S21 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S22 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S23 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S24 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S25 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S26 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S27 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S28 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S29 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S30 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S31 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S32 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S33 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S34 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | O1 | CUB1 | I2> START | SIGNAL_OUT | RW | 0...4294967295
32 | O2 | CUB1 | I2> TRIP | SIGNAL_OUT | RW | 0...4294967295
32 | O3 | CUB1 | I2> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
32 | I6 | CUB1 | Newest Register | UINT32 | R | 0...12
32 | I7 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I8 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I9 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I10 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I11 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I12 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I13 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I14 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I15 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I16 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I17 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I18 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I19 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I20 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I21 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I22 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I23 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I24 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I25 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I26 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I27 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I28 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I29 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I30 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | S35 | CUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
33 | S1 | CUB2 | I2>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
33 | V1 | CUB2 | I2>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
33 | I1 | CUB2 | I2>> starts | UINT32 | R | 0...4294967295
33 | I2 | CUB2 | I2>> trips | UINT32 | R | 0...4294967295
33 | I3 | CUB2 | I2>> blocks | UINT32 | R | 0...4294967295
33 | S2 | CUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
33 | I4 | CUB2 | I2>> I2I1 relation | FLOAT | R | 0...100000
33 | I5 | CUB2 | I2 meas/I2 set | FLOAT | R | 0...100000
33 | S3 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S4 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S5 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S6 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S7 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S8 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S9 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S10 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S11 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S12 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S13 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S14 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S15 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S16 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S17 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S18 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S19 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S20 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S21 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S22 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S23 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S24 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S25 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S26 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S27 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S28 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S29 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S30 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S31 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S32 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S33 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S34 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | O1 | CUB2 | I2>> START | SIGNAL_OUT | RW | 0...4294967295
33 | O2 | CUB2 | I2>> TRIP | SIGNAL_OUT | RW | 0...4294967295
33 | O3 | CUB2 | I2>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
33 | I6 | CUB2 | Newest Register | UINT32 | R | 0...12
33 | I7 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I8 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I9 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I10 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I11 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I12 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I13 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I14 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I15 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I16 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I17 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I18 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I19 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I20 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I21 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I22 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I23 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I24 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I25 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I26 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I27 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I28 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I29 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I30 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | S35 | CUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
34 | S1 | CUB3 | I2>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
34 | V1 | CUB3 | I2>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
34 | I1 | CUB3 | I2>>> starts | UINT32 | R | 0...4294967295
34 | I2 | CUB3 | I2>>> trips | UINT32 | R | 0...4294967295
34 | I3 | CUB3 | I2>>> blocks | UINT32 | R | 0...4294967295
34 | S2 | CUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
34 | I4 | CUB3 | I2>>> I2I1 relation | FLOAT | R | 0...100000
34 | I5 | CUB3 | I2 meas/I2 set | FLOAT | R | 0...100000
34 | S3 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S4 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S5 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S6 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S7 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S8 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S9 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S10 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S11 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S12 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S13 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S14 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S15 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S16 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S17 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S18 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S19 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S20 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S21 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S22 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S23 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S24 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S25 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S26 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S27 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S28 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S29 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S30 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S31 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S32 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S33 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S34 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | O1 | CUB3 | I2>>> START | SIGNAL_OUT | RW | 0...4294967295
34 | O2 | CUB3 | I2>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
34 | O3 | CUB3 | I2>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
34 | I6 | CUB3 | Newest Register | UINT32 | R | 0...12
34 | I7 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I8 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I9 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I10 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I11 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I12 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I13 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I14 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I15 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I16 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I17 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I18 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I19 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I20 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I21 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I22 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I23 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I24 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I25 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I26 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I27 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I28 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I29 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I30 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | S35 | CUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
35 | S1 | CUB4 | I2>>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
35 | V1 | CUB4 | I2>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
35 | I1 | CUB4 | I2>>>> starts | UINT32 | R | 0...4294967295
35 | I2 | CUB4 | I2>>>> trips | UINT32 | R | 0...4294967295
35 | I3 | CUB4 | I2>>>> blocks | UINT32 | R | 0...4294967295
35 | S2 | CUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
35 | I4 | CUB4 | I2>>>> I2I1 relation | FLOAT | R | 0...100000
35 | I5 | CUB4 | I2 meas/I2 set | FLOAT | R | 0...100000
35 | S3 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S4 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S5 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S6 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S7 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S8 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S9 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S10 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S11 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S12 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S13 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S14 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S15 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S16 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S17 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S18 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S19 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S20 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S21 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S22 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S23 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S24 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S25 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S26 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S27 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S28 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S29 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S30 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S31 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S32 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S33 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S34 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | O1 | CUB4 | I2>>>> START | SIGNAL_OUT | RW | 0...4294967295
35 | O2 | CUB4 | I2>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
35 | O3 | CUB4 | I2>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
35 | I6 | CUB4 | Newest Register | UINT32 | R | 0...12
35 | I7 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I8 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I9 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I10 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I11 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I12 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I13 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I14 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I15 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I16 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I17 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I18 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I19 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I20 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I21 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I22 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I23 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I24 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I25 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I26 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I27 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I28 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I29 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I30 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | S35 | CUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
37 | S1 | HOC1 | Ih> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
37 | V1 | HOC1 | Ih> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
37 | I1 | HOC1 | Ih> starts | UINT32 | R | 0...4294967295
37 | I2 | HOC1 | Ih> trips | UINT32 | R | 0...4294967295
37 | I3 | HOC1 | Ih> blocks | UINT32 | R | 0...4294967295
37 | S2 | HOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
37 | I4 | HOC1 | Ih meas/ Ih set | FLOAT | R | 0...100000
37 | S3 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S4 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S5 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S6 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S7 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S8 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S9 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S10 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S11 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S12 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S13 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S14 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S15 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S16 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S17 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S18 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S19 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S20 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S21 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S22 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S23 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S24 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S25 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S26 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S27 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S28 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S29 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S30 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S31 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S32 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S33 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S34 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | O1 | HOC1 | Ih> START | SIGNAL_OUT | RW | 0...4294967295
37 | O2 | HOC1 | Ih> TRIP | SIGNAL_OUT | RW | 0...4294967295
37 | O3 | HOC1 | Ih> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
37 | I5 | HOC1 | Newest Register | UINT32 | R | 0...12
37 | I6 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I7 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I8 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I9 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I10 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I11 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I12 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I13 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I14 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I15 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I16 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I17 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I18 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I19 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I20 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I21 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I22 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I23 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I24 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I25 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I26 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I27 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I28 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I29 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I30 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I31 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I32 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I33 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I34 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I35 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I36 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I37 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I38 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I39 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I40 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I41 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I42 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I43 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I44 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I45 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I46 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I47 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I48 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I49 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I50 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I51 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I52 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I53 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I54 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I55 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I56 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I57 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I58 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I59 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I60 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I61 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I62 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I63 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I64 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I65 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | S35 | HOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
38 | S1 | HOC2 | Ih>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
38 | V1 | HOC2 | Ih>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
38 | I1 | HOC2 | Ih>> starts | UINT32 | R | 0...4294967295
38 | I2 | HOC2 | Ih>> trips | UINT32 | R | 0...4294967295
38 | I3 | HOC2 | Ih>> blocks | UINT32 | R | 0...4294967295
38 | S2 | HOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
38 | I4 | HOC2 | Ih meas/ Ih set | FLOAT | R | 0...100000
38 | S3 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S4 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S5 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S6 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S7 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S8 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S9 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S10 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S11 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S12 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S13 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S14 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S15 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S16 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S17 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S18 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S19 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S20 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S21 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S22 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S23 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S24 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S25 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S26 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S27 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S28 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S29 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S30 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S31 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S32 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S33 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S34 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | O1 | HOC2 | Ih>> START | SIGNAL_OUT | RW | 0...4294967295
38 | O2 | HOC2 | Ih>> TRIP | SIGNAL_OUT | RW | 0...4294967295
38 | O3 | HOC2 | Ih>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
38 | I5 | HOC2 | Newest Register | UINT32 | R | 0...12
38 | I6 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I7 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I8 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I9 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I10 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I11 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I12 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I13 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I14 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I15 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I16 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I17 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I18 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I19 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I20 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I21 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I22 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I23 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I24 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I25 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I26 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I27 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I28 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I29 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I30 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I31 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I32 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I33 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I34 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I35 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I36 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I37 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I38 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I39 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I40 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I41 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I42 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I43 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I44 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I45 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I46 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I47 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I48 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I49 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I50 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I51 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I52 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I53 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I54 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I55 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I56 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I57 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I58 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I59 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I60 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I61 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I62 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I63 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I64 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I65 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | S35 | HOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
39 | S1 | HOC3 | Ih>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
39 | V1 | HOC3 | Ih>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
39 | I1 | HOC3 | Ih>>> starts | UINT32 | R | 0...4294967295
39 | I2 | HOC3 | Ih>>> trips | UINT32 | R | 0...4294967295
39 | I3 | HOC3 | Ih>>> blocks | UINT32 | R | 0...4294967295
39 | S2 | HOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
39 | I4 | HOC3 | Ih meas/ Ih set | FLOAT | R | 0...100000
39 | S3 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S4 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S5 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S6 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S7 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S8 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S9 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S10 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S11 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S12 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S13 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S14 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S15 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S16 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S17 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S18 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S19 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S20 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S21 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S22 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S23 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S24 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S25 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S26 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S27 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S28 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S29 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S30 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S31 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S32 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S33 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S34 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | O1 | HOC3 | Ih>>> START | SIGNAL_OUT | RW | 0...4294967295
39 | O2 | HOC3 | Ih>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
39 | O3 | HOC3 | Ih>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
39 | I5 | HOC3 | Newest Register | UINT32 | R | 0...12
39 | I6 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I7 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I8 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I9 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I10 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I11 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I12 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I13 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I14 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I15 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I16 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I17 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I18 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I19 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I20 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I21 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I22 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I23 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I24 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I25 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I26 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I27 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I28 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I29 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I30 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I31 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I32 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I33 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I34 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I35 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I36 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I37 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I38 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I39 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I40 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I41 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I42 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I43 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I44 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I45 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I46 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I47 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I48 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I49 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I50 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I51 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I52 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I53 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I54 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I55 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I56 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I57 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I58 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I59 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I60 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I61 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I62 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I63 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I64 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I65 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | S35 | HOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
40 | S1 | HOC4 | Ih>>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
40 | V1 | HOC4 | Ih>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
40 | I1 | HOC4 | Ih>>>> starts | UINT32 | R | 0...4294967295
40 | I2 | HOC4 | Ih>>>> trips | UINT32 | R | 0...4294967295
40 | I3 | HOC4 | Ih>>>> blocks | UINT32 | R | 0...4294967295
40 | S2 | HOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
40 | I4 | HOC4 | Ih meas/ Ih set | FLOAT | R | 0...100000
40 | S3 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S4 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S5 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S6 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S7 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S8 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S9 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S10 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S11 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S12 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S13 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S14 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S15 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S16 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S17 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S18 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S19 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S20 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S21 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S22 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S23 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S24 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S25 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S26 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S27 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S28 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S29 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S30 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S31 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S32 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S33 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S34 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | O1 | HOC4 | Ih>>>> START | SIGNAL_OUT | RW | 0...4294967295
40 | O2 | HOC4 | Ih>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
40 | O3 | HOC4 | Ih>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
40 | I5 | HOC4 | Newest Register | UINT32 | R | 0...12
40 | I6 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I7 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I8 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I9 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I10 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I11 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I12 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I13 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I14 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I15 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I16 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I17 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I18 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I19 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I20 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I21 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I22 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I23 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I24 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I25 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I26 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I27 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I28 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I29 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I30 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I31 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I32 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I33 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I34 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I35 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I36 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I37 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I38 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I39 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I40 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I41 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I42 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I43 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I44 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I45 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I46 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I47 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I48 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I49 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I50 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I51 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I52 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I53 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I54 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I55 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I56 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I57 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I58 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I59 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I60 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I61 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I62 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I63 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I64 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I65 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | S35 | HOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
42 | S1 | CLP1 | CLP mode | UINT32 | RW | 0=Disabled;1=Activated
42 | V1 | CLP1 | CLP condition | UINT32 | R | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
42 | I1 | CLP1 | CLP starts | UINT32 | R | 0...4294967295
42 | I2 | CLP1 | CLP blocks | UINT32 | R | 0...4294967295
42 | S2 | CLP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
42 | S3 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S4 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S5 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S6 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S7 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S8 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S9 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S10 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S11 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S12 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S13 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S14 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S15 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S16 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S17 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S18 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S19 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S20 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S21 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S22 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S23 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S24 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S25 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S26 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S27 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S28 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S29 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S30 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S31 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S32 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S33 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S34 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S35 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S36 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S37 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S38 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S39 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S40 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S41 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S42 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S43 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S44 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S45 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S46 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S47 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S48 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S49 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S50 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | O1 | CLP1 | CLPU ACT | SIGNAL_OUT | RW | 0...4294967295
42 | O2 | CLP1 | CLPU BLOCKED | SIGNAL_OUT | RW | 0...4294967295
42 | I3 | CLP1 | Newest Register | UINT32 | R | 0...12
42 | I4 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I5 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I6 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I7 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I8 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I9 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I10 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I11 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I12 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I13 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I14 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I15 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I16 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I17 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I18 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I19 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I20 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I21 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I22 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I23 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I24 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I25 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I26 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I27 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I28 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I29 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I30 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I31 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I32 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I33 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I34 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I35 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I36 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I37 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I38 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I39 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | S51 | CLP1 | EventMaskLo | UINT32 | RW | 0...4294967295
44 | S1 | CBF1 | CBFP [50BF] mode | UINT32 | RW | 0=Disabled;1=Activated
44 | V1 | CBF1 | CBFP condition | UINT32 | R | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
44 | I1 | CBF1 | Retrips | UINT32 | R | 0...4294967295
44 | I2 | CBF1 | CBFPs | UINT32 | R | 0...4294967295
44 | I3 | CBF1 | CBFP starts | UINT32 | R | 0...4294967295
44 | I4 | CBF1 | CBFP blocks | UINT32 | R | 0...4294967295
44 | S2 | CBF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
44 | S3 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S4 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S5 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S6 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S7 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S8 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S9 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S10 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S11 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S12 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S13 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S14 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S15 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S16 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S17 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S18 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S19 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S20 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S21 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S22 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S23 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S24 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S25 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S26 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S27 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S28 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S29 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S30 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S31 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S32 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S33 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S34 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S35 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S36 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S37 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S38 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S39 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S40 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S41 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S42 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S43 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S44 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S45 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S46 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S47 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S48 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S49 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S50 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S51 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S52 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S53 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S54 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S55 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S56 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S57 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S58 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | O1 | CBF1 | CBFP START | SIGNAL_OUT | RW | 0...4294967295
44 | O2 | CBF1 | CBFP RETRIP | SIGNAL_OUT | RW | 0...4294967295
44 | O3 | CBF1 | CBFP ACT | SIGNAL_OUT | RW | 0...4294967295
44 | O4 | CBF1 | CBFP BLOCKED | SIGNAL_OUT | RW | 0...4294967295
44 | I5 | CBF1 | Newest Register | UINT32 | R | 0...12
44 | I6 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I7 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I8 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I9 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I10 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I11 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I12 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I13 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I14 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I15 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I16 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I17 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I18 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I19 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I20 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I21 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I22 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I23 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I24 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I25 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I26 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I27 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I28 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I29 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I30 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I31 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I32 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I33 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I34 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I35 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I36 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I37 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I38 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I39 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I40 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I41 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I42 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I43 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I44 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I45 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I46 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I47 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I48 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I49 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I50 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I51 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I52 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I53 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | S59 | CBF1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S1 | MST1 | MST mode | UINT32 | R | 0=Disabled; 1=Activated
62 | V1 | MST1 | Motor is now | UINT32 | R | 0=Stopped;1=Starting;2=Running;3=Stalled
62 | I1 | MST1 | Times motor started | UINT32 | R | 0...4294967295
62 | I2 | MST1 | Times motor starts succeed | UINT32 | R | 0...4294967295
62 | I3 | MST1 | Times motor stopped | UINT32 | R | 0...4294967295
62 | S2 | MST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
62 | I4 | MST1 | Run after last start | UINT32 | R | 0...4294967295
62 | I5 | MST1 | Total motor run time | UINT32 | R | 0...4294967295
62 | I6 | MST1 | Last start duration | UINT32 | R | 0...4294967295
62 | I7 | MST1 | Total starting time | UINT32 | R | 0...4294967295
62 | I8 | MST1 | Last stopped duration | UINT32 | R | 0...4294967295
62 | I9 | MST1 | Total stopped time | UINT32 | R | 0...4294967295
62 | S3 | MST1 | Clear total times | UINT32 | W | 0=-;1=Clear
62 | S4 | MST1 | Per unitize relay currents to Motor In | UINT32 | RW | 0=No, use CT nominal as pu.;1=Yes, scale all to Imot
62 | S5 | MST1 | Motor nominal current | FLOAT | RW | 0.1...10000
62 | S6 | MST1 | Nominal Starting current | FLOAT | RW | 0.1...40
62 | S7 | MST1 | Start detect current | FLOAT | RW | 0.1...40
62 | S8 | MST1 | Min locked rotor current | FLOAT | RW | 0.1...40
62 | S9 | MST1 | Max locked rotor current | FLOAT | RW | 0.1...40
62 | S10 | MST1 | Maximum overload current | FLOAT | RW | 0.1...40
62 | S11 | MST1 | No Load current | FLOAT | RW | 0.1...40
62 | S12 | MST1 | Motor service factor | FLOAT | RW | 0.01...5
62 | S13 | MST1 | Hot condition theta limit | FLOAT | RW | 0...100
62 | S14 | MST1 | Safe stall time cold | FLOAT | RW | 0.1...600
62 | S15 | MST1 | Safe stall time hot | FLOAT | RW | 0.1...600
62 | S16 | MST1 | Allowed Starts when cold | UINT32 | RW | 1...100
62 | S17 | MST1 | Allowed Starts when hot | UINT32 | RW | 1...100
62 | S18 | MST1 | Given Hot/Cold starts in time of: | FLOAT | RW | 0.01...1800
62 | S19 | MST1 | Min time betw. starts | FLOAT | RW | 0...3600
62 | S20 | MST1 | Overall differential protection | UINT32 | RW | 0=Machine diff. (Yy);1=Diff.with trafo(Xx)
62 | O1 | MST1 | Motor stopped | SIGNAL_OUT | RW | 0...4294967295
62 | O2 | MST1 | Motor starting | SIGNAL_OUT | RW | 0...4294967295
62 | O3 | MST1 | Motor running | SIGNAL_OUT | RW | 0...4294967295
62 | O4 | MST1 | Motor stalled | SIGNAL_OUT | RW | 0...4294967295
62 | O5 | MST1 | Missing phase | SIGNAL_OUT | RW | 0...4294967295
62 | O6 | MST1 | Load Normal | SIGNAL_OUT | RW | 0...4294967295
62 | O7 | MST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
62 | O8 | MST1 | High overcurrent | SIGNAL_OUT | RW | 0...4294967295
62 | I10 | MST1 | Newest Register | UINT32 | R | 0...12
62 | I11 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I12 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I13 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I14 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I15 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I16 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I17 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I18 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I19 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I20 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I21 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I22 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I23 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I24 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I25 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I26 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I27 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I28 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I29 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I30 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I31 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I32 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I33 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I34 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I35 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I36 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I37 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I38 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I39 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I40 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I41 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I42 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I43 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I44 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I45 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I46 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I47 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I48 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I49 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I50 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I51 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I52 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I53 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I54 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I55 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I56 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I57 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I58 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I59 | MST1 | Motor load | FLOAT | R | 0...250
62 | I60 | MST1 | Motor load | FLOAT | R | 0...250
62 | I61 | MST1 | Motor load | FLOAT | R | 0...250
62 | I62 | MST1 | Motor load | FLOAT | R | 0...250
62 | I63 | MST1 | Motor load | FLOAT | R | 0...250
62 | I64 | MST1 | Motor load | FLOAT | R | 0...250
62 | I65 | MST1 | Motor load | FLOAT | R | 0...250
62 | I66 | MST1 | Motor load | FLOAT | R | 0...250
62 | I67 | MST1 | Motor load | FLOAT | R | 0...250
62 | I68 | MST1 | Motor load | FLOAT | R | 0...250
62 | I69 | MST1 | Motor load | FLOAT | R | 0...250
62 | I70 | MST1 | Motor load | FLOAT | R | 0...250
62 | S21 | MST1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S22 | MST1 | EventMaskHi | UINT32 | RW | 0...4294967295
72 | V1 | TRF1 | Transformer is now | UINT32 | R | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
72 | I1 | TRF1 | Times Overloaded | UINT32 | R | 0...4294967295
72 | I2 | TRF1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
72 | S1 | TRF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
72 | I3 | TRF1 | Normal loading | UINT32 | R | 0...4294967295
72 | I4 | TRF1 | Overloading cumulative | UINT32 | R | 0...4294967295
72 | I5 | TRF1 | Last overload duration | UINT32 | R | 0...4294967295
72 | I6 | TRF1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
72 | I7 | TRF1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
72 | S2 | TRF1 | Clear total times | UINT32 | W | 0=-;1=Clear
72 | S3 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.1...500
72 | S4 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...500
72 | S5 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...500
72 | S6 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S7 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | V2 | TRF1 | Bias selection | UINT32 | R | 0=Selection Ok;1=Selection different
72 | V3 | TRF1 | Pick-up setting | UINT32 | R | 0=not checked;1=Setting seems ok;2=Sensitive ok;3=Too sensitive;4=False trip likely;5=Coarse ok;6=Insensitive;7=Dangerously high
72 | V4 | TRF1 | Turnpoint1 setting | UINT32 | R | 0=not checked;1=Ok;2=Seems average;3=Is sensitive;4=Ok;5=Is conservative;6=Is sensitive;7=Ok;8=Is average;9=Is conservative;10=Ok;11=Too conservative;12=Too sensitive
72 | V5 | TRF1 | Slope1 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V6 | TRF1 | Turnpoint2 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V7 | TRF1 | Slope2 setting | UINT32 | R | 0=not checked;1=Ok;2=Wrong;
72 | O1 | TRF1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
72 | O2 | TRF1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O3 | TRF1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O4 | TRF1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
72 | O5 | TRF1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | O6 | TRF1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | I8 | TRF1 | Newest Register | UINT32 | R | 0...12
72 | I9 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I10 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I11 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I12 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I13 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I14 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I15 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I16 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I17 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I18 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I19 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I20 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I21 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I22 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I23 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I24 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I25 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I26 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I27 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I28 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I29 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I30 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I31 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I32 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I33 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I34 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I35 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I36 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I37 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I38 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I39 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I40 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I41 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I42 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I43 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I44 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I45 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I46 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I47 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I48 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I49 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I50 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I51 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I52 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I53 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I54 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I55 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I56 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I57 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I58 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I59 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I60 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I61 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I62 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I63 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I64 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I65 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I66 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I67 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I68 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I69 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I70 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I71 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I72 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I73 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I74 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I75 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I76 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I77 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I78 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I79 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I80 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | S8 | TRF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S1 | DIF1 | Idx> [87T/87N] mode | UINT32 | RW | 0=Disabled;1=Activated
71 | V1 | DIF1 | Idx> condition | UINT32 | R | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On
71 | V2 | DIF1 | REFHV> condition | UINT32 | R | 0b=HV REF Blocked;1b=HV REF Trip
71 | V3 | DIF1 | REFLV> condition | UINT32 | R | 0b=LV REF Blocked;1b=LV REF Trip
71 | I1 | DIF1 | Idb> trips | UINT32 | R | 0...4294967295
71 | I2 | DIF1 | Idb> f2h blocks | UINT32 | R | 0...4294967295
71 | I3 | DIF1 | Idb> f5h blocks | UINT32 | R | 0...4294967295
71 | I4 | DIF1 | Idb> Ext blocks | UINT32 | R | 0...4294967295
71 | I5 | DIF1 | Idi> trips | UINT32 | R | 0...4294967295
71 | I6 | DIF1 | Idi> Ext blocks | UINT32 | R | 0...4294967295
71 | I7 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I8 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | I9 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I10 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | S2 | DIF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
71 | I11 | DIF1 | L1 Bias current | FLOAT | R | 0...50
71 | I12 | DIF1 | L1 Diff current | FLOAT | R | 0...4000
71 | I13 | DIF1 | L1 Char current | FLOAT | R | 0...4000
71 | I14 | DIF1 | L2 Bias current | FLOAT | R | 0...50
71 | I15 | DIF1 | L2 Diff current | FLOAT | R | 0...4000
71 | I16 | DIF1 | L2 Char current | FLOAT | R | 0...4000
71 | I17 | DIF1 | L3 Bias current | FLOAT | R | 0...50
71 | I18 | DIF1 | L3 Diff current | FLOAT | R | 0...4000
71 | I19 | DIF1 | L3 Char current | FLOAT | R | 0...4000
71 | I20 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...50
71 | I21 | DIF1 | HV I0d> Diff current | FLOAT | R | 0...4000
71 | I22 | DIF1 | HV I0d> Char current | FLOAT | R | 0...4000
71 | I23 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...50
71 | I24 | DIF1 | LV I0d> Diff current | FLOAT | R | 0...4000
71 | I25 | DIF1 | LV I0d> Char current | FLOAT | R | 0...4000
71 | S3 | DIF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
71 | V4 | DIF1 | L1 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V5 | DIF1 | L2 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V6 | DIF1 | L3 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | I26 | DIF1 | L1 Mag. diff. | FLOAT | R | 0...50
71 | I27 | DIF1 | L1 Ang. diff. | FLOAT | R | -360...360
71 | I28 | DIF1 | L2 Mag. diff. | FLOAT | R | 0...50
71 | I29 | DIF1 | L2 Ang. diff. | FLOAT | R | -360...360
71 | I30 | DIF1 | L3 Mag. diff. | FLOAT | R | 0...50
71 | I31 | DIF1 | L3 Ang. diff. | FLOAT | R | -360...360
71 | S4 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S5 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S6 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S7 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S8 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S9 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S10 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S11 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S12 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S13 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S14 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S15 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S16 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S17 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S18 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S19 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S20 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S21 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S22 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S23 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S24 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S25 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S26 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S27 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S28 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S29 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S30 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S31 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S32 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S33 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S34 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S35 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S36 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S37 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S38 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S39 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S40 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S41 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S42 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S43 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S44 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S45 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S46 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S47 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S48 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S49 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S50 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S51 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S52 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S53 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S54 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S55 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S56 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S57 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S58 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S59 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S60 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S61 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S62 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S63 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S64 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S65 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S66 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S67 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S68 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S69 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S70 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S71 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S72 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S73 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S74 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S75 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S76 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S77 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S78 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S79 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S80 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S81 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S82 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S83 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S84 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S85 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S86 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S87 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S88 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S89 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S90 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S91 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S92 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S93 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S94 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S95 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S96 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S97 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S98 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S99 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S100 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S101 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S102 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S103 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S104 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S105 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S106 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S107 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S108 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S109 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S110 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S111 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S112 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S113 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S114 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S115 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S116 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S117 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S118 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S119 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S120 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S121 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S122 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S123 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S124 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S125 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S126 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S127 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S128 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S129 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S130 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S131 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S132 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S133 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S134 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S135 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S136 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S137 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S138 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S139 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S140 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S141 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S142 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S143 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S144 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S145 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S146 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S147 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S148 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S149 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S150 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S151 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S152 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S153 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S154 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S155 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S156 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S157 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S158 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S159 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S160 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S161 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S162 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S163 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S164 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S165 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S166 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S167 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S168 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S169 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S170 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S171 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S172 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S173 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S174 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S175 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S176 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S177 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S178 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S179 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S180 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S181 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S182 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S183 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S184 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S185 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S186 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S187 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S188 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S189 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S190 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S191 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S192 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S193 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S194 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S195 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S196 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S197 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S198 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S199 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S200 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S201 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S202 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S203 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S204 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S205 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S206 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S207 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S208 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S209 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S210 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S211 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | O1 | DIF1 | Idb> BIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O2 | DIF1 | Idb> BIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O3 | DIF1 | Idi> NOBIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O4 | DIF1 | Idi> NOBIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O5 | DIF1 | Id> 2nd harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O6 | DIF1 | Id> 5th harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O7 | DIF1 | HV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O8 | DIF1 | HV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O9 | DIF1 | LV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O10 | DIF1 | LV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | I32 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I33 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I34 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I35 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I36 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I37 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I38 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I39 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I40 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I41 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I42 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I43 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I44 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I45 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I46 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I47 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I48 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I49 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I50 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I51 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I52 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I53 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I54 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I55 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I56 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I57 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I58 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I59 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I60 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I61 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I62 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I63 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I64 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I65 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I66 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I67 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I68 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I69 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I70 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I71 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I72 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I73 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I74 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I75 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I76 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I77 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I78 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I79 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I80 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I81 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I82 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I83 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I84 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I85 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I86 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I87 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I88 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I89 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I90 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I91 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I92 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I93 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I94 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I95 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I96 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I97 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I98 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I99 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I100 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I101 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I102 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I103 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I104 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I105 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I106 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I107 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I108 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I109 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I110 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I111 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I112 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I113 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I114 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I115 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I116 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I117 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I118 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I119 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I120 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I121 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I122 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I123 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I124 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I125 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I126 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I127 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I128 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I129 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I130 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I131 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I132 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I133 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I134 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I135 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I136 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I137 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I138 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I139 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I140 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | V7 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V8 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V9 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V10 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V11 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V12 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V13 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V14 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V15 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V16 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V17 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V18 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | I141 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I142 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I143 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I144 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I145 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I146 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I147 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I148 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I149 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I150 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I151 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I152 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I153 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I154 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I155 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I156 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I157 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I158 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I159 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I160 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I161 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I162 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I163 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I164 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I165 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I166 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I167 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I168 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I169 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I170 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I171 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I172 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I173 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I174 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I175 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I176 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I177 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I178 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I179 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I180 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I181 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I182 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I183 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I184 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I185 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I186 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I187 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I188 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I189 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I190 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I191 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I192 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I193 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I194 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I195 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I196 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I197 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I198 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I199 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I200 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I201 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I202 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I203 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I204 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I205 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I206 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I207 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I208 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I209 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I210 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I211 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I212 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I213 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I214 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | S212 | DIF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S213 | DIF1 | EventMaskHi | UINT32 | RW | 0...4294967295
66 | S1 | REF1 | I0d> [87N] mode | UINT32 | RW | 0=Disabled;1=Activated
66 | V1 | REF1 | I0d> condition | UINT32 | R | 0=Normal;1=Trip;2=Blocked
66 | S2 | REF1 | Select | UINT32 | RW | 0=Primary A;1=Secondary A;2=Per Unit
66 | S3 | REF1 | Select | UINT32 | RW | 0=REF Curr
66 | I1 | REF1 | I0d> Bias current | FLOAT | R | 0...50
66 | I2 | REF1 | I0d> Diff current | FLOAT | R | 0...50
66 | I3 | REF1 | I0d> Char current | FLOAT | R | 0...50
66 | I4 | REF1 | Calculated I0 (I0Calc) | FLOAT | R | 0...50
66 | I5 | REF1 | Measured I0 (3I0) | FLOAT | R | 0...50
66 | S4 | REF1 | REF or Cable end Diff | UINT32 | RW | 0=REF;1=CED
66 | S5 | REF1 | Comp. natural unbal. | UINT32 | RW | 0=-;1=Comp
66 | I6 | REF1 | Natural unbalance | FLOAT | R | 0...50
66 | I7 | REF1 | Natural unbalance ang | FLOAT | R | -360...360
66 | I8 | REF1 | Current for CED | FLOAT | R | 0...50
66 | I9 | REF1 | Angle for CED | FLOAT | R | -360...360
66 | S6 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S7 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S8 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S9 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S10 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S11 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S12 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S13 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S14 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S15 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S16 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S17 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S18 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S19 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S20 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S21 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S22 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S23 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S24 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S25 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S26 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S27 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S28 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S29 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S30 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S31 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S32 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S33 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S34 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S35 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S36 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S37 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S38 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S39 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S40 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S41 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S42 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S43 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S44 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S45 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S46 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S47 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S48 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S49 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S50 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S51 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S52 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S53 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S54 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S55 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S56 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S57 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S58 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S59 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S60 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S61 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S62 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S63 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S64 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S65 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S66 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S67 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S68 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S69 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S70 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S71 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S72 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S73 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S74 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S75 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S76 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S77 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | O1 | REF1 | I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
66 | O2 | REF1 | I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
66 | I10 | REF1 | Newest Register | UINT32 | R | 0...12
66 | I11 | REF1 | Bias current | FLOAT | R | 0...250
66 | I12 | REF1 | Bias current | FLOAT | R | 0...250
66 | I13 | REF1 | Bias current | FLOAT | R | 0...250
66 | I14 | REF1 | Bias current | FLOAT | R | 0...250
66 | I15 | REF1 | Bias current | FLOAT | R | 0...250
66 | I16 | REF1 | Bias current | FLOAT | R | 0...250
66 | I17 | REF1 | Bias current | FLOAT | R | 0...250
66 | I18 | REF1 | Bias current | FLOAT | R | 0...250
66 | I19 | REF1 | Bias current | FLOAT | R | 0...250
66 | I20 | REF1 | Bias current | FLOAT | R | 0...250
66 | I21 | REF1 | Bias current | FLOAT | R | 0...250
66 | I22 | REF1 | Bias current | FLOAT | R | 0...250
66 | I23 | REF1 | Differential current | FLOAT | R | 0...250
66 | I24 | REF1 | Differential current | FLOAT | R | 0...250
66 | I25 | REF1 | Differential current | FLOAT | R | 0...250
66 | I26 | REF1 | Differential current | FLOAT | R | 0...250
66 | I27 | REF1 | Differential current | FLOAT | R | 0...250
66 | I28 | REF1 | Differential current | FLOAT | R | 0...250
66 | I29 | REF1 | Differential current | FLOAT | R | 0...250
66 | I30 | REF1 | Differential current | FLOAT | R | 0...250
66 | I31 | REF1 | Differential current | FLOAT | R | 0...250
66 | I32 | REF1 | Differential current | FLOAT | R | 0...250
66 | I33 | REF1 | Differential current | FLOAT | R | 0...250
66 | I34 | REF1 | Differential current | FLOAT | R | 0...250
66 | I35 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I36 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I37 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I38 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I39 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I40 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I41 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I42 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I43 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I44 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I45 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I46 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | S78 | REF1 | EventMaskLo | UINT32 | RW | 0...4294967295
66 | S79 | REF1 | EventMaskHi | UINT32 | RW | 0...4294967295
73 | S1 | TOLT1 | TT> [49T] mode | UINT32 | RW | 0=Disabled;1=Activated
73 | V1 | TOLT1 | TT> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
73 | V2 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
73 | V3 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
73 | V4 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
73 | V5 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
73 | V6 | TOLT1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
73 | I1 | TOLT1 | IN thermal cap current | FLOAT | RW | 0...40
73 | I2 | TOLT1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
73 | S2 | TOLT1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
73 | S3 | TOLT1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
73 | I3 | TOLT1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
73 | I4 | TOLT1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
73 | S4 | TOLT1 | tau1 (t const heating) | FLOAT | RW | 0...500
73 | S5 | TOLT1 | tau2 (t const cooling) | FLOAT | RW | 0...500
73 | S6 | TOLT1 | kSF (service factor) | FLOAT | RW | 0.01...5
73 | S7 | TOLT1 | Cold Reset default theta | FLOAT | RW | 0...150
73 | V7 | TOLT1 | TT> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
73 | I5 | TOLT1 | TT> Time to 100% Theta | UINT32 | R | 0...4294967295
73 | I6 | TOLT1 | TT> Reference T curr. | FLOAT | R | 0...50
73 | I7 | TOLT1 | TT> Active meas curr. | FLOAT | R | 0...50
73 | I8 | TOLT1 | TT> T est.with act. curr. | FLOAT | R | 0...500
73 | I9 | TOLT1 | TT> T at the moment | FLOAT | R | 0...500
73 | I10 | TOLT1 | TT> Max.Temp.Rise All. | FLOAT | R | 0...250
73 | I11 | TOLT1 | TT> Temp.Rise atm. | FLOAT | R | 0...250
73 | I12 | TOLT1 | TT> Hot Spot estimate | FLOAT | R | 0...250
73 | I13 | TOLT1 | TT> Hot Spot Max. All | FLOAT | R | 0...250
73 | I14 | TOLT1 | TT> Used k for amb. temp | FLOAT | R | 0...3
73 | I15 | TOLT1 | TT> Trip delay remaining | UINT32 | R | 0...4294967295
73 | I16 | TOLT1 | TT> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
73 | I17 | TOLT1 | TT> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
73 | I18 | TOLT1 | TT> Inhibit time to rel. | UINT32 | R | 0...4294967295
73 | I19 | TOLT1 | TT> Trip time to rel. | UINT32 | R | 0...4294967295
73 | I20 | TOLT1 | TT> Thermal cap used | FLOAT | R | 0...500
73 | I21 | TOLT1 | Alarm1 inits | UINT32 | R | 0...4294967295
73 | I22 | TOLT1 | Alarm2 inits | UINT32 | R | 0...4294967295
73 | I23 | TOLT1 | Restart Inhibits | UINT32 | R | 0...4294967295
73 | I24 | TOLT1 | Trips | UINT32 | R | 0...4294967295
73 | I25 | TOLT1 | Trips Blocked | UINT32 | R | 0...4294967295
73 | S8 | TOLT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
73 | S9 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S10 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S11 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S12 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S13 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S14 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S15 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S16 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S17 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S18 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S19 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S20 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S21 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S22 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S23 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S24 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S25 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S26 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S27 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S28 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S29 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S30 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S31 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S32 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S33 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S34 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S35 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S36 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S37 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S38 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S39 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S40 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S41 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S42 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S43 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S44 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S45 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S46 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S47 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S48 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S49 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S50 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S51 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S52 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S53 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S54 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S55 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S56 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S57 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S58 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S59 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S60 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S61 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S62 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S63 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S64 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S65 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S66 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S67 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S68 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S69 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S70 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S71 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S72 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | O1 | TOLT1 | TT> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
73 | O2 | TOLT1 | TT> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
73 | O3 | TOLT1 | TT> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
73 | O4 | TOLT1 | TT> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
73 | O5 | TOLT1 | TT> Trip | SIGNAL_OUT | RW | 0...4294967295
73 | I26 | TOLT1 | Newest Register | UINT32 | R | 0...12
73 | I27 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I28 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I29 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I30 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I31 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I32 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I33 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I34 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I35 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I36 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I37 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I38 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I39 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I40 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I41 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I42 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I43 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I44 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I45 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I46 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I47 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I48 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I49 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I50 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I51 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I52 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I53 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I54 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I55 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I56 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I57 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I58 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I59 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I60 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I61 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I62 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | S73 | TOLT1 | EventMaskLo | UINT32 | RW | 0...4294967295
73 | S74 | TOLT1 | EventMaskHi | UINT32 | RW | 0...4294967295
67 | S1 | TOLF1 | TF> [49F] mode | UINT32 | RW | 0=Disabled;1=Activated
67 | V1 | TOLF1 | TF> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
67 | V2 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
67 | V3 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
67 | V4 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
67 | V5 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
67 | V6 | TOLF1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
67 | I1 | TOLF1 | IN thermal cap current | FLOAT | RW | 0...40
67 | I2 | TOLF1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
67 | I3 | TOLF1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
67 | I4 | TOLF1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
67 | I5 | TOLF1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
67 | I6 | TOLF1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
67 | S2 | TOLF1 | tau (t const) | FLOAT | RW | 0...500
67 | S3 | TOLF1 | Nominal current | FLOAT | RW | 1...9999999
67 | S4 | TOLF1 | kSF (service factor) | FLOAT | RW | 0.01...5
67 | I7 | TOLF1 | TF> Time to 100% Theta | UINT32 | R | 0...4294967295
67 | I8 | TOLF1 | TF> Reference T curr. | FLOAT | R | 0...50
67 | I9 | TOLF1 | TF> Active meas curr. | FLOAT | R | 0...50
67 | I10 | TOLF1 | TF> T est.with act. curr. | FLOAT | R | 0...500
67 | I11 | TOLF1 | TF> T at the moment | FLOAT | R | 0...500
67 | I12 | TOLF1 | TF> Max.Temp.Rise All. | FLOAT | R | 0...250
67 | I13 | TOLF1 | TF> Temp.Rise atm. | FLOAT | R | 0...250
67 | I14 | TOLF1 | TF> Hot Spot estimate | FLOAT | R | 0...250
67 | I15 | TOLF1 | TF> Hot Spot Max. All | FLOAT | R | 0...250
67 | I16 | TOLF1 | TF> Used k for amb. temp | FLOAT | R | 0...3
67 | I17 | TOLF1 | TF> Trip delay remaining | UINT32 | R | 0...4294967295
67 | I18 | TOLF1 | TF> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
67 | I19 | TOLF1 | TF> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
67 | I20 | TOLF1 | TF> Inhibit time to rel. | UINT32 | R | 0...4294967295
67 | I21 | TOLF1 | TF> Trip time to rel. | UINT32 | R | 0...4294967295
67 | I22 | TOLF1 | TF> Thermal cap used | FLOAT | R | 0...500
67 | I23 | TOLF1 | Alarm1 inits | UINT32 | R | 0...4294967295
67 | I24 | TOLF1 | Alarm2 inits | UINT32 | R | 0...4294967295
67 | I25 | TOLF1 | Restart Inhibits | UINT32 | R | 0...4294967295
67 | I26 | TOLF1 | Trips | UINT32 | R | 0...4294967295
67 | I27 | TOLF1 | Trips Blocked | UINT32 | R | 0...4294967295
67 | S5 | TOLF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
67 | S6 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S7 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S8 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S9 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S10 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S11 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S12 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S13 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S14 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S15 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S16 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S17 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S18 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S19 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S20 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S21 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S22 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S23 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S24 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S25 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S26 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S27 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S28 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S29 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S30 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S31 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S32 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S33 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S34 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S35 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S36 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S37 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S38 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S39 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S40 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S41 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S42 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S43 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S44 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S45 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S46 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S47 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S48 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S49 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S50 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S51 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S52 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S53 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S54 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S55 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S56 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S57 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S58 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S59 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S60 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S61 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S62 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S63 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S64 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S65 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S66 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S67 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S68 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S69 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | O1 | TOLF1 | TF> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
67 | O2 | TOLF1 | TF> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
67 | O3 | TOLF1 | TF> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
67 | O4 | TOLF1 | TF> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
67 | O5 | TOLF1 | TF> Trip | SIGNAL_OUT | RW | 0...4294967295
67 | I28 | TOLF1 | Newest Register | UINT32 | R | 0...12
67 | I29 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I30 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I31 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I32 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I33 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I34 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I35 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I36 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I37 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I38 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I39 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I40 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I41 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I42 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I43 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I44 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I45 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I46 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I47 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I48 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I49 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I50 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I51 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I52 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I53 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I54 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I55 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I56 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I57 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I58 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I59 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I60 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I61 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I62 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I63 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I64 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I65 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I66 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I67 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I68 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I69 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I70 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I71 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I72 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I73 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I74 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I75 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I76 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | S70 | TOLF1 | EventMaskLo | UINT32 | RW | 0...4294967295
67 | S71 | TOLF1 | EventMaskHi | UINT32 | RW | 0...4294967295
68 | S1 | TOLM1 | TM> [49M] mode | UINT32 | RW | 0=Disabled; 1=Activated
68 | V1 | TOLM1 | TM> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
68 | V2 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
68 | V3 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
68 | V4 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
68 | V5 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
68 | V6 | TOLM1 | Motor status | UINT32 | R | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
68 | S2 | TOLM1 | Pick-up current (x In) | FLOAT | RW | 0...40
68 | S3 | TOLM1 | NPS Biasing in use | UINT32 | RW | 0=No NPS biasing;1=NPS Biasing in use
68 | S4 | TOLM1 | NPS Bias factor | FLOAT | RW | 0.1...10
68 | S5 | TOLM1 | Time constants | UINT32 | RW | 0=Single;1=Multiple
68 | S6 | TOLM1 | Long Heat T const (cold) | FLOAT | RW | 0...500
68 | S7 | TOLM1 | Long Heat T const (hot) | FLOAT | RW | 0...500
68 | S8 | TOLM1 | Long Cool T const Run | FLOAT | RW | 0...3000
68 | S9 | TOLM1 | Long Cool T const Stop | FLOAT | RW | 0...3000
68 | S10 | TOLM1 | Short Heat T const (cold) | FLOAT | RW | 0...500
68 | S11 | TOLM1 | Short Heat T const (hot) | FLOAT | RW | 0...500
68 | S12 | TOLM1 | Short Cool T const | FLOAT | RW | 0...3000
68 | S13 | TOLM1 | Wf factor for L/S T const | FLOAT | RW | 0...1
68 | S14 | TOLM1 | T const dyn. balancing | UINT32 | RW | 0=Fixed;1=Dynamic
68 | S15 | TOLM1 | Short Cool T used when stop | FLOAT | RW | 0...3000
68 | S16 | TOLM1 | Cold Reset Theta Default | FLOAT | RW | 0...150
68 | I1 | TOLM1 | Wf in use | FLOAT | R | 0...1
68 | I2 | TOLM1 | Long heat TC in use | FLOAT | R | 0...500
68 | I3 | TOLM1 | Short heat TC in use | FLOAT | R | 0...500
68 | I4 | TOLM1 | Long cool TC in use | FLOAT | R | 0...500
68 | I5 | TOLM1 | Short cool TC in use | FLOAT | R | 0...500
68 | I6 | TOLM1 | Cold stall time | FLOAT | R | 0...500
68 | I7 | TOLM1 | Hot stall time | FLOAT | R | 0...500
68 | S17 | TOLM1 | Dev.Temp (tmax) | UINT32 | RW | 0=A;1=B;2=F;3=H;4=Manual set
68 | S18 | TOLM1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
68 | S19 | TOLM1 | Amb. T Selection | UINT32 | RW | 0=Manual set;1=RTD
68 | S20 | TOLM1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
68 | V7 | TOLM1 | TM> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
68 | I8 | TOLM1 | TM> Time to 100% T | UINT32 | R | 0...4294967295
68 | I9 | TOLM1 | TM> Reference T curr. | FLOAT | R | 0...50
68 | I10 | TOLM1 | TM> Active meas curr. | FLOAT | R | 0...50
68 | I11 | TOLM1 | TM> T est.with act. curr. | FLOAT | R | 0...500
68 | I12 | TOLM1 | TM> T at the moment | FLOAT | R | 0...500
68 | I13 | TOLM1 | TM> Max.Temp.Rise All. | FLOAT | R | 0...250
68 | I14 | TOLM1 | TM> Temp.Rise atm. | FLOAT | R | 0...250
68 | I15 | TOLM1 | TM> Hot Spot estimate | FLOAT | R | 0...250
68 | I16 | TOLM1 | TM> Hot Spot Max. All | FLOAT | R | 0...250
68 | I17 | TOLM1 | TM> Used k for amb. temp | FLOAT | R | 0...5
68 | I18 | TOLM1 | TM> Trip delay remaining | UINT32 | R | 0...4294967295
68 | I19 | TOLM1 | TM> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
68 | I20 | TOLM1 | TM> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
68 | I21 | TOLM1 | TM> Inhibit time to rel. | UINT32 | R | 0...4294967295
68 | I22 | TOLM1 | TM> Trip time to rel. | UINT32 | R | 0...4294967295
68 | I23 | TOLM1 | TM> Thermal cap used | FLOAT | R | 0...500
68 | I24 | TOLM1 | Alarm1 inits | UINT32 | R | 0...4294967295
68 | I25 | TOLM1 | Alarm2 inits | UINT32 | R | 0...4294967295
68 | I26 | TOLM1 | Restart Inhibits | UINT32 | R | 0...4294967295
68 | I27 | TOLM1 | Trips | UINT32 | R | 0...4294967295
68 | I28 | TOLM1 | Trips Blocked | UINT32 | R | 0...4294967295
68 | S21 | TOLM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
68 | S22 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S23 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S24 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S25 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S26 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S27 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S28 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S29 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S30 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S31 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S32 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S33 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S34 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S35 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S36 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S37 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S38 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S39 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S40 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S41 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S42 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S43 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S44 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S45 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S46 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S47 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S48 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S49 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S50 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S51 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S52 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S53 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S54 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S55 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S56 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S57 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S58 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S59 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S60 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S61 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S62 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S63 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S64 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S65 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S66 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S67 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S68 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S69 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S70 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S71 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S72 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S73 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S74 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S75 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S76 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S77 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S78 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S79 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S80 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S81 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S82 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S83 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S84 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S85 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | O1 | TOLM1 | TM> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
68 | O2 | TOLM1 | TM> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
68 | O3 | TOLM1 | TM> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
68 | O4 | TOLM1 | TM> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
68 | O5 | TOLM1 | TM> Trip | SIGNAL_OUT | RW | 0...4294967295
68 | I29 | TOLM1 | Newest Register | UINT32 | R | 0...12
68 | I30 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I31 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I32 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I33 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I34 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I35 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I36 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I37 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I38 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I39 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I40 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I41 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I42 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I43 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I44 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I45 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I46 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I47 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I48 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I49 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I50 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I51 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I52 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I53 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I54 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I55 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I56 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I57 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I58 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I59 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I60 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I61 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I62 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I63 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I64 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I65 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I66 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I67 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I68 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I69 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I70 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I71 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I72 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I73 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I74 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I75 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I76 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I77 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I78 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I79 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I80 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I81 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I82 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I83 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I84 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I85 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I86 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I87 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I88 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I89 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I90 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I91 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I92 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I93 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I94 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I95 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I96 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I97 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I98 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I99 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I100 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I101 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I102 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I103 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I104 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I105 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I106 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I107 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I108 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I109 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I110 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I111 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I112 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I113 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I114 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I115 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I116 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I117 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I118 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I119 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I120 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I121 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I122 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I123 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I124 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I125 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I126 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I127 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I128 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I129 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I130 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I131 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I132 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I133 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I134 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I135 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I136 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I137 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | S86 | TOLM1 | EventMaskLo | UINT32 | RW | 0...4294967295
68 | S87 | TOLM1 | EventMaskHi | UINT32 | RW | 0...4294967295
57 | S1 | LCR1 | ISt> [48/14/50LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
57 | V1 | LCR1 | ISt> condition | UINT32 | R | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
57 | I1 | LCR1 | ISt> starts | UINT32 | R | 0...4294967295
57 | I2 | LCR1 | ISt> Set cap used in last start | FLOAT | R | 0...500
57 | I3 | LCR1 | ISt> Max cap used in last start | FLOAT | R | 0...500
57 | I4 | LCR1 | ISt> Set time trips | UINT32 | R | 0...4294967295
57 | I5 | LCR1 | ISt> Max cap trips | UINT32 | R | 0...4294967295
57 | I6 | LCR1 | ISt> blocks | UINT32 | R | 0...4294967295
57 | S2 | LCR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
57 | S3 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S4 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S5 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S6 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S7 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S8 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S9 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S10 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S11 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S12 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S13 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S14 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S15 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S16 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S17 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S18 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S19 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S20 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S21 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S22 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S23 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S24 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S25 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S26 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S27 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S28 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S29 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S30 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S31 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S32 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S33 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S34 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S35 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S36 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S37 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S38 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S39 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S40 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S41 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S42 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S43 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S44 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S45 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S46 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S47 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S48 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S49 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S50 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | O1 | LCR1 | ISt> START | SIGNAL_OUT | RW | 0...4294967295
57 | O2 | LCR1 | ISt> Set time TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O3 | LCR1 | ISt> Machine cap.TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O4 | LCR1 | ISt> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
57 | I7 | LCR1 | Newest Register | UINT32 | R | 0...12
57 | I8 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I9 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I10 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I11 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I12 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I13 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I14 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I15 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I16 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I17 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I18 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I19 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I20 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I21 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I22 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I23 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I24 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I25 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I26 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I27 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I28 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I29 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I30 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I31 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I32 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I33 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I34 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I35 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I36 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I37 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I38 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I39 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I40 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I41 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I42 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I43 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I44 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I45 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I46 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I47 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I48 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I49 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I50 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I51 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I52 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I53 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I54 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I55 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I56 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I57 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I58 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I59 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I60 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I61 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I62 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I63 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I64 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I65 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I66 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I67 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I68 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I69 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I70 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I71 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I72 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I73 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I74 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I75 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I76 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I77 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I78 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I79 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I80 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I81 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I82 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I83 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I84 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I85 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I86 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I87 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I88 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I89 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I90 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I91 | LCR1 | Phase C current | FLOAT | R | 0...250
56 | S1 | FSP1 | N> [66/86] mode | UINT32 | RW | 0=Disabled; 1=Activated
56 | V1 | FSP1 | N> condition | UINT32 | R | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
56 | I1 | FSP1 | N> alarms | UINT32 | R | 0...4294967295
56 | I2 | FSP1 | N> Inhibits | UINT32 | R | 0...4294967295
56 | I3 | FSP1 | N> blocks | UINT32 | R | 0...4294967295
56 | S2 | FSP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
56 | I4 | FSP1 | Start monitoring time left | UINT32 | R | 0...4294967295
56 | I5 | FSP1 | Inhibit time on | UINT32 | R | 0...4294967295
56 | I6 | FSP1 | Alarm time on | UINT32 | R | 0...4294967295
56 | I7 | FSP1 | Time since last start | UINT32 | R | 0...4294967295
56 | I8 | FSP1 | Start count atm. | UINT32 | R | 0...4294967295
56 | I9 | FSP1 | Starts left atm. | UINT32 | R | 0...4294967295
56 | S3 | FSP1 | Give one more start (Warning! Motor may overheat) | UINT32 | W | 0=-;1=Deduct one start
56 | O1 | FSP1 | N> One start remaining (Alarm) | SIGNAL_OUT | RW | 0...4294967295
56 | O2 | FSP1 | N> INHIBIT ON (General) | SIGNAL_OUT | RW | 0...4294967295
56 | O3 | FSP1 | N> INHIBIT ON Mot Running | SIGNAL_OUT | RW | 0...4294967295
56 | O4 | FSP1 | N> INHIBIT ON Mot Stopped | SIGNAL_OUT | RW | 0...4294967295
56 | O5 | FSP1 | N> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
56 | I10 | FSP1 | Newest Register | UINT32 | R | 0...12
56 | S4 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S5 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S6 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S7 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S8 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S9 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S10 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S11 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S12 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S13 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S14 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S15 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S16 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S17 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S18 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S19 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S20 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S21 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S22 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S23 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S24 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S25 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S26 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S27 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S28 | FSP1 | Start count | FLOAT | R | 0...250
56 | S29 | FSP1 | Start count | FLOAT | R | 0...250
56 | S30 | FSP1 | Start count | FLOAT | R | 0...250
56 | S31 | FSP1 | Start count | FLOAT | R | 0...250
56 | S32 | FSP1 | Start count | FLOAT | R | 0...250
56 | S33 | FSP1 | Start count | FLOAT | R | 0...250
56 | S34 | FSP1 | Start count | FLOAT | R | 0...250
56 | S35 | FSP1 | Start count | FLOAT | R | 0...250
56 | S36 | FSP1 | Start count | FLOAT | R | 0...250
56 | S37 | FSP1 | Start count | FLOAT | R | 0...250
56 | S38 | FSP1 | Start count | FLOAT | R | 0...250
56 | S39 | FSP1 | Start count | FLOAT | R | 0...250
56 | S40 | FSP1 | EventMaskLo | UINT32 | RW | 0...4294967295
60 | S1 | NUC1 | I< [37] mode | UINT32 | RW | 0=Disabled; 1=Activated
60 | V1 | NUC1 | I< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
60 | I1 | NUC1 | I< starts | UINT32 | R | 0...4294967295
60 | I2 | NUC1 | I< trips | UINT32 | R | 0...4294967295
60 | I3 | NUC1 | I< blocks | UINT32 | R | 0...4294967295
60 | S2 | NUC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
60 | S3 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S4 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S5 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S6 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S7 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S8 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S9 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S10 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S11 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S12 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S13 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S14 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S15 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S16 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S17 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S18 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S19 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S20 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S21 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S22 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S23 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S24 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S25 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S26 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | O1 | NUC1 | I< START | SIGNAL_OUT | RW | 0...4294967295
60 | O2 | NUC1 | I< TRIP | SIGNAL_OUT | RW | 0...4294967295
60 | O3 | NUC1 | I< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
60 | I4 | NUC1 | Newest Register | UINT32 | R | 0...12
60 | I5 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I6 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I7 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I8 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I9 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I10 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I11 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I12 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I13 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I14 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I15 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I16 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I17 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I18 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I19 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I20 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I21 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I22 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I23 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I24 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I25 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I26 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I27 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I28 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I29 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I30 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I31 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I32 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I33 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I34 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I35 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I36 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I37 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I38 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I39 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I40 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | S27 | NUC1 | EventMaskLo | UINT32 | RW | 0...4294967295
59 | S1 | MJP1 | Im> [51LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
59 | V1 | MJP1 | Im> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
59 | I1 | MJP1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
59 | I2 | MJP1 | Im> starts | UINT32 | R | 0...4294967295
59 | I3 | MJP1 | Im> trips | UINT32 | R | 0...4294967295
59 | I4 | MJP1 | Im> blocks | UINT32 | R | 0...4294967295
59 | S2 | MJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
59 | S3 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S4 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S5 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S6 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S7 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S8 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S9 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S10 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S11 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S12 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S13 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S14 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S15 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S16 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S17 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S18 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | O1 | MJP1 | Im> START | SIGNAL_OUT | RW | 0...4294967295
59 | O2 | MJP1 | Im> TRIP | SIGNAL_OUT | RW | 0...4294967295
59 | O3 | MJP1 | Im> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
59 | I5 | MJP1 | Newest Register | UINT32 | R | 0...12
59 | I6 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I7 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I8 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I9 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I10 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I11 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I12 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I13 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I14 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I15 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I16 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I17 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I18 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I19 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I20 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I21 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I22 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I23 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I24 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I25 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I26 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I27 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I28 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I29 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I30 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I31 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I32 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I33 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I34 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I35 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I36 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I37 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I38 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I39 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I40 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I41 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | S19 | MJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
85 | S1 | OV1 | U> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
85 | V1 | OV1 | U> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
85 | I1 | OV1 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
85 | I2 | OV1 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
85 | I3 | OV1 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
85 | I4 | OV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
85 | I5 | OV1 | U> starts | UINT32 | R | 0...4294967295
85 | I6 | OV1 | U> trips | UINT32 | R | 0...4294967295
85 | I7 | OV1 | U> blocks | UINT32 | R | 0...4294967295
85 | S2 | OV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
85 | S3 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S4 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S5 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S6 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S7 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S8 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S9 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S10 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S11 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S12 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S13 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S14 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S15 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S16 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S17 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S18 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S19 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S20 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S21 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S22 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S23 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S24 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S25 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S26 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | O1 | OV1 | U> START | SIGNAL_OUT | RW | 0...4294967295
85 | O2 | OV1 | U> TRIP | SIGNAL_OUT | RW | 0...4294967295
85 | O3 | OV1 | U> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
85 | I8 | OV1 | Newest Register | UINT32 | R | 0...12
85 | I9 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I10 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I11 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I12 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I13 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I14 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I15 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I16 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I17 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I18 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I19 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I20 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I21 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I22 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I23 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I24 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I25 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I26 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I27 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I28 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I29 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I30 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I31 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I32 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I33 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I34 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I35 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I36 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I37 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I38 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I39 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I40 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I41 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I42 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I43 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I44 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | S27 | OV1 | EventMaskLo | UINT32 | RW | 0...4294967295
86 | S1 | OV2 | U>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
86 | V1 | OV2 | U>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
86 | I1 | OV2 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
86 | I2 | OV2 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
86 | I3 | OV2 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
86 | I4 | OV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
86 | I5 | OV2 | U>> starts | UINT32 | R | 0...4294967295
86 | I6 | OV2 | U>> trips | UINT32 | R | 0...4294967295
86 | I7 | OV2 | U>> blocks | UINT32 | R | 0...4294967295
86 | S2 | OV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
86 | S3 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S4 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S5 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S6 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S7 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S8 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S9 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S10 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S11 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S12 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S13 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S14 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S15 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S16 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S17 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S18 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S19 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S20 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S21 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S22 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S23 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S24 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S25 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S26 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | O1 | OV2 | U>> START | SIGNAL_OUT | RW | 0...4294967295
86 | O2 | OV2 | U>> TRIP | SIGNAL_OUT | RW | 0...4294967295
86 | O3 | OV2 | U>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
86 | I8 | OV2 | Newest Register | UINT32 | R | 0...12
86 | I9 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I10 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I11 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I12 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I13 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I14 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I15 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I16 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I17 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I18 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I19 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I20 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I21 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I22 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I23 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I24 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I25 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I26 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I27 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I28 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I29 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I30 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I31 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I32 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I33 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I34 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I35 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I36 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I37 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I38 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I39 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I40 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I41 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I42 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I43 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I44 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | S27 | OV2 | EventMaskLo | UINT32 | RW | 0...4294967295
87 | S1 | OV3 | U>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
87 | V1 | OV3 | U>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
87 | I1 | OV3 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
87 | I2 | OV3 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
87 | I3 | OV3 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
87 | I4 | OV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
87 | I5 | OV3 | U>>> starts | UINT32 | R | 0...4294967295
87 | I6 | OV3 | U>>> trips | UINT32 | R | 0...4294967295
87 | I7 | OV3 | U>>> blocks | UINT32 | R | 0...4294967295
87 | S2 | OV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
87 | S3 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S4 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S5 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S6 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S7 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S8 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S9 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S10 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S11 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S12 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S13 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S14 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S15 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S16 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S17 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S18 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S19 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S20 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S21 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S22 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S23 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S24 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S25 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S26 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | O1 | OV3 | U>>> START | SIGNAL_OUT | RW | 0...4294967295
87 | O2 | OV3 | U>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
87 | O3 | OV3 | U>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
87 | I8 | OV3 | Newest Register | UINT32 | R | 0...12
87 | I9 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I10 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I11 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I12 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I13 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I14 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I15 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I16 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I17 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I18 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I19 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I20 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I21 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I22 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I23 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I24 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I25 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I26 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I27 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I28 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I29 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I30 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I31 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I32 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I33 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I34 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I35 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I36 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I37 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I38 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I39 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I40 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I41 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I42 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I43 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I44 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | S27 | OV3 | EventMaskLo | UINT32 | RW | 0...4294967295
88 | S1 | OV4 | U>>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
88 | V1 | OV4 | U>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
88 | I1 | OV4 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
88 | I2 | OV4 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
88 | I3 | OV4 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
88 | I4 | OV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
88 | I5 | OV4 | U>>>> starts | UINT32 | R | 0...4294967295
88 | I6 | OV4 | U>>>> trips | UINT32 | R | 0...4294967295
88 | I7 | OV4 | U>>>> blocks | UINT32 | R | 0...4294967295
88 | S2 | OV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
88 | S3 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S4 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S5 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S6 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S7 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S8 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S9 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S10 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S11 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S12 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S13 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S14 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S15 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S16 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S17 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S18 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S19 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S20 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S21 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S22 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S23 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S24 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S25 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S26 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | O1 | OV4 | U>>>> START | SIGNAL_OUT | RW | 0...4294967295
88 | O2 | OV4 | U>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
88 | O3 | OV4 | U>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
88 | I8 | OV4 | Newest Register | UINT32 | R | 0...12
88 | I9 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I10 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I11 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I12 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I13 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I14 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I15 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I16 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I17 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I18 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I19 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I20 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I21 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I22 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I23 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I24 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I25 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I26 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I27 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I28 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I29 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I30 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I31 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I32 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I33 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I34 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I35 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I36 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I37 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I38 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I39 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I40 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I41 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I42 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I43 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I44 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | S27 | OV4 | EventMaskLo | UINT32 | RW | 0...4294967295
89 | S1 | UV1 | U< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
89 | V1 | UV1 | U< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
89 | I1 | UV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
89 | I2 | UV1 | U< starts | UINT32 | R | 0...4294967295
89 | I3 | UV1 | U< trips | UINT32 | R | 0...4294967295
89 | I4 | UV1 | U< blocks | UINT32 | R | 0...4294967295
89 | S2 | UV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
89 | S3 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S4 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S5 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S6 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S7 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S8 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S9 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S10 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S11 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S12 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S13 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S14 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S15 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S16 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S17 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S18 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S19 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S20 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S21 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S22 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S23 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S24 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S25 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S26 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S27 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S28 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S29 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S30 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S31 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S32 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S33 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S34 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | O1 | UV1 | U< START | SIGNAL_OUT | RW | 0...4294967295
89 | O2 | UV1 | U< TRIP | SIGNAL_OUT | RW | 0...4294967295
89 | O3 | UV1 | U< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
89 | I5 | UV1 | Newest Register | UINT32 | R | 0...12
89 | I6 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I7 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I8 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I9 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I10 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I11 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I12 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I13 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I14 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I15 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I16 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I17 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I18 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I19 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I20 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I21 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I22 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I23 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I24 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I25 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I26 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I27 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I28 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I29 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I30 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I31 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I32 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I33 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I34 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I35 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I36 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I37 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I38 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I39 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I40 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I41 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | S35 | UV1 | EventMaskLo | UINT32 | RW | 0...4294967295
90 | S1 | UV2 | U<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
90 | V1 | UV2 | U<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
90 | I1 | UV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
90 | I2 | UV2 | U<< starts | UINT32 | R | 0...4294967295
90 | I3 | UV2 | U<< trips | UINT32 | R | 0...4294967295
90 | I4 | UV2 | U<< blocks | UINT32 | R | 0...4294967295
90 | S2 | UV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
90 | S3 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S4 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S5 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S6 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S7 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S8 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S9 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S10 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S11 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S12 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S13 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S14 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S15 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S16 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S17 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S18 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S19 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S20 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S21 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S22 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S23 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S24 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S25 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S26 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S27 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S28 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S29 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S30 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S31 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S32 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S33 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S34 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | O1 | UV2 | U<< START | SIGNAL_OUT | RW | 0...4294967295
90 | O2 | UV2 | U<< TRIP | SIGNAL_OUT | RW | 0...4294967295
90 | O3 | UV2 | U<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
90 | I5 | UV2 | Newest Register | UINT32 | R | 0...12
90 | I6 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I7 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I8 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I9 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I10 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I11 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I12 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I13 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I14 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I15 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I16 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I17 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I18 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I19 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I20 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I21 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I22 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I23 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I24 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I25 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I26 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I27 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I28 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I29 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I30 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I31 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I32 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I33 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I34 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I35 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I36 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I37 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I38 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I39 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I40 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I41 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | S35 | UV2 | EventMaskLo | UINT32 | RW | 0...4294967295
91 | S1 | UV3 | U<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
91 | V1 | UV3 | U<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
91 | I1 | UV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
91 | I2 | UV3 | U<<< starts | UINT32 | R | 0...4294967295
91 | I3 | UV3 | U<<< trips | UINT32 | R | 0...4294967295
91 | I4 | UV3 | U<<< blocks | UINT32 | R | 0...4294967295
91 | S2 | UV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
91 | S3 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S4 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S5 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S6 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S7 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S8 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S9 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S10 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S11 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S12 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S13 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S14 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S15 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S16 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S17 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S18 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S19 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S20 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S21 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S22 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S23 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S24 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S25 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S26 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S27 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S28 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S29 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S30 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S31 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S32 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S33 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S34 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | O1 | UV3 | U<<< START | SIGNAL_OUT | RW | 0...4294967295
91 | O2 | UV3 | U<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
91 | O3 | UV3 | U<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
91 | I5 | UV3 | Newest Register | UINT32 | R | 0...12
91 | I6 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I7 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I8 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I9 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I10 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I11 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I12 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I13 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I14 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I15 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I16 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I17 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I18 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I19 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I20 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I21 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I22 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I23 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I24 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I25 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I26 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I27 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I28 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I29 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I30 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I31 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I32 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I33 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I34 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I35 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I36 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I37 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I38 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I39 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I40 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I41 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | S35 | UV3 | EventMaskLo | UINT32 | RW | 0...4294967295
92 | S1 | UV4 | U<<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
92 | V1 | UV4 | U<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
92 | I1 | UV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
92 | I2 | UV4 | U<<<< starts | UINT32 | R | 0...4294967295
92 | I3 | UV4 | U<<<< trips | UINT32 | R | 0...4294967295
92 | I4 | UV4 | U<<<< blocks | UINT32 | R | 0...4294967295
92 | S2 | UV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
92 | S3 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S4 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S5 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S6 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S7 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S8 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S9 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S10 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S11 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S12 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S13 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S14 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S15 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S16 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S17 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S18 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S19 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S20 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S21 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S22 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S23 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S24 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S25 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S26 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S27 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S28 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S29 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S30 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S31 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S32 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S33 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S34 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | O1 | UV4 | U<<<< START | SIGNAL_OUT | RW | 0...4294967295
92 | O2 | UV4 | U<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
92 | O3 | UV4 | U<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
92 | I5 | UV4 | Newest Register | UINT32 | R | 0...12
92 | I6 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I7 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I8 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I9 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I10 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I11 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I12 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I13 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I14 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I15 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I16 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I17 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I18 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I19 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I20 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I21 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I22 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I23 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I24 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I25 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I26 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I27 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I28 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I29 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I30 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I31 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I32 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I33 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I34 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I35 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I36 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I37 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I38 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I39 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I40 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I41 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | S35 | UV4 | EventMaskLo | UINT32 | RW | 0...4294967295
93 | S1 | NOV1 | U0> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
93 | V1 | NOV1 | U0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
93 | I1 | NOV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
93 | I2 | NOV1 | U0> starts | UINT32 | R | 0...4294967295
93 | I3 | NOV1 | U0> trips | UINT32 | R | 0...4294967295
93 | I4 | NOV1 | U0> blocks | UINT32 | R | 0...4294967295
93 | S2 | NOV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
93 | S3 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S4 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S5 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S6 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S7 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S8 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S9 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S10 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S11 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S12 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S13 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S14 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S15 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S16 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S17 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S18 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | O1 | NOV1 | U0> START | SIGNAL_OUT | RW | 0...4294967295
93 | O2 | NOV1 | U0> TRIP | SIGNAL_OUT | RW | 0...4294967295
93 | O3 | NOV1 | U0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
93 | I5 | NOV1 | Newest Register | UINT32 | R | 0...12
93 | I6 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I7 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I8 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I9 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I10 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I11 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I12 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I13 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I14 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I15 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I16 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I17 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I18 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I19 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I20 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I21 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I22 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I23 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I24 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I25 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I26 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I27 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I28 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I29 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | S19 | NOV1 | EventMaskLo | UINT32 | RW | 0...4294967295
94 | S1 | NOV2 | U0>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
94 | V1 | NOV2 | U0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
94 | I1 | NOV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
94 | I2 | NOV2 | U0>> starts | UINT32 | R | 0...4294967295
94 | I3 | NOV2 | U0>> trips | UINT32 | R | 0...4294967295
94 | I4 | NOV2 | U0>> blocks | UINT32 | R | 0...4294967295
94 | S2 | NOV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
94 | S3 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S4 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S5 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S6 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S7 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S8 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S9 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S10 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S11 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S12 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S13 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S14 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S15 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S16 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S17 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S18 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | O1 | NOV2 | U0>> START | SIGNAL_OUT | RW | 0...4294967295
94 | O2 | NOV2 | U0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
94 | O3 | NOV2 | U0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
94 | I5 | NOV2 | Newest Register | UINT32 | R | 0...12
94 | I6 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I7 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I8 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I9 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I10 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I11 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I12 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I13 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I14 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I15 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I16 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I17 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I18 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I19 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I20 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I21 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I22 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I23 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I24 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I25 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I26 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I27 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I28 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I29 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | S19 | NOV2 | EventMaskLo | UINT32 | RW | 0...4294967295
95 | S1 | NOV3 | U0>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
95 | V1 | NOV3 | U0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
95 | I1 | NOV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
95 | I2 | NOV3 | U0>>> starts | UINT32 | R | 0...4294967295
95 | I3 | NOV3 | U0>>> trips | UINT32 | R | 0...4294967295
95 | I4 | NOV3 | U0>>> blocks | UINT32 | R | 0...4294967295
95 | S2 | NOV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
95 | S3 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S4 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S5 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S6 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S7 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S8 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S9 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S10 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S11 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S12 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S13 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S14 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S15 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S16 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S17 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S18 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | O1 | NOV3 | U0>>> START | SIGNAL_OUT | RW | 0...4294967295
95 | O2 | NOV3 | U0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
95 | O3 | NOV3 | U0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
95 | I5 | NOV3 | Newest Register | UINT32 | R | 0...12
95 | I6 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I7 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I8 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I9 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I10 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I11 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I12 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I13 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I14 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I15 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I16 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I17 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I18 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I19 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I20 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I21 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I22 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I23 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I24 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I25 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I26 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I27 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I28 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I29 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | S19 | NOV3 | EventMaskLo | UINT32 | RW | 0...4294967295
96 | S1 | NOV4 | U0>>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
96 | V1 | NOV4 | U0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
96 | I1 | NOV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
96 | I2 | NOV4 | U0>>>> starts | UINT32 | R | 0...4294967295
96 | I3 | NOV4 | U0>>>> trips | UINT32 | R | 0...4294967295
96 | I4 | NOV4 | U0>>>> blocks | UINT32 | R | 0...4294967295
96 | S2 | NOV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
96 | S3 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S4 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S5 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S6 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S7 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S8 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S9 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S10 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S11 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S12 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S13 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S14 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S15 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S16 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S17 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S18 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | O1 | NOV4 | U0>>>> START | SIGNAL_OUT | RW | 0...4294967295
96 | O2 | NOV4 | U0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
96 | O3 | NOV4 | U0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
96 | I5 | NOV4 | Newest Register | UINT32 | R | 0...12
96 | I6 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I7 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I8 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I9 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I10 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I11 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I12 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I13 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I14 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I15 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I16 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I17 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I18 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I19 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I20 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I21 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I22 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I23 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I24 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I25 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I26 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I27 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I28 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I29 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | S19 | NOV4 | EventMaskLo | UINT32 | RW | 0...4294967295
130 | S1 | VUB1 | U1/2 >/< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
130 | V1 | VUB1 | U1/2 >/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
130 | I1 | VUB1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
130 | I2 | VUB1 | U1/2 >/< starts | UINT32 | R | 0...4294967295
130 | I3 | VUB1 | U1/2 >/< trips | UINT32 | R | 0...4294967295
130 | I4 | VUB1 | U1/2 >/< blocks | UINT32 | R | 0...4294967295
130 | S2 | VUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
130 | S3 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S4 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S5 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S6 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S7 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S8 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S9 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S10 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S11 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S12 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S13 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S14 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S15 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S16 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S17 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S18 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S19 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S20 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S21 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S22 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S23 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S24 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S25 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S26 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S27 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S28 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S29 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S30 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S31 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S32 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S33 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S34 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | O1 | VUB1 | U1/2 >/< START | SIGNAL_OUT | RW | 0...4294967295
130 | O2 | VUB1 | U1/2 >/< TRIP | SIGNAL_OUT | RW | 0...4294967295
130 | O3 | VUB1 | U1/2 >/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
130 | I5 | VUB1 | Newest Register | UINT32 | R | 0...12
130 | I6 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I7 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I8 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I9 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I10 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I11 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I12 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I13 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I14 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I15 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I16 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I17 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I18 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I19 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I20 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I21 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I22 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I23 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I24 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I25 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I26 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I27 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I28 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I29 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | S35 | VUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
131 | S1 | VUB2 | U1/2 >>/<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
131 | V1 | VUB2 | U1/2 >>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
131 | I1 | VUB2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
131 | I2 | VUB2 | U1/2 >>/<< starts | UINT32 | R | 0...4294967295
131 | I3 | VUB2 | U1/2 >>/<< trips | UINT32 | R | 0...4294967295
131 | I4 | VUB2 | U1/2 >>/<< blocks | UINT32 | R | 0...4294967295
131 | S2 | VUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
131 | S3 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S4 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S5 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S6 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S7 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S8 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S9 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S10 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S11 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S12 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S13 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S14 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S15 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S16 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S17 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S18 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S19 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S20 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S21 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S22 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S23 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S24 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S25 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S26 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S27 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S28 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S29 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S30 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S31 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S32 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S33 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S34 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | O1 | VUB2 | U1/2 >>/<< START | SIGNAL_OUT | RW | 0...4294967295
131 | O2 | VUB2 | U1/2 >>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
131 | O3 | VUB2 | U1/2 >>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
131 | I5 | VUB2 | Newest Register | UINT32 | R | 0...12
131 | I6 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I7 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I8 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I9 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I10 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I11 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I12 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I13 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I14 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I15 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I16 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I17 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I18 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I19 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I20 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I21 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I22 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I23 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I24 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I25 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I26 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I27 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I28 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I29 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | S35 | VUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
132 | S1 | VUB3 | U1/2 >>>/<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
132 | V1 | VUB3 | U1/2 >>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
132 | I1 | VUB3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
132 | I2 | VUB3 | U1/2 >>>/<<< starts | UINT32 | R | 0...4294967295
132 | I3 | VUB3 | U1/2 >>>/<<< trips | UINT32 | R | 0...4294967295
132 | I4 | VUB3 | U1/2 >>>/<<< blocks | UINT32 | R | 0...4294967295
132 | S2 | VUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
132 | S3 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S4 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S5 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S6 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S7 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S8 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S9 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S10 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S11 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S12 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S13 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S14 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S15 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S16 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S17 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S18 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S19 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S20 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S21 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S22 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S23 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S24 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S25 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S26 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S27 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S28 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S29 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S30 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S31 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S32 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S33 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S34 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | O1 | VUB3 | U1/2 >>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
132 | O2 | VUB3 | U1/2 >>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
132 | O3 | VUB3 | U1/2 >>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
132 | I5 | VUB3 | Newest Register | UINT32 | R | 0...12
132 | I6 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I7 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I8 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I9 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I10 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I11 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I12 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I13 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I14 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I15 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I16 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I17 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I18 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I19 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I20 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I21 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I22 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I23 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I24 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I25 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I26 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I27 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I28 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I29 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | S35 | VUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
133 | S1 | VUB4 | U1/2 >>>>/<<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
133 | V1 | VUB4 | U1/2 >>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
133 | I1 | VUB4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
133 | I2 | VUB4 | U1/2 >>>>/<<<< starts | UINT32 | R | 0...4294967295
133 | I3 | VUB4 | U1/2 >>>>/<<<< trips | UINT32 | R | 0...4294967295
133 | I4 | VUB4 | U1/2 >>>>/<<<< blocks | UINT32 | R | 0...4294967295
133 | S2 | VUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
133 | S3 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S4 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S5 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S6 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S7 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S8 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S9 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S10 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S11 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S12 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S13 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S14 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S15 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S16 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S17 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S18 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S19 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S20 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S21 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S22 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S23 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S24 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S25 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S26 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S27 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S28 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S29 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S30 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S31 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S32 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S33 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S34 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | O1 | VUB4 | U1/2 >>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
133 | O2 | VUB4 | U1/2 >>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
133 | O3 | VUB4 | U1/2 >>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
133 | I5 | VUB4 | Newest Register | UINT32 | R | 0...12
133 | I6 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I7 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I8 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I9 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I10 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I11 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I12 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I13 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I14 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I15 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I16 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I17 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I18 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I19 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I20 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I21 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I22 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I23 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I24 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I25 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I26 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I27 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I28 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I29 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | S35 | VUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
99 | S1 | FRQV1 | f</> [81O/81U] mode | UINT32 | RW | 0=Disabled;1=Activated
99 | V1 | FRQV1 | f> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I1 | FRQV1 | f> fmeas / fset | FLOAT | R | 0...20
99 | S2 | FRQV1 | f>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V2 | FRQV1 | f>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I2 | FRQV1 | f>> fmeas / fset | FLOAT | R | 0...20
99 | S3 | FRQV1 | f>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V3 | FRQV1 | f>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I3 | FRQV1 | f>>> fmeas / fset | FLOAT | R | 0...20
99 | S4 | FRQV1 | f>>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V4 | FRQV1 | f>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I4 | FRQV1 | f>>>> fmeas / fset | FLOAT | R | 0...20
99 | S5 | FRQV1 | f< Enable | UINT32 | RW | 0=No;1=Yes
99 | V5 | FRQV1 | f< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I5 | FRQV1 | f< fmeas / fset | FLOAT | R | 0...20
99 | S6 | FRQV1 | f<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V6 | FRQV1 | f<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I6 | FRQV1 | f<< fmeas / fset | FLOAT | R | 0...20
99 | S7 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V7 | FRQV1 | f<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I7 | FRQV1 | f<<< fmeas / fset | FLOAT | R | 0...20
99 | S8 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V8 | FRQV1 | f<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I8 | FRQV1 | f<<<< fmeas / fset | FLOAT | R | 0...20
99 | I9 | FRQV1 | f> starts | UINT32 | R | 0...4294967295
99 | I10 | FRQV1 | f> trips | UINT32 | R | 0...4294967295
99 | I11 | FRQV1 | f> blocks | UINT32 | R | 0...4294967295
99 | I12 | FRQV1 | f>> starts | UINT32 | R | 0...4294967295
99 | I13 | FRQV1 | f>> trips | UINT32 | R | 0...4294967295
99 | I14 | FRQV1 | f>> blocks | UINT32 | R | 0...4294967295
99 | I15 | FRQV1 | f>>> starts | UINT32 | R | 0...4294967295
99 | I16 | FRQV1 | f>>> trips | UINT32 | R | 0...4294967295
99 | I17 | FRQV1 | f>>> blocks | UINT32 | R | 0...4294967295
99 | I18 | FRQV1 | f>>>> starts | UINT32 | R | 0...4294967295
99 | I19 | FRQV1 | f>>>> trips | UINT32 | R | 0...4294967295
99 | I20 | FRQV1 | f>>>> blocks | UINT32 | R | 0...4294967295
99 | I21 | FRQV1 | f< starts | UINT32 | R | 0...4294967295
99 | I22 | FRQV1 | f< trips | UINT32 | R | 0...4294967295
99 | I23 | FRQV1 | f< blocks | UINT32 | R | 0...4294967295
99 | I24 | FRQV1 | f<< starts | UINT32 | R | 0...4294967295
99 | I25 | FRQV1 | f<< trips | UINT32 | R | 0...4294967295
99 | I26 | FRQV1 | f<< blocks | UINT32 | R | 0...4294967295
99 | I27 | FRQV1 | f<<< starts | UINT32 | R | 0...4294967295
99 | I28 | FRQV1 | f<<< trips | UINT32 | R | 0...4294967295
99 | I29 | FRQV1 | f<<< blocks | UINT32 | R | 0...4294967295
99 | I30 | FRQV1 | f<<<< starts | UINT32 | R | 0...4294967295
99 | I31 | FRQV1 | f<<<< trips | UINT32 | R | 0...4294967295
99 | I32 | FRQV1 | f<<<< blocks | UINT32 | R | 0...4294967295
99 | S9 | FRQV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
99 | S10 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S11 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S12 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S13 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S14 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S15 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S16 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S17 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S18 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S19 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S20 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S21 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S22 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S23 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S24 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S25 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S26 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S27 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S28 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S29 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S30 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S31 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S32 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S33 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S34 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S35 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S36 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S37 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S38 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S39 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S40 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S41 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S42 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S43 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S44 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S45 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S46 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S47 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S48 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S49 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S50 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S51 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S52 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S53 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S54 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S55 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S56 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S57 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S58 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S59 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S60 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S61 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S62 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S63 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S64 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S65 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S66 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S67 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S68 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S69 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S70 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S71 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S72 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S73 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S74 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S75 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S76 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S77 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S78 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S79 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S80 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S81 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S82 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S83 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S84 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S85 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S86 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S87 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S88 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S89 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S90 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S91 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S92 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S93 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S94 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S95 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S96 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S97 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S98 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S99 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S100 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S101 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S102 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S103 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S104 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S105 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S106 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S107 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S108 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S109 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S110 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S111 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S112 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S113 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S114 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S115 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S116 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S117 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S118 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S119 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S120 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S121 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S122 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S123 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S124 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S125 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S126 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S127 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S128 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S129 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S130 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S131 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S132 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S133 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S134 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S135 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S136 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S137 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S138 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S139 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S140 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S141 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S142 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S143 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S144 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S145 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S146 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S147 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S148 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S149 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S150 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S151 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S152 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S153 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S154 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S155 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S156 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S157 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S158 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S159 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S160 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S161 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S162 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S163 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S164 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S165 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S166 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S167 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S168 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S169 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S170 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S171 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S172 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S173 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S174 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S175 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S176 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S177 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S178 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S179 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S180 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S181 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S182 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S183 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S184 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S185 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S186 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S187 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S188 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S189 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S190 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S191 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S192 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S193 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S194 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S195 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S196 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S197 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S198 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S199 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S200 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S201 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | O1 | FRQV1 | f> START | SIGNAL_OUT | RW | 0...4294967295
99 | O2 | FRQV1 | f> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O3 | FRQV1 | f> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O4 | FRQV1 | f>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O5 | FRQV1 | f>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O6 | FRQV1 | f>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O7 | FRQV1 | f>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O8 | FRQV1 | f>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O9 | FRQV1 | f>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O10 | FRQV1 | f>>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O11 | FRQV1 | f>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O12 | FRQV1 | f>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O13 | FRQV1 | f< START | SIGNAL_OUT | RW | 0...4294967295
99 | O14 | FRQV1 | f< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O15 | FRQV1 | f< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O16 | FRQV1 | f<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O17 | FRQV1 | f<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O18 | FRQV1 | f<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O19 | FRQV1 | f<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O20 | FRQV1 | f<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O21 | FRQV1 | f<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O22 | FRQV1 | f<<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O23 | FRQV1 | f<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O24 | FRQV1 | f<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | I33 | FRQV1 | Newest Register | UINT32 | R | 0...12
99 | I34 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I35 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I36 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I37 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I38 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I39 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I40 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I41 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I42 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I43 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I44 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I45 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | S202 | FRQV1 | EventMaskLo | UINT32 | RW | 0...4294967295
103 | S1 | DFT1 | df/dt >/< [81] mode | UINT32 | RW | 0=Disabled;1=Activated
103 | S2 | DFT1 | Max allowed df/dt rate | FLOAT | RW | 0.1...50
103 | I1 | DFT1 | Measured df/dt | FLOAT | R | 0...20
103 | S3 | DFT1 | df/dt >/< (1) Enable | UINT32 | RW | 0=No;1=Yes
103 | V1 | DFT1 | df/dt >/< (1) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I2 | DFT1 | df/dt >/< (1) fmeas / fset | FLOAT | R | 0...20
103 | S4 | DFT1 | df/dt >/< (2) Enable | UINT32 | RW | 0=No;1=Yes
103 | V2 | DFT1 | df/dt >/< (2) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I3 | DFT1 | df/dt >/< (2) fmeas / fset | FLOAT | R | 0...20
103 | S5 | DFT1 | df/dt >/< (3) Enable | UINT32 | RW | 0=No;1=Yes
103 | V3 | DFT1 | df/dt >/< (3) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I4 | DFT1 | df/dt >/< (3) fmeas / fset | FLOAT | R | 0...20
103 | S6 | DFT1 | df/dt >/< (4) Enable | UINT32 | RW | 0=No;1=Yes
103 | V4 | DFT1 | df/dt >/< (4) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I5 | DFT1 | df/dt >/< (4) fmeas / fset | FLOAT | R | 0...20
103 | S7 | DFT1 | df/dt >/< (5) Enable | UINT32 | RW | 0=No;1=Yes
103 | V5 | DFT1 | df/dt >/< (5) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I6 | DFT1 | df/dt >/< (5) fmeas / fset | FLOAT | R | 0...20
103 | S8 | DFT1 | df/dt >/< (6) Enable | UINT32 | RW | 0=No;1=Yes
103 | V6 | DFT1 | df/dt >/< (6) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I7 | DFT1 | df/dt >/< (6) fmeas / fset | FLOAT | R | 0...20
103 | S9 | DFT1 | df/dt >/< (7) Enable | UINT32 | RW | 0=No;1=Yes
103 | V7 | DFT1 | df/dt >/< (7) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I8 | DFT1 | df/dt >/< (7) fmeas / fset | FLOAT | R | 0...20
103 | S10 | DFT1 | df/dt >/< (8) Enable | UINT32 | RW | 0=No;1=Yes
103 | V8 | DFT1 | df/dt >/< (8) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I9 | DFT1 | df/dt >/< (8) fmeas / fset | FLOAT | R | 0...20
103 | I10 | DFT1 | df/dt >/< (1) starts | UINT32 | R | 0...4294967295
103 | I11 | DFT1 | df/dt >/< (1) trips | UINT32 | R | 0...4294967295
103 | I12 | DFT1 | df/dt >/< (1) blocks | UINT32 | R | 0...4294967295
103 | I13 | DFT1 | df/dt >/< (2) starts | UINT32 | R | 0...4294967295
103 | I14 | DFT1 | df/dt >/< (2) trips | UINT32 | R | 0...4294967295
103 | I15 | DFT1 | df/dt >/< (2) blocks | UINT32 | R | 0...4294967295
103 | I16 | DFT1 | df/dt >/< (3) starts | UINT32 | R | 0...4294967295
103 | I17 | DFT1 | df/dt >/< (3) trips | UINT32 | R | 0...4294967295
103 | I18 | DFT1 | df/dt >/< (3) blocks | UINT32 | R | 0...4294967295
103 | I19 | DFT1 | df/dt >/< (4) starts | UINT32 | R | 0...4294967295
103 | I20 | DFT1 | df/dt >/< (4) trips | UINT32 | R | 0...4294967295
103 | I21 | DFT1 | df/dt >/< (4) blocks | UINT32 | R | 0...4294967295
103 | I22 | DFT1 | df/dt >/< (5) starts | UINT32 | R | 0...4294967295
103 | I23 | DFT1 | df/dt >/< (5) trips | UINT32 | R | 0...4294967295
103 | I24 | DFT1 | df/dt >/< (5) blocks | UINT32 | R | 0...4294967295
103 | I25 | DFT1 | df/dt >/< (6) starts | UINT32 | R | 0...4294967295
103 | I26 | DFT1 | df/dt >/< (6) trips | UINT32 | R | 0...4294967295
103 | I27 | DFT1 | df/dt >/< (6) blocks | UINT32 | R | 0...4294967295
103 | I28 | DFT1 | df/dt >/< (7) starts | UINT32 | R | 0...4294967295
103 | I29 | DFT1 | df/dt >/< (7) trips | UINT32 | R | 0...4294967295
103 | I30 | DFT1 | df/dt >/< (7) blocks | UINT32 | R | 0...4294967295
103 | I31 | DFT1 | df/dt >/< (8) starts | UINT32 | R | 0...4294967295
103 | I32 | DFT1 | df/dt >/< (8) trips | UINT32 | R | 0...4294967295
103 | I33 | DFT1 | df/dt >/< (8) blocks | UINT32 | R | 0...4294967295
103 | S11 | DFT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
103 | S12 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S13 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S14 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S15 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S16 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S17 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S18 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S19 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S20 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S21 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S22 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S23 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S24 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S25 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S26 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S27 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S28 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S29 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S30 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S31 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S32 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S33 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S34 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S35 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S36 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S37 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S38 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S39 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S40 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S41 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S42 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S43 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S44 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S45 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S46 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S47 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S48 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S49 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S50 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S51 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S52 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S53 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S54 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S55 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S56 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S57 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S58 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S59 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S60 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S61 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S62 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S63 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S64 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S65 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S66 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S67 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S68 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S69 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S70 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S71 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S72 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S73 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S74 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S75 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S76 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S77 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S78 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S79 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S80 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S81 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S82 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S83 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S84 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S85 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S86 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S87 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S88 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S89 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S90 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S91 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S92 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S93 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S94 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S95 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S96 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S97 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S98 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S99 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S100 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S101 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S102 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S103 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S104 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S105 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S106 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S107 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S108 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S109 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S110 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S111 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S112 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S113 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S114 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S115 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S116 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S117 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S118 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S119 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S120 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S121 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S122 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S123 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S124 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S125 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S126 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S127 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S128 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S129 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S130 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S131 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S132 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S133 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S134 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S135 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S136 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S137 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S138 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S139 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S140 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S141 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S142 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S143 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S144 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S145 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S146 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S147 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S148 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S149 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S150 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S151 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S152 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S153 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S154 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S155 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S156 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S157 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S158 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S159 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S160 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S161 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S162 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S163 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S164 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S165 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S166 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S167 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S168 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S169 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S170 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S171 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S172 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S173 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S174 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S175 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S176 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S177 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S178 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S179 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S180 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S181 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S182 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S183 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S184 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S185 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S186 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S187 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S188 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S189 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S190 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S191 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S192 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S193 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S194 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S195 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S196 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S197 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S198 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S199 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S200 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S201 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S202 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S203 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S204 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S205 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S206 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S207 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S208 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S209 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S210 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S211 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S212 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S213 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S214 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S215 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S216 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S217 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S218 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S219 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S220 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S221 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S222 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S223 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S224 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S225 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S226 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S227 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S228 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S229 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S230 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S231 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S232 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S233 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S234 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S235 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S236 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S237 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S238 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S239 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S240 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S241 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S242 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S243 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S244 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S245 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S246 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S247 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S248 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S249 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S250 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S251 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S252 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S253 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S254 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S255 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S256 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S257 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S258 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S259 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S260 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S261 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S262 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S263 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S264 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S265 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S266 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S267 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S268 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S269 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S270 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S271 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S272 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S273 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S274 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S275 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S276 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S277 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S278 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S279 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S280 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S281 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S282 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S283 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S284 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S285 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S286 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S287 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S288 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S289 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S290 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S291 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S292 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S293 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S294 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S295 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S296 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S297 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S298 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S299 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S300 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S301 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S302 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S303 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S304 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S305 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S306 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S307 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S308 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S309 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S310 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S311 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S312 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S313 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S314 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S315 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S316 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S317 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S318 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S319 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S320 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S321 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S322 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S323 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S324 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S325 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S326 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S327 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S328 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S329 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S330 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S331 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S332 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S333 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S334 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S335 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S336 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S337 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S338 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S339 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S340 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S341 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S342 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S343 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S344 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S345 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S346 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S347 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S348 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S349 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S350 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S351 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S352 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S353 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S354 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S355 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S356 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S357 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S358 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S359 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S360 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S361 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S362 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S363 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S364 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S365 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S366 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S367 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S368 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S369 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S370 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S371 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S372 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S373 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S374 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S375 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S376 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S377 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S378 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S379 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S380 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S381 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S382 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S383 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S384 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S385 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S386 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S387 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S388 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S389 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S390 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S391 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S392 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S393 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S394 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S395 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S396 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S397 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S398 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S399 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S400 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S401 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S402 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S403 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S404 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S405 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S406 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S407 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S408 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S409 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S410 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S411 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S412 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S413 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S414 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S415 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S416 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S417 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S418 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S419 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S420 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S421 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S422 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S423 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S424 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S425 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S426 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S427 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S428 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S429 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S430 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S431 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S432 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S433 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S434 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S435 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S436 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S437 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S438 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S439 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S440 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S441 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S442 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S443 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S444 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S445 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S446 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S447 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S448 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S449 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S450 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S451 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S452 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S453 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S454 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S455 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S456 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S457 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S458 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S459 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | O1 | DFT1 | df/dt >/< (1) START | SIGNAL_OUT | RW | 0...4294967295
103 | O2 | DFT1 | df/dt >/< (1) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O3 | DFT1 | df/dt >/< (1) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O4 | DFT1 | df/dt >/< (2) START | SIGNAL_OUT | RW | 0...4294967295
103 | O5 | DFT1 | df/dt >/< (2) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O6 | DFT1 | df/dt >/< (2) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O7 | DFT1 | df/dt >/< (3) START | SIGNAL_OUT | RW | 0...4294967295
103 | O8 | DFT1 | df/dt >/< (3) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O9 | DFT1 | df/dt >/< (3) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O10 | DFT1 | df/dt >/< (4) START | SIGNAL_OUT | RW | 0...4294967295
103 | O11 | DFT1 | df/dt >/< (4) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O12 | DFT1 | df/dt >/< (4) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O13 | DFT1 | df/dt >/< (5) START | SIGNAL_OUT | RW | 0...4294967295
103 | O14 | DFT1 | df/dt >/< (5) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O15 | DFT1 | df/dt >/< (5) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O16 | DFT1 | df/dt >/< (6) START | SIGNAL_OUT | RW | 0...4294967295
103 | O17 | DFT1 | df/dt >/< (6) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O18 | DFT1 | df/dt >/< (6) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O19 | DFT1 | df/dt >/< (7) START | SIGNAL_OUT | RW | 0...4294967295
103 | O20 | DFT1 | df/dt >/< (7) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O21 | DFT1 | df/dt >/< (7) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O22 | DFT1 | df/dt >/< (8) START | SIGNAL_OUT | RW | 0...4294967295
103 | O23 | DFT1 | df/dt >/< (8) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O24 | DFT1 | df/dt >/< (8) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | I34 | DFT1 | Newest Register | UINT32 | R | 0...12
103 | I35 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I36 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I37 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I38 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I39 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I40 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I41 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I42 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I43 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I44 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I45 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I46 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I47 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I48 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I49 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I50 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I51 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I52 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I53 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I54 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I55 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I56 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I57 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I58 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | S460 | DFT1 | EventMaskLo | UINT32 | RW | 0...4294967295
183 | V1 | RHC1 | Counter is now | UINT32 | R | 0=Idle;1=Counting
183 | I1 | RHC1 | Running hours | UINT32 | RW | 0...4294967295
183 | I2 | RHC1 | Start count | UINT32 | RW | 0...4294967295
183 | I3 | RHC1 | Clear Hours | UINT32 | W | 0=-;1=Clear
183 | S1 | RHC1 | EventMaskLo | UINT32 | RW | 0...4294967295
113 | V1 | GST1 | Generator is now | UINT32 | R | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
113 | I1 | GST1 | Times Overloaded | UINT32 | R | 0...4294967295
113 | I2 | GST1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
113 | I3 | GST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
113 | I4 | GST1 | Generating time | UINT32 | R | 0...4294967295
113 | I5 | GST1 | Overloading cumulative | UINT32 | R | 0...4294967295
113 | I6 | GST1 | Last overload duration | UINT32 | R | 0...4294967295
113 | I7 | GST1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
113 | I8 | GST1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
113 | S1 | GST1 | Clear total times | UINT32 | W | 0=-;1=Clear
113 | S2 | GST1 | Generator nominal MVA (S) | FLOAT | RW | 0.1...500
113 | S3 | GST1 | Generator nominal Voltage (Vt) | FLOAT | RW | 0.1...25
113 | S4 | GST1 | Prime mover max power output (Pmax) | FLOAT | RW | 0.1...500
113 | S5 | GST1 | Block trafo in protection area | UINT32 | RW | 0=No;1=Yes
113 | S6 | GST1 | Generator voltage measurement | UINT32 | RW | 0=LV side VT (no corrections);1=HV side VT(Reduce to LV);2=HV side VT(HV measurements)
113 | S7 | GST1 | Ratio for generator nominal voltage scaling (1 p.u.) | UINT32 | RW | 0=Generator nominal voltage;1=Transformer LV nominal voltage;2=Set Un ratio by hand
113 | I9 | GST1 | Transformer ratio HV -> LV Trafo. | FLOAT | R | 0.01...100
113 | I10 | GST1 | Transformer ratio HV -> LV Gen. | FLOAT | R | 0.01...100
113 | I11 | GST1 | Voltage ratio | FLOAT | RW | 0.001...100
113 | I12 | GST1 | Voltage scaling | FLOAT | R | 0.01...100
113 | S8 | GST1 | Transformer nominal MVA | FLOAT | RW | 0.001...500
113 | S9 | GST1 | HV side nominal voltage | FLOAT | RW | 0.001...500
113 | S10 | GST1 | LV side nominal voltage | FLOAT | RW | 0.001...500
113 | S11 | GST1 | Transformer Zk % | FLOAT | RW | 0.001...25
113 | S12 | GST1 | Transformer nom freq. | FLOAT | RW | 10...75
113 | S13 | GST1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
113 | I13 | GST1 | HV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I14 | GST1 | HV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I15 | GST1 | HV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I16 | GST1 | LV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I17 | GST1 | LV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I18 | GST1 | LV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I19 | GST1 | Transformer nom impedance | FLOAT | R | 0.01...250
113 | I20 | GST1 | Transformer nom Zk ohm | FLOAT | R | 0.01...250
113 | I21 | GST1 | Transformer nom SC inductance | FLOAT | R | 0.001...100
113 | I22 | GST1 | LV side max 3ph SC curr | FLOAT | R | 0.001...500
113 | I23 | GST1 | LV side 3ph SC to HV side | FLOAT | R | 0.001...500
113 | I24 | GST1 | LV side max 2ph SC curr | FLOAT | R | 0.001...500
113 | I25 | GST1 | LV side 2ph SC to HV side | FLOAT | R | 0.001...500
113 | I26 | GST1 | Trafo HV nominal current | FLOAT | R | 0.01...50000
113 | I27 | GST1 | Trafo LV nominal current | FLOAT | R | 0.01...50000
113 | O1 | GST1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
113 | O2 | GST1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O3 | GST1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O4 | GST1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
113 | O5 | GST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | O6 | GST1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | I28 | GST1 | Newest Register | UINT32 | R | 0...12
113 | I29 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I30 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I31 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I32 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I33 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I34 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I35 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I36 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I37 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I38 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I39 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I40 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I41 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I42 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I43 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I44 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I45 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I46 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I47 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I48 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I49 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I50 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I51 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I52 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I53 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I54 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I55 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I56 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I57 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I58 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I59 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I60 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I61 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I62 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I63 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I64 | GST1 | L3 Current | FLOAT | R | 0...250
113 | S14 | GST1 | EventMaskLo | UINT32 | RW | 0...4294967295
164 | S1 | PWR1 | PQS>/< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
164 | V1 | PWR1 | PQS>/< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
164 | I1 | PWR1 | Meas/Set at the moment | FLOAT | R | -1250...1250
164 | I2 | PWR1 | Meas/Nom at the moment | FLOAT | R | -1250...1250
164 | I3 | PWR1 | PQS>/< starts | UINT32 | R | 0...4294967295
164 | I4 | PWR1 | PQS>/< trips | UINT32 | R | 0...4294967295
164 | I5 | PWR1 | PQS>/< blocks | UINT32 | R | 0...4294967295
164 | S2 | PWR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
164 | S3 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S4 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S5 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S6 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S7 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S8 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S9 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S10 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S11 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S12 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S13 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S14 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S15 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S16 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S17 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S18 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | O1 | PWR1 | PQS>/< START | SIGNAL_OUT | RW | 0...4294967295
164 | O2 | PWR1 | PQS>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
164 | O3 | PWR1 | PQS>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
164 | I6 | PWR1 | Newest Register | UINT32 | R | 0...12
164 | I7 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I8 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I9 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I10 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I11 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I12 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I13 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I14 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I15 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I16 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I17 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I18 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | S19 | PWR1 | EventMaskLo | UINT32 | RW | 0...4294967295
165 | S1 | PWR2 | PQS>>/<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
165 | V1 | PWR2 | PQS>>/<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
165 | I1 | PWR2 | Meas/Set at the moment | FLOAT | R | -1250...1250
165 | I2 | PWR2 | Meas/Nom at the moment | FLOAT | R | -1250...1250
165 | I3 | PWR2 | PQS>>/<< starts | UINT32 | R | 0...4294967295
165 | I4 | PWR2 | PQS>>/<< trips | UINT32 | R | 0...4294967295
165 | I5 | PWR2 | PQS>>/<< blocks | UINT32 | R | 0...4294967295
165 | S2 | PWR2 | Clear statistics | UINT32 | W | 0=-;1=Clear
165 | S3 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S4 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S5 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S6 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S7 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S8 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S9 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S10 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S11 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S12 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S13 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S14 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S15 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S16 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S17 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S18 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | O1 | PWR2 | PQS>>/<< START | SIGNAL_OUT | RW | 0...4294967295
165 | O2 | PWR2 | PQS>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
165 | O3 | PWR2 | PQS>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
165 | I6 | PWR2 | Newest Register | UINT32 | R | 0...12
165 | I7 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I8 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I9 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I10 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I11 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I12 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I13 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I14 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I15 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I16 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I17 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I18 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | S19 | PWR2 | EventMaskLo | UINT32 | RW | 0...4294967295
166 | S1 | PWR3 | PQS>>>/<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
166 | V1 | PWR3 | PQS>>>/<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
166 | I1 | PWR3 | Meas/Set at the moment | FLOAT | R | -1250...1250
166 | I2 | PWR3 | Meas/Nom at the moment | FLOAT | R | -1250...1250
166 | I3 | PWR3 | PQS>>>/<<< starts | UINT32 | R | 0...4294967295
166 | I4 | PWR3 | PQS>>>/<<< trips | UINT32 | R | 0...4294967295
166 | I5 | PWR3 | PQS>>>/<<< blocks | UINT32 | R | 0...4294967295
166 | S2 | PWR3 | Clear statistics | UINT32 | W | 0=-;1=Clear
166 | S3 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S4 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S5 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S6 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S7 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S8 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S9 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S10 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S11 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S12 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S13 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S14 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S15 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S16 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S17 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S18 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | O1 | PWR3 | PQS>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
166 | O2 | PWR3 | PQS>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
166 | O3 | PWR3 | PQS>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
166 | I6 | PWR3 | Newest Register | UINT32 | R | 0...12
166 | I7 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I8 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I9 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I10 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I11 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I12 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I13 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I14 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I15 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I16 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I17 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I18 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | S19 | PWR3 | EventMaskLo | UINT32 | RW | 0...4294967295
167 | S1 | PWR4 | PQS>>>>/<<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
167 | V1 | PWR4 | PQS>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
167 | I1 | PWR4 | Meas/Set at the moment | FLOAT | R | -1250...1250
167 | I2 | PWR4 | Meas/Nom at the moment | FLOAT | R | -1250...1250
167 | I3 | PWR4 | PQS>>>>/<<<< starts | UINT32 | R | 0...4294967295
167 | I4 | PWR4 | PQS>>>>/<<<< trips | UINT32 | R | 0...4294967295
167 | I5 | PWR4 | PQS>>>>/<<<< blocks | UINT32 | R | 0...4294967295
167 | S2 | PWR4 | Clear statistics | UINT32 | W | 0=-;1=Clear
167 | S3 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S4 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S5 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S6 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S7 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S8 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S9 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S10 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S11 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S12 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S13 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S14 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S15 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S16 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S17 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S18 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | O1 | PWR4 | PQS>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
167 | O2 | PWR4 | PQS>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
167 | O3 | PWR4 | PQS>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
167 | I6 | PWR4 | Newest Register | UINT32 | R | 0...12
167 | I7 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I8 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I9 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I10 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I11 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I12 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I13 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I14 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I15 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I16 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I17 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I18 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | S19 | PWR4 | EventMaskLo | UINT32 | RW | 0...4294967295
100 | S1 | OPW1 | P> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
100 | V1 | OPW1 | P> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
100 | I1 | OPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
100 | I2 | OPW1 | P> starts | UINT32 | R | 0...4294967295
100 | I3 | OPW1 | P> trips | UINT32 | R | 0...4294967295
100 | I4 | OPW1 | P> blocks | UINT32 | R | 0...4294967295
100 | S2 | OPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
100 | S3 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S4 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S5 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S6 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S7 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S8 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S9 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S10 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S11 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S12 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S13 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S14 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S15 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S16 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S17 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S18 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | O1 | OPW1 | P> START | SIGNAL_OUT | RW | 0...4294967295
100 | O2 | OPW1 | P> TRIP | SIGNAL_OUT | RW | 0...4294967295
100 | O3 | OPW1 | P> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
100 | I5 | OPW1 | Newest Register | UINT32 | R | 0...12
100 | I6 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I7 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I8 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I9 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I10 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I11 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I12 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I13 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I14 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I15 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I16 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I17 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | S19 | OPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
101 | S1 | UPW1 | P< [37] mode | UINT32 | RW | 0=Disabled;1=Activated
101 | V1 | UPW1 | P< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
101 | I1 | UPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
101 | I2 | UPW1 | P< starts | UINT32 | R | 0...4294967295
101 | I3 | UPW1 | P< trips | UINT32 | R | 0...4294967295
101 | I4 | UPW1 | P< blocks | UINT32 | R | 0...4294967295
101 | S2 | UPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
101 | S3 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S4 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S5 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S6 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S7 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S8 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S9 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S10 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S11 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S12 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S13 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S14 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S15 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S16 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S17 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S18 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S19 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S20 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S21 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S22 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S23 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S24 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S25 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S26 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | O1 | UPW1 | P< START | SIGNAL_OUT | RW | 0...4294967295
101 | O2 | UPW1 | P< TRIP | SIGNAL_OUT | RW | 0...4294967295
101 | O3 | UPW1 | P< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
101 | I5 | UPW1 | Newest Register | UINT32 | R | 0...12
101 | I6 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I7 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I8 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I9 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I10 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I11 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I12 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I13 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I14 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I15 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I16 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I17 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | S27 | UPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
102 | S1 | RPW1 | Prev> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
102 | V1 | RPW1 | Prev> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
102 | I1 | RPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
102 | I2 | RPW1 | Prev> starts | UINT32 | R | 0...4294967295
102 | I3 | RPW1 | Prev> trips | UINT32 | R | 0...4294967295
102 | I4 | RPW1 | Prev> blocks | UINT32 | R | 0...4294967295
102 | S2 | RPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
102 | S3 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S4 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S5 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S6 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S7 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S8 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S9 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S10 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S11 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S12 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S13 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S14 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S15 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S16 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S17 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S18 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | O1 | RPW1 | Prev> START | SIGNAL_OUT | RW | 0...4294967295
102 | O2 | RPW1 | Prev> TRIP | SIGNAL_OUT | RW | 0...4294967295
102 | O3 | RPW1 | Prev> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
102 | I5 | RPW1 | Newest Register | UINT32 | R | 0...12
102 | I6 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I7 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I8 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I9 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I10 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I11 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I12 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I13 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I14 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I15 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I16 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I17 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | S19 | RPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
110 | S1 | SEF1 | U03rd< [64S] mode | UINT32 | RW | 0=Disabled; 1=Activated
110 | V1 | SEF1 | U03rd< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
110 | I1 | SEF1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
110 | I2 | SEF1 | Measured U0 3rd harm (%) | FLOAT | R | 0...1250
110 | I3 | SEF1 | Measured U0 3rd harm (Pri) | FLOAT | R | 0...1250
110 | I4 | SEF1 | U03rd< starts | UINT32 | R | 0...4294967295
110 | I5 | SEF1 | U03rd< trips | UINT32 | R | 0...4294967295
110 | I6 | SEF1 | U03rd< blocks | UINT32 | R | 0...4294967295
110 | S2 | SEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
110 | S3 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S4 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S5 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S6 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S7 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S8 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S9 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S10 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S11 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S12 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S13 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S14 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S15 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S16 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S17 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S18 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S19 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S20 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S21 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S22 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S23 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S24 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S25 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S26 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | O1 | SEF1 | U03rd< START | SIGNAL_OUT | RW | 0...4294967295
110 | O2 | SEF1 | U03rd< TRIP | SIGNAL_OUT | RW | 0...4294967295
110 | O3 | SEF1 | U03rd< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
110 | I7 | SEF1 | Newest Register | UINT32 | R | 0...12
110 | I8 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I9 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I10 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I11 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I12 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I13 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I14 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I15 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I16 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I17 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I18 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I19 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I20 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I21 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I22 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I23 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I24 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I25 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I26 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I27 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I28 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I29 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I30 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I31 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | S27 | SEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
109 | S1 | UEX1 | Q< [40] mode | UINT32 | RW | 0=Disabled; 1=Activated
109 | V1 | UEX1 | Q< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
109 | I1 | UEX1 | Qmeas/Qset at the moment | FLOAT | R | -1250...1250
109 | I2 | UEX1 | Q< starts | UINT32 | R | 0...4294967295
109 | I3 | UEX1 | Q< trips | UINT32 | R | 0...4294967295
109 | I4 | UEX1 | Q< blocks | UINT32 | R | 0...4294967295
109 | S2 | UEX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
109 | S3 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S4 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S5 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S6 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S7 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S8 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S9 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S10 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S11 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S12 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S13 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S14 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S15 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S16 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S17 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S18 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S19 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S20 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S21 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S22 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S23 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S24 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S25 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S26 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S27 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S28 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S29 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S30 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S31 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S32 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S33 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S34 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S35 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S36 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S37 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S38 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S39 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S40 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S41 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S42 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S43 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S44 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S45 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S46 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S47 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S48 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S49 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S50 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | O1 | UEX1 | Q< START | SIGNAL_OUT | RW | 0...4294967295
109 | O2 | UEX1 | Q< TRIP | SIGNAL_OUT | RW | 0...4294967295
109 | O3 | UEX1 | Q< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
109 | I5 | UEX1 | Newest Register | UINT32 | R | 0...12
109 | I6 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I7 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I8 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I9 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I10 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I11 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I12 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I13 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I14 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I15 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I16 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I17 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I18 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I19 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I20 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I21 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I22 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I23 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I24 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I25 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I26 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I27 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I28 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I29 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | S51 | UEX1 | EventMaskLo | UINT32 | RW | 0...4294967295
111 | S1 | UIM1 | Z< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
111 | V1 | UIM1 | Z< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
111 | I1 | UIM1 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
111 | I2 | UIM1 | Z< starts | UINT32 | R | 0...4294967295
111 | I3 | UIM1 | Z< trips | UINT32 | R | 0...4294967295
111 | I4 | UIM1 | Z< blocks | UINT32 | R | 0...4294967295
111 | S2 | UIM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
111 | S3 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S4 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S5 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S6 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S7 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S8 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S9 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S10 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S11 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S12 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S13 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S14 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S15 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S16 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S17 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S18 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | O1 | UIM1 | Z< START | SIGNAL_OUT | RW | 0...4294967295
111 | O2 | UIM1 | Z< TRIP | SIGNAL_OUT | RW | 0...4294967295
111 | O3 | UIM1 | Z< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
111 | I5 | UIM1 | Newest Register | UINT32 | R | 0...12
111 | I6 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I7 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I8 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I9 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I10 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I11 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I12 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I13 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I14 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I15 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I16 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I17 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I18 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I19 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I20 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I21 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I22 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I23 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I24 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I25 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I26 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I27 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I28 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I29 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I30 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I31 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I32 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I33 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I34 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I35 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I36 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I37 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I38 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I39 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I40 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I41 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | S19 | UIM1 | EventMaskLo | UINT32 | RW | 0...4294967295
149 | S1 | UIM2 | Z<< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
149 | V1 | UIM2 | Z<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
149 | I1 | UIM2 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
149 | I2 | UIM2 | Z<< starts | UINT32 | R | 0...4294967295
149 | I3 | UIM2 | Z<< trips | UINT32 | R | 0...4294967295
149 | I4 | UIM2 | Z<< blocks | UINT32 | R | 0...4294967295
149 | S2 | UIM2 | Clear statistics | UINT32 | W | 0=-;1=Clear
149 | S3 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S4 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S5 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S6 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S7 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S8 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S9 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S10 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S11 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S12 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S13 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S14 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S15 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S16 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S17 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S18 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | O1 | UIM2 | Z<< START | SIGNAL_OUT | RW | 0...4294967295
149 | O2 | UIM2 | Z<< TRIP | SIGNAL_OUT | RW | 0...4294967295
149 | O3 | UIM2 | Z<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
149 | I5 | UIM2 | Newest Register | UINT32 | R | 0...12
149 | I6 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I7 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I8 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I9 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I10 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I11 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I12 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I13 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I14 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I15 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I16 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I17 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I18 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I19 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I20 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I21 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I22 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I23 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I24 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I25 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I26 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I27 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I28 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I29 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I30 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I31 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I32 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I33 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I34 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I35 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I36 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I37 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I38 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I39 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I40 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I41 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | S19 | UIM2 | EventMaskLo | UINT32 | RW | 0...4294967295
112 | S1 | VOC1 | Iv> [51V] mode | UINT32 | RW | 0=Disabled; 1=Activated
112 | V1 | VOC1 | Iv> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
112 | I1 | VOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
112 | I2 | VOC1 | Iv> starts | UINT32 | R | 0...4294967295
112 | I3 | VOC1 | Iv> trips | UINT32 | R | 0...4294967295
112 | I4 | VOC1 | Iv> blocks | UINT32 | R | 0...4294967295
112 | S2 | VOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
112 | S3 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S4 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S5 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S6 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S7 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S8 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S9 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S10 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S11 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S12 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S13 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S14 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S15 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S16 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S17 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S18 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S19 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S20 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S21 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S22 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S23 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S24 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S25 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S26 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S27 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S28 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S29 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S30 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S31 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S32 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S33 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S34 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S35 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S36 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S37 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S38 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S39 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S40 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S41 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S42 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | O1 | VOC1 | Iv> START | SIGNAL_OUT | RW | 0...4294967295
112 | O2 | VOC1 | Iv> TRIP | SIGNAL_OUT | RW | 0...4294967295
112 | O3 | VOC1 | Iv> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
112 | I5 | VOC1 | Newest Register | UINT32 | R | 0...12
112 | I6 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I7 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I8 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I9 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I10 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I11 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I12 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I13 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I14 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I15 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I16 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I17 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I18 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I19 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I20 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I21 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I22 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I23 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I24 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I25 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I26 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I27 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I28 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I29 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I30 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I31 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I32 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I33 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I34 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I35 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I36 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I37 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I38 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I39 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I40 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I41 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I42 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I43 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I44 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I45 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I46 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I47 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I48 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I49 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I50 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I51 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I52 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I53 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I54 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I55 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I56 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I57 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I58 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I59 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I60 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I61 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I62 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I63 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I64 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I65 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | S43 | VOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
128 | S1 | VHZ1 | V/Hz > [24] mode | UINT32 | RW | 0=Disabled;1=Activated
128 | S2 | VHZ1 | V/Hz(1) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V1 | VHZ1 | V/Hz(1) > condition | UINT32 | R | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
128 | I1 | VHZ1 | V/Hz(1) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | S3 | VHZ1 | V/Hz(2) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V2 | VHZ1 | V/Hz(2) > condition | UINT32 | R | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
128 | I2 | VHZ1 | V/Hz(2) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | I3 | VHZ1 | U/f at the moment | FLOAT | R | -100...100
128 | I4 | VHZ1 | U/f atm to nominal U/f ratio | FLOAT | R | -100...100
128 | I5 | VHZ1 | V/Hz(1) > Starts | UINT32 | R | 0...4294967295
128 | I6 | VHZ1 | V/Hz(1) > Alarms | UINT32 | R | 0...4294967295
128 | I7 | VHZ1 | V/Hz(1) > Trips | UINT32 | R | 0...4294967295
128 | I8 | VHZ1 | V/Hz(1) > Blocks | UINT32 | R | 0...4294967295
128 | I9 | VHZ1 | V/Hz(2) > Starts | UINT32 | R | 0...4294967295
128 | I10 | VHZ1 | V/Hz(2) > Alarms | UINT32 | R | 0...4294967295
128 | I11 | VHZ1 | V/Hz(2) > Trips | UINT32 | R | 0...4294967295
128 | I12 | VHZ1 | V/Hz(2) > Blocks | UINT32 | R | 0...4294967295
128 | S4 | VHZ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
128 | S5 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S6 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S7 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S8 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S9 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S10 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S11 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S12 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S13 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S14 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S15 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S16 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S17 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S18 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S19 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S20 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S21 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S22 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S23 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S24 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S25 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S26 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S27 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S28 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S29 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S30 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S31 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S32 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S33 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S34 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S35 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S36 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S37 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S38 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S39 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S40 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S41 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S42 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S43 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S44 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S45 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S46 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S47 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S48 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S49 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S50 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S51 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S52 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | O1 | VHZ1 | V/Hz(1) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O2 | VHZ1 | V/Hz(1) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O3 | VHZ1 | V/Hz(1) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O4 | VHZ1 | V/Hz(1) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | O5 | VHZ1 | V/Hz(2) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O6 | VHZ1 | V/Hz(2) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O7 | VHZ1 | V/Hz(2) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O8 | VHZ1 | V/Hz(2) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | I13 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I14 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I15 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I16 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I17 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I18 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I19 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I20 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I21 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I22 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I23 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I24 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I25 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I26 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I27 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I28 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I29 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I30 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I31 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I32 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I33 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I34 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I35 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I36 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I37 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I38 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I39 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I40 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I41 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I42 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I43 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I44 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I45 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I46 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I47 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I48 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I49 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I50 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I51 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I52 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I53 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I54 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I55 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I56 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I57 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I58 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I59 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I60 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I61 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I62 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I63 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I64 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I65 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I66 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I67 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I68 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I69 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I70 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I71 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I72 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I73 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I74 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I75 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I76 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I77 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I78 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I79 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I80 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I81 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I82 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I83 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I84 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I85 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I86 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I87 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I88 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I89 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I90 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I91 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I92 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I93 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I94 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I95 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I96 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I97 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I98 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I99 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I100 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I101 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I102 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I103 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I104 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I105 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I106 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I107 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I108 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I109 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I110 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | S53 | VHZ1 | EventMaskLo | UINT32 | RW | 0...4294967295
129 | S1 | UPF1 | PF< [55] mode | UINT32 | RW | 0=Disabled; 1=Activated
129 | V1 | UPF1 | PF< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
129 | S2 | UPF1 | Available modes | UINT32 | RW | 0=Trip;1=Trip and Alarm
129 | I1 | UPF1 | PFmeas/PFalarm at the moment | FLOAT | R | 0...1250
129 | I2 | UPF1 | PFmeas/PFtrip at the moment | FLOAT | R | 0...1250
129 | I3 | UPF1 | PF< Alarm Starts | UINT32 | R | 0...4294967295
129 | I4 | UPF1 | PF< Alarms | UINT32 | R | 0...4294967295
129 | I5 | UPF1 | PF< Starts | UINT32 | R | 0...4294967295
129 | I6 | UPF1 | PF< Trips | UINT32 | R | 0...4294967295
129 | I7 | UPF1 | PF< Blocks | UINT32 | R | 0...4294967295
129 | S3 | UPF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
129 | S4 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S5 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S6 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S7 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S8 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S9 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S10 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S11 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S12 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S13 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S14 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S15 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S16 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S17 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S18 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S19 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S20 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S21 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S22 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S23 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S24 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S25 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S26 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S27 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S28 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S29 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S30 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S31 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S32 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S33 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S34 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S35 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | O1 | UPF1 | PF< START | SIGNAL_OUT | RW | 0...4294967295
129 | O2 | UPF1 | PF< TRIP | SIGNAL_OUT | RW | 0...4294967295
129 | O3 | UPF1 | PF< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
129 | I8 | UPF1 | Newest Register | UINT32 | R | 0...12
129 | I9 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I10 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I11 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I12 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I13 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I14 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I15 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I16 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I17 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I18 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I19 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I20 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | S36 | UPF1 | EventMaskLo | UINT32 | RW | 0...4294967295
141 | I1 | RTDIN | S1 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I2 | RTDIN | S1 Resistance | FLOAT | R | 0...4000.000
141 | I3 | RTDIN | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I4 | RTDIN | S1 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I5 | RTDIN | S2 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I6 | RTDIN | S2 Resistance | FLOAT | R | 0...4000.000
141 | I7 | RTDIN | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I8 | RTDIN | S2 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I9 | RTDIN | S3 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I10 | RTDIN | S3 Resistance | FLOAT | R | 0...4000.000
141 | I11 | RTDIN | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I12 | RTDIN | S3 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I13 | RTDIN | S4 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I14 | RTDIN | S4 Resistance | FLOAT | R | 0...4000.000
141 | I15 | RTDIN | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I16 | RTDIN | S4 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I17 | RTDIN | S5 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I18 | RTDIN | S5 Resistance | FLOAT | R | 0...4000.000
141 | I19 | RTDIN | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I20 | RTDIN | S5 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I21 | RTDIN | S6 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I22 | RTDIN | S6 Resistance | FLOAT | R | 0...4000.000
141 | I23 | RTDIN | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I24 | RTDIN | S6 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I25 | RTDIN | S7 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I26 | RTDIN | S7 Resistance | FLOAT | R | 0...4000.000
141 | I27 | RTDIN | S7 Measurement mA | FLOAT | R | 0.000...20.000
141 | I28 | RTDIN | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I29 | RTDIN | S7 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I30 | RTDIN | S8 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I31 | RTDIN | S8 Resistance | FLOAT | R | 0...4000.000
141 | I32 | RTDIN | S8 Measurement mA | FLOAT | R | 0.000...20.000
141 | I33 | RTDIN | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I34 | RTDIN | S8 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I35 | RTDIN | S9 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I36 | RTDIN | S9 Resistance | FLOAT | R | 0...4000.000
141 | I37 | RTDIN | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I38 | RTDIN | S9 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I39 | RTDIN | S10 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I40 | RTDIN | S10 Resistance | FLOAT | R | 0...4000.000
141 | I41 | RTDIN | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I42 | RTDIN | S10 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I43 | RTDIN | S11 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I44 | RTDIN | S11 Resistance | FLOAT | R | 0...4000.000
141 | I45 | RTDIN | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I46 | RTDIN | S11 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I47 | RTDIN | S12 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I48 | RTDIN | S12 Resistance | FLOAT | R | 0...4000.000
141 | I49 | RTDIN | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I50 | RTDIN | S12 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I51 | RTDIN | S13 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I52 | RTDIN | S13 Resistance | FLOAT | R | 0...4000.000
141 | I53 | RTDIN | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I54 | RTDIN | S13 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I55 | RTDIN | S14 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I56 | RTDIN | S14 Resistance | FLOAT | R | 0...4000.000
141 | I57 | RTDIN | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I58 | RTDIN | S14 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I59 | RTDIN | S15 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I60 | RTDIN | S15 Resistance | FLOAT | R | 0...4000.000
141 | I61 | RTDIN | S15 Measurement mA | FLOAT | R | 0.000...20.000
141 | I62 | RTDIN | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I63 | RTDIN | S15 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I64 | RTDIN | S16 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I65 | RTDIN | S16 Resistance | FLOAT | R | 0...4000.000
141 | I66 | RTDIN | S16 Measurement mA | FLOAT | R | 0.000...20.000
141 | I67 | RTDIN | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I68 | RTDIN | S16 Filtered measurement | FLOAT | R | -200.0...2000.0
69 | S1 | RTD1 | RTD mode | UINT32 | RW | 0=Disabled;1=Activated
69 | S2 | RTD1 | S1 enable | UINT32 | RW | 0=No;1=Yes
69 | I1 | RTD1 | S1 Measurement (Protection) | FLOAT | R | -200...2000
69 | V1 | RTD1 | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S3 | RTD1 | S1 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I2 | RTD1 | S1 Alarm1 act | UINT32 | R | 0...4294967295
69 | S4 | RTD1 | S1 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S5 | RTD1 | S1 Alarm1 | FLOAT | RW | -200...2000
69 | S6 | RTD1 | S1 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I3 | RTD1 | S1 Alarm2 act | UINT32 | R | 0...4294967295
69 | S7 | RTD1 | S1 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S8 | RTD1 | S1 Alarm2 | FLOAT | RW | -200...2000
69 | I4 | RTD1 | S2 Measurement (Protection) | FLOAT | R | -200...2000
69 | V2 | RTD1 | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S9 | RTD1 | S2 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I5 | RTD1 | S2 Alarm1 act | UINT32 | R | 0...4294967295
69 | S10 | RTD1 | S2 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S11 | RTD1 | S2 Alarm1 | FLOAT | RW | -200...2000
69 | S12 | RTD1 | S2 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I6 | RTD1 | S2 Alarm2 act | UINT32 | R | 0...4294967295
69 | S13 | RTD1 | S2 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S14 | RTD1 | S2 Alarm2 | FLOAT | RW | -200...2000
69 | I7 | RTD1 | S3 Measurement (Protection) | FLOAT | R | -200...2000
69 | V3 | RTD1 | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S15 | RTD1 | S3 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I8 | RTD1 | S3 Alarm1 act | UINT32 | R | 0...4294967295
69 | S16 | RTD1 | S3 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S17 | RTD1 | S3 Alarm1 | FLOAT | RW | -200...2000
69 | S18 | RTD1 | S3 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I9 | RTD1 | S3 Alarm2 act | UINT32 | R | 0...4294967295
69 | S19 | RTD1 | S3 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S20 | RTD1 | S3 Alarm2 | FLOAT | RW | -200...2000
69 | I10 | RTD1 | S4 Measurement (Protection) | FLOAT | R | -200...2000
69 | V4 | RTD1 | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S21 | RTD1 | S4 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I11 | RTD1 | S4 Alarm1 act | UINT32 | R | 0...4294967295
69 | S22 | RTD1 | S4 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S23 | RTD1 | S4 Alarm1 | FLOAT | RW | -200...2000
69 | S24 | RTD1 | S4 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I12 | RTD1 | S4 Alarm2 act | UINT32 | R | 0...4294967295
69 | S25 | RTD1 | S4 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S26 | RTD1 | S4 Alarm2 | FLOAT | RW | -200...2000
69 | I13 | RTD1 | S5 Measurement (Protection) | FLOAT | R | -200...2000
69 | V5 | RTD1 | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S27 | RTD1 | S5 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I14 | RTD1 | S5 Alarm1 act | UINT32 | R | 0...4294967295
69 | S28 | RTD1 | S5 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S29 | RTD1 | S5 Alarm1 | FLOAT | RW | -200...2000
69 | S30 | RTD1 | S5 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I15 | RTD1 | S5 Alarm2 act | UINT32 | R | 0...4294967295
69 | S31 | RTD1 | S5 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S32 | RTD1 | S5 Alarm2 | FLOAT | RW | -200...2000
69 | I16 | RTD1 | S6 Measurement (Protection) | FLOAT | R | -200...2000
69 | V6 | RTD1 | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S33 | RTD1 | S6 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I17 | RTD1 | S6 Alarm1 act | UINT32 | R | 0...4294967295
69 | S34 | RTD1 | S6 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S35 | RTD1 | S6 Alarm1 | FLOAT | RW | -200...2000
69 | S36 | RTD1 | S6 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I18 | RTD1 | S6 Alarm2 act | UINT32 | R | 0...4294967295
69 | S37 | RTD1 | S6 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S38 | RTD1 | S6 Alarm2 | FLOAT | RW | -200...2000
69 | I19 | RTD1 | S7 Measurement (Protection) | FLOAT | R | -200...2000
69 | V7 | RTD1 | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S39 | RTD1 | S7 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I20 | RTD1 | S7 Alarm1 act | UINT32 | R | 0...4294967295
69 | S40 | RTD1 | S7 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S41 | RTD1 | S7 Alarm1 | FLOAT | RW | -200...2000
69 | S42 | RTD1 | S7 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I21 | RTD1 | S7 Alarm2 act | UINT32 | R | 0...4294967295
69 | S43 | RTD1 | S7 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S44 | RTD1 | S7 Alarm2 | FLOAT | RW | -200...2000
69 | I22 | RTD1 | S8 Measurement (Protection) | FLOAT | R | -200...2000
69 | V8 | RTD1 | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S45 | RTD1 | S8 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I23 | RTD1 | S8 Alarm1 act | UINT32 | R | 0...4294967295
69 | S46 | RTD1 | S8 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S47 | RTD1 | S8 Alarm1 | FLOAT | RW | -200...2000
69 | S48 | RTD1 | S8 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I24 | RTD1 | S8 Alarm2 act | UINT32 | R | 0...4294967295
69 | S49 | RTD1 | S8 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S50 | RTD1 | S8 Alarm2 | FLOAT | RW | -200...2000
69 | I25 | RTD1 | S9 Measurement (Protection) | FLOAT | R | -200...2000
69 | V9 | RTD1 | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S51 | RTD1 | S9 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I26 | RTD1 | S9 Alarm1 act | UINT32 | R | 0...4294967295
69 | S52 | RTD1 | S9 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S53 | RTD1 | S9 Alarm1 | FLOAT | RW | -200...2000
69 | S54 | RTD1 | S9 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I27 | RTD1 | S9 Alarm2 act | UINT32 | R | 0...4294967295
69 | S55 | RTD1 | S9 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S56 | RTD1 | S9 Alarm2 | FLOAT | RW | -200...2000
69 | I28 | RTD1 | S10 Measurement (Protection) | FLOAT | R | -200...2000
69 | V10 | RTD1 | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S57 | RTD1 | S10 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I29 | RTD1 | S10 Alarm1 act | UINT32 | R | 0...4294967295
69 | S58 | RTD1 | S10 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S59 | RTD1 | S10 Alarm1 | FLOAT | RW | -200...2000
69 | S60 | RTD1 | S10 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I30 | RTD1 | S10 Alarm2 act | UINT32 | R | 0...4294967295
69 | S61 | RTD1 | S10 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S62 | RTD1 | S10 Alarm2 | FLOAT | RW | -200...2000
69 | I31 | RTD1 | S11 Measurement (Protection) | FLOAT | R | -200...2000
69 | V11 | RTD1 | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S63 | RTD1 | S11 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I32 | RTD1 | S11 Alarm1 act | UINT32 | R | 0...4294967295
69 | S64 | RTD1 | S11 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S65 | RTD1 | S11 Alarm1 | FLOAT | RW | -200...2000
69 | S66 | RTD1 | S11 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I33 | RTD1 | S11 Alarm2 act | UINT32 | R | 0...4294967295
69 | S67 | RTD1 | S11 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S68 | RTD1 | S11 Alarm2 | FLOAT | RW | -200...2000
69 | I34 | RTD1 | S12 Measurement (Protection) | FLOAT | R | -200...2000
69 | V12 | RTD1 | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S69 | RTD1 | S12 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I35 | RTD1 | S12 Alarm1 act | UINT32 | R | 0...4294967295
69 | S70 | RTD1 | S12 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S71 | RTD1 | S12 Alarm1 | FLOAT | RW | -200...2000
69 | S72 | RTD1 | S12 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I36 | RTD1 | S12 Alarm2 act | UINT32 | R | 0...4294967295
69 | S73 | RTD1 | S12 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S74 | RTD1 | S12 Alarm2 | FLOAT | RW | -200...2000
69 | I37 | RTD1 | S13 Measurement (Protection) | FLOAT | R | -200...2000
69 | V13 | RTD1 | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S75 | RTD1 | S13 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I38 | RTD1 | S13 Alarm1 act | UINT32 | R | 0...4294967295
69 | S76 | RTD1 | S13 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S77 | RTD1 | S13 Alarm1 | FLOAT | RW | -200...2000
69 | S78 | RTD1 | S13 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I39 | RTD1 | S13 Alarm2 act | UINT32 | R | 0...4294967295
69 | S79 | RTD1 | S13 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S80 | RTD1 | S13 Alarm2 | FLOAT | RW | -200...2000
69 | I40 | RTD1 | S14 Measurement (Protection) | FLOAT | R | -200...2000
69 | V14 | RTD1 | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S81 | RTD1 | S14 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I41 | RTD1 | S14 Alarm1 act | UINT32 | R | 0...4294967295
69 | S82 | RTD1 | S14 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S83 | RTD1 | S14 Alarm1 | FLOAT | RW | -200...2000
69 | S84 | RTD1 | S14 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I42 | RTD1 | S14 Alarm2 act | UINT32 | R | 0...4294967295
69 | S85 | RTD1 | S14 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S86 | RTD1 | S14 Alarm2 | FLOAT | RW | -200...2000
69 | I43 | RTD1 | S15 Measurement (Protection) | FLOAT | R | -200...2000
69 | V15 | RTD1 | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S87 | RTD1 | S15 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I44 | RTD1 | S15 Alarm1 act | UINT32 | R | 0...4294967295
69 | S88 | RTD1 | S15 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S89 | RTD1 | S15 Alarm1 | FLOAT | RW | -200...2000
69 | S90 | RTD1 | S15 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I45 | RTD1 | S15 Alarm2 act | UINT32 | R | 0...4294967295
69 | S91 | RTD1 | S15 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S92 | RTD1 | S15 Alarm2 | FLOAT | RW | -200...2000
69 | I46 | RTD1 | S16 Measurement (Protection) | FLOAT | R | -200...2000
69 | V16 | RTD1 | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S93 | RTD1 | S16 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I47 | RTD1 | S16 Alarm1 act | UINT32 | R | 0...4294967295
69 | S94 | RTD1 | S16 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S95 | RTD1 | S16 Alarm1 | FLOAT | RW | -200...2000
69 | S96 | RTD1 | S16 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I48 | RTD1 | S16 Alarm2 act | UINT32 | R | 0...4294967295
69 | S97 | RTD1 | S16 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S98 | RTD1 | S16 Alarm2 | FLOAT | RW | -200...2000
69 | O1 | RTD1 | S1 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O2 | RTD1 | S1 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O3 | RTD1 | S1 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O4 | RTD1 | S2 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O5 | RTD1 | S2 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O6 | RTD1 | S2 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O7 | RTD1 | S3 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O8 | RTD1 | S3 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O9 | RTD1 | S3 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O10 | RTD1 | S4 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O11 | RTD1 | S4 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O12 | RTD1 | S4 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O13 | RTD1 | S5 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O14 | RTD1 | S5 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O15 | RTD1 | S5 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O16 | RTD1 | S6 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O17 | RTD1 | S6 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O18 | RTD1 | S6 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O19 | RTD1 | S7 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O20 | RTD1 | S7 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O21 | RTD1 | S7 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O22 | RTD1 | S8 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O23 | RTD1 | S8 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O24 | RTD1 | S8 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O25 | RTD1 | S9 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O26 | RTD1 | S9 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O27 | RTD1 | S9 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O28 | RTD1 | S10 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O29 | RTD1 | S10 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O30 | RTD1 | S10 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O31 | RTD1 | S11 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O32 | RTD1 | S11 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O33 | RTD1 | S11 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O34 | RTD1 | S12 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O35 | RTD1 | S12 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O36 | RTD1 | S12 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O37 | RTD1 | S13 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O38 | RTD1 | S13 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O39 | RTD1 | S13 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O40 | RTD1 | S14 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O41 | RTD1 | S14 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O42 | RTD1 | S14 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O43 | RTD1 | S15 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O44 | RTD1 | S15 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O45 | RTD1 | S15 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O46 | RTD1 | S16 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O47 | RTD1 | S16 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O48 | RTD1 | S16 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | S99 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
69 | S100 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
70 | S1 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
70 | S2 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
74 | S1 | ARC1 | I/I0 Arc> [50ARC/50NARC] mode | UINT32 | RW | 0=Disabled;1=Activated
74 | S2 | ARC1 | I/I0 Arc> Self supervision test pulse | UINT32 | RW | 0=Disabled;1=On
74 | V1 | ARC1 | I/I0 Arc> condition | UINT32 | R | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
74 | V2 | ARC1 | Sensor status | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I1 | ARC1 | I/I0 Arc> Zone1 Trips | UINT32 | R | 0...4294967295
74 | I2 | ARC1 | I/I0 Arc> Zone1 Blocks | UINT32 | R | 0...4294967295
74 | I3 | ARC1 | I/I0 Arc> Zone2 Trips | UINT32 | R | 0...4294967295
74 | I4 | ARC1 | I/I0 Arc> Zone2 Blocks | UINT32 | R | 0...4294967295
74 | I5 | ARC1 | I/I0 Arc> Zone3 Trips | UINT32 | R | 0...4294967295
74 | I6 | ARC1 | I/I0 Arc> Zone3 Blocks | UINT32 | R | 0...4294967295
74 | I7 | ARC1 | I/I0 Arc> Zone4 Trips | UINT32 | R | 0...4294967295
74 | I8 | ARC1 | I/I0 Arc> Zone4 Blocks | UINT32 | R | 0...4294967295
74 | S3 | ARC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
74 | I9 | ARC1 | Channel 1 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I10 | ARC1 | Channel 1 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I11 | ARC1 | Channel 2 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I12 | ARC1 | Channel 2 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I13 | ARC1 | Channel 3 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I14 | ARC1 | Channel 3 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I15 | ARC1 | Channel 4 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I16 | ARC1 | Channel 4 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | S4 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S5 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S6 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S7 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S8 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S9 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S10 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S11 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S12 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S13 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S14 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S15 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S16 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S17 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S18 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S19 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S20 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S21 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S22 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S23 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S24 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S25 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S26 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S27 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S28 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S29 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S30 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S31 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S32 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S33 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S34 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S35 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S36 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S37 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S38 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S39 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S40 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S41 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S42 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S43 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S44 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S45 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S46 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S47 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S48 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S49 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S50 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S51 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S52 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S53 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S54 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S55 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S56 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S57 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S58 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S59 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S60 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S61 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S62 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S63 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S64 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S65 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S66 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S67 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S68 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S69 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S70 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S71 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S72 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S73 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S74 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S75 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S76 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S77 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S78 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S79 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S80 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S81 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S82 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S83 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S84 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S85 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S86 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S87 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S88 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S89 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S90 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S91 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S92 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S93 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S94 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S95 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S96 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S97 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S98 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S99 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S100 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S101 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S102 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S103 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S104 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S105 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S106 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S107 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S108 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S109 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S110 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S111 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S112 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S113 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S114 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S115 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S116 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S117 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S118 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S119 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S120 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S121 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S122 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S123 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S124 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S125 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S126 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S127 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S128 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S129 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S130 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S131 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S132 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S133 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S134 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S135 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S136 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S137 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S138 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S139 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S140 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S141 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S142 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S143 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S144 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S145 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S146 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S147 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S148 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S149 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S150 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S151 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S152 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S153 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S154 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S155 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S156 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S157 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S158 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S159 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S160 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S161 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S162 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S163 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S164 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S165 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S166 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S167 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S168 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S169 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S170 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S171 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S172 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S173 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S174 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S175 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S176 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S177 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S178 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S179 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S180 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S181 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S182 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S183 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S184 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S185 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S186 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S187 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S188 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S189 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S190 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S191 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S192 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S193 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S194 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S195 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S196 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S197 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S198 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S199 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S200 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S201 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S202 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S203 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S204 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S205 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S206 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S207 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S208 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S209 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S210 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S211 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S212 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S213 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S214 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S215 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S216 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S217 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S218 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S219 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S220 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S221 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S222 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S223 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S224 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S225 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S226 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S227 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S228 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S229 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S230 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S231 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S232 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S233 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S234 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S235 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S236 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S237 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S238 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S239 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S240 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S241 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S242 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S243 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S244 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S245 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S246 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S247 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S248 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S249 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S250 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S251 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S252 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S253 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S254 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S255 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S256 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S257 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S258 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S259 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S260 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S261 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S262 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S263 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S264 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S265 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S266 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S267 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S268 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S269 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S270 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S271 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S272 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S273 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S274 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S275 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S276 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S277 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S278 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S279 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S280 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S281 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S282 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S283 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S284 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S285 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S286 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S287 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S288 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S289 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S290 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S291 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S292 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S293 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S294 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S295 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S296 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S297 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S298 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S299 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S300 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S301 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S302 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S303 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S304 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S305 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S306 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S307 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S308 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S309 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S310 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S311 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S312 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S313 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S314 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S315 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S316 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S317 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S318 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S319 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S320 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S321 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S322 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S323 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S324 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S325 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S326 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S327 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S328 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S329 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S330 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S331 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S332 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S333 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S334 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S335 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S336 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S337 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S338 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S339 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S340 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S341 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S342 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S343 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S344 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S345 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S346 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S347 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S348 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S349 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S350 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S351 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S352 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S353 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S354 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S355 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S356 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S357 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S358 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S359 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S360 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S361 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S362 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S363 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S364 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S365 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S366 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S367 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S368 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S369 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S370 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S371 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S372 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S373 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S374 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S375 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S376 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S377 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S378 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S379 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S380 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S381 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S382 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S383 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S384 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S385 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S386 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S387 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S388 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S389 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S390 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S391 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S392 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S393 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S394 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S395 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S396 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S397 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S398 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S399 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S400 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S401 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S402 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S403 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S404 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S405 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S406 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S407 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S408 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S409 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S410 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S411 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | O1 | ARC1 | I/I0 Arc> Ph.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O2 | ARC1 | I/I0 Arc> Res.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O3 | ARC1 | I/I0 Arc> Zone1.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O4 | ARC1 | I/I0 Arc> Zone2.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O5 | ARC1 | I/I0 Arc> Zone3.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O6 | ARC1 | I/I0 Arc> Zone4.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O7 | ARC1 | I/I0 Arc> Ph.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O8 | ARC1 | I/I0 Arc> Res.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O9 | ARC1 | I/I0 Arc> Ph.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O10 | ARC1 | I/I0 Arc> Res.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O11 | ARC1 | I/I0 Arc> Zone1 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O12 | ARC1 | I/I0 Arc> Zone1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O13 | ARC1 | I/I0 Arc> Zone2 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O14 | ARC1 | I/I0 Arc> Zone2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O15 | ARC1 | I/I0 Arc> Zone3 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O16 | ARC1 | I/I0 Arc> Zone3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O17 | ARC1 | I/I0 Arc> Zone4 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O18 | ARC1 | I/I0 Arc> Zone4 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O19 | ARC1 | I/I0 Arc> S1 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O20 | ARC1 | I/I0 Arc> S2 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O21 | ARC1 | I/I0 Arc> S3 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O22 | ARC1 | I/I0 Arc> S4 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O23 | ARC1 | I/I0 Arc> IO unit fault | SIGNAL_OUT | RW | 0...4294967295
74 | I17 | ARC1 | Newest Register | UINT32 | R | 0...12
74 | I18 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I19 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I20 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I21 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I22 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I23 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I24 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I25 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I26 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I27 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I28 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I29 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I30 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I31 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I32 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I33 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I34 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I35 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I36 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I37 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I38 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I39 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I40 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I41 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I42 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I43 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I44 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I45 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I46 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I47 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I48 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I49 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I50 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I51 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I52 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I53 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I54 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I55 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I56 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I57 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I58 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I59 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I60 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I61 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I62 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I63 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I64 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I65 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I66 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I67 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I68 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I69 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I70 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I71 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I72 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I73 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I74 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I75 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I76 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I77 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | S412 | ARC1 | EventMaskLo | UINT32 | RW | 0...4294967295
74 | S413 | ARC1 | EventMaskHi | UINT32 | RW | 0...4294967295
52 | S1 | CTS1 | CTS1 mode | UINT32 | RW | 0=Disabled;1=Activated
52 | V1 | CTS1 | CTS1 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
52 | I1 | CTS1 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
52 | I2 | CTS1 | Natural unbalance ang | FLOAT | R | -360...360
52 | I3 | CTS1 | Measured current difference Isum, I0 | FLOAT | R | 0...50
52 | I4 | CTS1 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
52 | I5 | CTS1 | CTS1 alarms | UINT32 | R | 0...4294967295
52 | I6 | CTS1 | CTS1 blocks | UINT32 | R | 0...4294967295
52 | S2 | CTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
52 | S3 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S4 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S5 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S6 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S7 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S8 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S9 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S10 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S11 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S12 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S13 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S14 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S15 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S16 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S17 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S18 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S19 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S20 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S21 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S22 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S23 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S24 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S25 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S26 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S27 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S28 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S29 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S30 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S31 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S32 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S33 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S34 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S35 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S36 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S37 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S38 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S39 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S40 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S41 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S42 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S43 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S44 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S45 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S46 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S47 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S48 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S49 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S50 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | O1 | CTS1 | CTS1 ALARM | SIGNAL_OUT | RW | 0...4294967295
52 | O2 | CTS1 | CTS1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
52 | I7 | CTS1 | Newest Register | UINT32 | R | 0...12
52 | I8 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I9 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I10 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I11 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I12 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I13 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I14 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I15 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I16 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I17 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I18 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I19 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I20 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I21 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I22 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I23 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I24 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I25 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I26 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I27 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I28 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I29 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I30 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I31 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I32 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I33 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I34 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I35 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I36 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I37 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I38 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I39 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I40 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I41 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I42 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I43 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I44 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I45 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I46 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I47 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I48 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I49 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I50 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I51 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I52 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I53 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I54 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I55 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I56 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I57 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I58 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I59 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I60 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I61 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I62 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I63 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I64 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I65 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I66 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I67 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I68 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I69 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I70 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I71 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I72 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I73 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I74 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I75 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I76 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I77 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I78 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I79 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | S51 | CTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
52 | S52 | CTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
54 | S1 | CTS2 | CTS2 mode | UINT32 | RW | 0=Disabled;1=Activated
54 | V1 | CTS2 | CTS2 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
54 | I1 | CTS2 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
54 | I2 | CTS2 | Natural unbalance ang | FLOAT | R | -360...360
54 | I3 | CTS2 | Measured current difference Isum, I0 | FLOAT | R | 0...50
54 | I4 | CTS2 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
54 | I5 | CTS2 | CTS2 alarms | UINT32 | R | 0...4294967295
54 | I6 | CTS2 | CTS2 blocks | UINT32 | R | 0...4294967295
54 | S2 | CTS2 | Clear statistics | UINT32 | W | 0=-;1=Clear
54 | S3 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S4 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S5 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S6 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S7 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S8 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S9 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S10 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S11 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S12 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S13 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S14 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S15 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S16 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S17 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S18 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S19 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S20 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S21 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S22 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S23 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S24 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S25 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S26 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S27 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S28 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S29 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S30 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S31 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S32 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S33 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S34 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S35 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S36 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S37 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S38 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S39 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S40 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S41 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S42 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S43 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S44 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S45 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S46 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S47 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S48 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S49 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S50 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | O1 | CTS2 | CTS2 ALARM | SIGNAL_OUT | RW | 0...4294967295
54 | O2 | CTS2 | CTS2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
54 | I7 | CTS2 | Newest Register | UINT32 | R | 0...12
54 | I8 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I9 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I10 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I11 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I12 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I13 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I14 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I15 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I16 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I17 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I18 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I19 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I20 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I21 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I22 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I23 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I24 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I25 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I26 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I27 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I28 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I29 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I30 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I31 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I32 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I33 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I34 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I35 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I36 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I37 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I38 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I39 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I40 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I41 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I42 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I43 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I44 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I45 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I46 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I47 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I48 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I49 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I50 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I51 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I52 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I53 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I54 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I55 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I56 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I57 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I58 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I59 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I60 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I61 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I62 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I63 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I64 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I65 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I66 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I67 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I68 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I69 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I70 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I71 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I72 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I73 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I74 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I75 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I76 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I77 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I78 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I79 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | S51 | CTS2 | EventMaskLo | UINT32 | RW | 0...4294967295
54 | S52 | CTS2 | EventMaskHi | UINT32 | RW | 0...4294967295
53 | S1 | VTS1 | VTS [60] mode | UINT32 | RW | 0=Disabled;1=Activated
53 | V1 | VTS1 | VTS condition | UINT32 | R | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
53 | V2 | VTS1 | Bus voltages | UINT32 | R | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
53 | I1 | VTS1 | VTS Starts | UINT32 | R | 0...4294967295
53 | I2 | VTS1 | Line fuse fails | UINT32 | R | 0...4294967295
53 | I3 | VTS1 | Bus fuse fails | UINT32 | R | 0...4294967295
53 | I4 | VTS1 | VTS Blocks | UINT32 | R | 0...4294967295
53 | S2 | VTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
53 | S3 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S4 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S5 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S6 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S7 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S8 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S9 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S10 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S11 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S12 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S13 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S14 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S15 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S16 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S17 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S18 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S19 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S20 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S21 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S22 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S23 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S24 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S25 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S26 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S27 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S28 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S29 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S30 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S31 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S32 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S33 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S34 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S35 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S36 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S37 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S38 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S39 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S40 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S41 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S42 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S43 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S44 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S45 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S46 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S47 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S48 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S49 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S50 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | O1 | VTS1 | VTS Start | SIGNAL_OUT | RW | 0...4294967295
53 | O2 | VTS1 | VTS Fail Alarm Bus | SIGNAL_OUT | RW | 0...4294967295
53 | O3 | VTS1 | VTS Fail Alarm Line | SIGNAL_OUT | RW | 0...4294967295
53 | O4 | VTS1 | VTS Blocked(time delay) | SIGNAL_OUT | RW | 0...4294967295
53 | I5 | VTS1 | Newest Register | UINT32 | R | 0...12
53 | I6 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I7 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I8 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I9 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I10 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I11 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I12 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I13 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I14 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I15 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I16 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I17 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I18 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I19 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I20 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I21 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I22 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I23 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I24 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I25 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I26 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I27 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I28 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I29 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I30 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I31 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I32 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I33 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I34 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I35 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I36 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I37 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I38 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I39 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I40 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I41 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I42 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I43 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I44 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I45 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I46 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I47 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I48 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I49 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I50 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I51 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I52 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I53 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I54 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I55 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I56 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I57 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I58 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I59 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I60 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I61 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I62 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I63 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I64 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I65 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | S51 | VTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
53 | S52 | VTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
43 | S1 | FLX1 | Fault locator mode | UINT32 | RW | 0=Disabled;1=Activated
43 | V1 | FLX1 | Fault locator condition | UINT32 | R | 0=Idle;1=Triggered;2=Calc ready
43 | I1 | FLX1 | Times Flocator triggered | UINT32 | R | 0...4294967295
43 | I2 | FLX1 | Last fault reactance | FLOAT | R | -1800...1800
43 | I3 | FLX1 | Last fault distance | FLOAT | R | -1800...1800
43 | V2 | FLX1 | Last fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I4 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I5 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I6 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | I7 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I8 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I9 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | V3 | FLX1 | Last fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | S2 | FLX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
43 | S3 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S4 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S5 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S6 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S7 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S8 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S9 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S10 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S11 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S12 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S13 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S14 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S15 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S16 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S17 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S18 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | I10 | FLX1 | Newest Register | UINT32 | R | 0...12
43 | I11 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I12 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I13 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I14 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I15 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I16 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I17 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I18 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I19 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I20 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I21 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I22 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I23 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I24 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I25 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I26 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I27 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I28 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I29 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I30 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I31 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I32 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I33 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I34 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I35 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I36 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I37 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I38 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I39 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I40 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I41 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I42 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I43 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I44 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I45 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I46 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I47 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I48 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I49 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I50 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I51 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I52 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I53 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I54 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I55 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I56 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I57 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I58 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I59 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I60 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I61 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I62 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I63 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I64 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I65 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I66 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I67 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I68 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I69 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I70 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I71 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I72 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I73 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I74 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I75 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I76 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I77 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I78 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I79 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I80 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I81 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I82 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I83 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I84 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I85 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I86 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I87 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I88 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I89 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I90 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I91 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I92 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I93 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I94 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I95 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I96 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I97 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I98 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I99 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I100 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I101 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I102 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I103 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I104 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I105 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I106 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I107 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I108 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I109 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I110 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I111 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I112 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I113 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I114 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I115 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I116 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I117 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I118 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I119 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I120 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I121 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I122 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I123 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I124 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I125 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I126 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I127 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I128 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I129 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I130 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | S19 | FLX1 | EventMaskLo | UINT32 | RW | 0...4294967295
55 | S1 | THD1 | THD mode | UINT32 | RW | 0=Disabled;1=Activated
55 | V1 | THD1 | THD condition | UINT32 | R | 0=Normal;1=Start;2=Alarm;3=Blocked
55 | S2 | THD1 | Measurement magnitude | UINT32 | RW | 0=Amplitude;1=Power
55 | I1 | THD1 | THD starts | UINT32 | R | 0...4294967295
55 | I2 | THD1 | THD alarms | UINT32 | R | 0...4294967295
55 | I3 | THD1 | THD blocks | UINT32 | R | 0...4294967295
55 | S3 | THD1 | Clear statistics | UINT32 | W | 0=-;1=Clear
55 | S4 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S5 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S6 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S7 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S8 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S9 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S10 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S11 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S12 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S13 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S14 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S15 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S16 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S17 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S18 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S19 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S20 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S21 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S22 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S23 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S24 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S25 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S26 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S27 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S28 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S29 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S30 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S31 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S32 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S33 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S34 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S35 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S36 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S37 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S38 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S39 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S40 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S41 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S42 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S43 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S44 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S45 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S46 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S47 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S48 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S49 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S50 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S51 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S52 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S53 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S54 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S55 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S56 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S57 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S58 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S59 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S60 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S61 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S62 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S63 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S64 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S65 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S66 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S67 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S68 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S69 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S70 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S71 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S72 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S73 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S74 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S75 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | O1 | THD1 | THDPH> START | SIGNAL_OUT | RW | 0...4294967295
55 | O2 | THD1 | THDPH> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O3 | THD1 | THDI01> START | SIGNAL_OUT | RW | 0...4294967295
55 | O4 | THD1 | THDI01> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O5 | THD1 | THDI02> START | SIGNAL_OUT | RW | 0...4294967295
55 | O6 | THD1 | THDI02> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O7 | THD1 | THD> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
55 | I4 | THD1 | Newest Register | UINT32 | R | 0...12
55 | I5 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I6 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I7 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I8 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I9 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I10 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I11 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I12 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I13 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I14 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I15 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I16 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I17 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I18 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I19 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I20 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I21 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I22 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I23 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I24 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I25 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I26 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I27 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I28 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I29 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I30 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I31 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I32 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I33 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I34 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I35 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I36 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I37 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I38 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I39 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I40 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | S76 | THD1 | EventMaskLo | UINT32 | RW | 0...4294967295
58 | S1 | CBW1 | CBW mode | UINT32 | RW | 0=Disabled;1=Activated
58 | V1 | CBW1 | CBW condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On
58 | I1 | CBW1 | Breaker operations | UINT32 | R | 0...4294967295
58 | I2 | CBW1 | Alarm 1 counter | UINT32 | R | 0...4294967295
58 | I3 | CBW1 | Alarm 2 counter | UINT32 | R | 0...4294967295
58 | I4 | CBW1 | L1 Operations Left | FLOAT | R | 0...4294967295
58 | I5 | CBW1 | L2 Operations Left | FLOAT | R | 0...4294967295
58 | I6 | CBW1 | L3 Operations Left | FLOAT | R | 0...4294967295
58 | S2 | CBW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
58 | S3 | CBW1 | Alarm 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S4 | CBW1 | Alarm 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S5 | CBW1 | Alarm 1 Set | UINT32 | RW | 0...200000
58 | S6 | CBW1 | Alarm 2 Set | UINT32 | RW | 0...200000
58 | S7 | CBW1 | Operations 1 | FLOAT | RW | 0...200000
58 | S8 | CBW1 | Operations 2 | FLOAT | RW | 0...200000
58 | S9 | CBW1 | Current 1 | FLOAT | RW | 0...100
58 | S10 | CBW1 | Current 2 | FLOAT | RW | 0...100
58 | O1 | CBW1 | CBW Alarm 1 act | SIGNAL_OUT | RW | 0...4294967295
58 | I7 | CBW1 | Newest Register | UINT32 | R | 0...12
58 | I8 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I9 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I10 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I11 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I12 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I13 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I14 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I15 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I16 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I17 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I18 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I19 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I20 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I21 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I22 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I23 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I24 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I25 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I26 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I27 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I28 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I29 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I30 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I31 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I32 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I33 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I34 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I35 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I36 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I37 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I38 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I39 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I40 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I41 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I42 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I43 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | S11 | CBW1 | EventMaskLo | UINT32 | RW | 0...4294967295
97 | S1 | NJK1 | U0> RECL [79] mode | UINT32 | RW | 0=Disabled;1=Activated
97 | V1 | NJK1 | U0> RECL condition | UINT32 | R | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
97 | I1 | NJK1 | Requests | UINT32 | R | 0...4294967295
97 | I2 | NJK1 | Blocks | UINT32 | R | 0...4294967295
97 | I3 | NJK1 | Starts | UINT32 | R | 0...4294967295
97 | I4 | NJK1 | Breaker closes | UINT32 | R | 0...4294967295
97 | S2 | NJK1 | Clear statistics | UINT32 | W | 0=-;1=Clear
97 | S3 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S4 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S5 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S6 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S7 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S8 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S9 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S10 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | O1 | NJK1 | U0> RECL Blocked | SIGNAL_OUT | RW | 0...4294967295
97 | O2 | NJK1 | U0> RECL Active | SIGNAL_OUT | RW | 0...4294967295
97 | O3 | NJK1 | U0> RECL CLOSE | SIGNAL_OUT | RW | 0...4294967295
97 | O4 | NJK1 | U0> RECL BLKU0 | SIGNAL_OUT | RW | 0...4294967295
97 | I5 | NJK1 | Newest Register | UINT32 | R | 0...12
97 | I6 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I7 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I8 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I9 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I10 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I11 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I12 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I13 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I14 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I15 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I16 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I17 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I18 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I19 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I20 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I21 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I22 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I23 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I24 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I25 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I26 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I27 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I28 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I29 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | S11 | NJK1 | EventMaskLo | UINT32 | RW | 0...4294967295
61 | S1 | SOF1 | SOTF mode | UINT32 | RW | 0=Disabled;1=Activated
61 | V1 | SOF1 | SOTF condition | UINT32 | R | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
61 | I1 | SOF1 | Inits | UINT32 | R | 0...4294967295
61 | I2 | SOF1 | Starts | UINT32 | R | 0...4294967295
61 | I3 | SOF1 | Trips | UINT32 | R | 0...4294967295
61 | I4 | SOF1 | Blocks | UINT32 | R | 0...4294967295
61 | S2 | SOF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
61 | S3 | SOF1 | SG in use | UINT32 | RW | 0...255
61 | S4 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S5 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S6 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S7 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S8 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S9 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S10 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S11 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | O1 | SOF1 | SOTF Blocked | SIGNAL_OUT | RW | 0...4294967295
61 | O2 | SOF1 | SOTF Active | SIGNAL_OUT | RW | 0...4294967295
61 | O3 | SOF1 | SOTF Trip | SIGNAL_OUT | RW | 0...4294967295
61 | I5 | SOF1 | Newest Register | UINT32 | R | 0...12
61 | I6 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I7 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I8 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I9 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I10 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I11 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I12 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I13 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I14 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I15 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I16 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I17 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I18 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I19 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I20 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I21 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I22 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I23 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I24 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I25 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I26 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I27 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I28 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I29 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | S12 | SOF1 | EventMaskLo | UINT32 | RW | 0...4294967295
142 | S1 | DOS1 | Energy dose counter mode | UINT32 | RW | 0=Disabled;1=Activated
142 | S2 | DOS1 | Clear pulsecounters | UINT32 | W | 0=-;1=Clear
142 | S3 | DOS1 | DC 1 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S4 | DOS1 | DC 1 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I1 | DOS1 | DC 1 Input signal | FLOAT | R | -1000000...1000000
142 | S5 | DOS1 | DC 1 Pulse magnitude | FLOAT | RW | 0...1800
142 | S6 | DOS1 | DC 1 Pulse Lenght | FLOAT | RW | 0...1800
142 | I2 | DOS1 | DC 1 Pulses sent | UINT32 | R | 0...4294967295
142 | S7 | DOS1 | DC 2 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S8 | DOS1 | DC 2 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I3 | DOS1 | DC 2 Input signal | FLOAT | R | -1000000...1000000
142 | S9 | DOS1 | DC 2 Pulse magnitude | FLOAT | RW | 0...1800
142 | S10 | DOS1 | DC 2 Pulse Lenght | FLOAT | RW | 0...1800
142 | I4 | DOS1 | DC 2 Pulses sent | UINT32 | R | 0...4294967295
142 | S11 | DOS1 | DC 3 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S12 | DOS1 | DC 3 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I5 | DOS1 | DC 3 Input signal | FLOAT | R | -1000000...1000000
142 | S13 | DOS1 | DC 3 Pulse magnitude | FLOAT | RW | 0...1800
142 | S14 | DOS1 | DC 3 Pulse Lenght | FLOAT | RW | 0...1800
142 | I6 | DOS1 | DC 3 Pulses sent | UINT32 | R | 0...4294967295
142 | S15 | DOS1 | DC 4 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S16 | DOS1 | DC 4 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I7 | DOS1 | DC 4 Input signal | FLOAT | R | -1000000...1000000
142 | S17 | DOS1 | DC 4 Pulse magnitude | FLOAT | RW | 0...1800
142 | S18 | DOS1 | DC 4 Pulse Lenght | FLOAT | RW | 0...1800
142 | I8 | DOS1 | DC 4 Pulses sent | UINT32 | R | 0...4294967295
142 | O1 | DOS1 | DC 1 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O2 | DOS1 | DC 2 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O3 | DOS1 | DC 3 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O4 | DOS1 | DC 4 Pulse out | SIGNAL_OUT | RW | 0...4294967295
144 | V1 | PCS1 | PCS1 Switch Status | SIGNAL_OUT | RW | 0...4294967295
145 | V1 | PCS2 | PCS2 Switch Status | SIGNAL_OUT | RW | 0...4294967295
146 | V1 | PCS3 | PCS3 Switch Status | SIGNAL_OUT | RW | 0...4294967295
147 | V1 | PCS4 | PCS4 Switch Status | SIGNAL_OUT | RW | 0...4294967295
148 | V1 | PCS5 | PCS5 Switch Status | SIGNAL_OUT | RW | 0...4294967295
45 | S1 | SYN1 | Synchrocheck (SYN1,2,3) [25] mode | UINT32 | RW | 0=Disabled;1=Activated
45 | V1 | SYN1 | SYN1 Condition | UINT32 | R | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok
45 | V2 | SYN1 | SYN2 Condition | UINT32 | R | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok
45 | V3 | SYN1 | SYN3 Condition | UINT32 | R | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok
45 | I1 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I2 | SYN1 | SYN1 Mag diff | FLOAT | R | -120...120
45 | I3 | SYN1 | SYN1 Ang diff | FLOAT | R | -360...360
45 | I4 | SYN1 | SYN1 freq diff | FLOAT | R | -75...75
45 | I5 | SYN1 | SYN1 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S2 | SYN1 | Estimated BRK Closing time | FLOAT | R | 0...360
45 | S3 | SYN1 | Networks rotating time | FLOAT | R | 0...360
45 | S4 | SYN1 | Networks placement atm | FLOAT | R | -360...360
45 | I6 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I7 | SYN1 | SYN2 Mag diff | FLOAT | R | -120...120
45 | I8 | SYN1 | SYN2 Ang diff | FLOAT | R | -360...360
45 | I9 | SYN1 | SYN2 freq diff | FLOAT | R | -75...75
45 | I10 | SYN1 | SYN2 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S5 | SYN1 | SYN2 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S6 | SYN1 | SYN2 Networks rotating time | FLOAT | R | 0...360.000
45 | S7 | SYN1 | SYN2 Networks placement atm | FLOAT | R | -360.000...360.000
45 | I11 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I12 | SYN1 | SYN3 Mag diff | FLOAT | R | -120...120
45 | I13 | SYN1 | SYN3 Ang diff | FLOAT | R | -360...360
45 | I14 | SYN1 | SYN3 freq diff | FLOAT | R | -75...75
45 | I15 | SYN1 | SYN3 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S8 | SYN1 | SYN3 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S9 | SYN1 | SYN3 Networks rotating time | FLOAT | R | 0...360.000
45 | S10 | SYN1 | SYN3 Networks placement atm | FLOAT | R | -360.000...360.000
45 | O1 | SYN1 | SYN1 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O2 | SYN1 | SYN1 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O3 | SYN1 | SYN1 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O4 | SYN1 | SYN1 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O5 | SYN1 | SYN1 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O6 | SYN1 | SYN1 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O7 | SYN1 | SYN1 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O8 | SYN1 | SYN1 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O9 | SYN1 | SYN1 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O10 | SYN1 | SYN1 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O11 | SYN1 | SYN1 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O12 | SYN1 | SYN1 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O13 | SYN1 | SYN1 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O14 | SYN1 | SYN1 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O15 | SYN1 | SYN1 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O16 | SYN1 | SYN1 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O17 | SYN1 | SYN1 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O18 | SYN1 | SYN1 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O19 | SYN1 | SYN1 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O20 | SYN1 | SYN1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O21 | SYN1 | SYN2 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O22 | SYN1 | SYN2 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O23 | SYN1 | SYN2 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O24 | SYN1 | SYN2 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O25 | SYN1 | SYN2 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O26 | SYN1 | SYN2 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O27 | SYN1 | SYN2 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O28 | SYN1 | SYN2 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O29 | SYN1 | SYN2 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O30 | SYN1 | SYN2 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O31 | SYN1 | SYN2 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O32 | SYN1 | SYN2 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O33 | SYN1 | SYN2 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O34 | SYN1 | SYN2 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O35 | SYN1 | SYN2 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O36 | SYN1 | SYN2 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O37 | SYN1 | SYN2 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O38 | SYN1 | SYN2 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O39 | SYN1 | SYN2 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O40 | SYN1 | SYN2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O41 | SYN1 | SYN3 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O42 | SYN1 | SYN3 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O43 | SYN1 | SYN3 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O44 | SYN1 | SYN3 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O45 | SYN1 | SYN3 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O46 | SYN1 | SYN3 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O47 | SYN1 | SYN3 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O48 | SYN1 | SYN3 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O49 | SYN1 | SYN3 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O50 | SYN1 | SYN3 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O51 | SYN1 | SYN3 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O52 | SYN1 | SYN3 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O53 | SYN1 | SYN3 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O54 | SYN1 | SYN3 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O55 | SYN1 | SYN3 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O56 | SYN1 | SYN3 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O57 | SYN1 | SYN3 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O58 | SYN1 | SYN3 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O59 | SYN1 | SYN3 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O60 | SYN1 | SYN3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | I16 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I17 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I18 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I19 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I20 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I21 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I22 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I23 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I24 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I25 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I26 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I27 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I28 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I29 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I30 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I31 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I32 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I33 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I34 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I35 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I36 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I37 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I38 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I39 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I40 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I41 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I42 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I43 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I44 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I45 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I46 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I47 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I48 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I49 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I50 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I51 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I52 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I53 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I54 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I55 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I56 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I57 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I58 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I59 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I60 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I61 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I62 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I63 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I64 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I65 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I66 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I67 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I68 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I69 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I70 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I71 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I72 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I73 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I74 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I75 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I76 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I77 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I78 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I79 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I80 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I81 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I82 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I83 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I84 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I85 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I86 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I87 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I88 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I89 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I90 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I91 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I92 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I93 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I94 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I95 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I96 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I97 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I98 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I99 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I100 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I101 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I102 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I103 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I104 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I105 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I106 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I107 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I108 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I109 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I110 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I111 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I112 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I113 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I114 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I115 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I116 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I117 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I118 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I119 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I120 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I121 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I122 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I123 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I124 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I125 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I126 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I127 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I128 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I129 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I130 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I131 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I132 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I133 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I134 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I135 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I136 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I137 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I138 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I139 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I140 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I141 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I142 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I143 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I144 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I145 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I146 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I147 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I148 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I149 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I150 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I151 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I152 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I153 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I154 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I155 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I156 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I157 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I158 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I159 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I160 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I161 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I162 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I163 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I164 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I165 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I166 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I167 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I168 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I169 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I170 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I171 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I172 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I173 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I174 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I175 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I176 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I177 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I178 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I179 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I180 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I181 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I182 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I183 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I184 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I185 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I186 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I187 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I188 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I189 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I190 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I191 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I192 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I193 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I194 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I195 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I196 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I197 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I198 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I199 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I200 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I201 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I202 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I203 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I204 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I205 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I206 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I207 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I208 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I209 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I210 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I211 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I212 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I213 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I214 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I215 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I216 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I217 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I218 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I219 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I220 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I221 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I222 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I223 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I224 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I225 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I226 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I227 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I228 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I229 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I230 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I231 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I232 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I233 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I234 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I235 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I236 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I237 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I238 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I239 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I240 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I241 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I242 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I243 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I244 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I245 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I246 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I247 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I248 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I249 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I250 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I251 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I252 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I253 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I254 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I255 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I256 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I257 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I258 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I259 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I260 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I261 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I262 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I263 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I264 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I265 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I266 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I267 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I268 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I269 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I270 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I271 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I272 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I273 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I274 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I275 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I276 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I277 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I278 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I279 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I280 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I281 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I282 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I283 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I284 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I285 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I286 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I287 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I288 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I289 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I290 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I291 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I292 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I293 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I294 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I295 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I296 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I297 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I298 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I299 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I300 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I301 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I302 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I303 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I304 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I305 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I306 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I307 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I308 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I309 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I310 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I311 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I312 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I313 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I314 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I315 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I316 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I317 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I318 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I319 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I320 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I321 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I322 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I323 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I324 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I325 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I326 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I327 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I328 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I329 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I330 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I331 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I332 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I333 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I334 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I335 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I336 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I337 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I338 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I339 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I340 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I341 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I342 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I343 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I344 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I345 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I346 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I347 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I348 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I349 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I350 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I351 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I352 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I353 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I354 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I355 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I356 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I357 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I358 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I359 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I360 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I361 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I362 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I363 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I364 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I365 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I366 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I367 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I368 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I369 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I370 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I371 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I372 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I373 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I374 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I375 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I376 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I377 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I378 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | S11 | SYN1 | EventMaskLo | UINT32 | RW | 0...4294967295
45 | S12 | SYN1 | EventMaskHi | UINT32 | RW | 0...4294967295
219 | S1 | SYNX1 | SYN1 Extra EventMaskLo | UINT32 | RW | 0...4294967295
219 | S2 | SYNX1 | SYN1 Extra EventMaskHi | UINT32 | RW | 0...4294967295
220 | S1 | SYNX2 | SYN2 Extra EventMaskLo | UINT32 | RW | 0...4294967295
220 | S2 | SYNX2 | SYN2 Extra EventMaskHi | UINT32 | RW | 0...4294967295
221 | S1 | SYNX3 | SYN3 Extra EventMaskLo | UINT32 | RW | 0...4294967295
221 | S2 | SYNX3 | SYN3 Extra EventMaskHi | UINT32 | RW | 0...4294967295
155 | S1 | VJP1 | <DELTA><alpha> > mode | UINT32 | RW | 0=Disabled;1=Activated
155 | V1 | VJP1 | <DELTA><alpha> > condition | UINT32 | R | 0=Normal;1=Blocked:2=Trip;3=Alarm
155 | S2 | VJP1 | Available stages | UINT32 | RW | 0=Trip;1=Trip and Alarm
155 | S3 | VJP1 | Monitored voltages | UINT32 | RW | 0=System all P-P Voltages;1=System any P-P Voltage;2=System L12 Voltage;3=System L23 Voltage;4=System L31 Voltage;5=System all P-E voltages;6=System any P-E voltage;7=System L1 Voltage;8=System L2 Voltage;9=System L3 Voltage;10=U3 Voltage;11=U4 Voltage
155 | V2 | VJP1 | Voltage meas selected | UINT32 | R | 0=Selection Ok;1=Selection not available
155 | I1 | VJP1 | <DELTA><alpha> > U1 Angle difference | FLOAT | R | -360...360
155 | I2 | VJP1 | <DELTA><alpha> U1meas/Set | FLOAT | R | -360...360
155 | I3 | VJP1 | <DELTA><alpha> U2 Angle difference | FLOAT | R | -360...360
155 | I4 | VJP1 | <DELTA><alpha> U2meas/Set | FLOAT | R | -360...360
155 | I5 | VJP1 | <DELTA><alpha> U3 Angle difference | FLOAT | R | -360...360
155 | I6 | VJP1 | <DELTA><alpha> U3meas/Set | FLOAT | R | -360...360
155 | I7 | VJP1 | <DELTA><alpha> > Alarms | UINT32 | R | 0...4294967295
155 | I8 | VJP1 | <DELTA><alpha> > Trips | UINT32 | R | 0...4294967295
155 | I9 | VJP1 | <DELTA><alpha> > Blocks | UINT32 | R | 0...4294967295
155 | S4 | VJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
155 | S5 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S6 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S7 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S8 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S9 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S10 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S11 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S12 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S13 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S14 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S15 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S16 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S17 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S18 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S19 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S20 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S21 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S22 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S23 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S24 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S25 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S26 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S27 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S28 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | O1 | VJP1 | <DELTA><alpha> > TRIP | SIGNAL_OUT | RW | 0...4294967295
155 | O2 | VJP1 | <DELTA><alpha> > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
155 | I10 | VJP1 | Newest Register | UINT32 | R | 0...12
155 | I11 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I12 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I13 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I14 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I15 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I16 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I17 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I18 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I19 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I20 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I21 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I22 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I23 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I24 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I25 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I26 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I27 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I28 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I29 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I30 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I31 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I32 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I33 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I34 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I35 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I36 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I37 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I38 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I39 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I40 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I41 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I42 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I43 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I44 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I45 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I46 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | S29 | VJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S1 | OBJ1 | Object1 mode | UINT32 | RW | 0=Disabled;1=Activated
46 | I1 | OBJ1 | Object1 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I2 | OBJ1 | Object1 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
46 | I3 | OBJ1 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | S2 | OBJ1 | Breaker traverse time | FLOAT | RW | 0.02...500
46 | S3 | OBJ1 | WD Cart traverse time | FLOAT | RW | 0.02...500
46 | S4 | OBJ1 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
46 | S5 | OBJ1 | Sync wait timeout | FLOAT | RW | 0.02...500
46 | S6 | OBJ1 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
46 | S7 | OBJ1 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
46 | S8 | OBJ1 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
46 | S9 | OBJ1 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
46 | S10 | OBJ1 | Control Termination Timeout | FLOAT | RW | 0.02...500
46 | O1 | OBJ1 | Object1 Status Open | SIGNAL_OUT | RW | 0...4294967295
46 | O2 | OBJ1 | Object1 Status Closed | SIGNAL_OUT | RW | 0...4294967295
46 | O3 | OBJ1 | Object1 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
46 | O4 | OBJ1 | Object1 Status Bad | SIGNAL_OUT | RW | 0...4294967295
46 | O5 | OBJ1 | Object1 Open Command | SIGNAL_OUT | RW | 0...4294967295
46 | O6 | OBJ1 | Object1 Close Command | SIGNAL_OUT | RW | 0...4294967295
46 | O7 | OBJ1 | Object1 Open Request | SIGNAL_OUT | RW | 0...4294967295
46 | O8 | OBJ1 | Object1 Close Request | SIGNAL_OUT | RW | 0...4294967295
46 | O9 | OBJ1 | Object1 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
46 | O10 | OBJ1 | Object1 No sync wait | SIGNAL_OUT | RW | 0...4294967295
46 | O11 | OBJ1 | Object1 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
46 | O12 | OBJ1 | Object1 No sync fail | SIGNAL_OUT | RW | 0...4294967295
46 | O13 | OBJ1 | Object1 Open timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O14 | OBJ1 | Object1 Close timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O15 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O16 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O17 | OBJ1 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
46 | S11 | OBJ1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S12 | OBJ1 | EventMaskHi | UINT32 | RW | 0...4294967295
46 | I4 | OBJ1 | Newest Register | UINT32 | R | 0...12
46 | I5 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I6 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I7 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I8 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I9 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I10 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I11 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I12 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I13 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I14 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I15 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I16 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I17 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I18 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I19 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I20 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I21 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I22 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I23 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I24 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I25 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I26 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I27 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I28 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I29 | OBJ1 | Open requests | UINT32 | R | 0...4294967295
46 | I30 | OBJ1 | Close requests | UINT32 | R | 0...4294967295
46 | I31 | OBJ1 | Open requests failed | UINT32 | R | 0...4294967295
46 | I32 | OBJ1 | Close requests failed | UINT32 | R | 0...4294967295
46 | S13 | OBJ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
47 | S1 | OBJ2 | Object2 mode | UINT32 | RW | 0=Disabled;1=Activated
47 | I1 | OBJ2 | Object2 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I2 | OBJ2 | Object2 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
47 | I3 | OBJ2 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | S2 | OBJ2 | Breaker traverse time | FLOAT | RW | 0.02...500
47 | S3 | OBJ2 | WD Cart traverse time | FLOAT | RW | 0.02...500
47 | S4 | OBJ2 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
47 | S5 | OBJ2 | Sync wait timeout | FLOAT | RW | 0.02...500
47 | S6 | OBJ2 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
47 | S7 | OBJ2 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
47 | S8 | OBJ2 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
47 | S9 | OBJ2 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
47 | S10 | OBJ2 | Control Termination Timeout | FLOAT | RW | 0.02...500
47 | O1 | OBJ2 | Object2 Status Open | SIGNAL_OUT | RW | 0...4294967295
47 | O2 | OBJ2 | Object2 Status Closed | SIGNAL_OUT | RW | 0...4294967295
47 | O3 | OBJ2 | Object2 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
47 | O4 | OBJ2 | Object2 Status Bad | SIGNAL_OUT | RW | 0...4294967295
47 | O5 | OBJ2 | Object2 Open Command | SIGNAL_OUT | RW | 0...4294967295
47 | O6 | OBJ2 | Object2 Close Command | SIGNAL_OUT | RW | 0...4294967295
47 | O7 | OBJ2 | Object2 Open Request | SIGNAL_OUT | RW | 0...4294967295
47 | O8 | OBJ2 | Object2 Close Request | SIGNAL_OUT | RW | 0...4294967295
47 | O9 | OBJ2 | Object2 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
47 | O10 | OBJ2 | Object2 No sync wait | SIGNAL_OUT | RW | 0...4294967295
47 | O11 | OBJ2 | Object2 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
47 | O12 | OBJ2 | Object2 No sync fail | SIGNAL_OUT | RW | 0...4294967295
47 | O13 | OBJ2 | Object2 Open timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O14 | OBJ2 | Object2 Close timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O15 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O16 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O17 | OBJ2 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
47 | S11 | OBJ2 | EventMaskLo | UINT32 | RW | 0...4294967295
47 | S12 | OBJ2 | EventMaskHi | UINT32 | RW | 0...4294967295
47 | I4 | OBJ2 | Newest Register | UINT32 | R | 0...12
47 | I5 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I6 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I7 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I8 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I9 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I10 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I11 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I12 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I13 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I14 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I15 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I16 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I17 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I18 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I19 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I20 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I21 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I22 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I23 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I24 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I25 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I26 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I27 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I28 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I29 | OBJ2 | Open requests | UINT32 | R | 0...4294967295
47 | I30 | OBJ2 | Close requests | UINT32 | R | 0...4294967295
47 | I31 | OBJ2 | Open requests failed | UINT32 | R | 0...4294967295
47 | I32 | OBJ2 | Close requests failed | UINT32 | R | 0...4294967295
47 | S13 | OBJ2 | Clear statistics | UINT32 | W | 0=-;1=Clear
48 | S1 | OBJ3 | Object3 mode | UINT32 | RW | 0=Disabled;1=Activated
48 | I1 | OBJ3 | Object3 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I2 | OBJ3 | Object3 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
48 | I3 | OBJ3 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | S2 | OBJ3 | Breaker traverse time | FLOAT | RW | 0.02...500
48 | S3 | OBJ3 | WD Cart traverse time | FLOAT | RW | 0.02...500
48 | S4 | OBJ3 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
48 | S5 | OBJ3 | Sync wait timeout | FLOAT | RW | 0.02...500
48 | S6 | OBJ3 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
48 | S7 | OBJ3 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
48 | S8 | OBJ3 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
48 | S9 | OBJ3 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
48 | S10 | OBJ3 | Control Termination Timeout | FLOAT | RW | 0.02...500
48 | O1 | OBJ3 | Object3 Status Open | SIGNAL_OUT | RW | 0...4294967295
48 | O2 | OBJ3 | Object3 Status Closed | SIGNAL_OUT | RW | 0...4294967295
48 | O3 | OBJ3 | Object3 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
48 | O4 | OBJ3 | Object3 Status Bad | SIGNAL_OUT | RW | 0...4294967295
48 | O5 | OBJ3 | Object3 Open Command | SIGNAL_OUT | RW | 0...4294967295
48 | O6 | OBJ3 | Object3 Close Command | SIGNAL_OUT | RW | 0...4294967295
48 | O7 | OBJ3 | Object3 Open Request | SIGNAL_OUT | RW | 0...4294967295
48 | O8 | OBJ3 | Object3 Close Request | SIGNAL_OUT | RW | 0...4294967295
48 | O9 | OBJ3 | Object3 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
48 | O10 | OBJ3 | Object3 No sync wait | SIGNAL_OUT | RW | 0...4294967295
48 | O11 | OBJ3 | Object3 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
48 | O12 | OBJ3 | Object3 No sync fail | SIGNAL_OUT | RW | 0...4294967295
48 | O13 | OBJ3 | Object3 Open timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O14 | OBJ3 | Object3 Close timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O15 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O16 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O17 | OBJ3 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
48 | S11 | OBJ3 | EventMaskLo | UINT32 | RW | 0...4294967295
48 | S12 | OBJ3 | EventMaskHi | UINT32 | RW | 0...4294967295
48 | I4 | OBJ3 | Newest Register | UINT32 | R | 0...12
48 | I5 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I6 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I7 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I8 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I9 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I10 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I11 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I12 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I13 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I14 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I15 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I16 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I17 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I18 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I19 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I20 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I21 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I22 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I23 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I24 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I25 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I26 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I27 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I28 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I29 | OBJ3 | Open requests | UINT32 | R | 0...4294967295
48 | I30 | OBJ3 | Close requests | UINT32 | R | 0...4294967295
48 | I31 | OBJ3 | Open requests failed | UINT32 | R | 0...4294967295
48 | I32 | OBJ3 | Close requests failed | UINT32 | R | 0...4294967295
48 | S13 | OBJ3 | Clear statistics | UINT32 | W | 0=-;1=Clear
49 | S1 | OBJ4 | Object4 mode | UINT32 | RW | 0=Disabled;1=Activated
49 | I1 | OBJ4 | Object4 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I2 | OBJ4 | Object4 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
49 | I3 | OBJ4 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | S2 | OBJ4 | Breaker traverse time | FLOAT | RW | 0.02...500
49 | S3 | OBJ4 | WD Cart traverse time | FLOAT | RW | 0.02...500
49 | S4 | OBJ4 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
49 | S5 | OBJ4 | Sync wait timeout | FLOAT | RW | 0.02...500
49 | S6 | OBJ4 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
49 | S7 | OBJ4 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
49 | S8 | OBJ4 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
49 | S9 | OBJ4 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
49 | S10 | OBJ4 | Control Termination Timeout | FLOAT | RW | 0.02...500
49 | O1 | OBJ4 | Object4 Status Open | SIGNAL_OUT | RW | 0...4294967295
49 | O2 | OBJ4 | Object4 Status Closed | SIGNAL_OUT | RW | 0...4294967295
49 | O3 | OBJ4 | Object4 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
49 | O4 | OBJ4 | Object4 Status Bad | SIGNAL_OUT | RW | 0...4294967295
49 | O5 | OBJ4 | Object4 Open Command | SIGNAL_OUT | RW | 0...4294967295
49 | O6 | OBJ4 | Object4 Close Command | SIGNAL_OUT | RW | 0...4294967295
49 | O7 | OBJ4 | Object4 Open Request | SIGNAL_OUT | RW | 0...4294967295
49 | O8 | OBJ4 | Object4 Close Request | SIGNAL_OUT | RW | 0...4294967295
49 | O9 | OBJ4 | Object4 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
49 | O10 | OBJ4 | Object4 No sync wait | SIGNAL_OUT | RW | 0...4294967295
49 | O11 | OBJ4 | Object4 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
49 | O12 | OBJ4 | Object4 No sync fail | SIGNAL_OUT | RW | 0...4294967295
49 | O13 | OBJ4 | Object4 Open timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O14 | OBJ4 | Object4 Close timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O15 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O16 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O17 | OBJ4 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
49 | S11 | OBJ4 | EventMaskLo | UINT32 | RW | 0...4294967295
49 | S12 | OBJ4 | EventMaskHi | UINT32 | RW | 0...4294967295
49 | I4 | OBJ4 | Newest Register | UINT32 | R | 0...12
49 | I5 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I6 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I7 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I8 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I9 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I10 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I11 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I12 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I13 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I14 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I15 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I16 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I17 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I18 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I19 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I20 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I21 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I22 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I23 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I24 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I25 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I26 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I27 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I28 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I29 | OBJ4 | Open requests | UINT32 | R | 0...4294967295
49 | I30 | OBJ4 | Close requests | UINT32 | R | 0...4294967295
49 | I31 | OBJ4 | Open requests failed | UINT32 | R | 0...4294967295
49 | I32 | OBJ4 | Close requests failed | UINT32 | R | 0...4294967295
49 | S13 | OBJ4 | Clear statistics | UINT32 | W | 0=-;1=Clear
50 | S1 | OBJ5 | Object5 mode | UINT32 | RW | 0=Disabled;1=Activated
50 | I1 | OBJ5 | Object5 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I2 | OBJ5 | Object5 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
50 | I3 | OBJ5 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | S2 | OBJ5 | Breaker traverse time | FLOAT | RW | 0.02...500
50 | S3 | OBJ5 | WD Cart traverse time | FLOAT | RW | 0.02...500
50 | S4 | OBJ5 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
50 | S5 | OBJ5 | Sync wait timeout | FLOAT | RW | 0.02...500
50 | S6 | OBJ5 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
50 | S7 | OBJ5 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
50 | S8 | OBJ5 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
50 | S9 | OBJ5 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
50 | S10 | OBJ5 | Control Termination Timeout | FLOAT | RW | 0.02...500
50 | O1 | OBJ5 | Object5 Status Open | SIGNAL_OUT | RW | 0...4294967295
50 | O2 | OBJ5 | Object5 Status Closed | SIGNAL_OUT | RW | 0...4294967295
50 | O3 | OBJ5 | Object5 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
50 | O4 | OBJ5 | Object5 Status Bad | SIGNAL_OUT | RW | 0...4294967295
50 | O5 | OBJ5 | Object5 Open Command | SIGNAL_OUT | RW | 0...4294967295
50 | O6 | OBJ5 | Object5 Close Command | SIGNAL_OUT | RW | 0...4294967295
50 | O7 | OBJ5 | Object5 Open Request | SIGNAL_OUT | RW | 0...4294967295
50 | O8 | OBJ5 | Object5 Close Request | SIGNAL_OUT | RW | 0...4294967295
50 | O9 | OBJ5 | Object5 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
50 | O10 | OBJ5 | Object5 No sync wait | SIGNAL_OUT | RW | 0...4294967295
50 | O11 | OBJ5 | Object5 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
50 | O12 | OBJ5 | Object5 No sync fail | SIGNAL_OUT | RW | 0...4294967295
50 | O13 | OBJ5 | Object5 Open timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O14 | OBJ5 | Object5 Close timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O15 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O16 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O17 | OBJ5 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
50 | S11 | OBJ5 | EventMaskLo | UINT32 | RW | 0...4294967295
50 | S12 | OBJ5 | EventMaskHi | UINT32 | RW | 0...4294967295
50 | I4 | OBJ5 | Newest Register | UINT32 | R | 0...12
50 | I5 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I6 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I7 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I8 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I9 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I10 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I11 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I12 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I13 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I14 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I15 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I16 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I17 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I18 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I19 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I20 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I21 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I22 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I23 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I24 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I25 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I26 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I27 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I28 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I29 | OBJ5 | Open requests | UINT32 | R | 0...4294967295
50 | I30 | OBJ5 | Close requests | UINT32 | R | 0...4294967295
50 | I31 | OBJ5 | Open requests failed | UINT32 | R | 0...4294967295
50 | I32 | OBJ5 | Close requests failed | UINT32 | R | 0...4294967295
50 | S13 | OBJ5 | Clear statistics | UINT32 | W | 0=-;1=Clear
150 | S1 | OBJ6 | Object6 mode | UINT32 | RW | 0=Disabled;1=Activated
150 | I1 | OBJ6 | Object6 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I2 | OBJ6 | Object6 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
150 | I3 | OBJ6 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | S2 | OBJ6 | Breaker traverse time | FLOAT | RW | 0.02...500
150 | S3 | OBJ6 | WD Cart traverse time | FLOAT | RW | 0.02...500
150 | S4 | OBJ6 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
150 | S5 | OBJ6 | Sync wait timeout | FLOAT | RW | 0.02...500
150 | S6 | OBJ6 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
150 | S7 | OBJ6 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
150 | S8 | OBJ6 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
150 | S9 | OBJ6 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
150 | S10 | OBJ6 | Control Termination Timeout | FLOAT | RW | 0.02...500
150 | O1 | OBJ6 | Object6 Status Open | SIGNAL_OUT | RW | 0...4294967295
150 | O2 | OBJ6 | Object6 Status Closed | SIGNAL_OUT | RW | 0...4294967295
150 | O3 | OBJ6 | Object6 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
150 | O4 | OBJ6 | Object6 Status Bad | SIGNAL_OUT | RW | 0...4294967295
150 | O5 | OBJ6 | Object6 Open Command | SIGNAL_OUT | RW | 0...4294967295
150 | O6 | OBJ6 | Object6 Close Command | SIGNAL_OUT | RW | 0...4294967295
150 | O7 | OBJ6 | Object6 Open Request | SIGNAL_OUT | RW | 0...4294967295
150 | O8 | OBJ6 | Object6 Close Request | SIGNAL_OUT | RW | 0...4294967295
150 | O9 | OBJ6 | Object6 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
150 | O10 | OBJ6 | Object6 No sync wait | SIGNAL_OUT | RW | 0...4294967295
150 | O11 | OBJ6 | Object6 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
150 | O12 | OBJ6 | Object6 No sync fail | SIGNAL_OUT | RW | 0...4294967295
150 | O13 | OBJ6 | Object6 Open timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O14 | OBJ6 | Object6 Close timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O15 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O16 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O17 | OBJ6 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
150 | S11 | OBJ6 | EventMaskLo | UINT32 | RW | 0...4294967295
150 | S12 | OBJ6 | EventMaskHi | UINT32 | RW | 0...4294967295
150 | I4 | OBJ6 | Newest Register | UINT32 | R | 0...12
150 | I5 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I6 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I7 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I8 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I9 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I10 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I11 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I12 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I13 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I14 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I15 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I16 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I17 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I18 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I19 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I20 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I21 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I22 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I23 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I24 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I25 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I26 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I27 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I28 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I29 | OBJ6 | Open requests | UINT32 | R | 0...4294967295
150 | I30 | OBJ6 | Close requests | UINT32 | R | 0...4294967295
150 | I31 | OBJ6 | Open requests failed | UINT32 | R | 0...4294967295
150 | I32 | OBJ6 | Close requests failed | UINT32 | R | 0...4294967295
150 | S13 | OBJ6 | Clear statistics | UINT32 | W | 0=-;1=Clear
151 | S1 | OBJ7 | Object7 mode | UINT32 | RW | 0=Disabled;1=Activated
151 | I1 | OBJ7 | Object7 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I2 | OBJ7 | Object7 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
151 | I3 | OBJ7 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | S2 | OBJ7 | Breaker traverse time | FLOAT | RW | 0.02...500
151 | S3 | OBJ7 | WD Cart traverse time | FLOAT | RW | 0.02...500
151 | S4 | OBJ7 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
151 | S5 | OBJ7 | Sync wait timeout | FLOAT | RW | 0.02...500
151 | S6 | OBJ7 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
151 | S7 | OBJ7 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
151 | S8 | OBJ7 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
151 | S9 | OBJ7 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
151 | S10 | OBJ7 | Control Termination Timeout | FLOAT | RW | 0.02...500
151 | O1 | OBJ7 | Object7 Status Open | SIGNAL_OUT | RW | 0...4294967295
151 | O2 | OBJ7 | Object7 Status Closed | SIGNAL_OUT | RW | 0...4294967295
151 | O3 | OBJ7 | Object7 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
151 | O4 | OBJ7 | Object7 Status Bad | SIGNAL_OUT | RW | 0...4294967295
151 | O5 | OBJ7 | Object7 Open Command | SIGNAL_OUT | RW | 0...4294967295
151 | O6 | OBJ7 | Object7 Close Command | SIGNAL_OUT | RW | 0...4294967295
151 | O7 | OBJ7 | Object7 Open Request | SIGNAL_OUT | RW | 0...4294967295
151 | O8 | OBJ7 | Object7 Close Request | SIGNAL_OUT | RW | 0...4294967295
151 | O9 | OBJ7 | Object7 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
151 | O10 | OBJ7 | Object7 No sync wait | SIGNAL_OUT | RW | 0...4294967295
151 | O11 | OBJ7 | Object7 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
151 | O12 | OBJ7 | Object7 No sync fail | SIGNAL_OUT | RW | 0...4294967295
151 | O13 | OBJ7 | Object7 Open timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O14 | OBJ7 | Object7 Close timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O15 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O16 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O17 | OBJ7 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
151 | S11 | OBJ7 | EventMaskLo | UINT32 | RW | 0...4294967295
151 | S12 | OBJ7 | EventMaskHi | UINT32 | RW | 0...4294967295
151 | I4 | OBJ7 | Newest Register | UINT32 | R | 0...12
151 | I5 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I6 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I7 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I8 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I9 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I10 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I11 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I12 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I13 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I14 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I15 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I16 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I17 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I18 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I19 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I20 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I21 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I22 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I23 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I24 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I25 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I26 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I27 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I28 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I29 | OBJ7 | Open requests | UINT32 | R | 0...4294967295
151 | I30 | OBJ7 | Close requests | UINT32 | R | 0...4294967295
151 | I31 | OBJ7 | Open requests failed | UINT32 | R | 0...4294967295
151 | I32 | OBJ7 | Close requests failed | UINT32 | R | 0...4294967295
151 | S13 | OBJ7 | Clear statistics | UINT32 | W | 0=-;1=Clear
152 | S1 | OBJ8 | Object8 mode | UINT32 | RW | 0=Disabled;1=Activated
152 | I1 | OBJ8 | Object8 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I2 | OBJ8 | Object8 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
152 | I3 | OBJ8 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | S2 | OBJ8 | Breaker traverse time | FLOAT | RW | 0.02...500
152 | S3 | OBJ8 | WD Cart traverse time | FLOAT | RW | 0.02...500
152 | S4 | OBJ8 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
152 | S5 | OBJ8 | Sync wait timeout | FLOAT | RW | 0.02...500
152 | S6 | OBJ8 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
152 | S7 | OBJ8 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
152 | S8 | OBJ8 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
152 | S9 | OBJ8 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
152 | S10 | OBJ8 | Control Termination Timeout | FLOAT | RW | 0.02...500
152 | O1 | OBJ8 | Object8 Status Open | SIGNAL_OUT | RW | 0...4294967295
152 | O2 | OBJ8 | Object8 Status Closed | SIGNAL_OUT | RW | 0...4294967295
152 | O3 | OBJ8 | Object8 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
152 | O4 | OBJ8 | Object8 Status Bad | SIGNAL_OUT | RW | 0...4294967295
152 | O5 | OBJ8 | Object8 Open Command | SIGNAL_OUT | RW | 0...4294967295
152 | O6 | OBJ8 | Object8 Close Command | SIGNAL_OUT | RW | 0...4294967295
152 | O7 | OBJ8 | Object8 Open Request | SIGNAL_OUT | RW | 0...4294967295
152 | O8 | OBJ8 | Object8 Close Request | SIGNAL_OUT | RW | 0...4294967295
152 | O9 | OBJ8 | Object8 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
152 | O10 | OBJ8 | Object8 No sync wait | SIGNAL_OUT | RW | 0...4294967295
152 | O11 | OBJ8 | Object8 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
152 | O12 | OBJ8 | Object8 No sync fail | SIGNAL_OUT | RW | 0...4294967295
152 | O13 | OBJ8 | Object8 Open timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O14 | OBJ8 | Object8 Close timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O15 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O16 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O17 | OBJ8 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
152 | S11 | OBJ8 | EventMaskLo | UINT32 | RW | 0...4294967295
152 | S12 | OBJ8 | EventMaskHi | UINT32 | RW | 0...4294967295
152 | I4 | OBJ8 | Newest Register | UINT32 | R | 0...12
152 | I5 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I6 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I7 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I8 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I9 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I10 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I11 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I12 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I13 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I14 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I15 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I16 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I17 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I18 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I19 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I20 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I21 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I22 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I23 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I24 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I25 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I26 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I27 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I28 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I29 | OBJ8 | Open requests | UINT32 | R | 0...4294967295
152 | I30 | OBJ8 | Close requests | UINT32 | R | 0...4294967295
152 | I31 | OBJ8 | Open requests failed | UINT32 | R | 0...4294967295
152 | I32 | OBJ8 | Close requests failed | UINT32 | R | 0...4294967295
152 | S13 | OBJ8 | Clear statistics | UINT32 | W | 0=-;1=Clear
153 | S1 | OBJ9 | Object9 mode | UINT32 | RW | 0=Disabled;1=Activated
153 | I1 | OBJ9 | Object9 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I2 | OBJ9 | Object9 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
153 | I3 | OBJ9 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | S2 | OBJ9 | Breaker traverse time | FLOAT | RW | 0.02...500
153 | S3 | OBJ9 | WD Cart traverse time | FLOAT | RW | 0.02...500
153 | S4 | OBJ9 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
153 | S5 | OBJ9 | Sync wait timeout | FLOAT | RW | 0.02...500
153 | S6 | OBJ9 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
153 | S7 | OBJ9 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
153 | S8 | OBJ9 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
153 | S9 | OBJ9 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
153 | S10 | OBJ9 | Control Termination Timeout | FLOAT | RW | 0.02...500
153 | O1 | OBJ9 | Object9 Status Open | SIGNAL_OUT | RW | 0...4294967295
153 | O2 | OBJ9 | Object9 Status Closed | SIGNAL_OUT | RW | 0...4294967295
153 | O3 | OBJ9 | Object9 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
153 | O4 | OBJ9 | Object9 Status Bad | SIGNAL_OUT | RW | 0...4294967295
153 | O5 | OBJ9 | Object9 Open Command | SIGNAL_OUT | RW | 0...4294967295
153 | O6 | OBJ9 | Object9 Close Command | SIGNAL_OUT | RW | 0...4294967295
153 | O7 | OBJ9 | Object9 Open Request | SIGNAL_OUT | RW | 0...4294967295
153 | O8 | OBJ9 | Object9 Close Request | SIGNAL_OUT | RW | 0...4294967295
153 | O9 | OBJ9 | Object9 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
153 | O10 | OBJ9 | Object9 No sync wait | SIGNAL_OUT | RW | 0...4294967295
153 | O11 | OBJ9 | Object9 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
153 | O12 | OBJ9 | Object9 No sync fail | SIGNAL_OUT | RW | 0...4294967295
153 | O13 | OBJ9 | Object9 Open timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O14 | OBJ9 | Object9 Close timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O15 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O16 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O17 | OBJ9 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
153 | S11 | OBJ9 | EventMaskLo | UINT32 | RW | 0...4294967295
153 | S12 | OBJ9 | EventMaskHi | UINT32 | RW | 0...4294967295
153 | I4 | OBJ9 | Newest Register | UINT32 | R | 0...12
153 | I5 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I6 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I7 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I8 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I9 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I10 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I11 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I12 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I13 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I14 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I15 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I16 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I17 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I18 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I19 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I20 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I21 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I22 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I23 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I24 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I25 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I26 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I27 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I28 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I29 | OBJ9 | Open requests | UINT32 | R | 0...4294967295
153 | I30 | OBJ9 | Close requests | UINT32 | R | 0...4294967295
153 | I31 | OBJ9 | Open requests failed | UINT32 | R | 0...4294967295
153 | I32 | OBJ9 | Close requests failed | UINT32 | R | 0...4294967295
153 | S13 | OBJ9 | Clear statistics | UINT32 | W | 0=-;1=Clear
154 | S1 | OBJ10 | Object10 mode | UINT32 | RW | 0=Disabled;1=Activated
154 | I1 | OBJ10 | Object10 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I2 | OBJ10 | Object10 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
154 | I3 | OBJ10 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | S2 | OBJ10 | Breaker traverse time | FLOAT | RW | 0.02...500
154 | S3 | OBJ10 | WD Cart traverse time | FLOAT | RW | 0.02...500
154 | S4 | OBJ10 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
154 | S5 | OBJ10 | Sync wait timeout | FLOAT | RW | 0.02...500
154 | S6 | OBJ10 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
154 | S7 | OBJ10 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
154 | S8 | OBJ10 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
154 | S9 | OBJ10 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
154 | S10 | OBJ10 | Control Termination Timeout | FLOAT | RW | 0.02...500
154 | O1 | OBJ10 | Object10 Status Open | SIGNAL_OUT | RW | 0...4294967295
154 | O2 | OBJ10 | Object10 Status Closed | SIGNAL_OUT | RW | 0...4294967295
154 | O3 | OBJ10 | Object10 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
154 | O4 | OBJ10 | Object10 Status Bad | SIGNAL_OUT | RW | 0...4294967295
154 | O5 | OBJ10 | Object10 Open Command | SIGNAL_OUT | RW | 0...4294967295
154 | O6 | OBJ10 | Object10 Close Command | SIGNAL_OUT | RW | 0...4294967295
154 | O7 | OBJ10 | Object10 Open Request | SIGNAL_OUT | RW | 0...4294967295
154 | O8 | OBJ10 | Object10 Close Request | SIGNAL_OUT | RW | 0...4294967295
154 | O9 | OBJ10 | Object10 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
154 | O10 | OBJ10 | Object10 No sync wait | SIGNAL_OUT | RW | 0...4294967295
154 | O11 | OBJ10 | Object10 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
154 | O12 | OBJ10 | Object10 No sync fail | SIGNAL_OUT | RW | 0...4294967295
154 | O13 | OBJ10 | Object10 Open timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O14 | OBJ10 | Object10 Close timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O15 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O16 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O17 | OBJ10 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
154 | S11 | OBJ10 | EventMaskLo | UINT32 | RW | 0...4294967295
154 | S12 | OBJ10 | EventMaskHi | UINT32 | RW | 0...4294967295
154 | I4 | OBJ10 | Newest Register | UINT32 | R | 0...12
154 | I5 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I6 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I7 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I8 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I9 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I10 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I11 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I12 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I13 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I14 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I15 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I16 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I17 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I18 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I19 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I20 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I21 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I22 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I23 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I24 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I25 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I26 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I27 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I28 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I29 | OBJ10 | Open requests | UINT32 | R | 0...4294967295
154 | I30 | OBJ10 | Close requests | UINT32 | R | 0...4294967295
154 | I31 | OBJ10 | Open requests failed | UINT32 | R | 0...4294967295
154 | I32 | OBJ10 | Close requests failed | UINT32 | R | 0...4294967295
154 | S13 | OBJ10 | Clear statistics | UINT32 | W | 0=-;1=Clear
104 | S1 | CIN1 | Indicator 1 mode | UINT32 | RW | 0=Disabled;1=Activated
104 | S2 | CIN1 | Ind.1 traverse time | FLOAT | RW | 0.02...500
104 | I1 | CIN1 | Ind.1 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
105 | S1 | CIN2 | Indicator 2 mode | UINT32 | RW | 0=Disabled;1=Activated
105 | S2 | CIN2 | Ind.2 traverse time | FLOAT | RW | 0.02...500
105 | I1 | CIN2 | Ind.2 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
106 | S1 | CIN3 | Indicator 3 mode | UINT32 | RW | 0=Disabled;1=Activated
106 | S2 | CIN3 | Ind.3 traverse time | FLOAT | RW | 0.02...500
106 | I1 | CIN3 | Ind.3 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
107 | S1 | CIN4 | Indicator 4 mode | UINT32 | RW | 0=Disabled;1=Activated
107 | S2 | CIN4 | Ind.4 traverse time | FLOAT | RW | 0.02...500
107 | I1 | CIN4 | Ind.4 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
108 | S1 | CIN5 | Indicator 5 mode | UINT32 | RW | 0=Disabled;1=Activated
108 | S2 | CIN5 | Ind.5 traverse time | FLOAT | RW | 0.02...500
108 | I1 | CIN5 | Ind.5 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
63 | S1 | AR1 | Auto-recloser [79] Mode | UINT32 | RW | 0=Disabled;1=Activated
63 | V1 | AR1 | AR Status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear
63 | V2 | AR1 | Timer active | UINT32 | R | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
63 | I1 | AR1 | AR Timer value | FLOAT | R | 0...1800
63 | I2 | AR1 | AR Started | UINT32 | R | 0...4294967295
63 | I3 | AR1 | Shot 1 Started | UINT32 | R | 0...4294967295
63 | I4 | AR1 | Shot 2 Started | UINT32 | R | 0...4294967295
63 | I5 | AR1 | Shot 3 Started | UINT32 | R | 0...4294967295
63 | I6 | AR1 | Shot 4 Started | UINT32 | R | 0...4294967295
63 | I7 | AR1 | Shot 5 Started | UINT32 | R | 0...4294967295
63 | I8 | AR1 | Shot 1 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I9 | AR1 | Shot 2 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I10 | AR1 | Shot 3 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I11 | AR1 | Shot 4 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I12 | AR1 | Shot 5 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I13 | AR1 | Shot 1 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I14 | AR1 | Shot 2 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I15 | AR1 | Shot 3 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I16 | AR1 | Shot 4 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I17 | AR1 | Shot 5 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I18 | AR1 | Shot 1 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I19 | AR1 | Shot 2 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I20 | AR1 | Shot 3 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I21 | AR1 | Shot 4 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I22 | AR1 | Shot 5 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I23 | AR1 | Shot 1 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I24 | AR1 | Shot 2 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I25 | AR1 | Shot 3 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I26 | AR1 | Shot 4 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I27 | AR1 | Shot 5 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I28 | AR1 | Shot 1 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I29 | AR1 | Shot 2 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I30 | AR1 | Shot 3 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I31 | AR1 | Shot 4 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I32 | AR1 | Shot 5 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I33 | AR1 | Shots failed | UINT32 | R | 0...4294967295
63 | I34 | AR1 | Shots cleared | UINT32 | R | 0...4294967295
63 | I35 | AR1 | Final trips | UINT32 | R | 0...4294967295
63 | S2 | AR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
63 | S3 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S4 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S5 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S6 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S7 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S8 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S9 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S10 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S11 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S12 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S13 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S14 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S15 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S16 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S17 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S18 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S19 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S20 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S21 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S22 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S23 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S24 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S25 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S26 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S27 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S28 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S29 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S30 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S31 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S32 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S33 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S34 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S35 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S36 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S37 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S38 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S39 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S40 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S41 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S42 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S43 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S44 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S45 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S46 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S47 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S48 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S49 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S50 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S51 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S52 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S53 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S54 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S55 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S56 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S57 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S58 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S59 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S60 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S61 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S62 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S63 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S64 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S65 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S66 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S67 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S68 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S69 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S70 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S71 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S72 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S73 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S74 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S75 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S76 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S77 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S78 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S79 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S80 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S81 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S82 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S83 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S84 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S85 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S86 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S87 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S88 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S89 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S90 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S91 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S92 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S93 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S94 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S95 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S96 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S97 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S98 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S99 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S100 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S101 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S102 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S103 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S104 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S105 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S106 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S107 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S108 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S109 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S110 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S111 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S112 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S113 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S114 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S115 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S116 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S117 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S118 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S119 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S120 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S121 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S122 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S123 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S124 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S125 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S126 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S127 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S128 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S129 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S130 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S131 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S132 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S133 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S134 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S135 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S136 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S137 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S138 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S139 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S140 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S141 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S142 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S143 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S144 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S145 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S146 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S147 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S148 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S149 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S150 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S151 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S152 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S153 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S154 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S155 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S156 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S157 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S158 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S159 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S160 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S161 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S162 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S163 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S164 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S165 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S166 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S167 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S168 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S169 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S170 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S171 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S172 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S173 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S174 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S175 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S176 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S177 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S178 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S179 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S180 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S181 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S182 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S183 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S184 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S185 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S186 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S187 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S188 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S189 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S190 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S191 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S192 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S193 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S194 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S195 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S196 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S197 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S198 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S199 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S200 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S201 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S202 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S203 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S204 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S205 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S206 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S207 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S208 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S209 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S210 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S211 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S212 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S213 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S214 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S215 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S216 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S217 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S218 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S219 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S220 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S221 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S222 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S223 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S224 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S225 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S226 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S227 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S228 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S229 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S230 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S231 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S232 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S233 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S234 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S235 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S236 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S237 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S238 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S239 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S240 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S241 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S242 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S243 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S244 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S245 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S246 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S247 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S248 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S249 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S250 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S251 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S252 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S253 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S254 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S255 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S256 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S257 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S258 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S259 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S260 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S261 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S262 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S263 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S264 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S265 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S266 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S267 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S268 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S269 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S270 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S271 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S272 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S273 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S274 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S275 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S276 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S277 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S278 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S279 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S280 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S281 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S282 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S283 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S284 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S285 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S286 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S287 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S288 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S289 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S290 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S291 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S292 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S293 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S294 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S295 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S296 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S297 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S298 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S299 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S300 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S301 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S302 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S303 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S304 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S305 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S306 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S307 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S308 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S309 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S310 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S311 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S312 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S313 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S314 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S315 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S316 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S317 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S318 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S319 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S320 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S321 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S322 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S323 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S324 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S325 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S326 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S327 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S328 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S329 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S330 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S331 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S332 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S333 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S334 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S335 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S336 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S337 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S338 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S339 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S340 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S341 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S342 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S343 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S344 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S345 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S346 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S347 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S348 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S349 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S350 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S351 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S352 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S353 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S354 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S355 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S356 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S357 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S358 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S359 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S360 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S361 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S362 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S363 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S364 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S365 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S366 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S367 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S368 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S369 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S370 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S371 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S372 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S373 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S374 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S375 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S376 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S377 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S378 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S379 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S380 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S381 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S382 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S383 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S384 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S385 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S386 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S387 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S388 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S389 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S390 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S391 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S392 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S393 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S394 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S395 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S396 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S397 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S398 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S399 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S400 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S401 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S402 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S403 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S404 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S405 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S406 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S407 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S408 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S409 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S410 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S411 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S412 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S413 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S414 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S415 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S416 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S417 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S418 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S419 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S420 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S421 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S422 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S423 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S424 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S425 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S426 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S427 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S428 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S429 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S430 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S431 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S432 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S433 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S434 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S435 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S436 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S437 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S438 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S439 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S440 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S441 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S442 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S443 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S444 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S445 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S446 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S447 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S448 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S449 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S450 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S451 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S452 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S453 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S454 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S455 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S456 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S457 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S458 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S459 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S460 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S461 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S462 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S463 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S464 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S465 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S466 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S467 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S468 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S469 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S470 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S471 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S472 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S473 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S474 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S475 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S476 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S477 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S478 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S479 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S480 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S481 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S482 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S483 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S484 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S485 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S486 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S487 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S488 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S489 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S490 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S491 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S492 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S493 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S494 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S495 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S496 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S497 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S498 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S499 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S500 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S501 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S502 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S503 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S504 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S505 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S506 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S507 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S508 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S509 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S510 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S511 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S512 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S513 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S514 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S515 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S516 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S517 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S518 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S519 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S520 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S521 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S522 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S523 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S524 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S525 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S526 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S527 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S528 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S529 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S530 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S531 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S532 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S533 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S534 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S535 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S536 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S537 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S538 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S539 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S540 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S541 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S542 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S543 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S544 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S545 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S546 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S547 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S548 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S549 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S550 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S551 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S552 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S553 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S554 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S555 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S556 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S557 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S558 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S559 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S560 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S561 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S562 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S563 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S564 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S565 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S566 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S567 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S568 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S569 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S570 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S571 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S572 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S573 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S574 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S575 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S576 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S577 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S578 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S579 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S580 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S581 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S582 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S583 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S584 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S585 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S586 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S587 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S588 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S589 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S590 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S591 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S592 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S593 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S594 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S595 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S596 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S597 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S598 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S599 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S600 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S601 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S602 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S603 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S604 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S605 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S606 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S607 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S608 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S609 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S610 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S611 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S612 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S613 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S614 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S615 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S616 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S617 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S618 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S619 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S620 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S621 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S622 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S623 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S624 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S625 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S626 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S627 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S628 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S629 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S630 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S631 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S632 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S633 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S634 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S635 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S636 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S637 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S638 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S639 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S640 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S641 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S642 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S643 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S644 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S645 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S646 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S647 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S648 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S649 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S650 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S651 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S652 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S653 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S654 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S655 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S656 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S657 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S658 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S659 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S660 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S661 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S662 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S663 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S664 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S665 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S666 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S667 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S668 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S669 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S670 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S671 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S672 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S673 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S674 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S675 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S676 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S677 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S678 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S679 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S680 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S681 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S682 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S683 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S684 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S685 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S686 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S687 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S688 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S689 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S690 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S691 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S692 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S693 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S694 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S695 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S696 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S697 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S698 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S699 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S700 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S701 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S702 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S703 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S704 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S705 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S706 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S707 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S708 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S709 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S710 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S711 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S712 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S713 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S714 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S715 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S716 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S717 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S718 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S719 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S720 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S721 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S722 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S723 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S724 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S725 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S726 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S727 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S728 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S729 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S730 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S731 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S732 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S733 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S734 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S735 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S736 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S737 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S738 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S739 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S740 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S741 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S742 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S743 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S744 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S745 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S746 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S747 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S748 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S749 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S750 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S751 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S752 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S753 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S754 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S755 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S756 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S757 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S758 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S759 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S760 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S761 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S762 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S763 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S764 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S765 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S766 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S767 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S768 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S769 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S770 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S771 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S772 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S773 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S774 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S775 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S776 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S777 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S778 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S779 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S780 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S781 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S782 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S783 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S784 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S785 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S786 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S787 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S788 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S789 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S790 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S791 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S792 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S793 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S794 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S795 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S796 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S797 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S798 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S799 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S800 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S801 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S802 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S803 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S804 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S805 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S806 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S807 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S808 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S809 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S810 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S811 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S812 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S813 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S814 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S815 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S816 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S817 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S818 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S819 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S820 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S821 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S822 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S823 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S824 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S825 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S826 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S827 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S828 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S829 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S830 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S831 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S832 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S833 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S834 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S835 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S836 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S837 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S838 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S839 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S840 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S841 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S842 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S843 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S844 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S845 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S846 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S847 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S848 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S849 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S850 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S851 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S852 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S853 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S854 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S855 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S856 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S857 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S858 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S859 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S860 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S861 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S862 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S863 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S864 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S865 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S866 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S867 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S868 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S869 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S870 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S871 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S872 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S873 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S874 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S875 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S876 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S877 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S878 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S879 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S880 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S881 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S882 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S883 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S884 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S885 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S886 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S887 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S888 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S889 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S890 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S891 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S892 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S893 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S894 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S895 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S896 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S897 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S898 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S899 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S900 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S901 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S902 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S903 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S904 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S905 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S906 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S907 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S908 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S909 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S910 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S911 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S912 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S913 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S914 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S915 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S916 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S917 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S918 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S919 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S920 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S921 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S922 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S923 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S924 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S925 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S926 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S927 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S928 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S929 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S930 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S931 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S932 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S933 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S934 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S935 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S936 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S937 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S938 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S939 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S940 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S941 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S942 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S943 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S944 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S945 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S946 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S947 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S948 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S949 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S950 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S951 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S952 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S953 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S954 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S955 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S956 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S957 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S958 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S959 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S960 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S961 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S962 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S963 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S964 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S965 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S966 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S967 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S968 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S969 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S970 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S971 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S972 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S973 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S974 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S975 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S976 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S977 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S978 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S979 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S980 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S981 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S982 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S983 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S984 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S985 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S986 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S987 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S988 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S989 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S990 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S991 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S992 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S993 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S994 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S995 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S996 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S997 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S998 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S999 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1000 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1001 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1002 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1003 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1004 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1005 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1006 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1007 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1008 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1009 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1010 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1011 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1012 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1013 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1014 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1015 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1016 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1017 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1018 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1019 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1020 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1021 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1022 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1023 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1024 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1025 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1026 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1027 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1028 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1029 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1030 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1031 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1032 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1033 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1034 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1035 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1036 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1037 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1038 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1039 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1040 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1041 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1042 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1043 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1044 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1045 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1046 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1047 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1048 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1049 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1050 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1051 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1052 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1053 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1054 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1055 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1056 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1057 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1058 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1059 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1060 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1061 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1062 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1063 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1064 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1065 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1066 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1067 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1068 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1069 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1070 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1071 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1072 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1073 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1074 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1075 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1076 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1077 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1078 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1079 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1080 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1081 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1082 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1083 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1084 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1085 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1086 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1087 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1088 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1089 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1090 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1091 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1092 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1093 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1094 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1095 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1096 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1097 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1098 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1099 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1100 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1101 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1102 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1103 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1104 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1105 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1106 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1107 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1108 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1109 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1110 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1111 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1112 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1113 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1114 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1115 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1116 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1117 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1118 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1119 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1120 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1121 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1122 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1123 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1124 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1125 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1126 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1127 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1128 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1129 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1130 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1131 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1132 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1133 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1134 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1135 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1136 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1137 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1138 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1139 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1140 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1141 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1142 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1143 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1144 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1145 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1146 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1147 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1148 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1149 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1150 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1151 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1152 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1153 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1154 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1155 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1156 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1157 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1158 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1159 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1160 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1161 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1162 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1163 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1164 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1165 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1166 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1167 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1168 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1169 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1170 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1171 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1172 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1173 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1174 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1175 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1176 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1177 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1178 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1179 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1180 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1181 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1182 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1183 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1184 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1185 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1186 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1187 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1188 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1189 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1190 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1191 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1192 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1193 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1194 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1195 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1196 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1197 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1198 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1199 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1200 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1201 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1202 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1203 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1204 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1205 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1206 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1207 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1208 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1209 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1210 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1211 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1212 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1213 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1214 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1215 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1216 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1217 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1218 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1219 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1220 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1221 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1222 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1223 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1224 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1225 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1226 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1227 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1228 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1229 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1230 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1231 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1232 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1233 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1234 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1235 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1236 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1237 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1238 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1239 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1240 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1241 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1242 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1243 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1244 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1245 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1246 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1247 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1248 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1249 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1250 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | O1 | AR1 | AR On | SIGNAL_OUT | RW | 0...4294967295
63 | O2 | AR1 | AR Off | SIGNAL_OUT | RW | 0...4294967295
63 | O3 | AR1 | AR In Progress | SIGNAL_OUT | RW | 0...4294967295
63 | O4 | AR1 | AR1 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O5 | AR1 | AR2 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O6 | AR1 | AR3 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O7 | AR1 | AR4 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O8 | AR1 | AR5 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O9 | AR1 | AR Running | SIGNAL_OUT | RW | 0...4294967295
63 | O10 | AR1 | AR Shot 1 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O11 | AR1 | AR Shot 2 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O12 | AR1 | AR Shot 3 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O13 | AR1 | AR Shot 4 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O14 | AR1 | AR Shot 5 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O15 | AR1 | AR Sequence finished | SIGNAL_OUT | RW | 0...4294967295
63 | O16 | AR1 | AR Final Trip | SIGNAL_OUT | RW | 0...4294967295
63 | O17 | AR1 | Dead time on | SIGNAL_OUT | RW | 0...4294967295
63 | O18 | AR1 | ARC time on | SIGNAL_OUT | RW | 0...4294967295
63 | O19 | AR1 | Reclaim time on | SIGNAL_OUT | RW | 0...4294967295
63 | O20 | AR1 | AR Ready | SIGNAL_OUT | RW | 0...4294967295
63 | O21 | AR1 | AR Lockout after successfull sequence | SIGNAL_OUT | RW | 0...4294967295
63 | O22 | AR1 | AR Operation Inhibit | SIGNAL_OUT | RW | 0...4294967295
63 | O23 | AR1 | AR Locked | SIGNAL_OUT | RW | 0...4294967295
63 | I36 | AR1 | Newest Register | UINT32 | R | 0...12
63 | I37 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I38 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I39 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I40 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I41 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I42 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I43 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I44 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I45 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I46 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I47 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I48 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I49 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I50 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I51 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I52 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I53 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I54 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I55 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I56 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I57 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I58 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I59 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I60 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I61 | AR1 | Active time | FLOAT | R | 0...1800
63 | I62 | AR1 | Active time | FLOAT | R | 0...1800
63 | I63 | AR1 | Active time | FLOAT | R | 0...1800
63 | I64 | AR1 | Active time | FLOAT | R | 0...1800
63 | I65 | AR1 | Active time | FLOAT | R | 0...1800
63 | I66 | AR1 | Active time | FLOAT | R | 0...1800
63 | I67 | AR1 | Active time | FLOAT | R | 0...1800
63 | I68 | AR1 | Active time | FLOAT | R | 0...1800
63 | I69 | AR1 | Active time | FLOAT | R | 0...1800
63 | I70 | AR1 | Active time | FLOAT | R | 0...1800
63 | I71 | AR1 | Active time | FLOAT | R | 0...1800
63 | I72 | AR1 | Active time | FLOAT | R | 0...1800
63 | S1251 | AR1 | EventMaskLo | UINT32 | RW | 0...4294967295
63 | S1252 | AR1 | EventMaskHi | UINT32 | RW | 0...4294967295
115 | S1 | VRG1 | Vreg [AVR/90] mode | UINT32 | RW | 0=Disabled;1=Activated
115 | V1 | VRG1 | Vreg settings condition | UINT32 | R | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok
115 | V2 | VRG1 | Vreg condition | UINT32 | R | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on
115 | V3 | VRG1 | Vreg timer active | UINT32 | R | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
115 | I1 | VRG1 | Time left to operation | FLOAT | R | 0...1800
115 | I2 | VRG1 | Voltage now | FLOAT | R | 0...140
115 | I3 | VRG1 | Voltage difference to set target | FLOAT | R | -140...140
115 | I4 | VRG1 | Voltage set now to | FLOAT | R | -50000...50000
115 | I5 | VRG1 | Tap location now (- 0 +) | FLOAT | R | -30...30
115 | I6 | VRG1 | Absolute tap location | FLOAT | R | 0...50
115 | V4 | VRG1 | Tap changer on high border | UINT32 | R | 0=No;1=Yes
115 | V5 | VRG1 | Tap changer on low border | UINT32 | R | 0=No;1=Yes
115 | I7 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual (loc&rem)
115 | V6 | VRG1 | Remote tap control input | UINT32 | RW | 0=Stop;1=Lower;2=Higher
115 | S2 | VRG1 | Control pulselength max | FLOAT | RW | 0...1800
115 | S3 | VRG1 | Control pulselength min | FLOAT | RW | 0...1800
115 | S4 | VRG1 | Min time between pulses | FLOAT | RW | 0...1800
115 | V7 | VRG1 | Tap position ind. Setting | UINT32 | R | 0=Not selected;1=Set Ok;2=Wrong setting;3=Meas.Quality Fault.
115 | I8 | VRG1 | AVR rised voltage | UINT32 | R | 0...4294967295
115 | I9 | VRG1 | AVR reduced voltage | UINT32 | R | 0...4294967295
115 | I10 | VRG1 | AVR control blocked | UINT32 | R | 0...4294967295
115 | I11 | VRG1 | AVR Undervoltage blocked | UINT32 | R | 0...4294967295
115 | I12 | VRG1 | AVR Overcurrent blocked | UINT32 | R | 0...4294967295
115 | S5 | VRG1 | Clear statistics | UINT32 | W | 0=-;1=Clear
115 | S6 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S7 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S8 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S9 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S10 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S11 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S12 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S13 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S14 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S15 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S16 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S17 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S18 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S19 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S20 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S21 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S22 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S23 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S24 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S25 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S26 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S27 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S28 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S29 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S30 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S31 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S32 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S33 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S34 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S35 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S36 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S37 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S38 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S39 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S40 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S41 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S42 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S43 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S44 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S45 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S46 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S47 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S48 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S49 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S50 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S51 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S52 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S53 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S54 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S55 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S56 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S57 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S58 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S59 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S60 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S61 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S62 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S63 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S64 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S65 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S66 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S67 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S68 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S69 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S70 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S71 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S72 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S73 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S74 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S75 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S76 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S77 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S78 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S79 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S80 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S81 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S82 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S83 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S84 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S85 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S86 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S87 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S88 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S89 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S90 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S91 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S92 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S93 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S94 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S95 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S96 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S97 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S98 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S99 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S100 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S101 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S102 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S103 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S104 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S105 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S106 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S107 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S108 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S109 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S110 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S111 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S112 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S113 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S114 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S115 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S116 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S117 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S118 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S119 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S120 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S121 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S122 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S123 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S124 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S125 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S126 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S127 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S128 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S129 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S130 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S131 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S132 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S133 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | I13 | VRG1 | AVR to Manual control | SIGNAL_IN | RW | 0...4294967295
115 | O1 | VRG1 | AVR Raise Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O2 | VRG1 | AVR Lower Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O3 | VRG1 | AVR In manual control | SIGNAL_OUT | RW | 0...4294967295
115 | O4 | VRG1 | AVR U>/< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O5 | VRG1 | AVR U>>/<< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O6 | VRG1 | AVR Outputs blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O7 | VRG1 | AVR Operation blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O8 | VRG1 | AVR Control wait on | SIGNAL_OUT | RW | 0...4294967295
115 | O9 | VRG1 | AVR U< block active | SIGNAL_OUT | RW | 0...4294967295
115 | O10 | VRG1 | AVR I> block active | SIGNAL_OUT | RW | 0...4294967295
115 | O11 | VRG1 | AVR Tap in highlimit | SIGNAL_OUT | RW | 0...4294967295
115 | O12 | VRG1 | AVR Tap in lowlimit | SIGNAL_OUT | RW | 0...4294967295
115 | I14 | VRG1 | Newest Register | UINT32 | R | 0...12
115 | I15 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I16 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I17 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I18 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I19 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I20 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I21 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I22 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I23 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I24 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I25 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I26 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I27 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I28 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I29 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I30 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I31 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I32 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I33 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I34 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I35 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I36 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I37 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I38 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I39 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I40 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I41 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I42 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I43 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I44 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I45 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I46 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I47 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I48 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I49 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I50 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I51 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I52 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I53 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I54 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I55 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I56 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I57 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I58 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I59 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I60 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I61 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I62 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | S134 | VRG1 | EventMaskLo | UINT32 | RW | 0...4294967295
115 | S135 | VRG1 | EventMaskHi | UINT32 | RW | 0...4294967295
135 | S1 | EMON1 | Monitor mode | UINT32 | RW | 0=Disabled;1=Activated
135 | S2 | EMON1 | I> (50) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V1 | EMON1 | I> (50) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S3 | EMON1 | I0> (50N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S4 | EMON1 | I0> (50N) I0input | UINT32 | RW | 0=I01;1=I02;2=I0Calc
135 | V2 | EMON1 | I0> (50N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S5 | EMON1 | Idir> (67) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V3 | EMON1 | Idir> (67) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S6 | EMON1 | I0dir> (67N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S7 | EMON1 | I0dir> (67N) I0input | UINT32 | RW | 0=I01;1=I02
135 | S8 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=select
135 | S9 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V4 | EMON1 | I0dir> (67N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S10 | EMON1 | I0Int> (67NT) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S11 | EMON1 | I0Int> (67NT) I0input | UINT32 | RW | 0=I01;1=I02
135 | V5 | EMON1 | I0Int> (67NT) Monitor condition | UINT32 | R | 0=Normal;1=FLT FW;2=FLT REV
135 | S12 | EMON1 | U< (27) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S13 | EMON1 | U< (27) Measured magnitude | UINT32 | RW | 0=P-P Voltages;1=P-E Voltages
135 | S14 | EMON1 | U< (27) Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
135 | V6 | EMON1 | U< (27) Monitor condition | UINT32 | R | 0=Normal;1=Undervoltage;2=No voltage
135 | S15 | EMON1 | U0> (59N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S16 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=Select
135 | S17 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V7 | EMON1 | U0> (59N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S18 | EMON1 | FL (21FL) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V8 | EMON1 | FL (21FL) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | I1 | EMON1 | I> (50) Alarms | UINT32 | R | 0...4294967295
135 | I2 | EMON1 | I0> (50N) Alarms | UINT32 | R | 0...4294967295
135 | I3 | EMON1 | Idir> (67) Alarms | UINT32 | R | 0...4294967295
135 | I4 | EMON1 | I0dir> (67N) Alarms | UINT32 | R | 0...4294967295
135 | I5 | EMON1 | I0Int> (67) Alarms FWD | UINT32 | R | 0...4294967295
135 | I6 | EMON1 | I0Int> (67) Alarms REV | UINT32 | R | 0...4294967295
135 | I7 | EMON1 | U< (27) Undervoltage Alarms | UINT32 | R | 0...4294967295
135 | I8 | EMON1 | U< (27) No voltage Alarms | UINT32 | R | 0...4294967295
135 | I9 | EMON1 | U0> (59N) Alarms | UINT32 | R | 0...4294967295
135 | I10 | EMON1 | FL (21FL) Triggered | UINT32 | R | 0...4294967295
135 | S19 | EMON1 | Clear statistics | UINT32 | W | 0=-;1=Clear
135 | S20 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S21 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S22 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S23 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S24 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S25 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S26 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S27 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S28 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S29 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S30 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S31 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S32 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S33 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S34 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S35 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S36 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S37 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S38 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S39 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S40 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S41 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S42 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S43 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S44 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S45 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S46 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S47 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S48 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S49 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S50 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S51 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S52 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S53 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S54 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S55 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S56 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S57 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S58 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S59 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S60 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S61 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S62 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S63 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S64 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S65 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S66 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S67 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S68 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S69 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S70 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S71 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S72 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S73 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S74 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S75 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S76 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S77 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S78 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S79 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S80 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S81 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S82 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S83 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S84 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S85 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S86 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S87 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S88 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S89 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S90 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S91 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S92 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S93 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S94 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S95 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S96 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S97 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S98 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S99 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S100 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S101 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S102 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S103 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S104 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S105 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S106 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S107 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S108 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S109 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S110 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S111 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S112 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S113 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S114 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S115 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S116 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S117 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S118 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S119 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S120 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S121 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S122 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S123 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S124 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S125 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S126 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S127 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S128 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S129 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S130 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S131 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S132 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S133 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S134 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S135 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S136 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S137 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S138 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S139 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S140 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S141 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S142 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S143 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S144 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S145 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S146 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S147 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S148 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S149 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S150 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S151 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S152 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S153 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S154 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S155 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S156 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S157 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S158 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S159 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S160 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S161 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S162 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S163 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S164 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S165 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S166 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S167 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S168 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S169 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S170 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S171 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S172 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S173 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S174 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S175 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S176 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S177 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S178 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S179 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S180 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S181 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S182 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S183 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S184 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S185 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S186 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S187 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S188 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S189 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S190 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S191 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S192 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S193 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S194 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S195 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S196 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S197 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S198 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S199 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S200 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S201 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S202 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S203 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S204 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S205 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S206 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S207 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S208 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S209 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S210 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S211 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S212 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S213 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S214 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S215 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S216 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S217 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S218 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S219 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S220 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S221 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S222 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S223 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S224 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S225 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S226 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S227 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | O1 | EMON1 | I> (50) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O2 | EMON1 | I0> (50N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O3 | EMON1 | Idir> (67) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O4 | EMON1 | I0dir> (67N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O5 | EMON1 | I0int> (67NT) Alarm FWD | SIGNAL_OUT | RW | 0...4294967295
135 | O6 | EMON1 | I0int> (67NT) Alarm REV | SIGNAL_OUT | RW | 0...4294967295
135 | O7 | EMON1 | U< (27) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O8 | EMON1 | U< (27) No voltage | SIGNAL_OUT | RW | 0...4294967295
135 | O9 | EMON1 | U0> (59N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O10 | EMON1 | FL (21FL) Triggered | SIGNAL_OUT | RW | 0...4294967295
135 | I11 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I12 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I13 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I14 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I15 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I16 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I17 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I18 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I19 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I20 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I21 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I22 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I23 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I24 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I25 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I26 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I27 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I28 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I29 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I30 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I31 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I32 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I33 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I34 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I35 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I36 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I37 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I38 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I39 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I40 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I41 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I42 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I43 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I44 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I45 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I46 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I47 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I48 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I49 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I50 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I51 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I52 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I53 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I54 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I55 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I56 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I57 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I58 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I59 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I60 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I61 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I62 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I63 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I64 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I65 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I66 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I67 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I68 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I69 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I70 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I71 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I72 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I73 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I74 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I75 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I76 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I77 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I78 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I79 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I80 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I81 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I82 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I83 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I84 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I85 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I86 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I87 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I88 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I89 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I90 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I91 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I92 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I93 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I94 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I95 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I96 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I97 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I98 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I99 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I100 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I101 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I102 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I103 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I104 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I105 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I106 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I107 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I108 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I109 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I110 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I111 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I112 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I113 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I114 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I115 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I116 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I117 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I118 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I119 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I120 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I121 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I122 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I123 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I124 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I125 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I126 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I127 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I128 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I129 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I130 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I131 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I132 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I133 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I134 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I135 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I136 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I137 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I138 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I139 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I140 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I141 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I142 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I143 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I144 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I145 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I146 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I147 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I148 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I149 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I150 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I151 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I152 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I153 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I154 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I155 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I156 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I157 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I158 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I159 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I160 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I161 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I162 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I163 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I164 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I165 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I166 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I167 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I168 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I169 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I170 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I171 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I172 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I173 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I174 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I175 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I176 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I177 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I178 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I179 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I180 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I181 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I182 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I183 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I184 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I185 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I186 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I187 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I188 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I189 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I190 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I191 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I192 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I193 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I194 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I195 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I196 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I197 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I198 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I199 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I200 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I201 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I202 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I203 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I204 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I205 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I206 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I207 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I208 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I209 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I210 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I211 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I212 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I213 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I214 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I215 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I216 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I217 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I218 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I219 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I220 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I221 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I222 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I223 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I224 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I225 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I226 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I227 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I228 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I229 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I230 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I231 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I232 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I233 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I234 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I235 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I236 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I237 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I238 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I239 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I240 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I241 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I242 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I243 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I244 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I245 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I246 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I247 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I248 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I249 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I250 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I251 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I252 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I253 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I254 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I255 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I256 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I257 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I258 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | S228 | EMON1 | EventMaskLo | UINT32 | RW | 0...4294967295
135 | S229 | EMON1 | EventMaskHi | UINT32 | RW | 0...4294967295
143 | O1 | ALARM | ALARM 1 | SIGNAL_IN | RW | 0...4294967295
143 | O2 | ALARM | ALARM 2 | SIGNAL_IN | RW | 0...4294967295
143 | O3 | ALARM | ALARM 3 | SIGNAL_IN | RW | 0...4294967295
143 | O4 | ALARM | ALARM 4 | SIGNAL_IN | RW | 0...4294967295
143 | O5 | ALARM | ALARM 5 | SIGNAL_IN | RW | 0...4294967295
143 | O6 | ALARM | ALARM 6 | SIGNAL_IN | RW | 0...4294967295
143 | O7 | ALARM | ALARM 7 | SIGNAL_IN | RW | 0...4294967295
143 | O8 | ALARM | ALARM 8 | SIGNAL_IN | RW | 0...4294967295
143 | O9 | ALARM | ALARM 9 | SIGNAL_IN | RW | 0...4294967295
143 | O10 | ALARM | ALARM 10 | SIGNAL_IN | RW | 0...4294967295
143 | O11 | ALARM | ALARM 11 | SIGNAL_IN | RW | 0...4294967295
143 | O12 | ALARM | ALARM 12 | SIGNAL_IN | RW | 0...4294967295
143 | O13 | ALARM | ALARM 13 | SIGNAL_IN | RW | 0...4294967295
143 | O14 | ALARM | ALARM 14 | SIGNAL_IN | RW | 0...4294967295
143 | O15 | ALARM | ALARM 15 | SIGNAL_IN | RW | 0...4294967295
143 | O16 | ALARM | ALARM 16 | SIGNAL_IN | RW | 0...4294967295
143 | O17 | ALARM | ALARM 17 | SIGNAL_IN | RW | 0...4294967295
143 | O18 | ALARM | ALARM 18 | SIGNAL_IN | RW | 0...4294967295
143 | O19 | ALARM | ALARM 19 | SIGNAL_IN | RW | 0...4294967295
143 | O20 | ALARM | ALARM 20 | SIGNAL_IN | RW | 0...4294967295
143 | O21 | ALARM | ALARM 21 | SIGNAL_IN | RW | 0...4294967295
143 | O22 | ALARM | ALARM 22 | SIGNAL_IN | RW | 0...4294967295
143 | O23 | ALARM | ALARM 23 | SIGNAL_IN | RW | 0...4294967295
143 | O24 | ALARM | ALARM 24 | SIGNAL_IN | RW | 0...4294967295
143 | O25 | ALARM | ALARM 25 | SIGNAL_IN | RW | 0...4294967295
143 | O26 | ALARM | ALARM 26 | SIGNAL_IN | RW | 0...4294967295
143 | O27 | ALARM | ALARM 27 | SIGNAL_IN | RW | 0...4294967295
143 | O28 | ALARM | ALARM 28 | SIGNAL_IN | RW | 0...4294967295
143 | O29 | ALARM | ALARM 29 | SIGNAL_IN | RW | 0...4294967295
143 | O30 | ALARM | ALARM 30 | SIGNAL_IN | RW | 0...4294967295
143 | O31 | ALARM | ALARM 31 | SIGNAL_IN | RW | 0...4294967295
143 | O32 | ALARM | ALARM 32 | SIGNAL_IN | RW | 0...4294967295
143 | O33 | ALARM | ALARM 33 | SIGNAL_IN | RW | 0...4294967295
143 | O34 | ALARM | ALARM 34 | SIGNAL_IN | RW | 0...4294967295
143 | O35 | ALARM | ALARM 35 | SIGNAL_IN | RW | 0...4294967295
143 | O36 | ALARM | ALARM 36 | SIGNAL_IN | RW | 0...4294967295
143 | O37 | ALARM | ALARM 37 | SIGNAL_IN | RW | 0...4294967295
143 | O38 | ALARM | ALARM 38 | SIGNAL_IN | RW | 0...4294967295
143 | O39 | ALARM | ALARM 39 | SIGNAL_IN | RW | 0...4294967295
143 | O40 | ALARM | ALARM 40 | SIGNAL_IN | RW | 0...4294967295
143 | O41 | ALARM | ALARM 41 | SIGNAL_IN | RW | 0...4294967295
143 | O42 | ALARM | ALARM 42 | SIGNAL_IN | RW | 0...4294967295
143 | O43 | ALARM | ALARM 43 | SIGNAL_IN | RW | 0...4294967295
143 | O44 | ALARM | ALARM 44 | SIGNAL_IN | RW | 0...4294967295
143 | O45 | ALARM | ALARM 45 | SIGNAL_IN | RW | 0...4294967295
143 | O46 | ALARM | ALARM 46 | SIGNAL_IN | RW | 0...4294967295
143 | O47 | ALARM | ALARM 47 | SIGNAL_IN | RW | 0...4294967295
143 | O48 | ALARM | ALARM 48 | SIGNAL_IN | RW | 0...4294967295
143 | O49 | ALARM | ALARM 49 | SIGNAL_IN | RW | 0...4294967295
143 | O50 | ALARM | ALARM 50 | SIGNAL_IN | RW | 0...4294967295
143 | O51 | ALARM | ALARM 51 | SIGNAL_IN | RW | 0...4294967295
143 | O52 | ALARM | ALARM 52 | SIGNAL_IN | RW | 0...4294967295
143 | O53 | ALARM | ALARM 53 | SIGNAL_IN | RW | 0...4294967295
143 | O54 | ALARM | ALARM 54 | SIGNAL_IN | RW | 0...4294967295
143 | O55 | ALARM | ALARM 55 | SIGNAL_IN | RW | 0...4294967295
143 | O56 | ALARM | ALARM 56 | SIGNAL_IN | RW | 0...4294967295
143 | O57 | ALARM | ALARM 57 | SIGNAL_IN | RW | 0...4294967295
143 | O58 | ALARM | ALARM 58 | SIGNAL_IN | RW | 0...4294967295
143 | O59 | ALARM | ALARM 59 | SIGNAL_IN | RW | 0...4294967295
143 | O60 | ALARM | ALARM 60 | SIGNAL_IN | RW | 0...4294967295
143 | O61 | ALARM | ALARM 61 | SIGNAL_IN | RW | 0...4294967295
143 | O62 | ALARM | ALARM 62 | SIGNAL_IN | RW | 0...4294967295
143 | O63 | ALARM | ALARM 63 | SIGNAL_IN | RW | 0...4294967295
143 | O64 | ALARM | ALARM 64 | SIGNAL_IN | RW | 0...4294967295
159 | S1 | ALARM1 | EventMaskLo | UINT32 | RW | 0...4294967295
159 | S2 | ALARM1 | EventMaskHi | UINT32 | RW | 0...4294967295
160 | S1 | ALARM2 | EventMaskLo | UINT32 | RW | 0...4294967295
160 | S2 | ALARM2 | EventMaskHi | UINT32 | RW | 0...4294967295
162 | S1 | GSYN | Synchronizer mode | UINT32 | RW | 0=Disabled;1=Activated
162 | S2 | GSYN | Synchronizer reference voltage input | UINT32 | RW | 0=U4 Input;1=U3 Input
162 | S3 | GSYN | Voltage difference calculation mode | UINT32 | RW | 0=System is reference;1=U3/U4 Input is reference
162 | S4 | GSYN | Synchronizer voltage reference | UINT32 | RW | 0=UL12;1=UL23;2=UL31;3=UL1;4=UL2;5=UL3
162 | S5 | GSYN | Synchronizer measurement settings | UINT32 | R | 0=Meas.Conf.Incorrect;1=PP and PE voltages;2=PP Voltages;
162 | S6 | GSYN | Synchronizer status | UINT32 | R | 0=Conf.Error;1=Idle Ready;2=Synchronizing;3=Blocked
162 | S7 | GSYN | Force control signals on | UINT32 | RW | 0=None;1=Blocked On;2=Running On;3=Increase U On;4=Decrease U On;5=Increase F On;6=Decrease F On;7=CB Close On;8=LongSyncTime On
162 | S8 | GSYN | Synchronizing by | UINT32 | RW | 0=Autosynchronizer;1=Manual commands
162 | S9 | GSYN | Manual switching mode | UINT32 | RW | 0=Assisted synchroswitch;1=I know what I am doing
162 | S10 | GSYN | Synchroswitch status | UINT32 | R | 0=Standstill;1=Departing;2=Enclosing
162 | S11 | GSYN | Magnitude side A | FLOAT | R | 0.000...200.000
162 | S12 | GSYN | Magnitude side B | FLOAT | R | 0.000...200.000
162 | S13 | GSYN | Frequency side A | FLOAT | R | 0.000...75.000
162 | S14 | GSYN | Frequency side B | FLOAT | R | 0.000...75.000
162 | S15 | GSYN | Magnitude difference | FLOAT | R | -200...200
162 | S16 | GSYN | Frequency difference | FLOAT | R | -100...100
162 | S17 | GSYN | Angle difference | FLOAT | R | -360...360
162 | S18 | GSYN | Magnitude difference on closing BRK | FLOAT | R | -200...200
162 | S19 | GSYN | Frequency difference on closing BRK | FLOAT | R | -100...100
162 | S20 | GSYN | Angle difference on closing BRK | FLOAT | R | -360...360
162 | S21 | GSYN | Estimated BRK Closing time | FLOAT | R | 0...360
162 | S22 | GSYN | Networks rotating time | FLOAT | R | 0...360
162 | S23 | GSYN | Networks placement atm | FLOAT | R | -360...360
162 | S24 | GSYN | Synchronizing time left | FLOAT | R | 0...1800
162 | S25 | GSYN | Get measurement errors for fine tuning | UINT32 | RW | 0=-;1=Get errors
162 | S26 | GSYN | Magnitude difference fine tune | FLOAT | RW | -200...200
162 | S27 | GSYN | Frequency difference fine tune | FLOAT | RW | -100...100
162 | S28 | GSYN | Angle difference fine tune | FLOAT | RW | -360...360
162 | S29 | GSYN | Minimum voltage allowed for synchronizing | FLOAT | RW | 0...105
162 | S30 | GSYN | Maximum voltage allowed for synchronizing | FLOAT | RW | 0...200
162 | S31 | GSYN | Maximum zero voltage allowed for synchronizing (100% disabled) | FLOAT | RW | 0...100
162 | S32 | GSYN | Maximum allowed voltage difference | FLOAT | RW | 0.1...50
162 | S33 | GSYN | Maximum allowed overfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S34 | GSYN | Maximum allowed underfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S35 | GSYN | Max.Time for synchronizing | FLOAT | RW | 0...1800
162 | S36 | GSYN | Maximum allowed angular disposition to allow synchronizing | FLOAT | RW | 0.01...25
162 | S37 | GSYN | Adjustment for measurement inaccuracy or set of desired volt. offset | FLOAT | RW | -95...95
162 | S38 | GSYN | Adjustment for measurement inaccuracy or set of desired angular offset | FLOAT | RW | -60...60
162 | S39 | GSYN | Adjustment for measurement inaccuracy or set of desired freq. offset | FLOAT | RW | -0.5...2
162 | S40 | GSYN | Voltage adjustment slope | FLOAT | RW | 0...25
162 | S41 | GSYN | Volt. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S42 | GSYN | Volt. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S43 | GSYN | Volt. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S44 | GSYN | Freq. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S45 | GSYN | Freq. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S46 | GSYN | Freq. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S47 | GSYN | Maximum allowed voltage difference to start synchronizing | FLOAT | RW | 0...50
162 | S48 | GSYN | Integrator sum when voltage adjustment pulse is generated | FLOAT | RW | 0...50
162 | S49 | GSYN | Voltage adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S50 | GSYN | Frequency adjustment slope when increasing | FLOAT | RW | 0...10
162 | S51 | GSYN | Frequency adjustment slope when decreasing | FLOAT | RW | -10...0
162 | S52 | GSYN | Maximum allowed frequency difference to start synchronizing | FLOAT | RW | 0...25
162 | S53 | GSYN | Integrator sum when frequency adjustment pulse is generated | FLOAT | RW | 0...50
162 | S54 | GSYN | Frequency adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S55 | GSYN | Filter time for angle derivative | FLOAT | RW | 0...1800
162 | S56 | GSYN | Circuit breaker pre-closing adjustment constant | FLOAT | RW | 0...10
162 | S57 | GSYN | Circuit breaker pre-closing time incl auxiliary relays | FLOAT | RW | 0...1800
162 | S58 | GSYN | Lenght of circuit breaker closing pulse | FLOAT | RW | 0...1800
162 | I1 | GSYN | Start Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I2 | GSYN | Stop Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I3 | GSYN | Block and Interrupt Synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I4 | GSYN | Breaker Closed | SIGNAL_IN | RW | 0...4294967295
162 | I5 | GSYN | Manual increase voltage | SIGNAL_IN | RW | 0...4294967295
162 | I6 | GSYN | Manual decrease voltage | SIGNAL_IN | RW | 0...4294967295
162 | I7 | GSYN | Manual increase frequency | SIGNAL_IN | RW | 0...4294967295
162 | I8 | GSYN | Manual decrease frequency | SIGNAL_IN | RW | 0...4294967295
162 | I9 | GSYN | Manual Close Breaker | SIGNAL_IN | RW | 0...4294967295
162 | O1 | GSYN | GSYN Voltage Mag.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O2 | GSYN | GSYN Voltage Freq.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O3 | GSYN | GSYN Voltage Ang.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O4 | GSYN | GSYN Blocked | SIGNAL_OUT | RW | 0...4294967295
162 | O5 | GSYN | GSYN Running | SIGNAL_OUT | RW | 0...4294967295
162 | O6 | GSYN | GSYN Increase Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O7 | GSYN | GSYN Decrease Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O8 | GSYN | GSYN Increase Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O9 | GSYN | GSYN Decrease Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O10 | GSYN | GSYN Breaker Close Pulse | SIGNAL_OUT | RW | 0...4294967295
162 | O11 | GSYN | GSYN Long Sync Time | SIGNAL_OUT | RW | 0...4294967295
162 | O12 | GSYN | GSYN Nets Standstill | SIGNAL_OUT | RW | 0...4294967295
162 | O13 | GSYN | GSYN Nets Departing | SIGNAL_OUT | RW | 0...4294967295
162 | O14 | GSYN | GSYN Nets Enclosing | SIGNAL_OUT | RW | 0...4294967295
162 | S59 | GSYN | Control EventMaskLo | UINT32 | RW | 0...4294967295
162 | S60 | GSYN | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | S1 | VREC | Measurement value recorder mode | UINT32 | RW | 0=Disabled;1=Activated
163 | S2 | VREC | Scale current values to primary | UINT32 | RW | 0=No;1=Yes
163 | S3 | VREC | Record fault types (Overcurrrent & Voltage Over/Under) faults | UINT32 | RW | 0=No;1=Yes
163 | I1 | VREC | Trigger register to memory | SIGNAL_IN | RW | 0...4294967295
163 | I2 | VREC | Tripped stage | UINT32 | R | 0=-;1=I> Trip;2=I>> Trip;3=I>>> Trip;4=I>>>> Trip;5=IDir> Trip;6=IDir>> Trip;7=IDir>>> Trip;8=IDir>>>> Trip;9=U> Trip;10=U>> Trip;11=U>>> Trip;12=U>>>> Trip;13=U< Trip;14=U<< Trip;15=U<<< Trip;16=U<<<< Trip;17=I0> TRIP;18=I0>> Trip;19=I0>>> Trip;20=I0>>>> Trip;21=I0Dir> Trip;22=I0Dir>> Trip;23=I0Dir>>> Trip;24=I0Dir>>>> Trip;25=f> Trip;26=f>> Trip;27=f>>> Trip;28=f>>>> Trip;29=f< Trip;30=f<< Trip;31=f<<< Trip;32=f<<<< Trip;33=P> Trip;34=P< Trip;35=Prev> Trip;36=T> Trip;37=I2> Trip;38=I2>> Trip;39=I2>>> Trip;40=I2>>>> Trip;41=U1/2 > Trip;42=U1/2 >> Trip;43=U1/2 >>> Trip;44=U1/2 >>>> Trip;45=U0> Trip;46=U0>> Trip;47=U0>>> Trip;48=U0>>>> Trip
163 | I3 | VREC | Overcurrent fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;
163 | I4 | VREC | Voltage fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C;8=-;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I5 | VREC | VREC Magnitude 1 | FLOAT | R | 0...1800
163 | I6 | VREC | VREC Magnitude 2 | FLOAT | R | 0...1800
163 | I7 | VREC | VREC Magnitude 3 | FLOAT | R | 0...1800
163 | I8 | VREC | VREC Magnitude 4 | FLOAT | R | 0...1800
163 | I9 | VREC | VREC Magnitude 5 | FLOAT | R | 0...1800
163 | I10 | VREC | VREC Magnitude 6 | FLOAT | R | 0...1800
163 | I11 | VREC | VREC Magnitude 7 | FLOAT | R | 0...1800
163 | I12 | VREC | VREC Magnitude 8 | FLOAT | R | 0...1800
163 | I13 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I14 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I15 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I16 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I17 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I18 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I19 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I20 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I21 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I22 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I23 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I24 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295
135 | I177 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I178 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I179 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I180 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I181 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I182 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I183 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I184 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I185 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I186 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I187 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I188 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I189 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I190 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I191 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I192 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I193 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I194 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I195 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I196 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I197 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I198 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I199 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I200 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I201 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I202 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I203 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I204 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I205 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I206 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I207 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I208 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I209 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I210 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I211 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I212 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I213 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I214 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I215 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I216 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I217 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I218 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I219 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I220 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I221 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I222 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I223 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I224 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I225 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I226 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I227 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I228 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I229 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I230 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I231 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I232 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I233 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I234 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I235 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I236 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I237 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I238 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I239 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I240 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I241 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I242 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I243 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I244 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I245 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I246 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I247 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I248 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I249 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I250 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I251 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I252 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I253 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I254 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I255 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I256 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I257 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I258 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | S228 | EMON1 | EventMaskLo | UINT32 | RW | 0...4294967295
135 | S229 | EMON1 | EventMaskHi | UINT32 | RW | 0...4294967295
143 | O1 | ALARM | ALARM 1 | SIGNAL_IN | RW | 0...4294967295
143 | O2 | ALARM | ALARM 2 | SIGNAL_IN | RW | 0...4294967295
143 | O3 | ALARM | ALARM 3 | SIGNAL_IN | RW | 0...4294967295
143 | O4 | ALARM | ALARM 4 | SIGNAL_IN | RW | 0...4294967295
143 | O5 | ALARM | ALARM 5 | SIGNAL_IN | RW | 0...4294967295
143 | O6 | ALARM | ALARM 6 | SIGNAL_IN | RW | 0...4294967295
143 | O7 | ALARM | ALARM 7 | SIGNAL_IN | RW | 0...4294967295
143 | O8 | ALARM | ALARM 8 | SIGNAL_IN | RW | 0...4294967295
143 | O9 | ALARM | ALARM 9 | SIGNAL_IN | RW | 0...4294967295
143 | O10 | ALARM | ALARM 10 | SIGNAL_IN | RW | 0...4294967295
143 | O11 | ALARM | ALARM 11 | SIGNAL_IN | RW | 0...4294967295
143 | O12 | ALARM | ALARM 12 | SIGNAL_IN | RW | 0...4294967295
143 | O13 | ALARM | ALARM 13 | SIGNAL_IN | RW | 0...4294967295
143 | O14 | ALARM | ALARM 14 | SIGNAL_IN | RW | 0...4294967295
143 | O15 | ALARM | ALARM 15 | SIGNAL_IN | RW | 0...4294967295
143 | O16 | ALARM | ALARM 16 | SIGNAL_IN | RW | 0...4294967295
143 | O17 | ALARM | ALARM 17 | SIGNAL_IN | RW | 0...4294967295
143 | O18 | ALARM | ALARM 18 | SIGNAL_IN | RW | 0...4294967295
143 | O19 | ALARM | ALARM 19 | SIGNAL_IN | RW | 0...4294967295
143 | O20 | ALARM | ALARM 20 | SIGNAL_IN | RW | 0...4294967295
143 | O21 | ALARM | ALARM 21 | SIGNAL_IN | RW | 0...4294967295
143 | O22 | ALARM | ALARM 22 | SIGNAL_IN | RW | 0...4294967295
143 | O23 | ALARM | ALARM 23 | SIGNAL_IN | RW | 0...4294967295
143 | O24 | ALARM | ALARM 24 | SIGNAL_IN | RW | 0...4294967295
143 | O25 | ALARM | ALARM 25 | SIGNAL_IN | RW | 0...4294967295
143 | O26 | ALARM | ALARM 26 | SIGNAL_IN | RW | 0...4294967295
143 | O27 | ALARM | ALARM 27 | SIGNAL_IN | RW | 0...4294967295
143 | O28 | ALARM | ALARM 28 | SIGNAL_IN | RW | 0...4294967295
143 | O29 | ALARM | ALARM 29 | SIGNAL_IN | RW | 0...4294967295
143 | O30 | ALARM | ALARM 30 | SIGNAL_IN | RW | 0...4294967295
143 | O31 | ALARM | ALARM 31 | SIGNAL_IN | RW | 0...4294967295
143 | O32 | ALARM | ALARM 32 | SIGNAL_IN | RW | 0...4294967295
143 | O33 | ALARM | ALARM 33 | SIGNAL_IN | RW | 0...4294967295
143 | O34 | ALARM | ALARM 34 | SIGNAL_IN | RW | 0...4294967295
143 | O35 | ALARM | ALARM 35 | SIGNAL_IN | RW | 0...4294967295
143 | O36 | ALARM | ALARM 36 | SIGNAL_IN | RW | 0...4294967295
143 | O37 | ALARM | ALARM 37 | SIGNAL_IN | RW | 0...4294967295
143 | O38 | ALARM | ALARM 38 | SIGNAL_IN | RW | 0...4294967295
143 | O39 | ALARM | ALARM 39 | SIGNAL_IN | RW | 0...4294967295
143 | O40 | ALARM | ALARM 40 | SIGNAL_IN | RW | 0...4294967295
143 | O41 | ALARM | ALARM 41 | SIGNAL_IN | RW | 0...4294967295
143 | O42 | ALARM | ALARM 42 | SIGNAL_IN | RW | 0...4294967295
143 | O43 | ALARM | ALARM 43 | SIGNAL_IN | RW | 0...4294967295
143 | O44 | ALARM | ALARM 44 | SIGNAL_IN | RW | 0...4294967295
143 | O45 | ALARM | ALARM 45 | SIGNAL_IN | RW | 0...4294967295
143 | O46 | ALARM | ALARM 46 | SIGNAL_IN | RW | 0...4294967295
143 | O47 | ALARM | ALARM 47 | SIGNAL_IN | RW | 0...4294967295
143 | O48 | ALARM | ALARM 48 | SIGNAL_IN | RW | 0...4294967295
143 | O49 | ALARM | ALARM 49 | SIGNAL_IN | RW | 0...4294967295
143 | O50 | ALARM | ALARM 50 | SIGNAL_IN | RW | 0...4294967295
143 | O51 | ALARM | ALARM 51 | SIGNAL_IN | RW | 0...4294967295
143 | O52 | ALARM | ALARM 52 | SIGNAL_IN | RW | 0...4294967295
143 | O53 | ALARM | ALARM 53 | SIGNAL_IN | RW | 0...4294967295
143 | O54 | ALARM | ALARM 54 | SIGNAL_IN | RW | 0...4294967295
143 | O55 | ALARM | ALARM 55 | SIGNAL_IN | RW | 0...4294967295
143 | O56 | ALARM | ALARM 56 | SIGNAL_IN | RW | 0...4294967295
143 | O57 | ALARM | ALARM 57 | SIGNAL_IN | RW | 0...4294967295
143 | O58 | ALARM | ALARM 58 | SIGNAL_IN | RW | 0...4294967295
143 | O59 | ALARM | ALARM 59 | SIGNAL_IN | RW | 0...4294967295
143 | O60 | ALARM | ALARM 60 | SIGNAL_IN | RW | 0...4294967295
143 | O61 | ALARM | ALARM 61 | SIGNAL_IN | RW | 0...4294967295
143 | O62 | ALARM | ALARM 62 | SIGNAL_IN | RW | 0...4294967295
143 | O63 | ALARM | ALARM 63 | SIGNAL_IN | RW | 0...4294967295
143 | O64 | ALARM | ALARM 64 | SIGNAL_IN | RW | 0...4294967295
159 | S1 | ALARM1 | EventMaskLo | UINT32 | RW | 0...4294967295
159 | S2 | ALARM1 | EventMaskHi | UINT32 | RW | 0...4294967295
160 | S1 | ALARM2 | EventMaskLo | UINT32 | RW | 0...4294967295
160 | S2 | ALARM2 | EventMaskHi | UINT32 | RW | 0...4294967295
162 | S1 | GSYN | Synchronizer mode | UINT32 | RW | 0=Disabled;1=Activated
162 | S2 | GSYN | Synchronizer reference voltage input | UINT32 | RW | 0=U4 Input;1=U3 Input
162 | S3 | GSYN | Voltage difference calculation mode | UINT32 | RW | 0=System is reference;1=U3/U4 Input is reference
162 | S4 | GSYN | Synchronizer voltage reference | UINT32 | RW | 0=UL12;1=UL23;2=UL31;3=UL1;4=UL2;5=UL3
162 | S5 | GSYN | Synchronizer measurement settings | UINT32 | R | 0=Meas.Conf.Incorrect;1=PP and PE voltages;2=PP Voltages;
162 | S6 | GSYN | Synchronizer status | UINT32 | R | 0=Conf.Error;1=Idle Ready;2=Synchronizing;3=Blocked
162 | S7 | GSYN | Force control signals on | UINT32 | RW | 0=None;1=Blocked On;2=Running On;3=Increase U On;4=Decrease U On;5=Increase F On;6=Decrease F On;7=CB Close On;8=LongSyncTime On
162 | S8 | GSYN | Synchronizing by | UINT32 | RW | 0=Autosynchronizer;1=Manual commands
162 | S9 | GSYN | Manual switching mode | UINT32 | RW | 0=Assisted synchroswitch;1=I know what I am doing
162 | S10 | GSYN | Synchroswitch status | UINT32 | R | 0=Standstill;1=Departing;2=Enclosing
162 | S11 | GSYN | Magnitude side A | FLOAT | R | 0.000...200.000
162 | S12 | GSYN | Magnitude side B | FLOAT | R | 0.000...200.000
162 | S13 | GSYN | Frequency side A | FLOAT | R | 0.000...75.000
162 | S14 | GSYN | Frequency side B | FLOAT | R | 0.000...75.000
162 | S15 | GSYN | Magnitude difference | FLOAT | R | -200...200
162 | S16 | GSYN | Frequency difference | FLOAT | R | -100...100
162 | S17 | GSYN | Angle difference | FLOAT | R | -360...360
162 | S18 | GSYN | Magnitude difference on closing BRK | FLOAT | R | -200...200
162 | S19 | GSYN | Frequency difference on closing BRK | FLOAT | R | -100...100
162 | S20 | GSYN | Angle difference on closing BRK | FLOAT | R | -360...360
162 | S21 | GSYN | Estimated BRK Closing time | FLOAT | R | 0...360
162 | S22 | GSYN | Networks rotating time | FLOAT | R | 0...360
162 | S23 | GSYN | Networks placement atm | FLOAT | R | -360...360
162 | S24 | GSYN | Synchronizing time left | FLOAT | R | 0...1800
162 | S25 | GSYN | Get measurement errors for fine tuning | UINT32 | RW | 0=-;1=Get errors
162 | S26 | GSYN | Magnitude difference fine tune | FLOAT | RW | -200...200
162 | S27 | GSYN | Frequency difference fine tune | FLOAT | RW | -100...100
162 | S28 | GSYN | Angle difference fine tune | FLOAT | RW | -360...360
162 | S29 | GSYN | Minimum voltage allowed for synchronizing | FLOAT | RW | 0...105
162 | S30 | GSYN | Maximum voltage allowed for synchronizing | FLOAT | RW | 0...200
162 | S31 | GSYN | Maximum zero voltage allowed for synchronizing (100% disabled) | FLOAT | RW | 0...100
162 | S32 | GSYN | Maximum allowed voltage difference | FLOAT | RW | 0.1...50
162 | S33 | GSYN | Maximum allowed overfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S34 | GSYN | Maximum allowed underfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S35 | GSYN | Max.Time for synchronizing | FLOAT | RW | 0...1800
162 | S36 | GSYN | Maximum allowed angular disposition to allow synchronizing | FLOAT | RW | 0.01...25
162 | S37 | GSYN | Adjustment for measurement inaccuracy or set of desired volt. offset | FLOAT | RW | -95...95
162 | S38 | GSYN | Adjustment for measurement inaccuracy or set of desired angular offset | FLOAT | RW | -60...60
162 | S39 | GSYN | Adjustment for measurement inaccuracy or set of desired freq. offset | FLOAT | RW | -0.5...2
162 | S40 | GSYN | Voltage adjustment slope | FLOAT | RW | 0...25
162 | S41 | GSYN | Volt. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S42 | GSYN | Volt. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S43 | GSYN | Volt. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S44 | GSYN | Freq. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S45 | GSYN | Freq. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S46 | GSYN | Freq. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S47 | GSYN | Maximum allowed voltage difference to start synchronizing | FLOAT | RW | 0...50
162 | S48 | GSYN | Integrator sum when voltage adjustment pulse is generated | FLOAT | RW | 0...50
162 | S49 | GSYN | Voltage adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S50 | GSYN | Frequency adjustment slope when increasing | FLOAT | RW | 0...10
162 | S51 | GSYN | Frequency adjustment slope when decreasing | FLOAT | RW | -10...0
162 | S52 | GSYN | Maximum allowed frequency difference to start synchronizing | FLOAT | RW | 0...25
162 | S53 | GSYN | Integrator sum when frequency adjustment pulse is generated | FLOAT | RW | 0...50
162 | S54 | GSYN | Frequency adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S55 | GSYN | Filter time for angle derivative | FLOAT | RW | 0...1800
162 | S56 | GSYN | Circuit breaker pre-closing adjustment constant | FLOAT | RW | 0...10
162 | S57 | GSYN | Circuit breaker pre-closing time incl auxiliary relays | FLOAT | RW | 0...1800
162 | S58 | GSYN | Lenght of circuit breaker closing pulse | FLOAT | RW | 0...1800
162 | I1 | GSYN | Start Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I2 | GSYN | Stop Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I3 | GSYN | Block and Interrupt Synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I4 | GSYN | Breaker Closed | SIGNAL_IN | RW | 0...4294967295
162 | I5 | GSYN | Manual increase voltage | SIGNAL_IN | RW | 0...4294967295
162 | I6 | GSYN | Manual decrease voltage | SIGNAL_IN | RW | 0...4294967295
162 | I7 | GSYN | Manual increase frequency | SIGNAL_IN | RW | 0...4294967295
162 | I8 | GSYN | Manual decrease frequency | SIGNAL_IN | RW | 0...4294967295
162 | I9 | GSYN | Manual Close Breaker | SIGNAL_IN | RW | 0...4294967295
162 | O1 | GSYN | GSYN Voltage Mag.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O2 | GSYN | GSYN Voltage Freq.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O3 | GSYN | GSYN Voltage Ang.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O4 | GSYN | GSYN Blocked | SIGNAL_OUT | RW | 0...4294967295
162 | O5 | GSYN | GSYN Running | SIGNAL_OUT | RW | 0...4294967295
162 | O6 | GSYN | GSYN Increase Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O7 | GSYN | GSYN Decrease Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O8 | GSYN | GSYN Increase Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O9 | GSYN | GSYN Decrease Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O10 | GSYN | GSYN Breaker Close Pulse | SIGNAL_OUT | RW | 0...4294967295
162 | O11 | GSYN | GSYN Long Sync Time | SIGNAL_OUT | RW | 0...4294967295
162 | O12 | GSYN | GSYN Nets Standstill | SIGNAL_OUT | RW | 0...4294967295
162 | O13 | GSYN | GSYN Nets Departing | SIGNAL_OUT | RW | 0...4294967295
162 | O14 | GSYN | GSYN Nets Enclosing | SIGNAL_OUT | RW | 0...4294967295
162 | S59 | GSYN | Control EventMaskLo | UINT32 | RW | 0...4294967295
162 | S60 | GSYN | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | S1 | VREC | Measurement value recorder mode | UINT32 | RW | 0=Disabled;1=Activated
163 | S2 | VREC | Scale current values to primary | UINT32 | RW | 0=No;1=Yes
163 | S3 | VREC | Record fault types (Overcurrrent & Voltage Over/Under) faults | UINT32 | RW | 0=No;1=Yes
163 | I1 | VREC | Trigger register to memory | SIGNAL_IN | RW | 0...4294967295
163 | I2 | VREC | Tripped stage | UINT32 | R | 0=-;1=I> Trip;2=I>> Trip;3=I>>> Trip;4=I>>>> Trip;5=IDir> Trip;6=IDir>> Trip;7=IDir>>> Trip;8=IDir>>>> Trip;9=U> Trip;10=U>> Trip;11=U>>> Trip;12=U>>>> Trip;13=U< Trip;14=U<< Trip;15=U<<< Trip;16=U<<<< Trip;17=I0> TRIP;18=I0>> Trip;19=I0>>> Trip;20=I0>>>> Trip;21=I0Dir> Trip;22=I0Dir>> Trip;23=I0Dir>>> Trip;24=I0Dir>>>> Trip;25=f> Trip;26=f>> Trip;27=f>>> Trip;28=f>>>> Trip;29=f< Trip;30=f<< Trip;31=f<<< Trip;32=f<<<< Trip;33=P> Trip;34=P< Trip;35=Prev> Trip;36=T> Trip;37=I2> Trip;38=I2>> Trip;39=I2>>> Trip;40=I2>>>> Trip;41=U1/2 > Trip;42=U1/2 >> Trip;43=U1/2 >>> Trip;44=U1/2 >>>> Trip;45=U0> Trip;46=U0>> Trip;47=U0>>> Trip;48=U0>>>> Trip
163 | I3 | VREC | Overcurrent fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;
163 | I4 | VREC | Voltage fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C;8=-;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I5 | VREC | VREC Magnitude 1 | FLOAT | R | 0...1800
163 | I6 | VREC | VREC Magnitude 2 | FLOAT | R | 0...1800
163 | I7 | VREC | VREC Magnitude 3 | FLOAT | R | 0...1800
163 | I8 | VREC | VREC Magnitude 4 | FLOAT | R | 0...1800
163 | I9 | VREC | VREC Magnitude 5 | FLOAT | R | 0...1800
163 | I10 | VREC | VREC Magnitude 6 | FLOAT | R | 0...1800
163 | I11 | VREC | VREC Magnitude 7 | FLOAT | R | 0...1800
163 | I12 | VREC | VREC Magnitude 8 | FLOAT | R | 0...1800
163 | I13 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I14 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I15 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I16 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I17 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I18 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I19 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I20 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I21 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I22 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I23 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I24 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295

## R SPA map AQ-210 v2.1.1.3-233
SPA Ch | SPA Data | Ch Name | Description | Type | Access | Range
46 | V1 | OBJ1 | Open Select | UINT32 | W | 1=Select
46 | V2 | OBJ1 | Close Select | UINT32 | W | 1=Select
46 | V3 | OBJ1 | Execute | UINT32 | W | 1=Execute
46 | V4 | OBJ1 | Cancel | UINT32 | W | 1=Cancel
46 | V5 | OBJ1 | Direct Open | UINT32 | W | 1=Open
46 | V6 | OBJ1 | Direct Close | UINT32 | W | 1=Close
47 | V1 | OBJ2 | Open Select | UINT32 | W | 1=Select
47 | V2 | OBJ2 | Close Select | UINT32 | W | 1=Select
47 | V3 | OBJ2 | Execute | UINT32 | W | 1=Execute
47 | V4 | OBJ2 | Cancel | UINT32 | W | 1=Cancel
47 | V5 | OBJ2 | Direct Open | UINT32 | W | 1=Open
47 | V6 | OBJ2 | Direct Close | UINT32 | W | 1=Close
48 | V1 | OBJ3 | Open Select | UINT32 | W | 1=Select
48 | V2 | OBJ3 | Close Select | UINT32 | W | 1=Select
48 | V3 | OBJ3 | Execute | UINT32 | W | 1=Execute
48 | V4 | OBJ3 | Cancel | UINT32 | W | 1=Cancel
48 | V5 | OBJ3 | Direct Open | UINT32 | W | 1=Open
48 | V6 | OBJ3 | Direct Close | UINT32 | W | 1=Close
49 | V1 | OBJ4 | Open Select | UINT32 | W | 1=Select
49 | V2 | OBJ4 | Close Select | UINT32 | W | 1=Select
49 | V3 | OBJ4 | Execute | UINT32 | W | 1=Execute
49 | V4 | OBJ4 | Cancel | UINT32 | W | 1=Cancel
49 | V5 | OBJ4 | Direct Open | UINT32 | W | 1=Open
49 | V6 | OBJ4 | Direct Close | UINT32 | W | 1=Close
50 | V1 | OBJ5 | Open Select | UINT32 | W | 1=Select
50 | V2 | OBJ5 | Close Select | UINT32 | W | 1=Select
50 | V3 | OBJ5 | Execute | UINT32 | W | 1=Execute
50 | V4 | OBJ5 | Cancel | UINT32 | W | 1=Cancel
50 | V5 | OBJ5 | Direct Open | UINT32 | W | 1=Open
50 | V6 | OBJ5 | Direct Close | UINT32 | W | 1=Close
150 | V1 | OBJ6 | Open Select | UINT32 | W | 1=Select
150 | V2 | OBJ6 | Close Select | UINT32 | W | 1=Select
150 | V3 | OBJ6 | Execute | UINT32 | W | 1=Execute
150 | V4 | OBJ6 | Cancel | UINT32 | W | 1=Cancel
150 | V5 | OBJ6 | Direct Open | UINT32 | W | 1=Open
150 | V6 | OBJ6 | Direct Close | UINT32 | W | 1=Close
151 | V1 | OBJ7 | Open Select | UINT32 | W | 1=Select
151 | V2 | OBJ7 | Close Select | UINT32 | W | 1=Select
151 | V3 | OBJ7 | Execute | UINT32 | W | 1=Execute
151 | V4 | OBJ7 | Cancel | UINT32 | W | 1=Cancel
151 | V5 | OBJ7 | Direct Open | UINT32 | W | 1=Open
151 | V6 | OBJ7 | Direct Close | UINT32 | W | 1=Close
152 | V1 | OBJ8 | Open Select | UINT32 | W | 1=Select
152 | V2 | OBJ8 | Close Select | UINT32 | W | 1=Select
152 | V3 | OBJ8 | Execute | UINT32 | W | 1=Execute
152 | V4 | OBJ8 | Cancel | UINT32 | W | 1=Cancel
152 | V5 | OBJ8 | Direct Open | UINT32 | W | 1=Open
152 | V6 | OBJ8 | Direct Close | UINT32 | W | 1=Close
153 | V1 | OBJ9 | Open Select | UINT32 | W | 1=Select
153 | V2 | OBJ9 | Close Select | UINT32 | W | 1=Select
153 | V3 | OBJ9 | Execute | UINT32 | W | 1=Execute
153 | V4 | OBJ9 | Cancel | UINT32 | W | 1=Cancel
153 | V5 | OBJ9 | Direct Open | UINT32 | W | 1=Open
153 | V6 | OBJ9 | Direct Close | UINT32 | W | 1=Close
154 | V1 | OBJ10 | Open Select | UINT32 | W | 1=Select
154 | V2 | OBJ10 | Close Select | UINT32 | W | 1=Select
154 | V3 | OBJ10 | Execute | UINT32 | W | 1=Execute
154 | V4 | OBJ10 | Cancel | UINT32 | W | 1=Cancel
154 | V5 | OBJ10 | Direct Open | UINT32 | W | 1=Open
154 | V6 | OBJ10 | Direct Close | UINT32 | W | 1=Close
116 | S1 | MEAS1 | Side 1 Current meas update interval | UINT32 | RW | 5...10000
116 | I1 | MEAS1 | Pri.Pha.curr.IL1 ff. | FLOAT | R | 0...100000
116 | I2 | MEAS1 | Pri.Pha.curr.IL2 ff. | FLOAT | R | 0...100000
116 | I3 | MEAS1 | Pri.Pha.curr.IL3 ff. | FLOAT | R | 0...100000
116 | I4 | MEAS1 | Pri.Pha.curr.IL1 3h. | FLOAT | R | 0...100000
116 | I5 | MEAS1 | Pri.Pha.curr.IL2 3h. | FLOAT | R | 0...100000
116 | I6 | MEAS1 | Pri.Pha.curr.IL3 3h. | FLOAT | R | 0...100000
116 | I7 | MEAS1 | Pha.angle IL1 | FLOAT | R | -360...360
116 | I8 | MEAS1 | Pha.angle IL2 | FLOAT | R | -360...360
116 | I9 | MEAS1 | Pha.angle IL3 | FLOAT | R | -360...360
116 | I10 | MEAS1 | Pri.Res.curr.I01 ff. | FLOAT | R | 0...100000
116 | I11 | MEAS1 | Pri.Res.curr.I01 3h. | FLOAT | R | 0...100000
116 | I12 | MEAS1 | Res.curr.angle I01 | FLOAT | R | -360...360
116 | I13 | MEAS1 | Pri.Res.curr.I02 ff. | FLOAT | R | 0...100000
116 | I14 | MEAS1 | Pri.Res.curr.I02 3h. | FLOAT | R | 0...100000
116 | I15 | MEAS1 | Res.curr.angle I02 | FLOAT | R | -360...360
116 | I16 | MEAS1 | Pri.calc.I0 | FLOAT | R | 0...100000
116 | I17 | MEAS1 | calc.I0 Pha.angle | FLOAT | R | -360...360
116 | I18 | MEAS1 | Pha.curr.IL1 TRMS Pri | FLOAT | R | 0...100000
116 | I19 | MEAS1 | Pha.curr.IL2 TRMS Pri | FLOAT | R | 0...100000
116 | I20 | MEAS1 | Pha.curr.IL3 TRMS Pri | FLOAT | R | 0...100000
116 | I21 | MEAS1 | Pri.Pos.seq.curr. | FLOAT | R | 0...100000
116 | I22 | MEAS1 | Pri.Neg.seq.curr. | FLOAT | R | 0...100000
116 | I23 | MEAS1 | Pri.Zero seq.curr. | FLOAT | R | 0...100000
116 | I24 | MEAS1 | Pos.seq.curr.angle | FLOAT | R | -360...360
116 | I25 | MEAS1 | Neg.seq.curr.angle | FLOAT | R | -360...360
116 | I26 | MEAS1 | Zero seq.curr.angle | FLOAT | R | -360...360
116 | I27 | MEAS1 | Res.curr.I01 TRMS Pri | FLOAT | R | 0...100000
116 | I28 | MEAS1 | Res.curr.I02 TRMS Pri | FLOAT | R | 0...100000
116 | I29 | MEAS1 | Pha.L1 ampl. THD | FLOAT | R | 0...100
116 | I30 | MEAS1 | Pha.L1 pow. THD | FLOAT | R | 0...100
116 | I31 | MEAS1 | Pha.L2 ampl. THD | FLOAT | R | 0...100
116 | I32 | MEAS1 | Pha.L2 pow. THD | FLOAT | R | 0...100
116 | I33 | MEAS1 | Pha.L3 ampl. THD | FLOAT | R | 0...100
116 | I34 | MEAS1 | Pha.L3 pow. THD | FLOAT | R | 0...100
116 | I35 | MEAS1 | Res.I01 ampl. THD | FLOAT | R | 0...100
116 | I36 | MEAS1 | Res.I01 pow. THD | FLOAT | R | 0...100
116 | I37 | MEAS1 | Res.I02 ampl. THD | FLOAT | R | 0...100
116 | I38 | MEAS1 | Res.I02 pow. THD | FLOAT | R | 0...100
116 | I39 | MEAS1 | Meas1 IL ang. Ref | FLOAT | R | -360...360
117 | S1 | MEAS2 | Side 2 Current meas update interval | UINT32 | RW | 5...10000
117 | I1 | MEAS2 | Pri.Pha.curr.I''L1 | FLOAT | R | 0...100000
117 | I2 | MEAS2 | Pri.Pha.curr.I''L2 | FLOAT | R | 0...100000
117 | I3 | MEAS2 | Pri.Pha.curr.I''L3 | FLOAT | R | 0...100000
117 | I4 | MEAS2 | Pha.angle I''L1 | FLOAT | R | -360...360
117 | I5 | MEAS2 | Pha.angle I''L2 | FLOAT | R | -360...360
117 | I6 | MEAS2 | Pha.angle I''L3 | FLOAT | R | -360...360
117 | I7 | MEAS2 | Pri.Res.curr.I''01 | FLOAT | R | 0...100000
117 | I8 | MEAS2 | Res.curr.angle I''01 | FLOAT | R | -360...360
117 | I9 | MEAS2 | Pri.Res.curr.I''02 | FLOAT | R | 0...100000
117 | I10 | MEAS2 | Res.curr.angle I''02 | FLOAT | R | -360...360
117 | I11 | MEAS2 | Pri.calc.I''0 | FLOAT | R | 0...100000
117 | I12 | MEAS2 | calc.I''0 Pha.angle | FLOAT | R | -360...360
117 | I13 | MEAS2 | Pha.curr.I''L1 TRMS Pri | FLOAT | R | 0...100000
117 | I14 | MEAS2 | Pha.curr.I''L2 TRMS Pri | FLOAT | R | 0...100000
117 | I15 | MEAS2 | Pha.curr.I''L3 TRMS Pri | FLOAT | R | 0...100000
117 | I16 | MEAS2 | I'' Pri.Pos.seq.curr. | FLOAT | R | 0...100000
117 | I17 | MEAS2 | I'' Pri.Neg.seq.curr. | FLOAT | R | 0...100000
117 | I18 | MEAS2 | I'' Pri.Zero seq.curr. | FLOAT | R | 0...100000
117 | I19 | MEAS2 | I'' Pos.seq.curr.angle | FLOAT | R | -360...360
117 | I20 | MEAS2 | I'' Neg.seq.curr.angle | FLOAT | R | -360...360
117 | I21 | MEAS2 | I'' Zero seq.curr.angle | FLOAT | R | -360...360
117 | I22 | MEAS2 | Res.curr.I''01 TRMS Pri | FLOAT | R | 0...100000
117 | I23 | MEAS2 | Res.curr.I''02 TRMS Pri | FLOAT | R | 0...100000
117 | I24 | MEAS2 | Pha.I''L1 ampl. THD | FLOAT | R | 0...100
117 | I25 | MEAS2 | Pha.I''L1 pow. THD | FLOAT | R | 0...100
117 | I26 | MEAS2 | Pha.I''L2 ampl. THD | FLOAT | R | 0...100
117 | I27 | MEAS2 | Pha.I''L2 pow. THD | FLOAT | R | 0...100
117 | I28 | MEAS2 | Pha.I''L3 ampl. THD | FLOAT | R | 0...100
117 | I29 | MEAS2 | Pha.I''L3 pow. THD | FLOAT | R | 0...100
117 | I30 | MEAS2 | Res.I''01 ampl. THD | FLOAT | R | 0...100
117 | I31 | MEAS2 | Res.I''01 pow. THD | FLOAT | R | 0...100
117 | I32 | MEAS2 | Res.I''02 ampl. THD | FLOAT | R | 0...100
117 | I33 | MEAS2 | Res.I''02 pow. THD | FLOAT | R | 0...100
117 | I34 | MEAS2 | MEAS2 IL ang. Ref | FLOAT | R | -360...360
118 | S1 | MEAS3 | Voltage meas update interval | UINT32 | RW | 5...10000
118 | I1 | MEAS3 | Pos.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I2 | MEAS3 | Neg.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I3 | MEAS3 | Zero.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I4 | MEAS3 | Pos.Seq volt.Angle | FLOAT | R | -360...360
118 | I5 | MEAS3 | Neg.Seq.volt.Angle | FLOAT | R | -360...360
118 | I6 | MEAS3 | Zero.Seq.volt.Angle | FLOAT | R | -360...360
118 | I7 | MEAS3 | System volt UL12 mag | FLOAT | R | 0...1000000
118 | I8 | MEAS3 | System volt UL12 mag(kV) | FLOAT | R | 0...1000
118 | I9 | MEAS3 | System volt UL12 ang | FLOAT | R | -360...360
118 | I10 | MEAS3 | System volt UL23 mag | FLOAT | R | 0...1000000
118 | I11 | MEAS3 | System volt UL23 mag(kV) | FLOAT | R | 0...1000
118 | I12 | MEAS3 | System volt UL23 ang | FLOAT | R | -360...360
118 | I13 | MEAS3 | System volt UL31 mag | FLOAT | R | 0...1000000
118 | I14 | MEAS3 | System volt UL31 mag(kV) | FLOAT | R | 0...1000
118 | I15 | MEAS3 | System volt UL31 ang | FLOAT | R | -360...360
118 | I16 | MEAS3 | System volt UL1 mag | FLOAT | R | 0...1000000
118 | I17 | MEAS3 | System volt UL1 mag(kV) | FLOAT | R | 0...1000
118 | I18 | MEAS3 | System volt UL1 ang | FLOAT | R | -360...360
118 | I19 | MEAS3 | System volt UL2 mag | FLOAT | R | 0...1000000
118 | I20 | MEAS3 | System volt UL2 mag(kV) | FLOAT | R | 0...1000
118 | I21 | MEAS3 | System volt UL2 ang | FLOAT | R | -360...360
118 | I22 | MEAS3 | System volt UL3 mag | FLOAT | R | 0...1000000
118 | I23 | MEAS3 | System volt UL3 mag(kV) | FLOAT | R | 0...1000
118 | I24 | MEAS3 | System volt UL3 ang | FLOAT | R | -360...360
118 | I25 | MEAS3 | System volt U0 mag | FLOAT | R | 0...1000000
118 | I26 | MEAS3 | System volt U0 mag(kV) | FLOAT | R | 0...1000
118 | I27 | MEAS3 | System volt U0 mag(%) | FLOAT | R | 0...120
118 | I28 | MEAS3 | System volt U0 ang | FLOAT | R | -360...360
118 | I29 | MEAS3 | System volt U3 mag | FLOAT | R | 0...1000000
118 | I30 | MEAS3 | System volt U3 mag(kV) | FLOAT | R | 0...1000
118 | I31 | MEAS3 | System volt U3 ang | FLOAT | R | -360...360
118 | I32 | MEAS3 | System volt U4 mag | FLOAT | R | 0...1000000
118 | I33 | MEAS3 | System volt U4 mag(kV) | FLOAT | R | 0...1000
118 | I34 | MEAS3 | System volt U4 ang | FLOAT | R | -360...360
188 | I1 | IMERX | IL1 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I2 | IMERX | IL1 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I3 | IMERX | IL2 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I4 | IMERX | IL2 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I5 | IMERX | IL3 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I6 | IMERX | IL3 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I7 | IMERX | Pos.seq. Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I8 | IMERX | Pos.Seq. Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I9 | IMERX | I01 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I10 | IMERX | I01 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I11 | IMERX | I02 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I12 | IMERX | I02 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I13 | IMERX | I01 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I14 | IMERX | I01 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
188 | I15 | IMERX | I02 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I16 | IMERX | I02 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
119 | S1 | POW1 | Power meas update interval | UINT32 | RW | 5...10000
119 | S2 | POW1 | Nominal Power kVA | FLOAT | RW | 0.1...500000
119 | I1 | POW1 | PQ Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Ind;2=Q2 Rev Cap;3=Q3 Rev Ind;4=Q4 Fwd Cap
119 | I2 | POW1 | VA Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Cap, AV;2=Q2 Rev Ind AV;3=Q3 Rev Cap VA;4=Q4 Fwd Ind VA
119 | I3 | POW1 | Export Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I4 | POW1 | Export Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I5 | POW1 | Import Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I6 | POW1 | Import Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I7 | POW1 | Active Energy (P) Export/Import balance MWh | INT32 | R | -2147483647...2147483647
119 | I8 | POW1 | Active Energy (P) Export/Import balance kWh | INT32 | R | -2147483647...2147483647
119 | I9 | POW1 | Exported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I10 | POW1 | Exported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I11 | POW1 | Imported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I12 | POW1 | Imported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I13 | POW1 | Reactive Energy (Q) balance while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I14 | POW1 | Reactive Energy (Q) balance while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I15 | POW1 | Exported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I16 | POW1 | Exported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I17 | POW1 | Imported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I18 | POW1 | Imported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I19 | POW1 | Reactive Energy (Q) balance while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I20 | POW1 | Reactive Energy (Q) balance while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I21 | POW1 | Apparent Energy (S) while Export (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I22 | POW1 | Apparent Energy (S) while Export (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I23 | POW1 | Apparent Energy (S) while Import (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I24 | POW1 | Apparent Energy (S) while Import (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I25 | POW1 | Apparent Energy (S) Net | INT32 | R | -2147483647...2147483647
119 | I26 | POW1 | Real Energy (P) Net | INT32 | RW | -2147483647...2147483647
119 | I27 | POW1 | Reactive Energy (Q) Net | INT32 | RW | -2147483647...2147483647
119 | I28 | POW1 | Real Energy (P) Supply (Default supply direction towards busbar) | INT32 | RW | -2147483647...2147483647
119 | I29 | POW1 | Reactive Energy (Q) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
119 | I30 | POW1 | Real Energy (P) Demand (Default demand direction from busbar) | INT32 | RW | -2147483647...2147483647
119 | I31 | POW1 | Reactive Energy (Q) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
119 | S3 | POW1 | Reset 3ph Energies | UINT32 | RW | 0=-;1=Reset
119 | I32 | POW1 | POW1 L1 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I33 | POW1 | POW1 L1 Active power (P) | FLOAT | R | -1000000...1000000
119 | I34 | POW1 | POW1 L1 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I35 | POW1 | POW1 L1 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I36 | POW1 | POW1 L1 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I37 | POW1 | L1 PF | FLOAT | R | -1000000...1000000
119 | I38 | POW1 | POW1 L2 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I39 | POW1 | POW1 L2 Active power (P) | FLOAT | R | -1000000...1000000
119 | I40 | POW1 | POW1 L2 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I41 | POW1 | POW1 L2 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I42 | POW1 | POW1 L2 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I43 | POW1 | L2 PF | FLOAT | R | -1000000...1000000
119 | I44 | POW1 | POW1 L3 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I45 | POW1 | POW1 L3 Active power (P) | FLOAT | R | -1000000...1000000
119 | I46 | POW1 | POW1 L3 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I47 | POW1 | POW1 L3 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I48 | POW1 | POW1 L3 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I49 | POW1 | L3 PF | FLOAT | R | -1000000...1000000
119 | I50 | POW1 | POW1 3PH Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I51 | POW1 | POW1 3PH Apparent power (S MVA) | FLOAT | R | -1000000...1000000
119 | I52 | POW1 | POW1 3PH Active power (P) | FLOAT | R | -1000000...1000000
119 | I53 | POW1 | POW1 3PH Active power (P MW) | FLOAT | R | -1000000...1000000
119 | I54 | POW1 | POW1 3PH Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I55 | POW1 | POW1 3PH Reactive power (QMVar) | FLOAT | R | -1000000...1000000
119 | I56 | POW1 | POW1 3PH Tan(phi) | FLOAT | R | -1000000...1000000
119 | I57 | POW1 | POW1 3PH Cos(phi) | FLOAT | R | -1000000...1000000
119 | I58 | POW1 | 3PH PF | FLOAT | R | -1000000...1000000
136 | S1 | IMP1 | Impedance meas. update interval | UINT32 | RW | 500...10000
136 | I1 | IMP1 | Primary L12 R | FLOAT | R | -1000000...1000000
136 | I2 | IMP1 | Primary L12 X | FLOAT | R | -1000000...1000000
136 | I3 | IMP1 | Primary L23 R | FLOAT | R | -1000000...1000000
136 | I4 | IMP1 | Primary L23 X | FLOAT | R | -1000000...1000000
136 | I5 | IMP1 | Primary L31 R | FLOAT | R | -1000000...1000000
136 | I6 | IMP1 | Primary L31 X | FLOAT | R | -1000000...1000000
136 | I7 | IMP1 | Primary Z12 | FLOAT | R | -1000000...1000000
136 | I8 | IMP1 | Primary Z23 | FLOAT | R | -1000000...1000000
136 | I9 | IMP1 | Primary Z31 | FLOAT | R | -1000000...1000000
136 | I10 | IMP1 | Angle Z12 | FLOAT | R | -360...360
136 | I11 | IMP1 | Angle Z23 | FLOAT | R | -360...360
136 | I12 | IMP1 | Angle Z31 | FLOAT | R | -360...360
136 | I13 | IMP1 | Primary L1 R | FLOAT | R | -1000000...1000000
136 | I14 | IMP1 | Primary L1 X | FLOAT | R | -1000000...1000000
136 | I15 | IMP1 | Primary L2 R | FLOAT | R | -1000000...1000000
136 | I16 | IMP1 | Primary L2 X | FLOAT | R | -1000000...1000000
136 | I17 | IMP1 | Primary L3 R | FLOAT | R | -1000000...1000000
136 | I18 | IMP1 | Primary L3 X | FLOAT | R | -1000000...1000000
136 | I19 | IMP1 | Primary Z1 | FLOAT | R | -1000000...1000000
136 | I20 | IMP1 | Primary Z2 | FLOAT | R | -1000000...1000000
136 | I21 | IMP1 | Primary Z3 | FLOAT | R | -1000000...1000000
136 | I22 | IMP1 | Angle Z1 | FLOAT | R | -360...360
136 | I23 | IMP1 | Angle Z2 | FLOAT | R | -360...360
136 | I24 | IMP1 | Angle Z3 | FLOAT | R | -360...360
137 | I1 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I2 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I3 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I4 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I5 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I6 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I7 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I8 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I9 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I10 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I11 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I12 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
120 | S1 | FREQS | Smpl mode | UINT32 | RW | 0=Fixed;1=Tracking
120 | S2 | FREQS | Max. Tracking freq. allowed (+Nom f) | FLOAT | RW | 0.001...75
120 | S3 | FREQS | Sys.nom.f | FLOAT | RW | 7...75
120 | S4 | FREQS | Min. Tracking freq. allowed (- Nom f) | FLOAT | RW | 0.001...75
120 | I1 | FREQS | Track.sys.f | FLOAT | R | 0...75
120 | I2 | FREQS | f atm. Protections (when not measurable returns to nominal) | FLOAT | R | 0...75
120 | I3 | FREQS | f atm. Display (when not measurable is 0Hz) | FLOAT | R | 0...75
10 | I1 | DIGI | Dis 1-32 | UINT32 | R | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32
10 | I2 | DIGI | Dis 33-64 | UINT32 | R | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51
10 | I3 | DIGI | DI1 | SIGNAL_OUT | R | 0...4294967295
10 | V1 | DIGI | DI1 Counter | UINT32 | R | 0...4294967295
10 | V2 | DIGI | DI1 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I4 | DIGI | DI2 | SIGNAL_OUT | R | 0...4294967295
10 | V3 | DIGI | DI2 Counter | UINT32 | R | 0...4294967295
10 | V4 | DIGI | DI2 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I5 | DIGI | DI3 | SIGNAL_OUT | R | 0...4294967295
10 | V5 | DIGI | DI3 Counter | UINT32 | R | 0...4294967295
10 | V6 | DIGI | DI3 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I6 | DIGI | DI4 | SIGNAL_OUT | R | 0...4294967295
10 | V7 | DIGI | DI4 Counter | UINT32 | R | 0...4294967295
10 | V8 | DIGI | DI4 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I7 | DIGI | DI5 | SIGNAL_OUT | R | 0...4294967295
10 | V9 | DIGI | DI5 Counter | UINT32 | R | 0...4294967295
10 | V10 | DIGI | DI5 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I8 | DIGI | DI6 | SIGNAL_OUT | R | 0...4294967295
10 | V11 | DIGI | DI6 Counter | UINT32 | R | 0...4294967295
10 | V12 | DIGI | DI6 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I9 | DIGI | DI7 | SIGNAL_OUT | R | 0...4294967295
10 | V13 | DIGI | DI7 Counter | UINT32 | R | 0...4294967295
10 | V14 | DIGI | DI7 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I10 | DIGI | DI8 | SIGNAL_OUT | R | 0...4294967295
10 | V15 | DIGI | DI8 Counter | UINT32 | R | 0...4294967295
10 | V16 | DIGI | DI8 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I11 | DIGI | DI9 | SIGNAL_OUT | R | 0...4294967295
10 | V17 | DIGI | DI9 Counter | UINT32 | R | 0...4294967295
10 | V18 | DIGI | DI9 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I12 | DIGI | DI10 | SIGNAL_OUT | R | 0...4294967295
10 | V19 | DIGI | DI10 Counter | UINT32 | R | 0...4294967295
10 | V20 | DIGI | DI10 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I13 | DIGI | DI11 | SIGNAL_OUT | R | 0...4294967295
10 | V21 | DIGI | DI11 Counter | UINT32 | R | 0...4294967295
10 | V22 | DIGI | DI11 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I14 | DIGI | DI12 | SIGNAL_OUT | R | 0...4294967295
10 | V23 | DIGI | DI12 Counter | UINT32 | R | 0...4294967295
10 | V24 | DIGI | DI12 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I15 | DIGI | DI13 | SIGNAL_OUT | R | 0...4294967295
10 | V25 | DIGI | DI13 Counter | UINT32 | R | 0...4294967295
10 | V26 | DIGI | DI13 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I16 | DIGI | DI14 | SIGNAL_OUT | R | 0...4294967295
10 | V27 | DIGI | DI14 Counter | UINT32 | R | 0...4294967295
10 | V28 | DIGI | DI14 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I17 | DIGI | DI15 | SIGNAL_OUT | R | 0...4294967295
10 | V29 | DIGI | DI15 Counter | UINT32 | R | 0...4294967295
10 | V30 | DIGI | DI15 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I18 | DIGI | DI16 | SIGNAL_OUT | R | 0...4294967295
10 | V31 | DIGI | DI16 Counter | UINT32 | R | 0...4294967295
10 | V32 | DIGI | DI16 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I19 | DIGI | DI17 | SIGNAL_OUT | R | 0...4294967295
10 | V33 | DIGI | DI17 Counter | UINT32 | R | 0...4294967295
10 | V34 | DIGI | DI17 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I20 | DIGI | DI18 | SIGNAL_OUT | R | 0...4294967295
10 | V35 | DIGI | DI18 Counter | UINT32 | R | 0...4294967295
10 | V36 | DIGI | DI18 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I21 | DIGI | DI19 | SIGNAL_OUT | R | 0...4294967295
10 | V37 | DIGI | DI19 Counter | UINT32 | R | 0...4294967295
10 | V38 | DIGI | DI19 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I22 | DIGI | DI20 | SIGNAL_OUT | R | 0...4294967295
10 | V39 | DIGI | DI20 Counter | UINT32 | R | 0...4294967295
10 | V40 | DIGI | DI20 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I23 | DIGI | DI21 | SIGNAL_OUT | R | 0...4294967295
10 | V41 | DIGI | DI21 Counter | UINT32 | R | 0...4294967295
10 | V42 | DIGI | DI21 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I24 | DIGI | DI22 | SIGNAL_OUT | R | 0...4294967295
10 | V43 | DIGI | DI22 Counter | UINT32 | R | 0...4294967295
10 | V44 | DIGI | DI22 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I25 | DIGI | DI23 | SIGNAL_OUT | R | 0...4294967295
10 | V45 | DIGI | DI23 Counter | UINT32 | R | 0...4294967295
10 | V46 | DIGI | DI23 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I26 | DIGI | DI24 | SIGNAL_OUT | R | 0...4294967295
10 | V47 | DIGI | DI24 Counter | UINT32 | R | 0...4294967295
10 | V48 | DIGI | DI24 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I27 | DIGI | DI25 | SIGNAL_OUT | R | 0...4294967295
10 | V49 | DIGI | DI25 Counter | UINT32 | R | 0...4294967295
10 | V50 | DIGI | DI25 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I28 | DIGI | DI26 | SIGNAL_OUT | R | 0...4294967295
10 | V51 | DIGI | DI26 Counter | UINT32 | R | 0...4294967295
10 | V52 | DIGI | DI26 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I29 | DIGI | DI27 | SIGNAL_OUT | R | 0...4294967295
10 | V53 | DIGI | DI27 Counter | UINT32 | R | 0...4294967295
10 | V54 | DIGI | DI27 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I30 | DIGI | DI28 | SIGNAL_OUT | R | 0...4294967295
10 | V55 | DIGI | DI28 Counter | UINT32 | R | 0...4294967295
10 | V56 | DIGI | DI28 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I31 | DIGI | DI29 | SIGNAL_OUT | R | 0...4294967295
10 | V57 | DIGI | DI29 Counter | UINT32 | R | 0...4294967295
10 | V58 | DIGI | DI29 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I32 | DIGI | DI30 | SIGNAL_OUT | R | 0...4294967295
10 | V59 | DIGI | DI30 Counter | UINT32 | R | 0...4294967295
10 | V60 | DIGI | DI30 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I33 | DIGI | DI31 | SIGNAL_OUT | R | 0...4294967295
10 | V61 | DIGI | DI31 Counter | UINT32 | R | 0...4294967295
10 | V62 | DIGI | DI31 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I34 | DIGI | DI32 | SIGNAL_OUT | R | 0...4294967295
10 | V63 | DIGI | DI32 Counter | UINT32 | R | 0...4294967295
10 | V64 | DIGI | DI32 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I35 | DIGI | DI33 | SIGNAL_OUT | R | 0...4294967295
10 | V65 | DIGI | DI33 Counter | UINT32 | R | 0...4294967295
10 | V66 | DIGI | DI33 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I36 | DIGI | DI34 | SIGNAL_OUT | R | 0...4294967295
10 | V67 | DIGI | DI34 Counter | UINT32 | R | 0...4294967295
10 | V68 | DIGI | DI34 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I37 | DIGI | DI35 | SIGNAL_OUT | R | 0...4294967295
10 | V69 | DIGI | DI35 Counter | UINT32 | R | 0...4294967295
10 | V70 | DIGI | DI35 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I38 | DIGI | DI36 | SIGNAL_OUT | R | 0...4294967295
10 | V71 | DIGI | DI36 Counter | UINT32 | R | 0...4294967295
10 | V72 | DIGI | DI36 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I39 | DIGI | DI37 | SIGNAL_OUT | R | 0...4294967295
10 | V73 | DIGI | DI37 Counter | UINT32 | R | 0...4294967295
10 | V74 | DIGI | DI37 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I40 | DIGI | DI38 | SIGNAL_OUT | R | 0...4294967295
10 | V75 | DIGI | DI38 Counter | UINT32 | R | 0...4294967295
10 | V76 | DIGI | DI38 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I41 | DIGI | DI39 | SIGNAL_OUT | R | 0...4294967295
10 | V77 | DIGI | DI39 Counter | UINT32 | R | 0...4294967295
10 | V78 | DIGI | DI39 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I42 | DIGI | DI40 | SIGNAL_OUT | R | 0...4294967295
10 | V79 | DIGI | DI40 Counter | UINT32 | R | 0...4294967295
10 | V80 | DIGI | DI40 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I43 | DIGI | DI41 | SIGNAL_OUT | R | 0...4294967295
10 | V81 | DIGI | DI41 Counter | UINT32 | R | 0...4294967295
10 | V82 | DIGI | DI41 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I44 | DIGI | DI42 | SIGNAL_OUT | R | 0...4294967295
10 | V83 | DIGI | DI42 Counter | UINT32 | R | 0...4294967295
10 | V84 | DIGI | DI42 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I45 | DIGI | DI43 | SIGNAL_OUT | R | 0...4294967295
10 | V85 | DIGI | DI43 Counter | UINT32 | R | 0...4294967295
10 | V86 | DIGI | DI43 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I46 | DIGI | DI44 | SIGNAL_OUT | R | 0...4294967295
10 | V87 | DIGI | DI44 Counter | UINT32 | R | 0...4294967295
10 | V88 | DIGI | DI44 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I47 | DIGI | DI45 | SIGNAL_OUT | R | 0...4294967295
10 | V89 | DIGI | DI45 Counter | UINT32 | R | 0...4294967295
10 | V90 | DIGI | DI45 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I48 | DIGI | DI46 | SIGNAL_OUT | R | 0...4294967295
10 | V91 | DIGI | DI46 Counter | UINT32 | R | 0...4294967295
10 | V92 | DIGI | DI46 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I49 | DIGI | DI47 | SIGNAL_OUT | R | 0...4294967295
10 | V93 | DIGI | DI47 Counter | UINT32 | R | 0...4294967295
10 | V94 | DIGI | DI47 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I50 | DIGI | DI48 | SIGNAL_OUT | R | 0...4294967295
10 | V95 | DIGI | DI48 Counter | UINT32 | R | 0...4294967295
10 | V96 | DIGI | DI48 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I51 | DIGI | DI49 | SIGNAL_OUT | R | 0...4294967295
10 | V97 | DIGI | DI49 Counter | UINT32 | R | 0...4294967295
10 | V98 | DIGI | DI49 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I52 | DIGI | DI50 | SIGNAL_OUT | R | 0...4294967295
10 | V99 | DIGI | DI50 Counter | UINT32 | R | 0...4294967295
10 | V100 | DIGI | DI50 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I53 | DIGI | DI51 | SIGNAL_OUT | R | 0...4294967295
10 | V101 | DIGI | DI51 Counter | UINT32 | R | 0...4294967295
10 | V102 | DIGI | DI51 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | S1 | DIGI | EventMaskLo | UINT32 | RW | 0...4294967295
10 | S2 | DIGI | EventMaskHi | UINT32 | RW | 0...4294967295
11 | S1 | DIGI2 | EventMaskLo | UINT32 | RW | 0...4294967295
11 | S2 | DIGI2 | EventMaskHi | UINT32 | RW | 0...4294967295
15 | O1 | RELE | Outputs status | UINT32 | R | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15
15 | O2 | RELE | OUT1 | SIGNAL_IN | RW | 0...4294967295
15 | O3 | RELE | OUT2 | SIGNAL_IN | RW | 0...4294967295
15 | O4 | RELE | OUT3 | SIGNAL_IN | RW | 0...4294967295
15 | O5 | RELE | OUT4 | SIGNAL_IN | RW | 0...4294967295
15 | O6 | RELE | OUT5 | SIGNAL_IN | RW | 0...4294967295
15 | O7 | RELE | OUT6 | SIGNAL_IN | RW | 0...4294967295
15 | O8 | RELE | OUT7 | SIGNAL_IN | RW | 0...4294967295
15 | O9 | RELE | OUT8 | SIGNAL_IN | RW | 0...4294967295
15 | O10 | RELE | OUT9 | SIGNAL_IN | RW | 0...4294967295
15 | O11 | RELE | OUT10 | SIGNAL_IN | RW | 0...4294967295
15 | O12 | RELE | OUT11 | SIGNAL_IN | RW | 0...4294967295
15 | O13 | RELE | OUT12 | SIGNAL_IN | RW | 0...4294967295
15 | O14 | RELE | OUT13 | SIGNAL_IN | RW | 0...4294967295
15 | O15 | RELE | OUT14 | SIGNAL_IN | RW | 0...4294967295
15 | O16 | RELE | OUT15 | SIGNAL_IN | RW | 0...4294967295
121 | O1 | LED | LED START | SIGNAL_IN | RW | 0...4294967295
121 | O2 | LED | LED TRIP | SIGNAL_IN | RW | 0...4294967295
121 | O3 | LED | User LED 1 | SIGNAL_IN | RW | 0...4294967295
121 | O4 | LED | User LED 2 | SIGNAL_IN | RW | 0...4294967295
121 | O5 | LED | User LED 3 | SIGNAL_IN | RW | 0...4294967295
121 | O6 | LED | User LED 4 | SIGNAL_IN | RW | 0...4294967295
121 | O7 | LED | User LED 5 | SIGNAL_IN | RW | 0...4294967295
121 | O8 | LED | User LED 6 | SIGNAL_IN | RW | 0...4294967295
121 | O9 | LED | User LED 7 | SIGNAL_IN | RW | 0...4294967295
121 | O10 | LED | User LED 8 | SIGNAL_IN | RW | 0...4294967295
121 | O11 | LED | User LED 9 | SIGNAL_IN | RW | 0...4294967295
121 | O12 | LED | User LED 10 | SIGNAL_IN | RW | 0...4294967295
121 | O13 | LED | User LED 11 | SIGNAL_IN | RW | 0...4294967295
121 | O14 | LED | User LED 12 | SIGNAL_IN | RW | 0...4294967295
121 | O15 | LED | User LED 13 | SIGNAL_IN | RW | 0...4294967295
121 | O16 | LED | User LED 14 | SIGNAL_IN | RW | 0...4294967295
121 | O17 | LED | User LED 15 | SIGNAL_IN | RW | 0...4294967295
121 | O18 | LED | User LED 16 | SIGNAL_IN | RW | 0...4294967295
122 | O1 | LEDX | User LED 17 | SIGNAL_IN | RW | 0...4294967295
122 | O2 | LEDX | User LED 18 | SIGNAL_IN | RW | 0...4294967295
122 | O3 | LEDX | User LED 19 | SIGNAL_IN | RW | 0...4294967295
122 | O4 | LEDX | User LED 20 | SIGNAL_IN | RW | 0...4294967295
122 | O5 | LEDX | User LED 21 | SIGNAL_IN | RW | 0...4294967295
122 | O6 | LEDX | User LED 22 | SIGNAL_IN | RW | 0...4294967295
122 | O7 | LEDX | User LED 23 | SIGNAL_IN | RW | 0...4294967295
122 | O8 | LEDX | User LED 24 | SIGNAL_IN | RW | 0...4294967295
122 | O9 | LEDX | User LED 25 | SIGNAL_IN | RW | 0...4294967295
122 | O10 | LEDX | User LED 26 | SIGNAL_IN | RW | 0...4294967295
122 | O11 | LEDX | User LED 27 | SIGNAL_IN | RW | 0...4294967295
122 | O12 | LEDX | User LED 28 | SIGNAL_IN | RW | 0...4294967295
122 | O13 | LEDX | User LED 29 | SIGNAL_IN | RW | 0...4294967295
122 | O14 | LEDX | User LED 30 | SIGNAL_IN | RW | 0...4294967295
122 | O15 | LEDX | User LED 31 | SIGNAL_IN | RW | 0...4294967295
122 | O16 | LEDX | User LED 32 | SIGNAL_IN | RW | 0...4294967295
122 | O17 | LEDX | User LED 33 | SIGNAL_IN | RW | 0...4294967295
122 | O18 | LEDX | User LED 34 | SIGNAL_IN | RW | 0...4294967295
122 | O19 | LEDX | User LED 35 | SIGNAL_IN | RW | 0...4294967295
122 | O20 | LEDX | User LED 36 | SIGNAL_IN | RW | 0...4294967295
122 | O21 | LEDX | User LED 37 | SIGNAL_IN | RW | 0...4294967295
122 | O22 | LEDX | User LED 38 | SIGNAL_IN | RW | 0...4294967295
122 | O23 | LEDX | User LED 39 | SIGNAL_IN | RW | 0...4294967295
122 | O24 | LEDX | User LED 40 | SIGNAL_IN | RW | 0...4294967295
122 | O25 | LEDX | User LED 41 | SIGNAL_IN | RW | 0...4294967295
122 | O26 | LEDX | User LED 42 | SIGNAL_IN | RW | 0...4294967295
122 | O27 | LEDX | User LED 43 | SIGNAL_IN | RW | 0...4294967295
122 | O28 | LEDX | User LED 44 | SIGNAL_IN | RW | 0...4294967295
122 | O29 | LEDX | User LED 45 | SIGNAL_IN | RW | 0...4294967295
122 | O30 | LEDX | User LED 46 | SIGNAL_IN | RW | 0...4294967295
122 | O31 | LEDX | User LED 47 | SIGNAL_IN | RW | 0...4294967295
122 | O32 | LEDX | User LED 48 | SIGNAL_IN | RW | 0...4294967295
65 | V1 | SGS | Active setting group | UINT32 | R | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
65 | S1 | SGS | Force SG | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | S2 | SGS | Force SG change | UINT32 | RW | 0=Disabled;1=Enabled
65 | S3 | SGS | Used setting groups | UINT32 | RW | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
65 | S4 | SGS | Remote SG change | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | O1 | SGS | Forced SG in use | SIGNAL_OUT | RW | 0...4294967295
65 | O2 | SGS | SG1 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O3 | SGS | SG2 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O4 | SGS | SG3 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O5 | SGS | SG4 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O6 | SGS | SG5 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O7 | SGS | SG6 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O8 | SGS | SG7 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O9 | SGS | SG8 Active | SIGNAL_OUT | RW | 0...4294967295
7 | I1 | CTRL | Local/Remote status | UINT32 | R | 0=Remote;1=Local
123 | V1 | DEV | Serial number | UINT32 | R | 0...4294967295
123 | V2 | DEV | SW version | STRING | R | ...32
124 | S1 | EVENT | Clear Events | UINT32 | RW | 0=-;1=Clear
125 | I1 | DIAG | Diagnostic alarm status | UINT32 | R | 0b=Temp. out of range;1b=Voltage out of range;2b=HW configuration invalid;3b=Relay output failure;4b=Option card A alarm;5b=Option card B alarm;6b=Option card C alarm;7b=Option card D alarm;8b=Option card E alarm;9b=Option card F alarm;10b=GOOSE invalid;
125 | S1 | DIAG | Clear diagnostic alarm | UINT32 | W | 0=-;1=Clear
125 | I2 | DIAG | Internal temperature | FLOAT | R | 0...200
125 | I3 | DIAG | Internal voltage 24V | FLOAT | R | 0...50
125 | I4 | DIAG | Internal voltage 24V max | FLOAT | R | 0...50
125 | I5 | DIAG | Internal voltage 24V min | FLOAT | R | 0...50
125 | I6 | DIAG | Internal voltage 24V deviation | FLOAT | R | 0...50
138 | I1 | MBIO | Input value | FLOAT | R | -101...2000
138 | I2 | MBIO | Input value | FLOAT | R | -101...2000
138 | I3 | MBIO | Input value | FLOAT | R | -101...2000
138 | I4 | MBIO | Input value | FLOAT | R | -101...2000
138 | I5 | MBIO | Input value | FLOAT | R | -101...2000
138 | I6 | MBIO | Input value | FLOAT | R | -101...2000
138 | I7 | MBIO | Input value | FLOAT | R | -101...2000
138 | I8 | MBIO | Input value | FLOAT | R | -101...2000
138 | I9 | MBIO | Input value | FLOAT | R | -101...2000
138 | I10 | MBIO | Input value | FLOAT | R | -101...2000
138 | I11 | MBIO | Input value | FLOAT | R | -101...2000
138 | I12 | MBIO | Input value | FLOAT | R | -101...2000
138 | I13 | MBIO | Input value | FLOAT | R | -101...2000
138 | I14 | MBIO | Input value | FLOAT | R | -101...2000
138 | I15 | MBIO | Input value | FLOAT | R | -101...2000
138 | I16 | MBIO | Input value | FLOAT | R | -101...2000
138 | I17 | MBIO | Input value | FLOAT | R | -101...2000
138 | I18 | MBIO | Input value | FLOAT | R | -101...2000
138 | I19 | MBIO | Input value | FLOAT | R | -101...2000
138 | I20 | MBIO | Input value | FLOAT | R | -101...2000
138 | I21 | MBIO | Input value | FLOAT | R | -101...2000
138 | I22 | MBIO | Input value | FLOAT | R | -101...2000
138 | I23 | MBIO | Input value | FLOAT | R | -101...2000
138 | I24 | MBIO | Input value | FLOAT | R | -101...2000
138 | I25 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I26 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I27 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I28 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I29 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I30 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I31 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I32 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I33 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I34 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I35 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I36 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I37 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I38 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I39 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I40 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I41 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I42 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I43 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I44 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I45 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I46 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I47 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I48 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | O1 | MBIO | MBIO ModA Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O2 | MBIO | MBIO ModA Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O3 | MBIO | MBIO ModA Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O4 | MBIO | MBIO ModA Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O5 | MBIO | MBIO ModA Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O6 | MBIO | MBIO ModA Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O7 | MBIO | MBIO ModA Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O8 | MBIO | MBIO ModA Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O9 | MBIO | MBIO ModB Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O10 | MBIO | MBIO ModB Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O11 | MBIO | MBIO ModB Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O12 | MBIO | MBIO ModB Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O13 | MBIO | MBIO ModB Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O14 | MBIO | MBIO ModB Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O15 | MBIO | MBIO ModB Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O16 | MBIO | MBIO ModB Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O17 | MBIO | MBIO ModC Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O18 | MBIO | MBIO ModC Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O19 | MBIO | MBIO ModC Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O20 | MBIO | MBIO ModC Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O21 | MBIO | MBIO ModC Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O22 | MBIO | MBIO ModC Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O23 | MBIO | MBIO ModC Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O24 | MBIO | MBIO ModC Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
139 | V1 | LOGIC | Reset Latches | UINT32 | RW | 0=-;1=Reset
8 | O1 | LOGIC1 | Logic out 1-32 | UINT32 | RW | 0...4294967295
139 | O1 | LOGIC | Logical Output 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O2 | LOGIC | Logical Output 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O3 | LOGIC | Logical Output 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O4 | LOGIC | Logical Output 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O5 | LOGIC | Logical Output 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O6 | LOGIC | Logical Output 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O7 | LOGIC | Logical Output 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O8 | LOGIC | Logical Output 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O9 | LOGIC | Logical Output 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O10 | LOGIC | Logical Output 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O11 | LOGIC | Logical Output 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O12 | LOGIC | Logical Output 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O13 | LOGIC | Logical Output 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O14 | LOGIC | Logical Output 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O15 | LOGIC | Logical Output 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O16 | LOGIC | Logical Output 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O17 | LOGIC | Logical Output 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O18 | LOGIC | Logical Output 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O19 | LOGIC | Logical Output 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O20 | LOGIC | Logical Output 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O21 | LOGIC | Logical Output 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O22 | LOGIC | Logical Output 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O23 | LOGIC | Logical Output 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O24 | LOGIC | Logical Output 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O25 | LOGIC | Logical Output 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O26 | LOGIC | Logical Output 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O27 | LOGIC | Logical Output 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O28 | LOGIC | Logical Output 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O29 | LOGIC | Logical Output 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O30 | LOGIC | Logical Output 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O31 | LOGIC | Logical Output 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O32 | LOGIC | Logical Output 32 | SIGNAL_OUT | RW | 0...4294967295
139 | O33 | LOGIC | Logical Input 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O34 | LOGIC | Logical Input 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O35 | LOGIC | Logical Input 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O36 | LOGIC | Logical Input 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O37 | LOGIC | Logical Input 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O38 | LOGIC | Logical Input 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O39 | LOGIC | Logical Input 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O40 | LOGIC | Logical Input 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O41 | LOGIC | Logical Input 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O42 | LOGIC | Logical Input 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O43 | LOGIC | Logical Input 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O44 | LOGIC | Logical Input 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O45 | LOGIC | Logical Input 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O46 | LOGIC | Logical Input 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O47 | LOGIC | Logical Input 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O48 | LOGIC | Logical Input 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O49 | LOGIC | Logical Input 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O50 | LOGIC | Logical Input 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O51 | LOGIC | Logical Input 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O52 | LOGIC | Logical Input 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O53 | LOGIC | Logical Input 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O54 | LOGIC | Logical Input 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O55 | LOGIC | Logical Input 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O56 | LOGIC | Logical Input 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O57 | LOGIC | Logical Input 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O58 | LOGIC | Logical Input 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O59 | LOGIC | Logical Input 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O60 | LOGIC | Logical Input 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O61 | LOGIC | Logical Input 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O62 | LOGIC | Logical Input 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O63 | LOGIC | Logical Input 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O64 | LOGIC | Logical Input 32 | SIGNAL_OUT | RW | 0...4294967295
8 | S1 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
8 | S2 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
9 | S1 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
9 | S2 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
140 | O1 | TIMER | Timer1 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O2 | TIMER | Timer2 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O3 | TIMER | Timer3 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O4 | TIMER | Timer4 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O5 | TIMER | Timer5 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O6 | TIMER | Timer6 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O7 | TIMER | Timer7 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O8 | TIMER | Timer8 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O9 | TIMER | Timer9 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O10 | TIMER | Timer10 Output | SIGNAL_OUT | RW | 0...4294967295
2 | I1 | IRF | Internal Relay Fault status | UINT32 | R | 0b=Storage error;1b=Logic file missing;2b=Aquisition unit error;3b=Measurement config error;4b=Relay hardware setup error;5b=System overload error;6b=Not configured yet;7b=Firmware upgrade done;8b=Slot supervision error;9b=Software inconsistency error;10b=Safe setting mode active;
2 | S1 | IRF | Clear Fault status | UINT32 | W | 0=-;1=Clear
2 | I2 | IRF | Option card health status | UINT32 | R | 0b=Baseboard fault;1b=Card slot A fault;2b=Card slot B fault;3b=Card slot C fault;4b=Card slot D fault;5b=Card slot E fault;6b=Card slot F fault;
20 | S1 | NOC1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
20 | V1 | NOC1 | I> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
20 | V2 | NOC1 | I> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
20 | I1 | NOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
20 | I2 | NOC1 | I> starts | UINT32 | R | 0...4294967295
20 | I3 | NOC1 | I> trips | UINT32 | R | 0...4294967295
20 | I4 | NOC1 | I> blocks | UINT32 | R | 0...4294967295
20 | S2 | NOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
20 | S3 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S4 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S5 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S6 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S7 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S8 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S9 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S10 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S11 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S12 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S13 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S14 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S15 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S16 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S17 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S18 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S19 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S20 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S21 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S22 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S23 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S24 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S25 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S26 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S27 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S28 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S29 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S30 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S31 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S32 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S33 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S34 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | O1 | NOC1 | I> START (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O2 | NOC1 | I> START(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O3 | NOC1 | I> START(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O4 | NOC1 | I> START(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O5 | NOC1 | I> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O6 | NOC1 | I> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O7 | NOC1 | I> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O8 | NOC1 | I> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O9 | NOC1 | I> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
20 | V3 | NOC1 | Newest Register | UINT32 | R | 0...12
20 | V4 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V5 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V6 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V7 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V8 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V9 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V10 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V11 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V12 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V13 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V14 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V15 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V16 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V17 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V18 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V19 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V20 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V21 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V22 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V23 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V24 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V25 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V26 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V27 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V28 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V29 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V30 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V31 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V32 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V33 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V34 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V35 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V36 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V37 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V38 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V39 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | S35 | NOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
21 | S1 | NOC2 | I>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
21 | S2 | NOC2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
21 | V1 | NOC2 | I>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
21 | V2 | NOC2 | I>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
21 | I1 | NOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
21 | I2 | NOC2 | I>> starts | UINT32 | R | 0...4294967295
21 | I3 | NOC2 | I>> trips | UINT32 | R | 0...4294967295
21 | I4 | NOC2 | I>> blocks | UINT32 | R | 0...4294967295
21 | S3 | NOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
21 | S4 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S5 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S6 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S7 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S8 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S9 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S10 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S11 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S12 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S13 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S14 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S15 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S16 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S17 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S18 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S19 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S20 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S21 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S22 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S23 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S24 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S25 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S26 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S27 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S28 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S29 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S30 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S31 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S32 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S33 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S34 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S35 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | O1 | NOC2 | I>> START (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O2 | NOC2 | I>> START(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O3 | NOC2 | I>> START(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O4 | NOC2 | I>> START(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O5 | NOC2 | I>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O6 | NOC2 | I>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O7 | NOC2 | I>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O8 | NOC2 | I>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O9 | NOC2 | I>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
21 | V3 | NOC2 | Newest Register | UINT32 | R | 0...12
21 | V4 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V5 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V6 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V7 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V8 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V9 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V10 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V11 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V12 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V13 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V14 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V15 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V16 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V17 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V18 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V19 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V20 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V21 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V22 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V23 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V24 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V25 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V26 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V27 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V28 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V29 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V30 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V31 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V32 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V33 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V34 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V35 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V36 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V37 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V38 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V39 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | S36 | NOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
22 | S1 | NOC3 | I>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
22 | S2 | NOC3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
22 | V1 | NOC3 | I>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
22 | V2 | NOC3 | I>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
22 | I1 | NOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
22 | I2 | NOC3 | I>>> starts | UINT32 | R | 0...4294967295
22 | I3 | NOC3 | I>>> trips | UINT32 | R | 0...4294967295
22 | I4 | NOC3 | I>>> blocks | UINT32 | R | 0...4294967295
22 | S3 | NOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
22 | S4 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S5 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S6 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S7 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S8 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S9 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S10 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S11 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S12 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S13 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S14 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S15 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S16 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S17 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S18 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S19 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S20 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S21 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S22 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S23 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S24 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S25 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S26 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S27 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S28 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S29 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S30 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S31 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S32 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S33 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S34 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S35 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | O1 | NOC3 | I>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O2 | NOC3 | I>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O3 | NOC3 | I>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O4 | NOC3 | I>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O5 | NOC3 | I>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O6 | NOC3 | I>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O7 | NOC3 | I>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O8 | NOC3 | I>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O9 | NOC3 | I>>>BLOCKED | SIGNAL_OUT | RW | 0...4294967295
22 | V3 | NOC3 | Newest Register | UINT32 | R | 0...12
22 | V4 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V5 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V6 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V7 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V8 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V9 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V10 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V11 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V12 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V13 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V14 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V15 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V16 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V17 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V18 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V19 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V20 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V21 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V22 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V23 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V24 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V25 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V26 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V27 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V28 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V29 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V30 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V31 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V32 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V33 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V34 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V35 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V36 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V37 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V38 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V39 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | S36 | NOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
23 | S1 | NOC4 | I>>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
23 | S2 | NOC4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
23 | V1 | NOC4 | I>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
23 | V2 | NOC4 | I>>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
23 | I1 | NOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
23 | I2 | NOC4 | I>>>> starts | UINT32 | R | 0...4294967295
23 | I3 | NOC4 | I>>>> trips | UINT32 | R | 0...4294967295
23 | I4 | NOC4 | I>>>> blocks | UINT32 | R | 0...4294967295
23 | S3 | NOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
23 | S4 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S5 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S6 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S7 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S8 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S9 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S10 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S11 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S12 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S13 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S14 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S15 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S16 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S17 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S18 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S19 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S20 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S21 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S22 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S23 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S24 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S25 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S26 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S27 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S28 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S29 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S30 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S31 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S32 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S33 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S34 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S35 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | O1 | NOC4 | I>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O2 | NOC4 | I>>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O3 | NOC4 | I>>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O4 | NOC4 | I>>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O5 | NOC4 | I>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O6 | NOC4 | I>>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O7 | NOC4 | I>>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O8 | NOC4 | I>>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O9 | NOC4 | I>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
23 | V3 | NOC4 | Newest Register | UINT32 | R | 0...12
23 | V4 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V5 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V6 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V7 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V8 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V9 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V10 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V11 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V12 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V13 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V14 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V15 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V16 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V17 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V18 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V19 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V20 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V21 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V22 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V23 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V24 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V25 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V26 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V27 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V28 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V29 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V30 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V31 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V32 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V33 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V34 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V35 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V36 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V37 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V38 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V39 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | S36 | NOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
205 | V1 | ROC1 | Idrw> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
205 | I1 | ROC1 | Idrw> Imeas/Iset at the moment | FLOAT | R | -1250...1250
205 | I2 | ROC1 | Idrw> I/U Angle atm. | FLOAT | R | -360...360
205 | I3 | ROC1 | Idrw> I measured p.u. | FLOAT | R | 0...1250
205 | I4 | ROC1 | Idrw> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
205 | I5 | ROC1 | Idrw> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
205 | I6 | ROC1 | Idrw> U measured p.u. | FLOAT | R | 0...1250
205 | I7 | ROC1 | Idrw> starts | UINT32 | R | 0...4294967295
205 | I8 | ROC1 | Idrw> trips | UINT32 | R | 0...4294967295
205 | I9 | ROC1 | Idrw> blocks | UINT32 | R | 0...4294967295
205 | S1 | ROC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
205 | S2 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S3 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S4 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S5 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S6 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S7 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S8 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S9 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S10 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S11 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S12 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S13 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S14 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S15 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S16 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S17 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S18 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S19 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S20 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S21 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S22 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S23 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S24 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S25 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S26 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S27 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S28 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S29 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S30 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S31 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S32 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S33 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S34 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S35 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S36 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S37 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S38 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S39 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S40 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S41 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S42 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S43 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S44 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S45 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S46 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S47 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S48 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S49 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S50 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S51 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S52 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S53 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S54 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S55 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S56 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S57 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S58 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S59 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S60 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S61 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S62 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S63 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S64 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S65 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | O1 | ROC1 | Idrw> START | SIGNAL_OUT | RW | 0...4294967295
205 | O2 | ROC1 | Idrw> TRIP | SIGNAL_OUT | RW | 0...4294967295
205 | O3 | ROC1 | Idrw> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
205 | V2 | ROC1 | Newest Register | UINT32 | R | 0...12
205 | V3 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V4 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V5 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V6 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V7 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V8 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V9 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V10 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V11 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V12 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V13 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V14 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V15 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V16 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V17 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V18 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V19 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V20 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V21 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V22 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V23 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V24 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V25 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V26 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | S66 | ROC1 | EventMaskLo | UINT32 | RW | 0...4294967295
206 | V1 | ROC2 | Idrw>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
206 | I1 | ROC2 | Idrw>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
206 | I2 | ROC2 | Idrw>> I/U Angle atm. | FLOAT | R | -360...360
206 | I3 | ROC2 | Idrw>> I measured p.u. | FLOAT | R | 0...1250
206 | I4 | ROC2 | Idrw>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
206 | I5 | ROC2 | Idrw>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
206 | I6 | ROC2 | Idrw>> U measured p.u. | FLOAT | R | 0...1250
206 | I7 | ROC2 | Idrw>> starts | UINT32 | R | 0...4294967295
206 | I8 | ROC2 | Idrw>> trips | UINT32 | R | 0...4294967295
206 | I9 | ROC2 | Idrw>> blocks | UINT32 | R | 0...4294967295
206 | S1 | ROC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
206 | S2 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S3 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S4 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S5 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S6 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S7 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S8 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S9 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S10 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S11 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S12 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S13 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S14 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S15 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S16 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S17 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S18 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S19 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S20 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S21 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S22 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S23 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S24 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S25 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S26 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S27 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S28 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S29 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S30 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S31 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S32 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S33 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S34 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S35 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S36 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S37 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S38 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S39 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S40 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S41 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S42 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S43 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S44 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S45 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S46 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S47 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S48 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S49 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S50 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S51 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S52 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S53 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S54 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S55 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S56 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S57 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S58 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S59 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S60 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S61 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S62 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S63 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S64 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S65 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | O1 | ROC2 | Idrw>> START | SIGNAL_OUT | RW | 0...4294967295
206 | O2 | ROC2 | Idrw>> TRIP | SIGNAL_OUT | RW | 0...4294967295
206 | O3 | ROC2 | Idrw>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
206 | V2 | ROC2 | Newest Register | UINT32 | R | 0...12
206 | V3 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V4 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V5 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V6 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V7 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V8 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V9 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V10 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V11 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V12 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V13 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V14 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V15 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V16 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V17 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V18 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V19 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V20 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V21 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V22 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V23 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V24 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V25 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V26 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | S66 | ROC2 | EventMaskLo | UINT32 | RW | 0...4294967295
207 | V1 | ROC3 | Idrw>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
207 | I1 | ROC3 | Idrw>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
207 | I2 | ROC3 | Idrw>>> I/U Angle atm. | FLOAT | R | -360...360
207 | I3 | ROC3 | Idrw>>> I measured p.u. | FLOAT | R | 0...1250
207 | I4 | ROC3 | Idrw>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
207 | I5 | ROC3 | Idrw>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
207 | I6 | ROC3 | Idrw>>> U measured p.u. | FLOAT | R | 0...1250
207 | I7 | ROC3 | Idrw>>> starts | UINT32 | R | 0...4294967295
207 | I8 | ROC3 | Idrw>>> trips | UINT32 | R | 0...4294967295
207 | I9 | ROC3 | Idrw>>> blocks | UINT32 | R | 0...4294967295
207 | S1 | ROC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
207 | S2 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S3 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S4 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S5 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S6 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S7 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S8 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S9 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S10 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S11 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S12 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S13 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S14 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S15 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S16 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S17 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S18 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S19 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S20 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S21 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S22 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S23 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S24 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S25 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S26 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S27 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S28 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S29 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S30 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S31 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S32 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S33 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S34 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S35 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S36 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S37 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S38 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S39 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S40 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S41 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S42 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S43 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S44 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S45 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S46 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S47 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S48 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S49 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S50 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S51 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S52 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S53 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S54 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S55 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S56 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S57 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S58 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S59 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S60 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S61 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S62 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S63 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S64 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S65 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | O1 | ROC3 | Idrw>>> START | SIGNAL_OUT | RW | 0...4294967295
207 | O2 | ROC3 | Idrw>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
207 | O3 | ROC3 | Idrw>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
207 | V2 | ROC3 | Newest Register | UINT32 | R | 0...12
207 | V3 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V4 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V5 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V6 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V7 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V8 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V9 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V10 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V11 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V12 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V13 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V14 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V15 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V16 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V17 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V18 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V19 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V20 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V21 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V22 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V23 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V24 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V25 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V26 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | S66 | ROC3 | EventMaskLo | UINT32 | RW | 0...4294967295
208 | V1 | ROC4 | Idrw>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
208 | I1 | ROC4 | Idrw>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
208 | I2 | ROC4 | Idrw>>>> I/U Angle atm. | FLOAT | R | -360...360
208 | I3 | ROC4 | Idrw>>>> I measured p.u. | FLOAT | R | 0...1250
208 | I4 | ROC4 | Idrw>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
208 | I5 | ROC4 | Idrw>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
208 | I6 | ROC4 | Idrw>>>> U measured p.u. | FLOAT | R | 0...1250
208 | I7 | ROC4 | Idrw>>>> starts | UINT32 | R | 0...4294967295
208 | I8 | ROC4 | Idrw>>>> trips | UINT32 | R | 0...4294967295
208 | I9 | ROC4 | Idrw>>>> blocks | UINT32 | R | 0...4294967295
208 | S1 | ROC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
208 | S2 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S3 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S4 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S5 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S6 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S7 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S8 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S9 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S10 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S11 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S12 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S13 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S14 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S15 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S16 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S17 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S18 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S19 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S20 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S21 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S22 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S23 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S24 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S25 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S26 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S27 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S28 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S29 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S30 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S31 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S32 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S33 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S34 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S35 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S36 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S37 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S38 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S39 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S40 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S41 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S42 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S43 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S44 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S45 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S46 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S47 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S48 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S49 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S50 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S51 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S52 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S53 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S54 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S55 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S56 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S57 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S58 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S59 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S60 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S61 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S62 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S63 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S64 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S65 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | O1 | ROC4 | Idrw>>>> START | SIGNAL_OUT | RW | 0...4294967295
208 | O2 | ROC4 | Idrw>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
208 | O3 | ROC4 | Idrw>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
208 | V2 | ROC4 | Newest Register | UINT32 | R | 0...12
208 | V3 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V4 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V5 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V6 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V7 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V8 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V9 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V10 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V11 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V12 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V13 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V14 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V15 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V16 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V17 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V18 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V19 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V20 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V21 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V22 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V23 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V24 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V25 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V26 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | S66 | ROC4 | EventMaskLo | UINT32 | RW | 0...4294967295
209 | V1 | ROC5 | Idrw>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
209 | I1 | ROC5 | Idrw>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
209 | I2 | ROC5 | Idrw>>>>> I/U Angle atm. | FLOAT | R | -360...360
209 | I3 | ROC5 | Idrw>>>>> I measured p.u. | FLOAT | R | 0...1250
209 | I4 | ROC5 | Idrw>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
209 | I5 | ROC5 | Idrw>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
209 | I6 | ROC5 | Idrw>>>>> U measured p.u. | FLOAT | R | 0...1250
209 | I7 | ROC5 | Idrw>>>>> starts | UINT32 | R | 0...4294967295
209 | I8 | ROC5 | Idrw>>>>> trips | UINT32 | R | 0...4294967295
209 | I9 | ROC5 | Idrw>>>>> blocks | UINT32 | R | 0...4294967295
209 | S1 | ROC5 | Clear statistics | UINT32 | W | 0=-;1=Clear
209 | S2 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S3 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S4 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S5 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S6 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S7 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S8 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S9 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S10 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S11 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S12 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S13 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S14 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S15 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S16 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S17 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S18 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S19 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S20 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S21 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S22 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S23 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S24 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S25 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S26 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S27 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S28 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S29 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S30 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S31 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S32 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S33 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S34 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S35 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S36 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S37 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S38 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S39 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S40 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S41 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S42 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S43 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S44 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S45 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S46 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S47 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S48 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S49 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S50 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S51 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S52 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S53 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S54 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S55 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S56 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S57 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S58 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S59 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S60 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S61 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S62 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S63 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S64 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S65 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | O1 | ROC5 | Idrw>>>>> START | SIGNAL_OUT | RW | 0...4294967295
209 | O2 | ROC5 | Idrw>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
209 | O3 | ROC5 | Idrw>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
209 | V2 | ROC5 | Newest Register | UINT32 | R | 0...12
209 | V3 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V4 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V5 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V6 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V7 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V8 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V9 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V10 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V11 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V12 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V13 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V14 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V15 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V16 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V17 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V18 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V19 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V20 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V21 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V22 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V23 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V24 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V25 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V26 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | S66 | ROC5 | EventMaskLo | UINT32 | RW | 0...4294967295
210 | V1 | ROC6 | Idrw>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
210 | I1 | ROC6 | Idrw>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
210 | I2 | ROC6 | Idrw>>>>>> I/U Angle atm. | FLOAT | R | -360...360
210 | I3 | ROC6 | Idrw>>>>>> I measured p.u. | FLOAT | R | 0...1250
210 | I4 | ROC6 | Idrw>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
210 | I5 | ROC6 | Idrw>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
210 | I6 | ROC6 | Idrw>>>>>> U measured p.u. | FLOAT | R | 0...1250
210 | I7 | ROC6 | Idrw>>>>>> starts | UINT32 | R | 0...4294967295
210 | I8 | ROC6 | Idrw>>>>>> trips | UINT32 | R | 0...4294967295
210 | I9 | ROC6 | Idrw>>>>>> blocks | UINT32 | R | 0...4294967295
210 | S1 | ROC6 | Clear statistics | UINT32 | W | 0=-;1=Clear
210 | S2 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S3 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S4 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S5 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S6 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S7 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S8 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S9 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S10 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S11 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S12 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S13 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S14 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S15 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S16 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S17 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S18 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S19 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S20 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S21 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S22 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S23 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S24 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S25 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S26 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S27 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S28 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S29 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S30 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S31 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S32 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S33 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S34 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S35 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S36 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S37 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S38 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S39 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S40 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S41 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S42 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S43 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S44 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S45 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S46 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S47 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S48 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S49 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S50 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S51 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S52 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S53 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S54 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S55 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S56 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S57 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S58 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S59 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S60 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S61 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S62 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S63 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S64 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S65 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | O1 | ROC6 | Idrw>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
210 | O2 | ROC6 | Idrw>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
210 | O3 | ROC6 | Idrw>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
210 | V2 | ROC6 | Newest Register | UINT32 | R | 0...12
210 | V3 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V4 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V5 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V6 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V7 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V8 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V9 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V10 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V11 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V12 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V13 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V14 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V15 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V16 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V17 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V18 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V19 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V20 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V21 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V22 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V23 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V24 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V25 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V26 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | S66 | ROC6 | EventMaskLo | UINT32 | RW | 0...4294967295
211 | V1 | ROC7 | Idrw>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
211 | I1 | ROC7 | Idrw>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
211 | I2 | ROC7 | Idrw>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
211 | I3 | ROC7 | Idrw>>>>>>> I measured p.u. | FLOAT | R | 0...1250
211 | I4 | ROC7 | Idrw>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
211 | I5 | ROC7 | Idrw>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
211 | I6 | ROC7 | Idrw>>>>>>> U measured p.u. | FLOAT | R | 0...1250
211 | I7 | ROC7 | Idrw>>>>>>> starts | UINT32 | R | 0...4294967295
211 | I8 | ROC7 | Idrw>>>>>>> trips | UINT32 | R | 0...4294967295
211 | I9 | ROC7 | Idrw>>>>>>> blocks | UINT32 | R | 0...4294967295
211 | S1 | ROC7 | Clear statistics | UINT32 | W | 0=-;1=Clear
211 | S2 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S3 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S4 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S5 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S6 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S7 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S8 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S9 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S10 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S11 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S12 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S13 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S14 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S15 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S16 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S17 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S18 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S19 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S20 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S21 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S22 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S23 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S24 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S25 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S26 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S27 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S28 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S29 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S30 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S31 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S32 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S33 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S34 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S35 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S36 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S37 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S38 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S39 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S40 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S41 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S42 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S43 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S44 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S45 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S46 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S47 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S48 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S49 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S50 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S51 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S52 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S53 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S54 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S55 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S56 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S57 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S58 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S59 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S60 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S61 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S62 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S63 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S64 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S65 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | O1 | ROC7 | Idrw>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
211 | O2 | ROC7 | Idrw>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
211 | O3 | ROC7 | Idrw>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
211 | V2 | ROC7 | Newest Register | UINT32 | R | 0...12
211 | V3 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V4 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V5 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V6 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V7 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V8 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V9 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V10 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V11 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V12 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V13 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V14 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V15 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V16 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V17 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V18 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V19 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V20 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V21 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V22 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V23 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V24 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V25 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V26 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | S66 | ROC7 | EventMaskLo | UINT32 | RW | 0...4294967295
212 | V1 | ROC8 | Idrw>>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
212 | I1 | ROC8 | Idrw>>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
212 | I2 | ROC8 | Idrw>>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
212 | I3 | ROC8 | Idrw>>>>>>>> I measured p.u. | FLOAT | R | 0...1250
212 | I4 | ROC8 | Idrw>>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
212 | I5 | ROC8 | Idrw>>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
212 | I6 | ROC8 | Idrw>>>>>>>> U measured p.u. | FLOAT | R | 0...1250
212 | I7 | ROC8 | Idrw>>>>>>>> starts | UINT32 | R | 0...4294967295
212 | I8 | ROC8 | Idrw>>>>>>>> trips | UINT32 | R | 0...4294967295
212 | I9 | ROC8 | Idrw>>>>>>>> blocks | UINT32 | R | 0...4294967295
212 | S1 | ROC8 | Clear statistics | UINT32 | W | 0=-;1=Clear
212 | S2 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S3 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S4 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S5 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S6 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S7 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S8 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S9 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S10 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S11 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S12 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S13 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S14 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S15 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S16 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S17 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S18 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S19 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S20 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S21 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S22 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S23 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S24 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S25 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S26 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S27 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S28 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S29 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S30 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S31 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S32 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S33 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S34 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S35 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S36 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S37 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S38 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S39 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S40 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S41 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S42 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S43 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S44 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S45 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S46 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S47 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S48 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S49 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S50 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S51 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S52 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S53 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S54 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S55 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S56 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S57 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S58 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S59 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S60 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S61 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S62 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S63 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S64 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S65 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | O1 | ROC8 | Idrw>>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
212 | O2 | ROC8 | Idrw>>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
212 | O3 | ROC8 | Idrw>>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
212 | V2 | ROC8 | Newest Register | UINT32 | R | 0...12
212 | V3 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V4 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V5 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V6 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V7 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V8 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V9 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V10 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V11 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V12 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V13 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V14 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V15 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V16 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V17 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V18 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V19 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V20 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V21 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V22 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V23 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V24 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V25 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V26 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | S66 | ROC8 | EventMaskLo | UINT32 | RW | 0...4294967295
213 | V1 | ROV1 | Urw>/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
213 | I1 | ROV1 | Urw>/< Umeas/Uset at the moment | FLOAT | R | 0...1250
213 | I2 | ROV1 | Urw>/< U measured p.u. | FLOAT | R | 0...1250
213 | I3 | ROV1 | Urw>/< starts | UINT32 | R | 0...4294967295
213 | I4 | ROV1 | Urw>/< trips | UINT32 | R | 0...4294967295
213 | I5 | ROV1 | Urw>/< blocks | UINT32 | R | 0...4294967295
213 | S1 | ROV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
213 | S2 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S3 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S4 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S5 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S6 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S7 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S8 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S9 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S10 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S11 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S12 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S13 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S14 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S15 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S16 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S17 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S18 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S19 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S20 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S21 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S22 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S23 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S24 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S25 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S26 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S27 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S28 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S29 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S30 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S31 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S32 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S33 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S34 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S35 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S36 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S37 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S38 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S39 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S40 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S41 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S42 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S43 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S44 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S45 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S46 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S47 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S48 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S49 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | O1 | ROV1 | Urw>/< START | SIGNAL_OUT | RW | 0...4294967295
213 | O2 | ROV1 | Urw>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
213 | O3 | ROV1 | Urw>/< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
213 | O4 | ROV1 | Urw>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
213 | V2 | ROV1 | Newest Register | UINT32 | R | 0...12
213 | V3 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V4 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V5 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V6 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V7 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V8 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V9 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V10 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V11 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V12 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V13 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V14 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V15 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V16 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V17 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V18 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V19 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V20 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V21 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V22 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V23 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V24 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V25 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V26 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | S50 | ROV1 | EventMaskLo | UINT32 | RW | 0...4294967295
214 | V1 | ROV2 | Urw>>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
214 | I1 | ROV2 | Urw>>/<< Umeas/Uset at the moment | FLOAT | R | 0...1250
214 | I2 | ROV2 | Urw>>/<< U measured p.u. | FLOAT | R | 0...1250
214 | I3 | ROV2 | Urw>>/<< starts | UINT32 | R | 0...4294967295
214 | I4 | ROV2 | Urw>>/<< trips | UINT32 | R | 0...4294967295
214 | I5 | ROV2 | Urw>>/<< blocks | UINT32 | R | 0...4294967295
214 | S1 | ROV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
214 | S2 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S3 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S4 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S5 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S6 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S7 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S8 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S9 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S10 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S11 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S12 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S13 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S14 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S15 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S16 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S17 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S18 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S19 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S20 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S21 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S22 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S23 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S24 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S25 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S26 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S27 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S28 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S29 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S30 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S31 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S32 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S33 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S34 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S35 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S36 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S37 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S38 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S39 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S40 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S41 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S42 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S43 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S44 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S45 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S46 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S47 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S48 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S49 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | O1 | ROV2 | Urw>>/<< START | SIGNAL_OUT | RW | 0...4294967295
214 | O2 | ROV2 | Urw>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
214 | O3 | ROV2 | Urw>>/<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
214 | O4 | ROV2 | Urw>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
214 | V2 | ROV2 | Newest Register | UINT32 | R | 0...12
214 | V3 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V4 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V5 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V6 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V7 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V8 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V9 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V10 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V11 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V12 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V13 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V14 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V15 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V16 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V17 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V18 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V19 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V20 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V21 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V22 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V23 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V24 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V25 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V26 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | S50 | ROV2 | EventMaskLo | UINT32 | RW | 0...4294967295
215 | V1 | ROV3 | Urw>>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
215 | I1 | ROV3 | Urw>>>/<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
215 | I2 | ROV3 | Urw>>>/<<< U measured p.u. | FLOAT | R | 0...1250
215 | I3 | ROV3 | Urw>>>/<<< starts | UINT32 | R | 0...4294967295
215 | I4 | ROV3 | Urw>>>/<<< trips | UINT32 | R | 0...4294967295
215 | I5 | ROV3 | Urw>>>/<<< blocks | UINT32 | R | 0...4294967295
215 | S1 | ROV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
215 | S2 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S3 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S4 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S5 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S6 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S7 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S8 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S9 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S10 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S11 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S12 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S13 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S14 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S15 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S16 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S17 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S18 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S19 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S20 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S21 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S22 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S23 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S24 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S25 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S26 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S27 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S28 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S29 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S30 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S31 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S32 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S33 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S34 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S35 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S36 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S37 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S38 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S39 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S40 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S41 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S42 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S43 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S44 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S45 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S46 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S47 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S48 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S49 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | O1 | ROV3 | Urw>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
215 | O2 | ROV3 | Urw>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
215 | O3 | ROV3 | Urw>>>/<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
215 | O4 | ROV3 | Urw>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
215 | V2 | ROV3 | Newest Register | UINT32 | R | 0...12
215 | V3 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V4 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V5 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V6 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V7 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V8 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V9 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V10 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V11 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V12 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V13 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V14 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V15 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V16 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V17 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V18 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V19 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V20 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V21 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V22 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V23 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V24 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V25 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V26 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | S50 | ROV3 | EventMaskLo | UINT32 | RW | 0...4294967295
216 | V1 | ROV4 | Urw>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
216 | I1 | ROV4 | Urw>>>>/<<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
216 | I2 | ROV4 | Urw>>>>/<<<< U measured p.u. | FLOAT | R | 0...1250
216 | I3 | ROV4 | Urw>>>>/<<<< starts | UINT32 | R | 0...4294967295
216 | I4 | ROV4 | Urw>>>>/<<<< trips | UINT32 | R | 0...4294967295
216 | I5 | ROV4 | Urw>>>>/<<<< blocks | UINT32 | R | 0...4294967295
216 | S1 | ROV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
216 | S2 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S3 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S4 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S5 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S6 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S7 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S8 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S9 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S10 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S11 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S12 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S13 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S14 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S15 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S16 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S17 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S18 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S19 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S20 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S21 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S22 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S23 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S24 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S25 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S26 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S27 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S28 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S29 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S30 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S31 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S32 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S33 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S34 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S35 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S36 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S37 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S38 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S39 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S40 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S41 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S42 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S43 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S44 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S45 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S46 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S47 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S48 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S49 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | O1 | ROV4 | Urw>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
216 | O2 | ROV4 | Urw>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
216 | O3 | ROV4 | Urw>>>>/<<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
216 | O4 | ROV4 | Urw>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
216 | V2 | ROV4 | Newest Register | UINT32 | R | 0...12
216 | V3 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V4 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V5 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V6 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V7 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V8 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V9 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V10 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V11 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V12 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V13 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V14 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V15 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V16 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V17 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V18 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V19 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V20 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V21 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V22 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V23 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V24 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V25 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V26 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | S50 | ROV4 | EventMaskLo | UINT32 | RW | 0...4294967295
224 | I1 | CNU1 | Measured unbalance current | FLOAT | R | 0...50.00
224 | I2 | CNU1 | Unbalance current angle | FLOAT | R | -360.00...360.00
224 | S1 | CNU1 | Natural unbalance compensation | UINT32 | RW | 0=Not used;1=In use
224 | S2 | CNU1 | Compensate natural unbal. | UINT32 | RW | 0=-;1=Comp
224 | I3 | CNU1 | Natural unbalance | FLOAT | R | -50.00...50.00
224 | I4 | CNU1 | Natural unbalance ang | FLOAT | R | -360.00...360.00
224 | I5 | CNU1 | Compensated magnitude | FLOAT | R | -50.00...50.00
224 | I6 | CNU1 | Compensated angle | FLOAT | R | -360.00...360.00
217 | V1 | UCP1 | IUC> condition | UINT32 | R | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
217 | I1 | UCP1 | Unbalance current atm. | FLOAT | R | 0...1250
217 | I2 | UCP1 | Imeas/Iset (ALARM) atm. | FLOAT | R | 0...1250
217 | I3 | UCP1 | Imeas/Iset (TRIP) atm. | FLOAT | R | 0...1250
217 | I4 | UCP1 | IUC> Alarm Starts | UINT32 | R | 0...4294967295
217 | I5 | UCP1 | IUC> Alarms | UINT32 | R | 0...4294967295
217 | I6 | UCP1 | IUC> Starts | UINT32 | R | 0...4294967295
217 | I7 | UCP1 | IUC> Trips | UINT32 | R | 0...4294967295
217 | I8 | UCP1 | IUC> Blocks | UINT32 | R | 0...4294967295
217 | S1 | UCP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
217 | S2 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S3 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S4 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S5 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S6 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S7 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S8 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S9 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S10 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S11 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S12 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S13 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S14 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S15 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S16 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S17 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S18 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S19 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S20 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S21 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S22 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S23 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S24 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S25 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S26 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S27 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S28 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S29 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S30 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S31 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S32 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S33 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S34 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S35 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S36 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S37 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S38 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S39 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S40 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S41 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | O1 | UCP1 | IUC> ALARM START | SIGNAL_OUT | RW | 0...4294967295
217 | O2 | UCP1 | IUC> ALARM | SIGNAL_OUT | RW | 0...4294967295
217 | O3 | UCP1 | IUC> START | SIGNAL_OUT | RW | 0...4294967295
217 | O4 | UCP1 | IUC> TRIP | SIGNAL_OUT | RW | 0...4294967295
217 | O5 | UCP1 | IUC> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
217 | V2 | UCP1 | Newest Register | UINT32 | R | 0...12
217 | V3 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V4 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V5 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V6 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V7 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V8 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V9 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V10 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V11 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V12 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V13 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V14 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | S42 | UCP1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S1 | DOC1 | Idir> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
75 | V1 | DOC1 | Idir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
75 | I1 | DOC1 | Operating angle now | FLOAT | R | -360...360
75 | I2 | DOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
75 | I3 | DOC1 | Idir> starts | UINT32 | R | 0...4294967295
75 | I4 | DOC1 | Idir> trips | UINT32 | R | 0...4294967295
75 | I5 | DOC1 | Idir> blocks | UINT32 | R | 0...4294967295
75 | S2 | DOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
75 | S3 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S4 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S5 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S6 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S7 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S8 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S9 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S10 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S11 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S12 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S13 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S14 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S15 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S16 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S17 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S18 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S19 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S20 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S21 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S22 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S23 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S24 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S25 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S26 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S27 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S28 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S29 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S30 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S31 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S32 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S33 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S34 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S35 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S36 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S37 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S38 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S39 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S40 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S41 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S42 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S43 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S44 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S45 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S46 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S47 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S48 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S49 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S50 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S51 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S52 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S53 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S54 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S55 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S56 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S57 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S58 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | O1 | DOC1 | Idir> START | SIGNAL_OUT | RW | 0...4294967295
75 | O2 | DOC1 | Idir> TRIP | SIGNAL_OUT | RW | 0...4294967295
75 | O3 | DOC1 | Idir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
75 | S59 | DOC1 | Clear registers | UINT32 | W | 0=-;1=Clear
75 | I6 | DOC1 | Newest Register | UINT32 | R | 0...12
75 | I7 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I8 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I9 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I10 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I11 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I12 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I13 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I14 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I15 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I16 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I17 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I18 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I19 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I20 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I21 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I22 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I23 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I24 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I25 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I26 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I27 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I28 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I29 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I30 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I31 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I32 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I33 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I34 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I35 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I36 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I37 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I38 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I39 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I40 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I41 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I42 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I43 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I44 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I45 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I46 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I47 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I48 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I49 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I50 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I51 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I52 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I53 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I54 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | S60 | DOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S61 | DOC1 | EventMaskHi | UINT32 | RW | 0...4294967295
76 | S1 | DOC2 | Idir>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
76 | V1 | DOC2 | Idir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
76 | I1 | DOC2 | Operating angle now | FLOAT | R | -360.00...360.00
76 | I2 | DOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
76 | I3 | DOC2 | Idir>> starts | UINT32 | R | 0...4294967295
76 | I4 | DOC2 | Idir>> trips | UINT32 | R | 0...4294967295
76 | I5 | DOC2 | Idir>> blocks | UINT32 | R | 0...4294967295
76 | S2 | DOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
76 | S3 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S4 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S5 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S6 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S7 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S8 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S9 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S10 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S11 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S12 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S13 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S14 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S15 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S16 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S17 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S18 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S19 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S20 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S21 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S22 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S23 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S24 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S25 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S26 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S27 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S28 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S29 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S30 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S31 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S32 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S33 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S34 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S35 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S36 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S37 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S38 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S39 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S40 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S41 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S42 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S43 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S44 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S45 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S46 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S47 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S48 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S49 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S50 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S51 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S52 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S53 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S54 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S55 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S56 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S57 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S58 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | O1 | DOC2 | Idir>> START | SIGNAL_OUT | RW | 0...4294967295
76 | O2 | DOC2 | Idir>> TRIP | SIGNAL_OUT | RW | 0...4294967295
76 | O3 | DOC2 | Idir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
76 | S59 | DOC2 | Clear registers | UINT32 | W | 0=-;1=Clear
76 | I6 | DOC2 | Newest Register | UINT32 | R | 0...12
76 | I7 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I8 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I9 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I10 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I11 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I12 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I13 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I14 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I15 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I16 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I17 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I18 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I19 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I20 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I21 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I22 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I23 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I24 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I25 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I26 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I27 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I28 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I29 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I30 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I31 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I32 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I33 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I34 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I35 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I36 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I37 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I38 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I39 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I40 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I41 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I42 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I43 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I44 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I45 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I46 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I47 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I48 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I49 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I50 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I51 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I52 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I53 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I54 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | S60 | DOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
76 | S61 | DOC2 | EventMaskHi | UINT32 | RW | 0...4294967295
77 | S1 | DOC3 | Idir>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
77 | V1 | DOC3 | Idir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
77 | I1 | DOC3 | Operating angle now | FLOAT | R | -360...360
77 | I2 | DOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
77 | I3 | DOC3 | Idir>>> starts | UINT32 | R | 0...4294967295
77 | I4 | DOC3 | Idir>>> trips | UINT32 | R | 0...4294967295
77 | I5 | DOC3 | Idir>>> blocks | UINT32 | R | 0...4294967295
77 | S2 | DOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
77 | S3 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S4 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S5 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S6 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S7 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S8 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S9 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S10 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S11 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S12 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S13 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S14 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S15 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S16 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S17 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S18 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S19 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S20 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S21 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S22 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S23 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S24 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S25 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S26 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S27 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S28 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S29 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S30 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S31 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S32 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S33 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S34 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S35 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S36 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S37 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S38 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S39 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S40 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S41 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S42 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S43 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S44 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S45 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S46 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S47 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S48 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S49 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S50 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S51 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S52 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S53 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S54 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S55 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S56 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S57 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S58 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | O1 | DOC3 | Idir>>> START | SIGNAL_OUT | RW | 0...4294967295
77 | O2 | DOC3 | Idir>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
77 | O3 | DOC3 | Idir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
77 | S59 | DOC3 | Clear registers | UINT32 | W | 0=-;1=Clear
77 | I6 | DOC3 | Newest Register | UINT32 | R | 0...12
77 | I7 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I8 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I9 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I10 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I11 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I12 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I13 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I14 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I15 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I16 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I17 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I18 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I19 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I20 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I21 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I22 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I23 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I24 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I25 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I26 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I27 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I28 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I29 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I30 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I31 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I32 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I33 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I34 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I35 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I36 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I37 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I38 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I39 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I40 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I41 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I42 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I43 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I44 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I45 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I46 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I47 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I48 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I49 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I50 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I51 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I52 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I53 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I54 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | S60 | DOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
77 | S61 | DOC3 | EventMaskHi | UINT32 | RW | 0...4294967295
78 | S1 | DOC4 | Idir>>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
78 | V1 | DOC4 | Idir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
78 | I1 | DOC4 | Operating angle now | FLOAT | R | -360.00...360.00
78 | I2 | DOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
78 | I3 | DOC4 | Idir>>>> starts | UINT32 | R | 0...4294967295
78 | I4 | DOC4 | Idir>>>> trips | UINT32 | R | 0...4294967295
78 | I5 | DOC4 | Idir>>>> blocks | UINT32 | R | 0...4294967295
78 | S2 | DOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
78 | S3 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S4 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S5 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S6 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S7 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S8 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S9 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S10 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S11 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S12 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S13 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S14 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S15 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S16 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S17 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S18 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S19 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S20 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S21 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S22 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S23 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S24 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S25 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S26 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S27 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S28 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S29 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S30 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S31 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S32 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S33 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S34 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S35 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S36 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S37 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S38 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S39 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S40 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S41 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S42 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S43 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S44 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S45 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S46 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S47 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S48 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S49 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S50 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S51 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S52 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S53 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S54 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S55 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S56 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S57 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S58 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | O1 | DOC4 | Idir>>>> START | SIGNAL_OUT | RW | 0...4294967295
78 | O2 | DOC4 | Idir>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
78 | O3 | DOC4 | Idir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
78 | S59 | DOC4 | Clear registers | UINT32 | W | 0=-;1=Clear
78 | I6 | DOC4 | Newest Register | UINT32 | R | 0...12
78 | I7 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I8 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I9 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I10 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I11 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I12 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I13 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I14 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I15 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I16 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I17 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I18 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I19 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I20 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I21 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I22 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I23 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I24 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I25 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I26 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I27 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I28 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I29 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I30 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I31 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I32 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I33 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I34 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I35 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I36 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I37 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I38 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I39 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I40 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I41 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I42 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I43 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I44 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I45 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I46 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I47 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I48 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I49 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I50 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I51 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I52 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I53 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I54 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | S60 | DOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
78 | S61 | DOC4 | EventMaskHi | UINT32 | RW | 0...4294967295
26 | S1 | NEF1 | I0> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
26 | S2 | NEF1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
26 | V1 | NEF1 | I0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
26 | I1 | NEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
26 | I2 | NEF1 | I0> starts | UINT32 | R | 0...4294967295
26 | I3 | NEF1 | I0> trips | UINT32 | R | 0...4294967295
26 | I4 | NEF1 | I0> blocks | UINT32 | R | 0...4294967295
26 | S3 | NEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
26 | S4 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S5 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S6 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S7 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S8 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S9 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S10 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S11 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S12 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S13 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S14 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S15 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S16 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S17 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S18 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S19 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S20 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S21 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S22 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S23 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S24 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S25 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S26 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S27 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S28 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S29 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S30 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S31 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S32 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S33 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S34 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S35 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | O1 | NEF1 | I0> START | SIGNAL_OUT | RW | 0...4294967295
26 | O2 | NEF1 | I0> TRIP | SIGNAL_OUT | RW | 0...4294967295
26 | O3 | NEF1 | I0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
26 | I5 | NEF1 | Newest Register | UINT32 | R | 0...12
26 | I6 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I7 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I8 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I9 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I10 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I11 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I12 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I13 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I14 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I15 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I16 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I17 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | S36 | NEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
27 | S1 | NEF2 | I0>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
27 | S2 | NEF2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
27 | V1 | NEF2 | I0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
27 | I1 | NEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
27 | I2 | NEF2 | I0>> starts | UINT32 | R | 0...4294967295
27 | I3 | NEF2 | I0>> trips | UINT32 | R | 0...4294967295
27 | I4 | NEF2 | I0>> blocks | UINT32 | R | 0...4294967295
27 | S3 | NEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
27 | S4 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S5 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S6 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S7 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S8 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S9 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S10 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S11 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S12 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S13 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S14 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S15 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S16 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S17 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S18 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S19 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S20 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S21 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S22 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S23 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S24 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S25 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S26 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S27 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S28 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S29 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S30 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S31 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S32 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S33 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S34 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S35 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | O1 | NEF2 | I0>> START | SIGNAL_OUT | RW | 0...4294967295
27 | O2 | NEF2 | I0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
27 | O3 | NEF2 | I0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
27 | I5 | NEF2 | Newest Register | UINT32 | R | 0...12
27 | I6 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I7 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I8 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I9 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I10 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I11 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I12 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I13 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I14 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I15 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I16 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I17 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | S36 | NEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
28 | S1 | NEF3 | I0>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
28 | S2 | NEF3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
28 | V1 | NEF3 | I0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
28 | I1 | NEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
28 | I2 | NEF3 | I0>>> starts | UINT32 | R | 0...4294967295
28 | I3 | NEF3 | I0>>> trips | UINT32 | R | 0...4294967295
28 | I4 | NEF3 | I0>>> blocks | UINT32 | R | 0...4294967295
28 | S3 | NEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
28 | S4 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S5 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S6 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S7 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S8 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S9 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S10 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S11 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S12 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S13 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S14 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S15 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S16 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S17 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S18 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S19 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S20 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S21 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S22 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S23 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S24 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S25 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S26 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S27 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S28 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S29 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S30 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S31 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S32 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S33 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S34 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S35 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | O1 | NEF3 | I0>>> START | SIGNAL_OUT | RW | 0...4294967295
28 | O2 | NEF3 | I0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
28 | O3 | NEF3 | I0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
28 | I5 | NEF3 | Newest Register | UINT32 | R | 0...12
28 | I6 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I7 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I8 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I9 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I10 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I11 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I12 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I13 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I14 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I15 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I16 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I17 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | S36 | NEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
29 | S1 | NEF4 | I0>>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
29 | S2 | NEF4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
29 | V1 | NEF4 | I0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
29 | I1 | NEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
29 | I2 | NEF4 | I0>>>> starts | UINT32 | R | 0...4294967295
29 | I3 | NEF4 | I0>>>> trips | UINT32 | R | 0...4294967295
29 | I4 | NEF4 | I0>>>> blocks | UINT32 | R | 0...4294967295
29 | S3 | NEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
29 | S4 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S5 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S6 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S7 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S8 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S9 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S10 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S11 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S12 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S13 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S14 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S15 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S16 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S17 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S18 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S19 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S20 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S21 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S22 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S23 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S24 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S25 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S26 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S27 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S28 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S29 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S30 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S31 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S32 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S33 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S34 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S35 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | O1 | NEF4 | I0>>>> START | SIGNAL_OUT | RW | 0...4294967295
29 | O2 | NEF4 | I0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
29 | O3 | NEF4 | I0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
29 | I5 | NEF4 | Newest Register | UINT32 | R | 0...12
29 | I6 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I7 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I8 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I9 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I10 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I11 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I12 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I13 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I14 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I15 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I16 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I17 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | S36 | NEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | S1 | DEF1 | I0dir> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
81 | V1 | DEF1 | I0dir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
81 | I1 | DEF1 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
81 | I2 | DEF1 | I0 Magnitude | FLOAT | R | 0...250
81 | I3 | DEF1 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
81 | I4 | DEF1 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
81 | I5 | DEF1 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
81 | I6 | DEF1 | DEF(1) Measured residual current change | FLOAT | R | 0...250
81 | I7 | DEF1 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
81 | I8 | DEF1 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
81 | I9 | DEF1 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
81 | I10 | DEF1 | I0 meas / I0 set now | FLOAT | R | -250...250
81 | I11 | DEF1 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
81 | I12 | DEF1 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
81 | I13 | DEF1 | U0 meas now | FLOAT | R | 0...500
81 | I14 | DEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
81 | I15 | DEF1 | I0dir> starts | UINT32 | R | 0...4294967295
81 | I16 | DEF1 | I0dir> trips | UINT32 | R | 0...4294967295
81 | I17 | DEF1 | I0dir> blocks | UINT32 | R | 0...4294967295
81 | S2 | DEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
81 | S3 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S4 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S5 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S6 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S7 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S8 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S9 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S10 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S11 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S12 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S13 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S14 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S15 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S16 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S17 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S18 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S19 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S20 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S21 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S22 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S23 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S24 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S25 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S26 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S27 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S28 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S29 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S30 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S31 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S32 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S33 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S34 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S35 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S36 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S37 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S38 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S39 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S40 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S41 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S42 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S43 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S44 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S45 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S46 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S47 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S48 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S49 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S50 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S51 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S52 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S53 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S54 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S55 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S56 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S57 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S58 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S59 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S60 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S61 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S62 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S63 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S64 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S65 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S66 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S67 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S68 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S69 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S70 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S71 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S72 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S73 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S74 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S75 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S76 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S77 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S78 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S79 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S80 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S81 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S82 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S83 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S84 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S85 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S86 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S87 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S88 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S89 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S90 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S91 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S92 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S93 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S94 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S95 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S96 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S97 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S98 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S99 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S100 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S101 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S102 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S103 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S104 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S105 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S106 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S107 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S108 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S109 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S110 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S111 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S112 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S113 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S114 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S115 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S116 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S117 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S118 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S119 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S120 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S121 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S122 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | O1 | DEF1 | I0dir> START (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O2 | DEF1 | I0dir> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O3 | DEF1 | I0dir> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O4 | DEF1 | I0dir> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O5 | DEF1 | I0dir> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O6 | DEF1 | I0dir> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O7 | DEF1 | I0dir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
81 | I18 | DEF1 | Newest Register | UINT32 | R | 0...12
81 | I19 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I20 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I21 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I22 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I23 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I24 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I25 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I26 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I27 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I28 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I29 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I30 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I31 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I32 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I33 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I34 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I35 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I36 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I37 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I38 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I39 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I40 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I41 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I42 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I43 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I44 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I45 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I46 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I47 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I48 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I49 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I50 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I51 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I52 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I53 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I54 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I55 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I56 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I57 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I58 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I59 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I60 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I61 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I62 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I63 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I64 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I65 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I66 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I67 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I68 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I69 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I70 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I71 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I72 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I73 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I74 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I75 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I76 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I77 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I78 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I79 | DEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | I80 | DEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
82 | S1 | DEF2 | I0dir>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
82 | V1 | DEF2 | I0dir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
82 | I1 | DEF2 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
82 | I2 | DEF2 | I0 Magnitude | FLOAT | R | 0...250
82 | I3 | DEF2 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
82 | I4 | DEF2 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
82 | I5 | DEF2 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
82 | I6 | DEF2 | DEF(1) Measured residual current change | FLOAT | R | 0...250
82 | I7 | DEF2 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
82 | I8 | DEF2 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
82 | I9 | DEF2 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
82 | I10 | DEF2 | I0 meas / I0 set now | FLOAT | R | -250...250
82 | I11 | DEF2 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
82 | I12 | DEF2 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
82 | I13 | DEF2 | U0 meas now | FLOAT | R | 0...500
82 | I14 | DEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
82 | I15 | DEF2 | I0dir>> starts | UINT32 | R | 0...4294967295
82 | I16 | DEF2 | I0dir>> trips | UINT32 | R | 0...4294967295
82 | I17 | DEF2 | I0dir>> blocks | UINT32 | R | 0...4294967295
82 | S2 | DEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
82 | S3 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S4 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S5 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S6 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S7 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S8 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S9 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S10 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S11 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S12 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S13 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S14 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S15 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S16 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S17 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S18 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S19 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S20 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S21 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S22 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S23 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S24 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S25 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S26 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S27 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S28 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S29 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S30 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S31 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S32 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S33 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S34 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S35 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S36 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S37 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S38 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S39 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S40 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S41 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S42 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S43 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S44 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S45 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S46 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S47 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S48 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S49 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S50 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S51 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S52 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S53 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S54 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S55 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S56 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S57 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S58 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S59 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S60 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S61 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S62 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S63 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S64 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S65 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S66 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S67 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S68 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S69 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S70 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S71 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S72 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S73 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S74 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S75 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S76 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S77 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S78 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S79 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S80 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S81 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S82 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S83 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S84 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S85 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S86 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S87 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S88 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S89 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S90 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S91 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S92 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S93 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S94 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S95 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S96 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S97 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S98 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S99 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S100 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S101 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S102 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S103 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S104 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S105 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S106 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S107 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S108 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S109 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S110 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S111 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S112 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S113 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S114 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S115 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S116 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S117 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S118 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S119 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S120 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S121 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S122 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | O1 | DEF2 | I0dir>> START (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O2 | DEF2 | I0dir>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O3 | DEF2 | I0dir>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O4 | DEF2 | I0dir>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O5 | DEF2 | I0dir>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O6 | DEF2 | I0dir>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O7 | DEF2 | I0dir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
82 | I18 | DEF2 | Newest Register | UINT32 | R | 0...12
82 | I19 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I20 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I21 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I22 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I23 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I24 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I25 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I26 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I27 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I28 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I29 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I30 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I31 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I32 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I33 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I34 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I35 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I36 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I37 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I38 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I39 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I40 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I41 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I42 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I43 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I44 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I45 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I46 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I47 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I48 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I49 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I50 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I51 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I52 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I53 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I54 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I55 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I56 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I57 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I58 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I59 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I60 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I61 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I62 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I63 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I64 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I65 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I66 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I67 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I68 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I69 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I70 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I71 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I72 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I73 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I74 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I75 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I76 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I77 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I78 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I79 | DEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
82 | I80 | DEF2 | EventMaskHi | UINT32 | RW | 0...4294967295
83 | S1 | DEF3 | I0dir>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
83 | V1 | DEF3 | I0dir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
83 | I1 | DEF3 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
83 | I2 | DEF3 | I0 Magnitude | FLOAT | R | 0...250
83 | I3 | DEF3 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
83 | I4 | DEF3 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
83 | I5 | DEF3 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
83 | I6 | DEF3 | DEF(1) Measured residual current change | FLOAT | R | 0...250
83 | I7 | DEF3 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
83 | I8 | DEF3 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
83 | I9 | DEF3 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
83 | I10 | DEF3 | I0 meas / I0 set now | FLOAT | R | -250...250
83 | I11 | DEF3 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
83 | I12 | DEF3 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
83 | I13 | DEF3 | U0 meas now | FLOAT | R | 0...500
83 | I14 | DEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
83 | I15 | DEF3 | I0dir>>> starts | UINT32 | R | 0...4294967295
83 | I16 | DEF3 | I0dir>>> trips | UINT32 | R | 0...4294967295
83 | I17 | DEF3 | I0dir>>> blocks | UINT32 | R | 0...4294967295
83 | S2 | DEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
83 | S3 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S4 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S5 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S6 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S7 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S8 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S9 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S10 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S11 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S12 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S13 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S14 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S15 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S16 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S17 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S18 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S19 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S20 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S21 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S22 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S23 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S24 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S25 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S26 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S27 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S28 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S29 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S30 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S31 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S32 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S33 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S34 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S35 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S36 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S37 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S38 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S39 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S40 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S41 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S42 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S43 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S44 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S45 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S46 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S47 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S48 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S49 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S50 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S51 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S52 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S53 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S54 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S55 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S56 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S57 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S58 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S59 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S60 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S61 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S62 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S63 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S64 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S65 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S66 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S67 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S68 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S69 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S70 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S71 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S72 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S73 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S74 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S75 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S76 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S77 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S78 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S79 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S80 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S81 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S82 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S83 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S84 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S85 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S86 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S87 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S88 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S89 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S90 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S91 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S92 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S93 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S94 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S95 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S96 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S97 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S98 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S99 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S100 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S101 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S102 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S103 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S104 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S105 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S106 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S107 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S108 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S109 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S110 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S111 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S112 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S113 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S114 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S115 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S116 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S117 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S118 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S119 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S120 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S121 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S122 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | O1 | DEF3 | I0dir>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O2 | DEF3 | I0dir>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O3 | DEF3 | I0dir>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O4 | DEF3 | I0dir>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O5 | DEF3 | I0dir>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O6 | DEF3 | I0dir>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O7 | DEF3 | I0dir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
83 | I18 | DEF3 | Newest Register | UINT32 | R | 0...12
83 | I19 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I20 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I21 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I22 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I23 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I24 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I25 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I26 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I27 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I28 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I29 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I30 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I31 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I32 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I33 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I34 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I35 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I36 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I37 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I38 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I39 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I40 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I41 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I42 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I43 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I44 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I45 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I46 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I47 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I48 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I49 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I50 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I51 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I52 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I53 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I54 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I55 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I56 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I57 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I58 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I59 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I60 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I61 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I62 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I63 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I64 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I65 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I66 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I67 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I68 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I69 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I70 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I71 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I72 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I73 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I74 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I75 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I76 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I77 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I78 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I79 | DEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
83 | I80 | DEF3 | EventMaskHi | UINT32 | RW | 0...4294967295
84 | S1 | DEF4 | I0dir>>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
84 | V1 | DEF4 | I0dir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
84 | I1 | DEF4 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
84 | I2 | DEF4 | I0 Magnitude | FLOAT | R | 0...250
84 | I3 | DEF4 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
84 | I4 | DEF4 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
84 | I5 | DEF4 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
84 | I6 | DEF4 | DEF(1) Measured residual current change | FLOAT | R | 0...250
84 | I7 | DEF4 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
84 | I8 | DEF4 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
84 | I9 | DEF4 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
84 | I10 | DEF4 | I0 meas / I0 set now | FLOAT | R | -250...250
84 | I11 | DEF4 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
84 | I12 | DEF4 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
84 | I13 | DEF4 | U0 meas now | FLOAT | R | 0...500
84 | I14 | DEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
84 | I15 | DEF4 | I0dir>>>> starts | UINT32 | R | 0...4294967295
84 | I16 | DEF4 | I0dir>>>> trips | UINT32 | R | 0...4294967295
84 | I17 | DEF4 | I0dir>>>> blocks | UINT32 | R | 0...4294967295
84 | S2 | DEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
84 | S3 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S4 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S5 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S6 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S7 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S8 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S9 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S10 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S11 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S12 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S13 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S14 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S15 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S16 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S17 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S18 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S19 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S20 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S21 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S22 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S23 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S24 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S25 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S26 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S27 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S28 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S29 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S30 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S31 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S32 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S33 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S34 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S35 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S36 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S37 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S38 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S39 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S40 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S41 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S42 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S43 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S44 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S45 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S46 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S47 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S48 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S49 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S50 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S51 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S52 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S53 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S54 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S55 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S56 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S57 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S58 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S59 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S60 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S61 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S62 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S63 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S64 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S65 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S66 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S67 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S68 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S69 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S70 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S71 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S72 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S73 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S74 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S75 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S76 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S77 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S78 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S79 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S80 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S81 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S82 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S83 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S84 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S85 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S86 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S87 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S88 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S89 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S90 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S91 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S92 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S93 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S94 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S95 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S96 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S97 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S98 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S99 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S100 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S101 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S102 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S103 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S104 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S105 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S106 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S107 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S108 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S109 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S110 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S111 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S112 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S113 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S114 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S115 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S116 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S117 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S118 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S119 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S120 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S121 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S122 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | O1 | DEF4 | I0dir>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O2 | DEF4 | I0dir>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O3 | DEF4 | I0dir>>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O4 | DEF4 | I0dir>>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O5 | DEF4 | I0dir>>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O6 | DEF4 | I0dir>>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O7 | DEF4 | I0dir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
84 | I18 | DEF4 | Newest Register | UINT32 | R | 0...12
84 | I19 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I20 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I21 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I22 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I23 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I24 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I25 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I26 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I27 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I28 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I29 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I30 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I31 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I32 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I33 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I34 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I35 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I36 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I37 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I38 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I39 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I40 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I41 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I42 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I43 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I44 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I45 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I46 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I47 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I48 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I49 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I50 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I51 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I52 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I53 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I54 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I55 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I56 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I57 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I58 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I59 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I60 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I61 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I62 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I63 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I64 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I65 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I66 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I67 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I68 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I69 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I70 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I71 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I72 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I73 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I74 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I75 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I76 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I77 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I78 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I79 | DEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
84 | I80 | DEF4 | EventMaskHi | UINT32 | RW | 0...4294967295
114 | S1 | IEF1 | I0Int> [67NT] mode | UINT32 | RW | 0=Disabled;1=Activated
114 | V1 | IEF1 | I0Int> condition | UINT32 | R | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
114 | I1 | IEF1 | Spikes needed for trip > | UINT32 | R | 0...4294967295
114 | I2 | IEF1 | I0Int> starts FWD | UINT32 | R | 0...4294967295
114 | I3 | IEF1 | I0Int> starts REV | UINT32 | R | 0...4294967295
114 | I4 | IEF1 | I0Int> trips | UINT32 | R | 0...4294967295
114 | I5 | IEF1 | I0Int> blocks | UINT32 | R | 0...4294967295
114 | S2 | IEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
114 | S3 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S4 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S5 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S6 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S7 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S8 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S9 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S10 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S11 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S12 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S13 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S14 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S15 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S16 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S17 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S18 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S19 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S20 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S21 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S22 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S23 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S24 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S25 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S26 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S27 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S28 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S29 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S30 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S31 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S32 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S33 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S34 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S35 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S36 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S37 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S38 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S39 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S40 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S41 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S42 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S43 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S44 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S45 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S46 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S47 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S48 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S49 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S50 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | O1 | IEF1 | I0Int> IEF DETECTED | SIGNAL_OUT | RW | 0...4294967295
114 | O2 | IEF1 | I0Int> STARTFWD | SIGNAL_OUT | RW | 0...4294967295
114 | O3 | IEF1 | I0Int> STARTREV | SIGNAL_OUT | RW | 0...4294967295
114 | O4 | IEF1 | I0Int> TRIP | SIGNAL_OUT | RW | 0...4294967295
114 | O5 | IEF1 | I0Int> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
114 | I6 | IEF1 | Newest Register | UINT32 | R | 0...12
114 | I7 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I8 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I9 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I10 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I11 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I12 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I13 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I14 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I15 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I16 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I17 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I18 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I19 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I20 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I21 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I22 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I23 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I24 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I25 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I26 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I27 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I28 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I29 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I30 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I31 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I32 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I33 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I34 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I35 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I36 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I37 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I38 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I39 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I40 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I41 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I42 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I43 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I44 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I45 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I46 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I47 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I48 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I49 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I50 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I51 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I52 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I53 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I54 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I55 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I56 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I57 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I58 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I59 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I60 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I61 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I62 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I63 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I64 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I65 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I66 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | S51 | IEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
114 | S52 | IEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
32 | S1 | CUB1 | I2> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
32 | V1 | CUB1 | I2> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
32 | I1 | CUB1 | I2> starts | UINT32 | R | 0...4294967295
32 | I2 | CUB1 | I2> trips | UINT32 | R | 0...4294967295
32 | I3 | CUB1 | I2> blocks | UINT32 | R | 0...4294967295
32 | S2 | CUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
32 | I4 | CUB1 | I2> I2I1 relation | FLOAT | R | 0...100000
32 | I5 | CUB1 | I2 meas/I2 set | FLOAT | R | 0...100000
32 | S3 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S4 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S5 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S6 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S7 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S8 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S9 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S10 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S11 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S12 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S13 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S14 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S15 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S16 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S17 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S18 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S19 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S20 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S21 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S22 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S23 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S24 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S25 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S26 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S27 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S28 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S29 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S30 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S31 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S32 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S33 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S34 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | O1 | CUB1 | I2> START | SIGNAL_OUT | RW | 0...4294967295
32 | O2 | CUB1 | I2> TRIP | SIGNAL_OUT | RW | 0...4294967295
32 | O3 | CUB1 | I2> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
32 | I6 | CUB1 | Newest Register | UINT32 | R | 0...12
32 | I7 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I8 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I9 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I10 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I11 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I12 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I13 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I14 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I15 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I16 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I17 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I18 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I19 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I20 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I21 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I22 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I23 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I24 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I25 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I26 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I27 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I28 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I29 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I30 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | S35 | CUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
33 | S1 | CUB2 | I2>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
33 | V1 | CUB2 | I2>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
33 | I1 | CUB2 | I2>> starts | UINT32 | R | 0...4294967295
33 | I2 | CUB2 | I2>> trips | UINT32 | R | 0...4294967295
33 | I3 | CUB2 | I2>> blocks | UINT32 | R | 0...4294967295
33 | S2 | CUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
33 | I4 | CUB2 | I2>> I2I1 relation | FLOAT | R | 0...100000
33 | I5 | CUB2 | I2 meas/I2 set | FLOAT | R | 0...100000
33 | S3 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S4 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S5 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S6 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S7 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S8 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S9 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S10 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S11 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S12 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S13 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S14 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S15 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S16 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S17 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S18 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S19 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S20 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S21 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S22 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S23 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S24 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S25 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S26 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S27 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S28 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S29 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S30 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S31 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S32 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S33 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S34 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | O1 | CUB2 | I2>> START | SIGNAL_OUT | RW | 0...4294967295
33 | O2 | CUB2 | I2>> TRIP | SIGNAL_OUT | RW | 0...4294967295
33 | O3 | CUB2 | I2>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
33 | I6 | CUB2 | Newest Register | UINT32 | R | 0...12
33 | I7 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I8 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I9 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I10 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I11 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I12 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I13 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I14 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I15 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I16 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I17 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I18 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I19 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I20 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I21 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I22 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I23 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I24 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I25 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I26 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I27 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I28 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I29 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I30 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | S35 | CUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
34 | S1 | CUB3 | I2>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
34 | V1 | CUB3 | I2>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
34 | I1 | CUB3 | I2>>> starts | UINT32 | R | 0...4294967295
34 | I2 | CUB3 | I2>>> trips | UINT32 | R | 0...4294967295
34 | I3 | CUB3 | I2>>> blocks | UINT32 | R | 0...4294967295
34 | S2 | CUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
34 | I4 | CUB3 | I2>>> I2I1 relation | FLOAT | R | 0...100000
34 | I5 | CUB3 | I2 meas/I2 set | FLOAT | R | 0...100000
34 | S3 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S4 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S5 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S6 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S7 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S8 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S9 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S10 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S11 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S12 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S13 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S14 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S15 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S16 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S17 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S18 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S19 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S20 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S21 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S22 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S23 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S24 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S25 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S26 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S27 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S28 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S29 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S30 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S31 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S32 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S33 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S34 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | O1 | CUB3 | I2>>> START | SIGNAL_OUT | RW | 0...4294967295
34 | O2 | CUB3 | I2>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
34 | O3 | CUB3 | I2>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
34 | I6 | CUB3 | Newest Register | UINT32 | R | 0...12
34 | I7 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I8 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I9 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I10 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I11 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I12 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I13 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I14 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I15 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I16 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I17 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I18 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I19 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I20 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I21 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I22 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I23 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I24 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I25 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I26 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I27 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I28 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I29 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I30 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | S35 | CUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
35 | S1 | CUB4 | I2>>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
35 | V1 | CUB4 | I2>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
35 | I1 | CUB4 | I2>>>> starts | UINT32 | R | 0...4294967295
35 | I2 | CUB4 | I2>>>> trips | UINT32 | R | 0...4294967295
35 | I3 | CUB4 | I2>>>> blocks | UINT32 | R | 0...4294967295
35 | S2 | CUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
35 | I4 | CUB4 | I2>>>> I2I1 relation | FLOAT | R | 0...100000
35 | I5 | CUB4 | I2 meas/I2 set | FLOAT | R | 0...100000
35 | S3 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S4 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S5 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S6 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S7 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S8 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S9 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S10 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S11 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S12 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S13 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S14 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S15 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S16 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S17 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S18 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S19 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S20 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S21 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S22 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S23 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S24 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S25 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S26 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S27 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S28 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S29 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S30 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S31 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S32 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S33 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S34 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | O1 | CUB4 | I2>>>> START | SIGNAL_OUT | RW | 0...4294967295
35 | O2 | CUB4 | I2>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
35 | O3 | CUB4 | I2>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
35 | I6 | CUB4 | Newest Register | UINT32 | R | 0...12
35 | I7 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I8 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I9 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I10 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I11 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I12 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I13 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I14 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I15 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I16 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I17 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I18 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I19 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I20 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I21 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I22 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I23 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I24 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I25 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I26 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I27 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I28 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I29 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I30 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | S35 | CUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
37 | S1 | HOC1 | Ih> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
37 | V1 | HOC1 | Ih> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
37 | I1 | HOC1 | Ih> starts | UINT32 | R | 0...4294967295
37 | I2 | HOC1 | Ih> trips | UINT32 | R | 0...4294967295
37 | I3 | HOC1 | Ih> blocks | UINT32 | R | 0...4294967295
37 | S2 | HOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
37 | I4 | HOC1 | Ih meas/ Ih set | FLOAT | R | 0...100000
37 | S3 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S4 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S5 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S6 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S7 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S8 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S9 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S10 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S11 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S12 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S13 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S14 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S15 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S16 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S17 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S18 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S19 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S20 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S21 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S22 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S23 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S24 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S25 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S26 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S27 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S28 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S29 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S30 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S31 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S32 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S33 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S34 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | O1 | HOC1 | Ih> START | SIGNAL_OUT | RW | 0...4294967295
37 | O2 | HOC1 | Ih> TRIP | SIGNAL_OUT | RW | 0...4294967295
37 | O3 | HOC1 | Ih> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
37 | I5 | HOC1 | Newest Register | UINT32 | R | 0...12
37 | I6 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I7 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I8 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I9 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I10 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I11 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I12 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I13 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I14 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I15 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I16 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I17 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I18 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I19 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I20 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I21 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I22 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I23 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I24 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I25 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I26 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I27 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I28 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I29 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I30 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I31 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I32 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I33 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I34 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I35 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I36 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I37 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I38 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I39 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I40 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I41 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I42 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I43 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I44 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I45 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I46 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I47 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I48 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I49 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I50 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I51 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I52 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I53 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I54 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I55 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I56 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I57 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I58 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I59 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I60 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I61 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I62 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I63 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I64 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I65 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | S35 | HOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
38 | S1 | HOC2 | Ih>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
38 | V1 | HOC2 | Ih>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
38 | I1 | HOC2 | Ih>> starts | UINT32 | R | 0...4294967295
38 | I2 | HOC2 | Ih>> trips | UINT32 | R | 0...4294967295
38 | I3 | HOC2 | Ih>> blocks | UINT32 | R | 0...4294967295
38 | S2 | HOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
38 | I4 | HOC2 | Ih meas/ Ih set | FLOAT | R | 0...100000
38 | S3 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S4 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S5 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S6 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S7 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S8 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S9 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S10 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S11 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S12 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S13 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S14 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S15 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S16 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S17 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S18 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S19 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S20 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S21 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S22 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S23 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S24 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S25 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S26 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S27 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S28 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S29 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S30 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S31 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S32 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S33 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S34 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | O1 | HOC2 | Ih>> START | SIGNAL_OUT | RW | 0...4294967295
38 | O2 | HOC2 | Ih>> TRIP | SIGNAL_OUT | RW | 0...4294967295
38 | O3 | HOC2 | Ih>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
38 | I5 | HOC2 | Newest Register | UINT32 | R | 0...12
38 | I6 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I7 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I8 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I9 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I10 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I11 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I12 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I13 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I14 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I15 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I16 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I17 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I18 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I19 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I20 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I21 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I22 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I23 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I24 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I25 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I26 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I27 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I28 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I29 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I30 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I31 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I32 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I33 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I34 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I35 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I36 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I37 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I38 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I39 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I40 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I41 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I42 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I43 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I44 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I45 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I46 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I47 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I48 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I49 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I50 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I51 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I52 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I53 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I54 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I55 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I56 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I57 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I58 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I59 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I60 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I61 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I62 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I63 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I64 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I65 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | S35 | HOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
39 | S1 | HOC3 | Ih>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
39 | V1 | HOC3 | Ih>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
39 | I1 | HOC3 | Ih>>> starts | UINT32 | R | 0...4294967295
39 | I2 | HOC3 | Ih>>> trips | UINT32 | R | 0...4294967295
39 | I3 | HOC3 | Ih>>> blocks | UINT32 | R | 0...4294967295
39 | S2 | HOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
39 | I4 | HOC3 | Ih meas/ Ih set | FLOAT | R | 0...100000
39 | S3 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S4 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S5 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S6 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S7 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S8 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S9 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S10 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S11 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S12 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S13 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S14 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S15 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S16 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S17 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S18 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S19 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S20 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S21 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S22 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S23 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S24 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S25 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S26 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S27 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S28 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S29 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S30 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S31 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S32 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S33 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S34 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | O1 | HOC3 | Ih>>> START | SIGNAL_OUT | RW | 0...4294967295
39 | O2 | HOC3 | Ih>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
39 | O3 | HOC3 | Ih>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
39 | I5 | HOC3 | Newest Register | UINT32 | R | 0...12
39 | I6 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I7 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I8 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I9 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I10 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I11 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I12 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I13 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I14 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I15 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I16 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I17 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I18 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I19 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I20 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I21 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I22 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I23 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I24 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I25 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I26 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I27 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I28 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I29 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I30 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I31 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I32 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I33 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I34 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I35 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I36 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I37 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I38 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I39 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I40 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I41 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I42 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I43 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I44 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I45 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I46 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I47 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I48 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I49 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I50 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I51 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I52 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I53 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I54 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I55 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I56 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I57 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I58 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I59 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I60 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I61 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I62 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I63 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I64 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I65 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | S35 | HOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
40 | S1 | HOC4 | Ih>>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
40 | V1 | HOC4 | Ih>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
40 | I1 | HOC4 | Ih>>>> starts | UINT32 | R | 0...4294967295
40 | I2 | HOC4 | Ih>>>> trips | UINT32 | R | 0...4294967295
40 | I3 | HOC4 | Ih>>>> blocks | UINT32 | R | 0...4294967295
40 | S2 | HOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
40 | I4 | HOC4 | Ih meas/ Ih set | FLOAT | R | 0...100000
40 | S3 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S4 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S5 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S6 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S7 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S8 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S9 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S10 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S11 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S12 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S13 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S14 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S15 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S16 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S17 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S18 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S19 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S20 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S21 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S22 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S23 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S24 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S25 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S26 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S27 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S28 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S29 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S30 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S31 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S32 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S33 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S34 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | O1 | HOC4 | Ih>>>> START | SIGNAL_OUT | RW | 0...4294967295
40 | O2 | HOC4 | Ih>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
40 | O3 | HOC4 | Ih>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
40 | I5 | HOC4 | Newest Register | UINT32 | R | 0...12
40 | I6 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I7 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I8 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I9 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I10 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I11 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I12 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I13 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I14 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I15 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I16 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I17 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I18 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I19 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I20 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I21 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I22 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I23 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I24 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I25 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I26 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I27 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I28 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I29 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I30 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I31 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I32 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I33 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I34 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I35 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I36 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I37 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I38 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I39 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I40 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I41 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I42 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I43 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I44 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I45 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I46 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I47 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I48 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I49 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I50 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I51 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I52 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I53 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I54 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I55 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I56 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I57 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I58 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I59 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I60 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I61 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I62 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I63 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I64 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I65 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | S35 | HOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
42 | S1 | CLP1 | CLP mode | UINT32 | RW | 0=Disabled;1=Activated
42 | V1 | CLP1 | CLP condition | UINT32 | R | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
42 | I1 | CLP1 | CLP starts | UINT32 | R | 0...4294967295
42 | I2 | CLP1 | CLP blocks | UINT32 | R | 0...4294967295
42 | S2 | CLP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
42 | S3 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S4 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S5 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S6 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S7 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S8 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S9 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S10 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S11 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S12 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S13 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S14 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S15 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S16 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S17 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S18 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S19 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S20 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S21 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S22 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S23 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S24 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S25 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S26 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S27 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S28 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S29 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S30 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S31 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S32 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S33 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S34 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S35 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S36 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S37 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S38 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S39 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S40 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S41 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S42 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S43 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S44 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S45 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S46 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S47 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S48 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S49 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S50 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | O1 | CLP1 | CLPU ACT | SIGNAL_OUT | RW | 0...4294967295
42 | O2 | CLP1 | CLPU BLOCKED | SIGNAL_OUT | RW | 0...4294967295
42 | I3 | CLP1 | Newest Register | UINT32 | R | 0...12
42 | I4 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I5 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I6 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I7 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I8 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I9 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I10 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I11 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I12 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I13 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I14 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I15 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I16 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I17 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I18 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I19 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I20 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I21 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I22 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I23 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I24 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I25 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I26 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I27 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I28 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I29 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I30 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I31 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I32 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I33 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I34 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I35 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I36 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I37 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I38 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I39 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | S51 | CLP1 | EventMaskLo | UINT32 | RW | 0...4294967295
44 | S1 | CBF1 | CBFP [50BF] mode | UINT32 | RW | 0=Disabled;1=Activated
44 | V1 | CBF1 | CBFP condition | UINT32 | R | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
44 | I1 | CBF1 | Retrips | UINT32 | R | 0...4294967295
44 | I2 | CBF1 | CBFPs | UINT32 | R | 0...4294967295
44 | I3 | CBF1 | CBFP starts | UINT32 | R | 0...4294967295
44 | I4 | CBF1 | CBFP blocks | UINT32 | R | 0...4294967295
44 | S2 | CBF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
44 | S3 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S4 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S5 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S6 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S7 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S8 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S9 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S10 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S11 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S12 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S13 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S14 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S15 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S16 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S17 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S18 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S19 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S20 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S21 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S22 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S23 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S24 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S25 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S26 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S27 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S28 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S29 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S30 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S31 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S32 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S33 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S34 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S35 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S36 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S37 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S38 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S39 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S40 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S41 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S42 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S43 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S44 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S45 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S46 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S47 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S48 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S49 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S50 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S51 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S52 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S53 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S54 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S55 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S56 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S57 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S58 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | O1 | CBF1 | CBFP START | SIGNAL_OUT | RW | 0...4294967295
44 | O2 | CBF1 | CBFP RETRIP | SIGNAL_OUT | RW | 0...4294967295
44 | O3 | CBF1 | CBFP ACT | SIGNAL_OUT | RW | 0...4294967295
44 | O4 | CBF1 | CBFP BLOCKED | SIGNAL_OUT | RW | 0...4294967295
44 | I5 | CBF1 | Newest Register | UINT32 | R | 0...12
44 | I6 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I7 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I8 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I9 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I10 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I11 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I12 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I13 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I14 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I15 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I16 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I17 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I18 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I19 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I20 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I21 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I22 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I23 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I24 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I25 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I26 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I27 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I28 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I29 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I30 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I31 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I32 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I33 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I34 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I35 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I36 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I37 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I38 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I39 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I40 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I41 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I42 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I43 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I44 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I45 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I46 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I47 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I48 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I49 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I50 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I51 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I52 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I53 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | S59 | CBF1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S1 | MST1 | MST mode | UINT32 | R | 0=Disabled; 1=Activated
62 | V1 | MST1 | Motor is now | UINT32 | R | 0=Stopped;1=Starting;2=Running;3=Stalled
62 | I1 | MST1 | Times motor started | UINT32 | R | 0...4294967295
62 | I2 | MST1 | Times motor starts succeed | UINT32 | R | 0...4294967295
62 | I3 | MST1 | Times motor stopped | UINT32 | R | 0...4294967295
62 | S2 | MST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
62 | I4 | MST1 | Run after last start | UINT32 | R | 0...4294967295
62 | I5 | MST1 | Total motor run time | UINT32 | R | 0...4294967295
62 | I6 | MST1 | Last start duration | UINT32 | R | 0...4294967295
62 | I7 | MST1 | Total starting time | UINT32 | R | 0...4294967295
62 | I8 | MST1 | Last stopped duration | UINT32 | R | 0...4294967295
62 | I9 | MST1 | Total stopped time | UINT32 | R | 0...4294967295
62 | S3 | MST1 | Clear total times | UINT32 | W | 0=-;1=Clear
62 | S4 | MST1 | Per unitize relay currents to Motor In | UINT32 | RW | 0=No, use CT nominal as pu.;1=Yes, scale all to Imot
62 | S5 | MST1 | Motor nominal current | FLOAT | RW | 0.1...10000
62 | S6 | MST1 | Nominal Starting current | FLOAT | RW | 0.1...40
62 | S7 | MST1 | Start detect current | FLOAT | RW | 0.1...40
62 | S8 | MST1 | Min locked rotor current | FLOAT | RW | 0.1...40
62 | S9 | MST1 | Max locked rotor current | FLOAT | RW | 0.1...40
62 | S10 | MST1 | Maximum overload current | FLOAT | RW | 0.1...40
62 | S11 | MST1 | No Load current | FLOAT | RW | 0.1...40
62 | S12 | MST1 | Motor service factor | FLOAT | RW | 0.01...5
62 | S13 | MST1 | Hot condition theta limit | FLOAT | RW | 0...100
62 | S14 | MST1 | Safe stall time cold | FLOAT | RW | 0.1...600
62 | S15 | MST1 | Safe stall time hot | FLOAT | RW | 0.1...600
62 | S16 | MST1 | Allowed Starts when cold | UINT32 | RW | 1...100
62 | S17 | MST1 | Allowed Starts when hot | UINT32 | RW | 1...100
62 | S18 | MST1 | Given Hot/Cold starts in time of: | FLOAT | RW | 0.01...1800
62 | S19 | MST1 | Min time betw. starts | FLOAT | RW | 0...3600
62 | S20 | MST1 | Overall differential protection | UINT32 | RW | 0=Machine diff. (Yy);1=Diff.with trafo(Xx)
62 | O1 | MST1 | Motor stopped | SIGNAL_OUT | RW | 0...4294967295
62 | O2 | MST1 | Motor starting | SIGNAL_OUT | RW | 0...4294967295
62 | O3 | MST1 | Motor running | SIGNAL_OUT | RW | 0...4294967295
62 | O4 | MST1 | Motor stalled | SIGNAL_OUT | RW | 0...4294967295
62 | O5 | MST1 | Missing phase | SIGNAL_OUT | RW | 0...4294967295
62 | O6 | MST1 | Load Normal | SIGNAL_OUT | RW | 0...4294967295
62 | O7 | MST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
62 | O8 | MST1 | High overcurrent | SIGNAL_OUT | RW | 0...4294967295
62 | I10 | MST1 | Newest Register | UINT32 | R | 0...12
62 | I11 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I12 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I13 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I14 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I15 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I16 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I17 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I18 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I19 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I20 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I21 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I22 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I23 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I24 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I25 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I26 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I27 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I28 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I29 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I30 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I31 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I32 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I33 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I34 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I35 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I36 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I37 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I38 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I39 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I40 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I41 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I42 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I43 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I44 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I45 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I46 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I47 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I48 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I49 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I50 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I51 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I52 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I53 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I54 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I55 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I56 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I57 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I58 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I59 | MST1 | Motor load | FLOAT | R | 0...250
62 | I60 | MST1 | Motor load | FLOAT | R | 0...250
62 | I61 | MST1 | Motor load | FLOAT | R | 0...250
62 | I62 | MST1 | Motor load | FLOAT | R | 0...250
62 | I63 | MST1 | Motor load | FLOAT | R | 0...250
62 | I64 | MST1 | Motor load | FLOAT | R | 0...250
62 | I65 | MST1 | Motor load | FLOAT | R | 0...250
62 | I66 | MST1 | Motor load | FLOAT | R | 0...250
62 | I67 | MST1 | Motor load | FLOAT | R | 0...250
62 | I68 | MST1 | Motor load | FLOAT | R | 0...250
62 | I69 | MST1 | Motor load | FLOAT | R | 0...250
62 | I70 | MST1 | Motor load | FLOAT | R | 0...250
62 | S21 | MST1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S22 | MST1 | EventMaskHi | UINT32 | RW | 0...4294967295
72 | V1 | TRF1 | Transformer is now | UINT32 | R | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
72 | I1 | TRF1 | Times Overloaded | UINT32 | R | 0...4294967295
72 | I2 | TRF1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
72 | S1 | TRF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
72 | I3 | TRF1 | Normal loading | UINT32 | R | 0...4294967295
72 | I4 | TRF1 | Overloading cumulative | UINT32 | R | 0...4294967295
72 | I5 | TRF1 | Last overload duration | UINT32 | R | 0...4294967295
72 | I6 | TRF1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
72 | I7 | TRF1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
72 | S2 | TRF1 | Clear total times | UINT32 | W | 0=-;1=Clear
72 | S3 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.1...500
72 | S4 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...500
72 | S5 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...500
72 | S6 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S7 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | V2 | TRF1 | Bias selection | UINT32 | R | 0=Selection Ok;1=Selection different
72 | V3 | TRF1 | Pick-up setting | UINT32 | R | 0=not checked;1=Setting seems ok;2=Sensitive ok;3=Too sensitive;4=False trip likely;5=Coarse ok;6=Insensitive;7=Dangerously high
72 | V4 | TRF1 | Turnpoint1 setting | UINT32 | R | 0=not checked;1=Ok;2=Seems average;3=Is sensitive;4=Ok;5=Is conservative;6=Is sensitive;7=Ok;8=Is average;9=Is conservative;10=Ok;11=Too conservative;12=Too sensitive
72 | V5 | TRF1 | Slope1 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V6 | TRF1 | Turnpoint2 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V7 | TRF1 | Slope2 setting | UINT32 | R | 0=not checked;1=Ok;2=Wrong;
72 | O1 | TRF1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
72 | O2 | TRF1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O3 | TRF1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O4 | TRF1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
72 | O5 | TRF1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | O6 | TRF1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | I8 | TRF1 | Newest Register | UINT32 | R | 0...12
72 | I9 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I10 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I11 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I12 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I13 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I14 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I15 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I16 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I17 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I18 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I19 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I20 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I21 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I22 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I23 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I24 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I25 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I26 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I27 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I28 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I29 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I30 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I31 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I32 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I33 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I34 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I35 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I36 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I37 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I38 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I39 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I40 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I41 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I42 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I43 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I44 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I45 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I46 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I47 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I48 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I49 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I50 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I51 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I52 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I53 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I54 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I55 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I56 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I57 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I58 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I59 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I60 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I61 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I62 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I63 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I64 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I65 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I66 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I67 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I68 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I69 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I70 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I71 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I72 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I73 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I74 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I75 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I76 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I77 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I78 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I79 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I80 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | S8 | TRF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S1 | DIF1 | Idx> [87T/87N] mode | UINT32 | RW | 0=Disabled;1=Activated
71 | V1 | DIF1 | Idx> condition | UINT32 | R | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On
71 | V2 | DIF1 | REFHV> condition | UINT32 | R | 0b=HV REF Blocked;1b=HV REF Trip
71 | V3 | DIF1 | REFLV> condition | UINT32 | R | 0b=LV REF Blocked;1b=LV REF Trip
71 | I1 | DIF1 | Idb> trips | UINT32 | R | 0...4294967295
71 | I2 | DIF1 | Idb> f2h blocks | UINT32 | R | 0...4294967295
71 | I3 | DIF1 | Idb> f5h blocks | UINT32 | R | 0...4294967295
71 | I4 | DIF1 | Idb> Ext blocks | UINT32 | R | 0...4294967295
71 | I5 | DIF1 | Idi> trips | UINT32 | R | 0...4294967295
71 | I6 | DIF1 | Idi> Ext blocks | UINT32 | R | 0...4294967295
71 | I7 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I8 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | I9 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I10 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | S2 | DIF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
71 | I11 | DIF1 | L1 Bias current | FLOAT | R | 0...50
71 | I12 | DIF1 | L1 Diff current | FLOAT | R | 0...4000
71 | I13 | DIF1 | L1 Char current | FLOAT | R | 0...4000
71 | I14 | DIF1 | L2 Bias current | FLOAT | R | 0...50
71 | I15 | DIF1 | L2 Diff current | FLOAT | R | 0...4000
71 | I16 | DIF1 | L2 Char current | FLOAT | R | 0...4000
71 | I17 | DIF1 | L3 Bias current | FLOAT | R | 0...50
71 | I18 | DIF1 | L3 Diff current | FLOAT | R | 0...4000
71 | I19 | DIF1 | L3 Char current | FLOAT | R | 0...4000
71 | I20 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...50
71 | I21 | DIF1 | HV I0d> Diff current | FLOAT | R | 0...4000
71 | I22 | DIF1 | HV I0d> Char current | FLOAT | R | 0...4000
71 | I23 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...50
71 | I24 | DIF1 | LV I0d> Diff current | FLOAT | R | 0...4000
71 | I25 | DIF1 | LV I0d> Char current | FLOAT | R | 0...4000
71 | S3 | DIF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
71 | V4 | DIF1 | L1 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V5 | DIF1 | L2 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V6 | DIF1 | L3 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | I26 | DIF1 | L1 Mag. diff. | FLOAT | R | 0...50
71 | I27 | DIF1 | L1 Ang. diff. | FLOAT | R | -360...360
71 | I28 | DIF1 | L2 Mag. diff. | FLOAT | R | 0...50
71 | I29 | DIF1 | L2 Ang. diff. | FLOAT | R | -360...360
71 | I30 | DIF1 | L3 Mag. diff. | FLOAT | R | 0...50
71 | I31 | DIF1 | L3 Ang. diff. | FLOAT | R | -360...360
71 | S4 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S5 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S6 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S7 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S8 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S9 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S10 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S11 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S12 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S13 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S14 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S15 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S16 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S17 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S18 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S19 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S20 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S21 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S22 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S23 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S24 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S25 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S26 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S27 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S28 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S29 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S30 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S31 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S32 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S33 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S34 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S35 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S36 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S37 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S38 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S39 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S40 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S41 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S42 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S43 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S44 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S45 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S46 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S47 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S48 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S49 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S50 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S51 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S52 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S53 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S54 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S55 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S56 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S57 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S58 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S59 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S60 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S61 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S62 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S63 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S64 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S65 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S66 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S67 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S68 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S69 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S70 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S71 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S72 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S73 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S74 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S75 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S76 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S77 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S78 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S79 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S80 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S81 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S82 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S83 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S84 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S85 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S86 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S87 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S88 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S89 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S90 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S91 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S92 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S93 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S94 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S95 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S96 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S97 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S98 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S99 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S100 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S101 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S102 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S103 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S104 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S105 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S106 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S107 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S108 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S109 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S110 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S111 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S112 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S113 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S114 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S115 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S116 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S117 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S118 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S119 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S120 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S121 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S122 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S123 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S124 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S125 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S126 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S127 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S128 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S129 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S130 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S131 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S132 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S133 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S134 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S135 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S136 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S137 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S138 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S139 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S140 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S141 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S142 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S143 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S144 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S145 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S146 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S147 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S148 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S149 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S150 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S151 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S152 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S153 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S154 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S155 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S156 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S157 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S158 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S159 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S160 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S161 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S162 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S163 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S164 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S165 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S166 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S167 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S168 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S169 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S170 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S171 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S172 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S173 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S174 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S175 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S176 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S177 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S178 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S179 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S180 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S181 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S182 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S183 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S184 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S185 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S186 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S187 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S188 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S189 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S190 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S191 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S192 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S193 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S194 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S195 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S196 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S197 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S198 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S199 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S200 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S201 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S202 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S203 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S204 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S205 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S206 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S207 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S208 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S209 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S210 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S211 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | O1 | DIF1 | Idb> BIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O2 | DIF1 | Idb> BIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O3 | DIF1 | Idi> NOBIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O4 | DIF1 | Idi> NOBIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O5 | DIF1 | Id> 2nd harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O6 | DIF1 | Id> 5th harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O7 | DIF1 | HV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O8 | DIF1 | HV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O9 | DIF1 | LV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O10 | DIF1 | LV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | I32 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I33 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I34 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I35 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I36 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I37 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I38 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I39 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I40 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I41 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I42 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I43 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I44 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I45 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I46 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I47 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I48 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I49 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I50 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I51 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I52 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I53 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I54 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I55 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I56 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I57 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I58 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I59 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I60 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I61 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I62 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I63 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I64 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I65 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I66 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I67 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I68 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I69 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I70 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I71 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I72 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I73 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I74 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I75 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I76 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I77 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I78 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I79 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I80 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I81 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I82 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I83 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I84 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I85 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I86 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I87 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I88 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I89 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I90 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I91 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I92 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I93 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I94 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I95 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I96 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I97 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I98 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I99 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I100 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I101 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I102 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I103 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I104 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I105 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I106 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I107 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I108 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I109 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I110 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I111 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I112 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I113 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I114 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I115 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I116 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I117 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I118 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I119 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I120 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I121 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I122 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I123 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I124 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I125 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I126 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I127 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I128 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I129 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I130 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I131 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I132 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I133 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I134 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I135 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I136 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I137 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I138 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I139 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I140 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | V7 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V8 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V9 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V10 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V11 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V12 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V13 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V14 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V15 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V16 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V17 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V18 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | I141 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I142 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I143 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I144 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I145 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I146 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I147 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I148 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I149 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I150 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I151 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I152 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I153 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I154 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I155 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I156 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I157 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I158 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I159 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I160 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I161 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I162 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I163 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I164 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I165 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I166 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I167 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I168 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I169 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I170 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I171 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I172 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I173 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I174 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I175 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I176 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I177 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I178 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I179 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I180 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I181 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I182 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I183 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I184 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I185 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I186 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I187 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I188 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I189 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I190 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I191 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I192 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I193 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I194 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I195 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I196 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I197 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I198 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I199 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I200 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I201 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I202 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I203 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I204 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I205 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I206 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I207 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I208 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I209 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I210 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I211 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I212 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I213 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I214 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | S212 | DIF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S213 | DIF1 | EventMaskHi | UINT32 | RW | 0...4294967295
66 | S1 | REF1 | I0d> [87N] mode | UINT32 | RW | 0=Disabled;1=Activated
66 | V1 | REF1 | I0d> condition | UINT32 | R | 0=Normal;1=Trip;2=Blocked
66 | S2 | REF1 | Select | UINT32 | RW | 0=Primary A;1=Secondary A;2=Per Unit
66 | S3 | REF1 | Select | UINT32 | RW | 0=REF Curr
66 | I1 | REF1 | I0d> Bias current | FLOAT | R | 0...50
66 | I2 | REF1 | I0d> Diff current | FLOAT | R | 0...50
66 | I3 | REF1 | I0d> Char current | FLOAT | R | 0...50
66 | I4 | REF1 | Calculated I0 (I0Calc) | FLOAT | R | 0...50
66 | I5 | REF1 | Measured I0 (3I0) | FLOAT | R | 0...50
66 | S4 | REF1 | REF or Cable end Diff | UINT32 | RW | 0=REF;1=CED
66 | S5 | REF1 | Comp. natural unbal. | UINT32 | RW | 0=-;1=Comp
66 | I6 | REF1 | Natural unbalance | FLOAT | R | 0...50
66 | I7 | REF1 | Natural unbalance ang | FLOAT | R | -360...360
66 | I8 | REF1 | Current for CED | FLOAT | R | 0...50
66 | I9 | REF1 | Angle for CED | FLOAT | R | -360...360
66 | S6 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S7 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S8 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S9 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S10 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S11 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S12 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S13 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S14 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S15 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S16 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S17 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S18 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S19 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S20 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S21 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S22 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S23 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S24 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S25 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S26 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S27 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S28 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S29 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S30 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S31 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S32 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S33 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S34 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S35 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S36 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S37 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S38 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S39 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S40 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S41 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S42 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S43 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S44 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S45 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S46 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S47 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S48 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S49 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S50 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S51 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S52 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S53 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S54 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S55 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S56 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S57 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S58 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S59 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S60 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S61 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S62 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S63 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S64 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S65 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S66 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S67 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S68 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S69 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S70 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S71 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S72 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S73 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S74 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S75 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S76 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S77 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | O1 | REF1 | I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
66 | O2 | REF1 | I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
66 | I10 | REF1 | Newest Register | UINT32 | R | 0...12
66 | I11 | REF1 | Bias current | FLOAT | R | 0...250
66 | I12 | REF1 | Bias current | FLOAT | R | 0...250
66 | I13 | REF1 | Bias current | FLOAT | R | 0...250
66 | I14 | REF1 | Bias current | FLOAT | R | 0...250
66 | I15 | REF1 | Bias current | FLOAT | R | 0...250
66 | I16 | REF1 | Bias current | FLOAT | R | 0...250
66 | I17 | REF1 | Bias current | FLOAT | R | 0...250
66 | I18 | REF1 | Bias current | FLOAT | R | 0...250
66 | I19 | REF1 | Bias current | FLOAT | R | 0...250
66 | I20 | REF1 | Bias current | FLOAT | R | 0...250
66 | I21 | REF1 | Bias current | FLOAT | R | 0...250
66 | I22 | REF1 | Bias current | FLOAT | R | 0...250
66 | I23 | REF1 | Differential current | FLOAT | R | 0...250
66 | I24 | REF1 | Differential current | FLOAT | R | 0...250
66 | I25 | REF1 | Differential current | FLOAT | R | 0...250
66 | I26 | REF1 | Differential current | FLOAT | R | 0...250
66 | I27 | REF1 | Differential current | FLOAT | R | 0...250
66 | I28 | REF1 | Differential current | FLOAT | R | 0...250
66 | I29 | REF1 | Differential current | FLOAT | R | 0...250
66 | I30 | REF1 | Differential current | FLOAT | R | 0...250
66 | I31 | REF1 | Differential current | FLOAT | R | 0...250
66 | I32 | REF1 | Differential current | FLOAT | R | 0...250
66 | I33 | REF1 | Differential current | FLOAT | R | 0...250
66 | I34 | REF1 | Differential current | FLOAT | R | 0...250
66 | I35 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I36 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I37 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I38 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I39 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I40 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I41 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I42 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I43 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I44 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I45 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I46 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | S78 | REF1 | EventMaskLo | UINT32 | RW | 0...4294967295
66 | S79 | REF1 | EventMaskHi | UINT32 | RW | 0...4294967295
73 | S1 | TOLT1 | TT> [49T] mode | UINT32 | RW | 0=Disabled;1=Activated
73 | V1 | TOLT1 | TT> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
73 | V2 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
73 | V3 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
73 | V4 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
73 | V5 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
73 | V6 | TOLT1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
73 | I1 | TOLT1 | IN thermal cap current | FLOAT | RW | 0...40
73 | I2 | TOLT1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
73 | S2 | TOLT1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
73 | S3 | TOLT1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
73 | I3 | TOLT1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
73 | I4 | TOLT1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
73 | S4 | TOLT1 | tau1 (t const heating) | FLOAT | RW | 0...500
73 | S5 | TOLT1 | tau2 (t const cooling) | FLOAT | RW | 0...500
73 | S6 | TOLT1 | kSF (service factor) | FLOAT | RW | 0.01...5
73 | S7 | TOLT1 | Cold Reset default theta | FLOAT | RW | 0...150
73 | V7 | TOLT1 | TT> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
73 | I5 | TOLT1 | TT> Time to 100% Theta | UINT32 | R | 0...4294967295
73 | I6 | TOLT1 | TT> Reference T curr. | FLOAT | R | 0...50
73 | I7 | TOLT1 | TT> Active meas curr. | FLOAT | R | 0...50
73 | I8 | TOLT1 | TT> T est.with act. curr. | FLOAT | R | 0...500
73 | I9 | TOLT1 | TT> T at the moment | FLOAT | R | 0...500
73 | I10 | TOLT1 | TT> Max.Temp.Rise All. | FLOAT | R | 0...250
73 | I11 | TOLT1 | TT> Temp.Rise atm. | FLOAT | R | 0...250
73 | I12 | TOLT1 | TT> Hot Spot estimate | FLOAT | R | 0...250
73 | I13 | TOLT1 | TT> Hot Spot Max. All | FLOAT | R | 0...250
73 | I14 | TOLT1 | TT> Used k for amb. temp | FLOAT | R | 0...3
73 | I15 | TOLT1 | TT> Trip delay remaining | UINT32 | R | 0...4294967295
73 | I16 | TOLT1 | TT> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
73 | I17 | TOLT1 | TT> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
73 | I18 | TOLT1 | TT> Inhibit time to rel. | UINT32 | R | 0...4294967295
73 | I19 | TOLT1 | TT> Trip time to rel. | UINT32 | R | 0...4294967295
73 | I20 | TOLT1 | TT> Thermal cap used | FLOAT | R | 0...500
73 | I21 | TOLT1 | Alarm1 inits | UINT32 | R | 0...4294967295
73 | I22 | TOLT1 | Alarm2 inits | UINT32 | R | 0...4294967295
73 | I23 | TOLT1 | Restart Inhibits | UINT32 | R | 0...4294967295
73 | I24 | TOLT1 | Trips | UINT32 | R | 0...4294967295
73 | I25 | TOLT1 | Trips Blocked | UINT32 | R | 0...4294967295
73 | S8 | TOLT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
73 | S9 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S10 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S11 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S12 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S13 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S14 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S15 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S16 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S17 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S18 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S19 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S20 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S21 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S22 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S23 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S24 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S25 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S26 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S27 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S28 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S29 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S30 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S31 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S32 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S33 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S34 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S35 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S36 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S37 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S38 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S39 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S40 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S41 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S42 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S43 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S44 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S45 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S46 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S47 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S48 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S49 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S50 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S51 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S52 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S53 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S54 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S55 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S56 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S57 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S58 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S59 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S60 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S61 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S62 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S63 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S64 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S65 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S66 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S67 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S68 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S69 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S70 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S71 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S72 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | O1 | TOLT1 | TT> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
73 | O2 | TOLT1 | TT> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
73 | O3 | TOLT1 | TT> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
73 | O4 | TOLT1 | TT> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
73 | O5 | TOLT1 | TT> Trip | SIGNAL_OUT | RW | 0...4294967295
73 | I26 | TOLT1 | Newest Register | UINT32 | R | 0...12
73 | I27 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I28 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I29 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I30 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I31 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I32 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I33 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I34 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I35 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I36 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I37 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I38 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I39 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I40 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I41 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I42 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I43 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I44 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I45 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I46 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I47 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I48 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I49 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I50 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I51 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I52 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I53 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I54 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I55 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I56 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I57 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I58 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I59 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I60 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I61 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I62 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | S73 | TOLT1 | EventMaskLo | UINT32 | RW | 0...4294967295
73 | S74 | TOLT1 | EventMaskHi | UINT32 | RW | 0...4294967295
67 | S1 | TOLF1 | TF> [49F] mode | UINT32 | RW | 0=Disabled;1=Activated
67 | V1 | TOLF1 | TF> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
67 | V2 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
67 | V3 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
67 | V4 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
67 | V5 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
67 | V6 | TOLF1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
67 | I1 | TOLF1 | IN thermal cap current | FLOAT | RW | 0...40
67 | I2 | TOLF1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
67 | I3 | TOLF1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
67 | I4 | TOLF1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
67 | I5 | TOLF1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
67 | I6 | TOLF1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
67 | S2 | TOLF1 | tau (t const) | FLOAT | RW | 0...500
67 | S3 | TOLF1 | Nominal current | FLOAT | RW | 1...9999999
67 | S4 | TOLF1 | kSF (service factor) | FLOAT | RW | 0.01...5
67 | I7 | TOLF1 | TF> Time to 100% Theta | UINT32 | R | 0...4294967295
67 | I8 | TOLF1 | TF> Reference T curr. | FLOAT | R | 0...50
67 | I9 | TOLF1 | TF> Active meas curr. | FLOAT | R | 0...50
67 | I10 | TOLF1 | TF> T est.with act. curr. | FLOAT | R | 0...500
67 | I11 | TOLF1 | TF> T at the moment | FLOAT | R | 0...500
67 | I12 | TOLF1 | TF> Max.Temp.Rise All. | FLOAT | R | 0...250
67 | I13 | TOLF1 | TF> Temp.Rise atm. | FLOAT | R | 0...250
67 | I14 | TOLF1 | TF> Hot Spot estimate | FLOAT | R | 0...250
67 | I15 | TOLF1 | TF> Hot Spot Max. All | FLOAT | R | 0...250
67 | I16 | TOLF1 | TF> Used k for amb. temp | FLOAT | R | 0...3
67 | I17 | TOLF1 | TF> Trip delay remaining | UINT32 | R | 0...4294967295
67 | I18 | TOLF1 | TF> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
67 | I19 | TOLF1 | TF> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
67 | I20 | TOLF1 | TF> Inhibit time to rel. | UINT32 | R | 0...4294967295
67 | I21 | TOLF1 | TF> Trip time to rel. | UINT32 | R | 0...4294967295
67 | I22 | TOLF1 | TF> Thermal cap used | FLOAT | R | 0...500
67 | I23 | TOLF1 | Alarm1 inits | UINT32 | R | 0...4294967295
67 | I24 | TOLF1 | Alarm2 inits | UINT32 | R | 0...4294967295
67 | I25 | TOLF1 | Restart Inhibits | UINT32 | R | 0...4294967295
67 | I26 | TOLF1 | Trips | UINT32 | R | 0...4294967295
67 | I27 | TOLF1 | Trips Blocked | UINT32 | R | 0...4294967295
67 | S5 | TOLF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
67 | S6 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S7 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S8 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S9 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S10 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S11 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S12 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S13 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S14 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S15 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S16 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S17 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S18 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S19 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S20 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S21 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S22 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S23 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S24 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S25 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S26 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S27 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S28 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S29 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S30 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S31 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S32 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S33 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S34 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S35 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S36 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S37 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S38 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S39 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S40 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S41 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S42 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S43 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S44 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S45 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S46 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S47 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S48 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S49 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S50 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S51 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S52 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S53 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S54 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S55 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S56 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S57 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S58 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S59 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S60 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S61 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S62 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S63 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S64 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S65 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S66 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S67 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S68 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S69 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | O1 | TOLF1 | TF> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
67 | O2 | TOLF1 | TF> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
67 | O3 | TOLF1 | TF> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
67 | O4 | TOLF1 | TF> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
67 | O5 | TOLF1 | TF> Trip | SIGNAL_OUT | RW | 0...4294967295
67 | I28 | TOLF1 | Newest Register | UINT32 | R | 0...12
67 | I29 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I30 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I31 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I32 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I33 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I34 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I35 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I36 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I37 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I38 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I39 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I40 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I41 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I42 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I43 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I44 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I45 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I46 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I47 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I48 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I49 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I50 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I51 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I52 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I53 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I54 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I55 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I56 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I57 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I58 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I59 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I60 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I61 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I62 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I63 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I64 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I65 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I66 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I67 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I68 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I69 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I70 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I71 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I72 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I73 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I74 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I75 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I76 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | S70 | TOLF1 | EventMaskLo | UINT32 | RW | 0...4294967295
67 | S71 | TOLF1 | EventMaskHi | UINT32 | RW | 0...4294967295
68 | S1 | TOLM1 | TM> [49M] mode | UINT32 | RW | 0=Disabled; 1=Activated
68 | V1 | TOLM1 | TM> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
68 | V2 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
68 | V3 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
68 | V4 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
68 | V5 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
68 | V6 | TOLM1 | Motor status | UINT32 | R | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
68 | S2 | TOLM1 | Pick-up current (x In) | FLOAT | RW | 0...40
68 | S3 | TOLM1 | NPS Biasing in use | UINT32 | RW | 0=No NPS biasing;1=NPS Biasing in use
68 | S4 | TOLM1 | NPS Bias factor | FLOAT | RW | 0.1...10
68 | S5 | TOLM1 | Time constants | UINT32 | RW | 0=Single;1=Multiple
68 | S6 | TOLM1 | Long Heat T const (cold) | FLOAT | RW | 0...500
68 | S7 | TOLM1 | Long Heat T const (hot) | FLOAT | RW | 0...500
68 | S8 | TOLM1 | Long Cool T const Run | FLOAT | RW | 0...3000
68 | S9 | TOLM1 | Long Cool T const Stop | FLOAT | RW | 0...3000
68 | S10 | TOLM1 | Short Heat T const (cold) | FLOAT | RW | 0...500
68 | S11 | TOLM1 | Short Heat T const (hot) | FLOAT | RW | 0...500
68 | S12 | TOLM1 | Short Cool T const | FLOAT | RW | 0...3000
68 | S13 | TOLM1 | Wf factor for L/S T const | FLOAT | RW | 0...1
68 | S14 | TOLM1 | T const dyn. balancing | UINT32 | RW | 0=Fixed;1=Dynamic
68 | S15 | TOLM1 | Short Cool T used when stop | FLOAT | RW | 0...3000
68 | S16 | TOLM1 | Cold Reset Theta Default | FLOAT | RW | 0...150
68 | I1 | TOLM1 | Wf in use | FLOAT | R | 0...1
68 | I2 | TOLM1 | Long heat TC in use | FLOAT | R | 0...500
68 | I3 | TOLM1 | Short heat TC in use | FLOAT | R | 0...500
68 | I4 | TOLM1 | Long cool TC in use | FLOAT | R | 0...500
68 | I5 | TOLM1 | Short cool TC in use | FLOAT | R | 0...500
68 | I6 | TOLM1 | Cold stall time | FLOAT | R | 0...500
68 | I7 | TOLM1 | Hot stall time | FLOAT | R | 0...500
68 | S17 | TOLM1 | Dev.Temp (tmax) | UINT32 | RW | 0=A;1=B;2=F;3=H;4=Manual set
68 | S18 | TOLM1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
68 | S19 | TOLM1 | Amb. T Selection | UINT32 | RW | 0=Manual set;1=RTD
68 | S20 | TOLM1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
68 | V7 | TOLM1 | TM> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
68 | I8 | TOLM1 | TM> Time to 100% T | UINT32 | R | 0...4294967295
68 | I9 | TOLM1 | TM> Reference T curr. | FLOAT | R | 0...50
68 | I10 | TOLM1 | TM> Active meas curr. | FLOAT | R | 0...50
68 | I11 | TOLM1 | TM> T est.with act. curr. | FLOAT | R | 0...500
68 | I12 | TOLM1 | TM> T at the moment | FLOAT | R | 0...500
68 | I13 | TOLM1 | TM> Max.Temp.Rise All. | FLOAT | R | 0...250
68 | I14 | TOLM1 | TM> Temp.Rise atm. | FLOAT | R | 0...250
68 | I15 | TOLM1 | TM> Hot Spot estimate | FLOAT | R | 0...250
68 | I16 | TOLM1 | TM> Hot Spot Max. All | FLOAT | R | 0...250
68 | I17 | TOLM1 | TM> Used k for amb. temp | FLOAT | R | 0...5
68 | I18 | TOLM1 | TM> Trip delay remaining | UINT32 | R | 0...4294967295
68 | I19 | TOLM1 | TM> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
68 | I20 | TOLM1 | TM> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
68 | I21 | TOLM1 | TM> Inhibit time to rel. | UINT32 | R | 0...4294967295
68 | I22 | TOLM1 | TM> Trip time to rel. | UINT32 | R | 0...4294967295
68 | I23 | TOLM1 | TM> Thermal cap used | FLOAT | R | 0...500
68 | I24 | TOLM1 | Alarm1 inits | UINT32 | R | 0...4294967295
68 | I25 | TOLM1 | Alarm2 inits | UINT32 | R | 0...4294967295
68 | I26 | TOLM1 | Restart Inhibits | UINT32 | R | 0...4294967295
68 | I27 | TOLM1 | Trips | UINT32 | R | 0...4294967295
68 | I28 | TOLM1 | Trips Blocked | UINT32 | R | 0...4294967295
68 | S21 | TOLM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
68 | S22 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S23 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S24 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S25 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S26 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S27 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S28 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S29 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S30 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S31 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S32 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S33 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S34 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S35 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S36 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S37 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S38 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S39 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S40 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S41 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S42 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S43 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S44 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S45 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S46 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S47 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S48 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S49 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S50 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S51 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S52 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S53 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S54 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S55 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S56 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S57 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S58 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S59 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S60 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S61 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S62 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S63 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S64 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S65 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S66 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S67 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S68 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S69 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S70 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S71 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S72 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S73 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S74 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S75 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S76 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S77 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S78 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S79 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S80 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S81 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S82 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S83 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S84 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S85 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | O1 | TOLM1 | TM> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
68 | O2 | TOLM1 | TM> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
68 | O3 | TOLM1 | TM> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
68 | O4 | TOLM1 | TM> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
68 | O5 | TOLM1 | TM> Trip | SIGNAL_OUT | RW | 0...4294967295
68 | I29 | TOLM1 | Newest Register | UINT32 | R | 0...12
68 | I30 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I31 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I32 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I33 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I34 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I35 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I36 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I37 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I38 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I39 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I40 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I41 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I42 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I43 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I44 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I45 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I46 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I47 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I48 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I49 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I50 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I51 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I52 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I53 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I54 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I55 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I56 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I57 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I58 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I59 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I60 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I61 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I62 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I63 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I64 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I65 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I66 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I67 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I68 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I69 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I70 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I71 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I72 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I73 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I74 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I75 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I76 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I77 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I78 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I79 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I80 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I81 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I82 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I83 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I84 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I85 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I86 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I87 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I88 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I89 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I90 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I91 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I92 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I93 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I94 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I95 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I96 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I97 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I98 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I99 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I100 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I101 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I102 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I103 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I104 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I105 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I106 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I107 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I108 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I109 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I110 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I111 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I112 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I113 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I114 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I115 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I116 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I117 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I118 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I119 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I120 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I121 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I122 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I123 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I124 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I125 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I126 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I127 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I128 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I129 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I130 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I131 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I132 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I133 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I134 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I135 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I136 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I137 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | S86 | TOLM1 | EventMaskLo | UINT32 | RW | 0...4294967295
68 | S87 | TOLM1 | EventMaskHi | UINT32 | RW | 0...4294967295
57 | S1 | LCR1 | ISt> [48/14/50LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
57 | V1 | LCR1 | ISt> condition | UINT32 | R | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
57 | I1 | LCR1 | ISt> starts | UINT32 | R | 0...4294967295
57 | I2 | LCR1 | ISt> Set cap used in last start | FLOAT | R | 0...500
57 | I3 | LCR1 | ISt> Max cap used in last start | FLOAT | R | 0...500
57 | I4 | LCR1 | ISt> Set time trips | UINT32 | R | 0...4294967295
57 | I5 | LCR1 | ISt> Max cap trips | UINT32 | R | 0...4294967295
57 | I6 | LCR1 | ISt> blocks | UINT32 | R | 0...4294967295
57 | S2 | LCR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
57 | S3 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S4 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S5 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S6 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S7 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S8 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S9 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S10 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S11 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S12 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S13 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S14 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S15 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S16 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S17 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S18 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S19 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S20 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S21 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S22 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S23 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S24 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S25 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S26 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S27 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S28 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S29 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S30 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S31 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S32 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S33 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S34 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S35 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S36 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S37 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S38 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S39 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S40 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S41 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S42 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S43 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S44 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S45 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S46 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S47 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S48 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S49 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S50 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | O1 | LCR1 | ISt> START | SIGNAL_OUT | RW | 0...4294967295
57 | O2 | LCR1 | ISt> Set time TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O3 | LCR1 | ISt> Machine cap.TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O4 | LCR1 | ISt> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
57 | I7 | LCR1 | Newest Register | UINT32 | R | 0...12
57 | I8 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I9 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I10 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I11 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I12 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I13 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I14 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I15 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I16 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I17 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I18 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I19 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I20 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I21 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I22 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I23 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I24 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I25 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I26 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I27 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I28 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I29 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I30 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I31 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I32 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I33 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I34 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I35 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I36 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I37 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I38 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I39 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I40 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I41 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I42 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I43 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I44 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I45 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I46 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I47 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I48 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I49 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I50 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I51 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I52 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I53 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I54 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I55 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I56 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I57 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I58 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I59 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I60 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I61 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I62 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I63 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I64 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I65 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I66 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I67 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I68 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I69 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I70 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I71 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I72 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I73 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I74 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I75 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I76 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I77 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I78 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I79 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I80 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I81 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I82 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I83 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I84 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I85 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I86 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I87 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I88 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I89 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I90 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I91 | LCR1 | Phase C current | FLOAT | R | 0...250
56 | S1 | FSP1 | N> [66/86] mode | UINT32 | RW | 0=Disabled; 1=Activated
56 | V1 | FSP1 | N> condition | UINT32 | R | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
56 | I1 | FSP1 | N> alarms | UINT32 | R | 0...4294967295
56 | I2 | FSP1 | N> Inhibits | UINT32 | R | 0...4294967295
56 | I3 | FSP1 | N> blocks | UINT32 | R | 0...4294967295
56 | S2 | FSP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
56 | I4 | FSP1 | Start monitoring time left | UINT32 | R | 0...4294967295
56 | I5 | FSP1 | Inhibit time on | UINT32 | R | 0...4294967295
56 | I6 | FSP1 | Alarm time on | UINT32 | R | 0...4294967295
56 | I7 | FSP1 | Time since last start | UINT32 | R | 0...4294967295
56 | I8 | FSP1 | Start count atm. | UINT32 | R | 0...4294967295
56 | I9 | FSP1 | Starts left atm. | UINT32 | R | 0...4294967295
56 | S3 | FSP1 | Give one more start (Warning! Motor may overheat) | UINT32 | W | 0=-;1=Deduct one start
56 | O1 | FSP1 | N> One start remaining (Alarm) | SIGNAL_OUT | RW | 0...4294967295
56 | O2 | FSP1 | N> INHIBIT ON (General) | SIGNAL_OUT | RW | 0...4294967295
56 | O3 | FSP1 | N> INHIBIT ON Mot Running | SIGNAL_OUT | RW | 0...4294967295
56 | O4 | FSP1 | N> INHIBIT ON Mot Stopped | SIGNAL_OUT | RW | 0...4294967295
56 | O5 | FSP1 | N> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
56 | I10 | FSP1 | Newest Register | UINT32 | R | 0...12
56 | S4 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S5 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S6 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S7 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S8 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S9 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S10 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S11 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S12 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S13 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S14 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S15 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S16 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S17 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S18 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S19 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S20 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S21 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S22 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S23 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S24 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S25 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S26 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S27 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S28 | FSP1 | Start count | FLOAT | R | 0...250
56 | S29 | FSP1 | Start count | FLOAT | R | 0...250
56 | S30 | FSP1 | Start count | FLOAT | R | 0...250
56 | S31 | FSP1 | Start count | FLOAT | R | 0...250
56 | S32 | FSP1 | Start count | FLOAT | R | 0...250
56 | S33 | FSP1 | Start count | FLOAT | R | 0...250
56 | S34 | FSP1 | Start count | FLOAT | R | 0...250
56 | S35 | FSP1 | Start count | FLOAT | R | 0...250
56 | S36 | FSP1 | Start count | FLOAT | R | 0...250
56 | S37 | FSP1 | Start count | FLOAT | R | 0...250
56 | S38 | FSP1 | Start count | FLOAT | R | 0...250
56 | S39 | FSP1 | Start count | FLOAT | R | 0...250
56 | S40 | FSP1 | EventMaskLo | UINT32 | RW | 0...4294967295
60 | S1 | NUC1 | I< [37] mode | UINT32 | RW | 0=Disabled; 1=Activated
60 | V1 | NUC1 | I< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
60 | I1 | NUC1 | I< starts | UINT32 | R | 0...4294967295
60 | I2 | NUC1 | I< trips | UINT32 | R | 0...4294967295
60 | I3 | NUC1 | I< blocks | UINT32 | R | 0...4294967295
60 | S2 | NUC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
60 | S3 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S4 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S5 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S6 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S7 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S8 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S9 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S10 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S11 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S12 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S13 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S14 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S15 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S16 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S17 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S18 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S19 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S20 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S21 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S22 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S23 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S24 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S25 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S26 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | O1 | NUC1 | I< START | SIGNAL_OUT | RW | 0...4294967295
60 | O2 | NUC1 | I< TRIP | SIGNAL_OUT | RW | 0...4294967295
60 | O3 | NUC1 | I< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
60 | I4 | NUC1 | Newest Register | UINT32 | R | 0...12
60 | I5 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I6 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I7 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I8 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I9 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I10 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I11 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I12 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I13 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I14 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I15 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I16 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I17 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I18 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I19 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I20 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I21 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I22 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I23 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I24 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I25 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I26 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I27 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I28 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I29 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I30 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I31 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I32 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I33 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I34 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I35 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I36 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I37 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I38 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I39 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I40 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | S27 | NUC1 | EventMaskLo | UINT32 | RW | 0...4294967295
59 | S1 | MJP1 | Im> [51LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
59 | V1 | MJP1 | Im> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
59 | I1 | MJP1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
59 | I2 | MJP1 | Im> starts | UINT32 | R | 0...4294967295
59 | I3 | MJP1 | Im> trips | UINT32 | R | 0...4294967295
59 | I4 | MJP1 | Im> blocks | UINT32 | R | 0...4294967295
59 | S2 | MJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
59 | S3 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S4 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S5 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S6 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S7 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S8 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S9 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S10 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S11 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S12 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S13 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S14 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S15 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S16 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S17 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S18 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | O1 | MJP1 | Im> START | SIGNAL_OUT | RW | 0...4294967295
59 | O2 | MJP1 | Im> TRIP | SIGNAL_OUT | RW | 0...4294967295
59 | O3 | MJP1 | Im> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
59 | I5 | MJP1 | Newest Register | UINT32 | R | 0...12
59 | I6 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I7 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I8 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I9 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I10 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I11 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I12 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I13 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I14 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I15 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I16 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I17 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I18 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I19 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I20 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I21 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I22 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I23 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I24 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I25 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I26 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I27 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I28 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I29 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I30 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I31 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I32 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I33 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I34 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I35 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I36 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I37 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I38 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I39 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I40 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I41 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | S19 | MJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
85 | S1 | OV1 | U> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
85 | V1 | OV1 | U> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
85 | I1 | OV1 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
85 | I2 | OV1 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
85 | I3 | OV1 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
85 | I4 | OV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
85 | I5 | OV1 | U> starts | UINT32 | R | 0...4294967295
85 | I6 | OV1 | U> trips | UINT32 | R | 0...4294967295
85 | I7 | OV1 | U> blocks | UINT32 | R | 0...4294967295
85 | S2 | OV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
85 | S3 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S4 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S5 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S6 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S7 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S8 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S9 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S10 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S11 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S12 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S13 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S14 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S15 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S16 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S17 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S18 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S19 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S20 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S21 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S22 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S23 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S24 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S25 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S26 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | O1 | OV1 | U> START | SIGNAL_OUT | RW | 0...4294967295
85 | O2 | OV1 | U> TRIP | SIGNAL_OUT | RW | 0...4294967295
85 | O3 | OV1 | U> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
85 | I8 | OV1 | Newest Register | UINT32 | R | 0...12
85 | I9 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I10 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I11 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I12 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I13 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I14 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I15 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I16 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I17 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I18 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I19 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I20 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I21 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I22 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I23 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I24 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I25 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I26 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I27 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I28 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I29 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I30 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I31 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I32 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I33 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I34 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I35 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I36 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I37 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I38 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I39 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I40 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I41 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I42 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I43 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I44 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | S27 | OV1 | EventMaskLo | UINT32 | RW | 0...4294967295
86 | S1 | OV2 | U>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
86 | V1 | OV2 | U>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
86 | I1 | OV2 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
86 | I2 | OV2 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
86 | I3 | OV2 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
86 | I4 | OV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
86 | I5 | OV2 | U>> starts | UINT32 | R | 0...4294967295
86 | I6 | OV2 | U>> trips | UINT32 | R | 0...4294967295
86 | I7 | OV2 | U>> blocks | UINT32 | R | 0...4294967295
86 | S2 | OV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
86 | S3 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S4 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S5 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S6 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S7 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S8 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S9 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S10 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S11 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S12 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S13 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S14 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S15 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S16 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S17 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S18 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S19 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S20 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S21 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S22 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S23 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S24 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S25 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S26 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | O1 | OV2 | U>> START | SIGNAL_OUT | RW | 0...4294967295
86 | O2 | OV2 | U>> TRIP | SIGNAL_OUT | RW | 0...4294967295
86 | O3 | OV2 | U>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
86 | I8 | OV2 | Newest Register | UINT32 | R | 0...12
86 | I9 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I10 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I11 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I12 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I13 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I14 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I15 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I16 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I17 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I18 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I19 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I20 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I21 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I22 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I23 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I24 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I25 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I26 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I27 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I28 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I29 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I30 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I31 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I32 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I33 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I34 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I35 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I36 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I37 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I38 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I39 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I40 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I41 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I42 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I43 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I44 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | S27 | OV2 | EventMaskLo | UINT32 | RW | 0...4294967295
87 | S1 | OV3 | U>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
87 | V1 | OV3 | U>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
87 | I1 | OV3 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
87 | I2 | OV3 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
87 | I3 | OV3 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
87 | I4 | OV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
87 | I5 | OV3 | U>>> starts | UINT32 | R | 0...4294967295
87 | I6 | OV3 | U>>> trips | UINT32 | R | 0...4294967295
87 | I7 | OV3 | U>>> blocks | UINT32 | R | 0...4294967295
87 | S2 | OV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
87 | S3 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S4 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S5 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S6 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S7 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S8 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S9 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S10 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S11 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S12 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S13 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S14 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S15 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S16 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S17 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S18 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S19 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S20 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S21 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S22 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S23 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S24 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S25 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S26 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | O1 | OV3 | U>>> START | SIGNAL_OUT | RW | 0...4294967295
87 | O2 | OV3 | U>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
87 | O3 | OV3 | U>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
87 | I8 | OV3 | Newest Register | UINT32 | R | 0...12
87 | I9 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I10 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I11 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I12 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I13 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I14 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I15 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I16 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I17 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I18 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I19 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I20 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I21 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I22 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I23 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I24 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I25 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I26 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I27 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I28 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I29 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I30 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I31 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I32 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I33 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I34 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I35 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I36 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I37 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I38 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I39 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I40 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I41 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I42 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I43 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I44 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | S27 | OV3 | EventMaskLo | UINT32 | RW | 0...4294967295
88 | S1 | OV4 | U>>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
88 | V1 | OV4 | U>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
88 | I1 | OV4 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
88 | I2 | OV4 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
88 | I3 | OV4 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
88 | I4 | OV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
88 | I5 | OV4 | U>>>> starts | UINT32 | R | 0...4294967295
88 | I6 | OV4 | U>>>> trips | UINT32 | R | 0...4294967295
88 | I7 | OV4 | U>>>> blocks | UINT32 | R | 0...4294967295
88 | S2 | OV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
88 | S3 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S4 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S5 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S6 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S7 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S8 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S9 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S10 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S11 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S12 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S13 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S14 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S15 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S16 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S17 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S18 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S19 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S20 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S21 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S22 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S23 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S24 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S25 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S26 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | O1 | OV4 | U>>>> START | SIGNAL_OUT | RW | 0...4294967295
88 | O2 | OV4 | U>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
88 | O3 | OV4 | U>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
88 | I8 | OV4 | Newest Register | UINT32 | R | 0...12
88 | I9 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I10 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I11 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I12 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I13 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I14 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I15 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I16 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I17 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I18 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I19 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I20 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I21 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I22 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I23 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I24 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I25 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I26 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I27 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I28 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I29 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I30 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I31 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I32 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I33 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I34 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I35 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I36 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I37 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I38 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I39 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I40 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I41 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I42 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I43 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I44 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | S27 | OV4 | EventMaskLo | UINT32 | RW | 0...4294967295
89 | S1 | UV1 | U< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
89 | V1 | UV1 | U< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
89 | I1 | UV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
89 | I2 | UV1 | U< starts | UINT32 | R | 0...4294967295
89 | I3 | UV1 | U< trips | UINT32 | R | 0...4294967295
89 | I4 | UV1 | U< blocks | UINT32 | R | 0...4294967295
89 | S2 | UV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
89 | S3 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S4 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S5 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S6 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S7 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S8 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S9 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S10 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S11 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S12 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S13 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S14 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S15 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S16 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S17 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S18 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S19 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S20 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S21 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S22 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S23 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S24 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S25 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S26 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S27 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S28 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S29 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S30 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S31 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S32 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S33 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S34 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | O1 | UV1 | U< START | SIGNAL_OUT | RW | 0...4294967295
89 | O2 | UV1 | U< TRIP | SIGNAL_OUT | RW | 0...4294967295
89 | O3 | UV1 | U< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
89 | I5 | UV1 | Newest Register | UINT32 | R | 0...12
89 | I6 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I7 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I8 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I9 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I10 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I11 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I12 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I13 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I14 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I15 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I16 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I17 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I18 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I19 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I20 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I21 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I22 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I23 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I24 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I25 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I26 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I27 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I28 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I29 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I30 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I31 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I32 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I33 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I34 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I35 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I36 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I37 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I38 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I39 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I40 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I41 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | S35 | UV1 | EventMaskLo | UINT32 | RW | 0...4294967295
90 | S1 | UV2 | U<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
90 | V1 | UV2 | U<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
90 | I1 | UV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
90 | I2 | UV2 | U<< starts | UINT32 | R | 0...4294967295
90 | I3 | UV2 | U<< trips | UINT32 | R | 0...4294967295
90 | I4 | UV2 | U<< blocks | UINT32 | R | 0...4294967295
90 | S2 | UV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
90 | S3 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S4 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S5 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S6 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S7 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S8 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S9 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S10 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S11 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S12 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S13 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S14 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S15 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S16 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S17 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S18 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S19 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S20 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S21 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S22 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S23 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S24 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S25 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S26 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S27 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S28 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S29 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S30 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S31 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S32 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S33 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S34 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | O1 | UV2 | U<< START | SIGNAL_OUT | RW | 0...4294967295
90 | O2 | UV2 | U<< TRIP | SIGNAL_OUT | RW | 0...4294967295
90 | O3 | UV2 | U<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
90 | I5 | UV2 | Newest Register | UINT32 | R | 0...12
90 | I6 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I7 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I8 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I9 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I10 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I11 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I12 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I13 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I14 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I15 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I16 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I17 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I18 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I19 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I20 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I21 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I22 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I23 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I24 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I25 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I26 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I27 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I28 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I29 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I30 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I31 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I32 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I33 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I34 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I35 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I36 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I37 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I38 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I39 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I40 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I41 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | S35 | UV2 | EventMaskLo | UINT32 | RW | 0...4294967295
91 | S1 | UV3 | U<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
91 | V1 | UV3 | U<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
91 | I1 | UV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
91 | I2 | UV3 | U<<< starts | UINT32 | R | 0...4294967295
91 | I3 | UV3 | U<<< trips | UINT32 | R | 0...4294967295
91 | I4 | UV3 | U<<< blocks | UINT32 | R | 0...4294967295
91 | S2 | UV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
91 | S3 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S4 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S5 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S6 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S7 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S8 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S9 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S10 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S11 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S12 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S13 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S14 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S15 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S16 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S17 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S18 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S19 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S20 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S21 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S22 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S23 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S24 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S25 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S26 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S27 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S28 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S29 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S30 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S31 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S32 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S33 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S34 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | O1 | UV3 | U<<< START | SIGNAL_OUT | RW | 0...4294967295
91 | O2 | UV3 | U<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
91 | O3 | UV3 | U<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
91 | I5 | UV3 | Newest Register | UINT32 | R | 0...12
91 | I6 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I7 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I8 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I9 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I10 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I11 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I12 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I13 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I14 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I15 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I16 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I17 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I18 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I19 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I20 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I21 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I22 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I23 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I24 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I25 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I26 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I27 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I28 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I29 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I30 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I31 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I32 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I33 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I34 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I35 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I36 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I37 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I38 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I39 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I40 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I41 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | S35 | UV3 | EventMaskLo | UINT32 | RW | 0...4294967295
92 | S1 | UV4 | U<<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
92 | V1 | UV4 | U<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
92 | I1 | UV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
92 | I2 | UV4 | U<<<< starts | UINT32 | R | 0...4294967295
92 | I3 | UV4 | U<<<< trips | UINT32 | R | 0...4294967295
92 | I4 | UV4 | U<<<< blocks | UINT32 | R | 0...4294967295
92 | S2 | UV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
92 | S3 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S4 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S5 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S6 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S7 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S8 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S9 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S10 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S11 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S12 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S13 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S14 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S15 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S16 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S17 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S18 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S19 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S20 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S21 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S22 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S23 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S24 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S25 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S26 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S27 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S28 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S29 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S30 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S31 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S32 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S33 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S34 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | O1 | UV4 | U<<<< START | SIGNAL_OUT | RW | 0...4294967295
92 | O2 | UV4 | U<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
92 | O3 | UV4 | U<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
92 | I5 | UV4 | Newest Register | UINT32 | R | 0...12
92 | I6 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I7 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I8 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I9 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I10 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I11 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I12 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I13 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I14 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I15 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I16 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I17 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I18 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I19 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I20 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I21 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I22 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I23 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I24 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I25 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I26 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I27 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I28 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I29 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I30 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I31 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I32 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I33 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I34 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I35 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I36 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I37 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I38 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I39 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I40 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I41 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | S35 | UV4 | EventMaskLo | UINT32 | RW | 0...4294967295
93 | S1 | NOV1 | U0> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
93 | V1 | NOV1 | U0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
93 | I1 | NOV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
93 | I2 | NOV1 | U0> starts | UINT32 | R | 0...4294967295
93 | I3 | NOV1 | U0> trips | UINT32 | R | 0...4294967295
93 | I4 | NOV1 | U0> blocks | UINT32 | R | 0...4294967295
93 | S2 | NOV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
93 | S3 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S4 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S5 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S6 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S7 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S8 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S9 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S10 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S11 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S12 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S13 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S14 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S15 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S16 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S17 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S18 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | O1 | NOV1 | U0> START | SIGNAL_OUT | RW | 0...4294967295
93 | O2 | NOV1 | U0> TRIP | SIGNAL_OUT | RW | 0...4294967295
93 | O3 | NOV1 | U0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
93 | I5 | NOV1 | Newest Register | UINT32 | R | 0...12
93 | I6 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I7 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I8 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I9 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I10 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I11 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I12 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I13 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I14 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I15 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I16 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I17 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I18 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I19 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I20 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I21 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I22 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I23 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I24 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I25 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I26 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I27 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I28 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I29 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | S19 | NOV1 | EventMaskLo | UINT32 | RW | 0...4294967295
94 | S1 | NOV2 | U0>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
94 | V1 | NOV2 | U0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
94 | I1 | NOV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
94 | I2 | NOV2 | U0>> starts | UINT32 | R | 0...4294967295
94 | I3 | NOV2 | U0>> trips | UINT32 | R | 0...4294967295
94 | I4 | NOV2 | U0>> blocks | UINT32 | R | 0...4294967295
94 | S2 | NOV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
94 | S3 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S4 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S5 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S6 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S7 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S8 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S9 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S10 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S11 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S12 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S13 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S14 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S15 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S16 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S17 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S18 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | O1 | NOV2 | U0>> START | SIGNAL_OUT | RW | 0...4294967295
94 | O2 | NOV2 | U0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
94 | O3 | NOV2 | U0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
94 | I5 | NOV2 | Newest Register | UINT32 | R | 0...12
94 | I6 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I7 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I8 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I9 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I10 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I11 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I12 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I13 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I14 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I15 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I16 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I17 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I18 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I19 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I20 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I21 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I22 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I23 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I24 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I25 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I26 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I27 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I28 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I29 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | S19 | NOV2 | EventMaskLo | UINT32 | RW | 0...4294967295
95 | S1 | NOV3 | U0>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
95 | V1 | NOV3 | U0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
95 | I1 | NOV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
95 | I2 | NOV3 | U0>>> starts | UINT32 | R | 0...4294967295
95 | I3 | NOV3 | U0>>> trips | UINT32 | R | 0...4294967295
95 | I4 | NOV3 | U0>>> blocks | UINT32 | R | 0...4294967295
95 | S2 | NOV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
95 | S3 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S4 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S5 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S6 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S7 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S8 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S9 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S10 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S11 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S12 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S13 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S14 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S15 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S16 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S17 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S18 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | O1 | NOV3 | U0>>> START | SIGNAL_OUT | RW | 0...4294967295
95 | O2 | NOV3 | U0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
95 | O3 | NOV3 | U0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
95 | I5 | NOV3 | Newest Register | UINT32 | R | 0...12
95 | I6 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I7 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I8 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I9 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I10 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I11 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I12 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I13 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I14 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I15 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I16 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I17 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I18 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I19 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I20 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I21 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I22 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I23 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I24 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I25 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I26 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I27 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I28 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I29 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | S19 | NOV3 | EventMaskLo | UINT32 | RW | 0...4294967295
96 | S1 | NOV4 | U0>>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
96 | V1 | NOV4 | U0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
96 | I1 | NOV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
96 | I2 | NOV4 | U0>>>> starts | UINT32 | R | 0...4294967295
96 | I3 | NOV4 | U0>>>> trips | UINT32 | R | 0...4294967295
96 | I4 | NOV4 | U0>>>> blocks | UINT32 | R | 0...4294967295
96 | S2 | NOV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
96 | S3 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S4 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S5 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S6 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S7 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S8 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S9 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S10 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S11 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S12 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S13 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S14 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S15 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S16 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S17 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S18 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | O1 | NOV4 | U0>>>> START | SIGNAL_OUT | RW | 0...4294967295
96 | O2 | NOV4 | U0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
96 | O3 | NOV4 | U0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
96 | I5 | NOV4 | Newest Register | UINT32 | R | 0...12
96 | I6 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I7 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I8 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I9 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I10 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I11 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I12 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I13 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I14 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I15 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I16 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I17 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I18 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I19 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I20 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I21 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I22 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I23 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I24 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I25 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I26 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I27 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I28 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I29 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | S19 | NOV4 | EventMaskLo | UINT32 | RW | 0...4294967295
130 | S1 | VUB1 | U1/2 >/< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
130 | V1 | VUB1 | U1/2 >/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
130 | I1 | VUB1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
130 | I2 | VUB1 | U1/2 >/< starts | UINT32 | R | 0...4294967295
130 | I3 | VUB1 | U1/2 >/< trips | UINT32 | R | 0...4294967295
130 | I4 | VUB1 | U1/2 >/< blocks | UINT32 | R | 0...4294967295
130 | S2 | VUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
130 | S3 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S4 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S5 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S6 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S7 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S8 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S9 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S10 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S11 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S12 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S13 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S14 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S15 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S16 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S17 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S18 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S19 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S20 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S21 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S22 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S23 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S24 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S25 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S26 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S27 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S28 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S29 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S30 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S31 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S32 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S33 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S34 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | O1 | VUB1 | U1/2 >/< START | SIGNAL_OUT | RW | 0...4294967295
130 | O2 | VUB1 | U1/2 >/< TRIP | SIGNAL_OUT | RW | 0...4294967295
130 | O3 | VUB1 | U1/2 >/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
130 | I5 | VUB1 | Newest Register | UINT32 | R | 0...12
130 | I6 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I7 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I8 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I9 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I10 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I11 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I12 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I13 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I14 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I15 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I16 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I17 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I18 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I19 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I20 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I21 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I22 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I23 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I24 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I25 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I26 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I27 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I28 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I29 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | S35 | VUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
131 | S1 | VUB2 | U1/2 >>/<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
131 | V1 | VUB2 | U1/2 >>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
131 | I1 | VUB2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
131 | I2 | VUB2 | U1/2 >>/<< starts | UINT32 | R | 0...4294967295
131 | I3 | VUB2 | U1/2 >>/<< trips | UINT32 | R | 0...4294967295
131 | I4 | VUB2 | U1/2 >>/<< blocks | UINT32 | R | 0...4294967295
131 | S2 | VUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
131 | S3 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S4 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S5 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S6 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S7 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S8 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S9 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S10 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S11 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S12 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S13 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S14 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S15 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S16 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S17 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S18 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S19 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S20 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S21 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S22 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S23 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S24 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S25 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S26 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S27 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S28 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S29 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S30 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S31 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S32 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S33 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S34 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | O1 | VUB2 | U1/2 >>/<< START | SIGNAL_OUT | RW | 0...4294967295
131 | O2 | VUB2 | U1/2 >>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
131 | O3 | VUB2 | U1/2 >>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
131 | I5 | VUB2 | Newest Register | UINT32 | R | 0...12
131 | I6 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I7 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I8 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I9 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I10 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I11 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I12 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I13 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I14 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I15 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I16 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I17 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I18 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I19 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I20 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I21 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I22 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I23 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I24 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I25 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I26 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I27 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I28 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I29 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | S35 | VUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
132 | S1 | VUB3 | U1/2 >>>/<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
132 | V1 | VUB3 | U1/2 >>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
132 | I1 | VUB3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
132 | I2 | VUB3 | U1/2 >>>/<<< starts | UINT32 | R | 0...4294967295
132 | I3 | VUB3 | U1/2 >>>/<<< trips | UINT32 | R | 0...4294967295
132 | I4 | VUB3 | U1/2 >>>/<<< blocks | UINT32 | R | 0...4294967295
132 | S2 | VUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
132 | S3 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S4 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S5 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S6 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S7 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S8 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S9 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S10 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S11 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S12 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S13 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S14 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S15 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S16 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S17 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S18 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S19 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S20 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S21 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S22 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S23 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S24 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S25 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S26 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S27 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S28 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S29 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S30 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S31 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S32 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S33 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S34 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | O1 | VUB3 | U1/2 >>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
132 | O2 | VUB3 | U1/2 >>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
132 | O3 | VUB3 | U1/2 >>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
132 | I5 | VUB3 | Newest Register | UINT32 | R | 0...12
132 | I6 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I7 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I8 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I9 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I10 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I11 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I12 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I13 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I14 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I15 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I16 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I17 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I18 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I19 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I20 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I21 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I22 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I23 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I24 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I25 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I26 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I27 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I28 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I29 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | S35 | VUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
133 | S1 | VUB4 | U1/2 >>>>/<<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
133 | V1 | VUB4 | U1/2 >>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
133 | I1 | VUB4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
133 | I2 | VUB4 | U1/2 >>>>/<<<< starts | UINT32 | R | 0...4294967295
133 | I3 | VUB4 | U1/2 >>>>/<<<< trips | UINT32 | R | 0...4294967295
133 | I4 | VUB4 | U1/2 >>>>/<<<< blocks | UINT32 | R | 0...4294967295
133 | S2 | VUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
133 | S3 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S4 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S5 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S6 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S7 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S8 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S9 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S10 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S11 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S12 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S13 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S14 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S15 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S16 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S17 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S18 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S19 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S20 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S21 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S22 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S23 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S24 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S25 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S26 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S27 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S28 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S29 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S30 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S31 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S32 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S33 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S34 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | O1 | VUB4 | U1/2 >>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
133 | O2 | VUB4 | U1/2 >>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
133 | O3 | VUB4 | U1/2 >>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
133 | I5 | VUB4 | Newest Register | UINT32 | R | 0...12
133 | I6 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I7 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I8 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I9 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I10 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I11 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I12 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I13 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I14 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I15 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I16 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I17 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I18 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I19 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I20 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I21 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I22 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I23 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I24 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I25 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I26 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I27 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I28 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I29 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | S35 | VUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
99 | S1 | FRQV1 | f</> [81O/81U] mode | UINT32 | RW | 0=Disabled;1=Activated
99 | V1 | FRQV1 | f> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I1 | FRQV1 | f> fmeas / fset | FLOAT | R | 0...20
99 | S2 | FRQV1 | f>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V2 | FRQV1 | f>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I2 | FRQV1 | f>> fmeas / fset | FLOAT | R | 0...20
99 | S3 | FRQV1 | f>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V3 | FRQV1 | f>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I3 | FRQV1 | f>>> fmeas / fset | FLOAT | R | 0...20
99 | S4 | FRQV1 | f>>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V4 | FRQV1 | f>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I4 | FRQV1 | f>>>> fmeas / fset | FLOAT | R | 0...20
99 | S5 | FRQV1 | f< Enable | UINT32 | RW | 0=No;1=Yes
99 | V5 | FRQV1 | f< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I5 | FRQV1 | f< fmeas / fset | FLOAT | R | 0...20
99 | S6 | FRQV1 | f<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V6 | FRQV1 | f<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I6 | FRQV1 | f<< fmeas / fset | FLOAT | R | 0...20
99 | S7 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V7 | FRQV1 | f<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I7 | FRQV1 | f<<< fmeas / fset | FLOAT | R | 0...20
99 | S8 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V8 | FRQV1 | f<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I8 | FRQV1 | f<<<< fmeas / fset | FLOAT | R | 0...20
99 | I9 | FRQV1 | f> starts | UINT32 | R | 0...4294967295
99 | I10 | FRQV1 | f> trips | UINT32 | R | 0...4294967295
99 | I11 | FRQV1 | f> blocks | UINT32 | R | 0...4294967295
99 | I12 | FRQV1 | f>> starts | UINT32 | R | 0...4294967295
99 | I13 | FRQV1 | f>> trips | UINT32 | R | 0...4294967295
99 | I14 | FRQV1 | f>> blocks | UINT32 | R | 0...4294967295
99 | I15 | FRQV1 | f>>> starts | UINT32 | R | 0...4294967295
99 | I16 | FRQV1 | f>>> trips | UINT32 | R | 0...4294967295
99 | I17 | FRQV1 | f>>> blocks | UINT32 | R | 0...4294967295
99 | I18 | FRQV1 | f>>>> starts | UINT32 | R | 0...4294967295
99 | I19 | FRQV1 | f>>>> trips | UINT32 | R | 0...4294967295
99 | I20 | FRQV1 | f>>>> blocks | UINT32 | R | 0...4294967295
99 | I21 | FRQV1 | f< starts | UINT32 | R | 0...4294967295
99 | I22 | FRQV1 | f< trips | UINT32 | R | 0...4294967295
99 | I23 | FRQV1 | f< blocks | UINT32 | R | 0...4294967295
99 | I24 | FRQV1 | f<< starts | UINT32 | R | 0...4294967295
99 | I25 | FRQV1 | f<< trips | UINT32 | R | 0...4294967295
99 | I26 | FRQV1 | f<< blocks | UINT32 | R | 0...4294967295
99 | I27 | FRQV1 | f<<< starts | UINT32 | R | 0...4294967295
99 | I28 | FRQV1 | f<<< trips | UINT32 | R | 0...4294967295
99 | I29 | FRQV1 | f<<< blocks | UINT32 | R | 0...4294967295
99 | I30 | FRQV1 | f<<<< starts | UINT32 | R | 0...4294967295
99 | I31 | FRQV1 | f<<<< trips | UINT32 | R | 0...4294967295
99 | I32 | FRQV1 | f<<<< blocks | UINT32 | R | 0...4294967295
99 | S9 | FRQV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
99 | S10 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S11 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S12 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S13 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S14 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S15 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S16 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S17 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S18 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S19 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S20 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S21 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S22 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S23 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S24 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S25 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S26 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S27 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S28 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S29 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S30 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S31 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S32 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S33 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S34 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S35 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S36 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S37 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S38 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S39 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S40 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S41 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S42 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S43 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S44 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S45 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S46 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S47 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S48 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S49 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S50 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S51 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S52 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S53 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S54 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S55 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S56 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S57 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S58 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S59 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S60 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S61 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S62 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S63 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S64 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S65 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S66 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S67 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S68 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S69 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S70 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S71 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S72 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S73 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S74 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S75 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S76 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S77 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S78 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S79 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S80 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S81 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S82 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S83 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S84 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S85 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S86 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S87 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S88 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S89 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S90 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S91 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S92 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S93 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S94 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S95 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S96 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S97 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S98 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S99 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S100 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S101 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S102 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S103 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S104 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S105 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S106 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S107 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S108 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S109 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S110 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S111 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S112 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S113 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S114 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S115 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S116 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S117 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S118 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S119 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S120 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S121 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S122 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S123 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S124 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S125 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S126 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S127 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S128 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S129 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S130 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S131 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S132 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S133 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S134 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S135 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S136 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S137 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S138 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S139 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S140 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S141 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S142 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S143 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S144 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S145 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S146 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S147 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S148 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S149 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S150 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S151 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S152 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S153 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S154 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S155 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S156 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S157 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S158 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S159 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S160 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S161 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S162 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S163 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S164 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S165 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S166 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S167 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S168 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S169 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S170 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S171 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S172 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S173 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S174 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S175 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S176 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S177 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S178 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S179 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S180 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S181 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S182 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S183 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S184 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S185 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S186 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S187 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S188 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S189 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S190 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S191 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S192 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S193 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S194 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S195 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S196 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S197 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S198 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S199 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S200 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S201 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | O1 | FRQV1 | f> START | SIGNAL_OUT | RW | 0...4294967295
99 | O2 | FRQV1 | f> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O3 | FRQV1 | f> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O4 | FRQV1 | f>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O5 | FRQV1 | f>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O6 | FRQV1 | f>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O7 | FRQV1 | f>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O8 | FRQV1 | f>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O9 | FRQV1 | f>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O10 | FRQV1 | f>>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O11 | FRQV1 | f>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O12 | FRQV1 | f>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O13 | FRQV1 | f< START | SIGNAL_OUT | RW | 0...4294967295
99 | O14 | FRQV1 | f< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O15 | FRQV1 | f< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O16 | FRQV1 | f<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O17 | FRQV1 | f<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O18 | FRQV1 | f<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O19 | FRQV1 | f<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O20 | FRQV1 | f<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O21 | FRQV1 | f<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O22 | FRQV1 | f<<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O23 | FRQV1 | f<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O24 | FRQV1 | f<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | I33 | FRQV1 | Newest Register | UINT32 | R | 0...12
99 | I34 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I35 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I36 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I37 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I38 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I39 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I40 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I41 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I42 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I43 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I44 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I45 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | S202 | FRQV1 | EventMaskLo | UINT32 | RW | 0...4294967295
103 | S1 | DFT1 | df/dt >/< [81] mode | UINT32 | RW | 0=Disabled;1=Activated
103 | S2 | DFT1 | Max allowed df/dt rate | FLOAT | RW | 0.1...50
103 | I1 | DFT1 | Measured df/dt | FLOAT | R | 0...20
103 | S3 | DFT1 | df/dt >/< (1) Enable | UINT32 | RW | 0=No;1=Yes
103 | V1 | DFT1 | df/dt >/< (1) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I2 | DFT1 | df/dt >/< (1) fmeas / fset | FLOAT | R | 0...20
103 | S4 | DFT1 | df/dt >/< (2) Enable | UINT32 | RW | 0=No;1=Yes
103 | V2 | DFT1 | df/dt >/< (2) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I3 | DFT1 | df/dt >/< (2) fmeas / fset | FLOAT | R | 0...20
103 | S5 | DFT1 | df/dt >/< (3) Enable | UINT32 | RW | 0=No;1=Yes
103 | V3 | DFT1 | df/dt >/< (3) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I4 | DFT1 | df/dt >/< (3) fmeas / fset | FLOAT | R | 0...20
103 | S6 | DFT1 | df/dt >/< (4) Enable | UINT32 | RW | 0=No;1=Yes
103 | V4 | DFT1 | df/dt >/< (4) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I5 | DFT1 | df/dt >/< (4) fmeas / fset | FLOAT | R | 0...20
103 | S7 | DFT1 | df/dt >/< (5) Enable | UINT32 | RW | 0=No;1=Yes
103 | V5 | DFT1 | df/dt >/< (5) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I6 | DFT1 | df/dt >/< (5) fmeas / fset | FLOAT | R | 0...20
103 | S8 | DFT1 | df/dt >/< (6) Enable | UINT32 | RW | 0=No;1=Yes
103 | V6 | DFT1 | df/dt >/< (6) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I7 | DFT1 | df/dt >/< (6) fmeas / fset | FLOAT | R | 0...20
103 | S9 | DFT1 | df/dt >/< (7) Enable | UINT32 | RW | 0=No;1=Yes
103 | V7 | DFT1 | df/dt >/< (7) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I8 | DFT1 | df/dt >/< (7) fmeas / fset | FLOAT | R | 0...20
103 | S10 | DFT1 | df/dt >/< (8) Enable | UINT32 | RW | 0=No;1=Yes
103 | V8 | DFT1 | df/dt >/< (8) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I9 | DFT1 | df/dt >/< (8) fmeas / fset | FLOAT | R | 0...20
103 | I10 | DFT1 | df/dt >/< (1) starts | UINT32 | R | 0...4294967295
103 | I11 | DFT1 | df/dt >/< (1) trips | UINT32 | R | 0...4294967295
103 | I12 | DFT1 | df/dt >/< (1) blocks | UINT32 | R | 0...4294967295
103 | I13 | DFT1 | df/dt >/< (2) starts | UINT32 | R | 0...4294967295
103 | I14 | DFT1 | df/dt >/< (2) trips | UINT32 | R | 0...4294967295
103 | I15 | DFT1 | df/dt >/< (2) blocks | UINT32 | R | 0...4294967295
103 | I16 | DFT1 | df/dt >/< (3) starts | UINT32 | R | 0...4294967295
103 | I17 | DFT1 | df/dt >/< (3) trips | UINT32 | R | 0...4294967295
103 | I18 | DFT1 | df/dt >/< (3) blocks | UINT32 | R | 0...4294967295
103 | I19 | DFT1 | df/dt >/< (4) starts | UINT32 | R | 0...4294967295
103 | I20 | DFT1 | df/dt >/< (4) trips | UINT32 | R | 0...4294967295
103 | I21 | DFT1 | df/dt >/< (4) blocks | UINT32 | R | 0...4294967295
103 | I22 | DFT1 | df/dt >/< (5) starts | UINT32 | R | 0...4294967295
103 | I23 | DFT1 | df/dt >/< (5) trips | UINT32 | R | 0...4294967295
103 | I24 | DFT1 | df/dt >/< (5) blocks | UINT32 | R | 0...4294967295
103 | I25 | DFT1 | df/dt >/< (6) starts | UINT32 | R | 0...4294967295
103 | I26 | DFT1 | df/dt >/< (6) trips | UINT32 | R | 0...4294967295
103 | I27 | DFT1 | df/dt >/< (6) blocks | UINT32 | R | 0...4294967295
103 | I28 | DFT1 | df/dt >/< (7) starts | UINT32 | R | 0...4294967295
103 | I29 | DFT1 | df/dt >/< (7) trips | UINT32 | R | 0...4294967295
103 | I30 | DFT1 | df/dt >/< (7) blocks | UINT32 | R | 0...4294967295
103 | I31 | DFT1 | df/dt >/< (8) starts | UINT32 | R | 0...4294967295
103 | I32 | DFT1 | df/dt >/< (8) trips | UINT32 | R | 0...4294967295
103 | I33 | DFT1 | df/dt >/< (8) blocks | UINT32 | R | 0...4294967295
103 | S11 | DFT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
103 | S12 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S13 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S14 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S15 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S16 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S17 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S18 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S19 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S20 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S21 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S22 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S23 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S24 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S25 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S26 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S27 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S28 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S29 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S30 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S31 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S32 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S33 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S34 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S35 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S36 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S37 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S38 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S39 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S40 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S41 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S42 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S43 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S44 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S45 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S46 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S47 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S48 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S49 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S50 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S51 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S52 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S53 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S54 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S55 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S56 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S57 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S58 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S59 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S60 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S61 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S62 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S63 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S64 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S65 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S66 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S67 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S68 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S69 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S70 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S71 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S72 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S73 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S74 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S75 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S76 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S77 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S78 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S79 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S80 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S81 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S82 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S83 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S84 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S85 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S86 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S87 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S88 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S89 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S90 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S91 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S92 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S93 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S94 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S95 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S96 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S97 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S98 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S99 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S100 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S101 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S102 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S103 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S104 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S105 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S106 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S107 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S108 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S109 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S110 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S111 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S112 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S113 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S114 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S115 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S116 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S117 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S118 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S119 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S120 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S121 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S122 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S123 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S124 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S125 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S126 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S127 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S128 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S129 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S130 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S131 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S132 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S133 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S134 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S135 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S136 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S137 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S138 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S139 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S140 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S141 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S142 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S143 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S144 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S145 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S146 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S147 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S148 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S149 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S150 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S151 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S152 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S153 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S154 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S155 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S156 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S157 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S158 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S159 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S160 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S161 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S162 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S163 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S164 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S165 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S166 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S167 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S168 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S169 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S170 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S171 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S172 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S173 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S174 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S175 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S176 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S177 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S178 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S179 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S180 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S181 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S182 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S183 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S184 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S185 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S186 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S187 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S188 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S189 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S190 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S191 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S192 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S193 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S194 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S195 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S196 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S197 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S198 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S199 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S200 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S201 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S202 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S203 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S204 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S205 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S206 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S207 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S208 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S209 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S210 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S211 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S212 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S213 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S214 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S215 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S216 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S217 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S218 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S219 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S220 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S221 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S222 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S223 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S224 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S225 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S226 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S227 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S228 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S229 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S230 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S231 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S232 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S233 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S234 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S235 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S236 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S237 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S238 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S239 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S240 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S241 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S242 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S243 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S244 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S245 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S246 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S247 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S248 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S249 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S250 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S251 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S252 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S253 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S254 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S255 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S256 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S257 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S258 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S259 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S260 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S261 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S262 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S263 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S264 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S265 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S266 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S267 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S268 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S269 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S270 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S271 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S272 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S273 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S274 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S275 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S276 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S277 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S278 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S279 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S280 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S281 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S282 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S283 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S284 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S285 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S286 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S287 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S288 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S289 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S290 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S291 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S292 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S293 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S294 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S295 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S296 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S297 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S298 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S299 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S300 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S301 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S302 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S303 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S304 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S305 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S306 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S307 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S308 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S309 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S310 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S311 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S312 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S313 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S314 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S315 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S316 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S317 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S318 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S319 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S320 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S321 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S322 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S323 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S324 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S325 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S326 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S327 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S328 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S329 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S330 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S331 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S332 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S333 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S334 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S335 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S336 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S337 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S338 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S339 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S340 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S341 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S342 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S343 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S344 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S345 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S346 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S347 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S348 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S349 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S350 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S351 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S352 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S353 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S354 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S355 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S356 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S357 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S358 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S359 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S360 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S361 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S362 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S363 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S364 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S365 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S366 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S367 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S368 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S369 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S370 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S371 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S372 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S373 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S374 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S375 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S376 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S377 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S378 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S379 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S380 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S381 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S382 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S383 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S384 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S385 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S386 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S387 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S388 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S389 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S390 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S391 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S392 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S393 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S394 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S395 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S396 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S397 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S398 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S399 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S400 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S401 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S402 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S403 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S404 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S405 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S406 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S407 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S408 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S409 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S410 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S411 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S412 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S413 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S414 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S415 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S416 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S417 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S418 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S419 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S420 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S421 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S422 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S423 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S424 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S425 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S426 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S427 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S428 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S429 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S430 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S431 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S432 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S433 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S434 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S435 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S436 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S437 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S438 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S439 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S440 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S441 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S442 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S443 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S444 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S445 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S446 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S447 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S448 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S449 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S450 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S451 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S452 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S453 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S454 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S455 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S456 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S457 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S458 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S459 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | O1 | DFT1 | df/dt >/< (1) START | SIGNAL_OUT | RW | 0...4294967295
103 | O2 | DFT1 | df/dt >/< (1) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O3 | DFT1 | df/dt >/< (1) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O4 | DFT1 | df/dt >/< (2) START | SIGNAL_OUT | RW | 0...4294967295
103 | O5 | DFT1 | df/dt >/< (2) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O6 | DFT1 | df/dt >/< (2) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O7 | DFT1 | df/dt >/< (3) START | SIGNAL_OUT | RW | 0...4294967295
103 | O8 | DFT1 | df/dt >/< (3) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O9 | DFT1 | df/dt >/< (3) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O10 | DFT1 | df/dt >/< (4) START | SIGNAL_OUT | RW | 0...4294967295
103 | O11 | DFT1 | df/dt >/< (4) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O12 | DFT1 | df/dt >/< (4) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O13 | DFT1 | df/dt >/< (5) START | SIGNAL_OUT | RW | 0...4294967295
103 | O14 | DFT1 | df/dt >/< (5) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O15 | DFT1 | df/dt >/< (5) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O16 | DFT1 | df/dt >/< (6) START | SIGNAL_OUT | RW | 0...4294967295
103 | O17 | DFT1 | df/dt >/< (6) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O18 | DFT1 | df/dt >/< (6) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O19 | DFT1 | df/dt >/< (7) START | SIGNAL_OUT | RW | 0...4294967295
103 | O20 | DFT1 | df/dt >/< (7) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O21 | DFT1 | df/dt >/< (7) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O22 | DFT1 | df/dt >/< (8) START | SIGNAL_OUT | RW | 0...4294967295
103 | O23 | DFT1 | df/dt >/< (8) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O24 | DFT1 | df/dt >/< (8) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | I34 | DFT1 | Newest Register | UINT32 | R | 0...12
103 | I35 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I36 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I37 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I38 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I39 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I40 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I41 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I42 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I43 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I44 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I45 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I46 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I47 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I48 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I49 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I50 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I51 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I52 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I53 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I54 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I55 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I56 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I57 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I58 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | S460 | DFT1 | EventMaskLo | UINT32 | RW | 0...4294967295
183 | V1 | RHC1 | Counter is now | UINT32 | R | 0=Idle;1=Counting
183 | I1 | RHC1 | Running hours | UINT32 | RW | 0...4294967295
183 | I2 | RHC1 | Start count | UINT32 | RW | 0...4294967295
183 | I3 | RHC1 | Clear Hours | UINT32 | W | 0=-;1=Clear
183 | S1 | RHC1 | EventMaskLo | UINT32 | RW | 0...4294967295
113 | V1 | GST1 | Generator is now | UINT32 | R | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
113 | I1 | GST1 | Times Overloaded | UINT32 | R | 0...4294967295
113 | I2 | GST1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
113 | I3 | GST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
113 | I4 | GST1 | Generating time | UINT32 | R | 0...4294967295
113 | I5 | GST1 | Overloading cumulative | UINT32 | R | 0...4294967295
113 | I6 | GST1 | Last overload duration | UINT32 | R | 0...4294967295
113 | I7 | GST1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
113 | I8 | GST1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
113 | S1 | GST1 | Clear total times | UINT32 | W | 0=-;1=Clear
113 | S2 | GST1 | Generator nominal MVA (S) | FLOAT | RW | 0.1...500
113 | S3 | GST1 | Generator nominal Voltage (Vt) | FLOAT | RW | 0.1...25
113 | S4 | GST1 | Prime mover max power output (Pmax) | FLOAT | RW | 0.1...500
113 | S5 | GST1 | Block trafo in protection area | UINT32 | RW | 0=No;1=Yes
113 | S6 | GST1 | Generator voltage measurement | UINT32 | RW | 0=LV side VT (no corrections);1=HV side VT(Reduce to LV);2=HV side VT(HV measurements)
113 | S7 | GST1 | Ratio for generator nominal voltage scaling (1 p.u.) | UINT32 | RW | 0=Generator nominal voltage;1=Transformer LV nominal voltage;2=Set Un ratio by hand
113 | I9 | GST1 | Transformer ratio HV -> LV Trafo. | FLOAT | R | 0.01...100
113 | I10 | GST1 | Transformer ratio HV -> LV Gen. | FLOAT | R | 0.01...100
113 | I11 | GST1 | Voltage ratio | FLOAT | RW | 0.001...100
113 | I12 | GST1 | Voltage scaling | FLOAT | R | 0.01...100
113 | S8 | GST1 | Transformer nominal MVA | FLOAT | RW | 0.001...500
113 | S9 | GST1 | HV side nominal voltage | FLOAT | RW | 0.001...500
113 | S10 | GST1 | LV side nominal voltage | FLOAT | RW | 0.001...500
113 | S11 | GST1 | Transformer Zk % | FLOAT | RW | 0.001...25
113 | S12 | GST1 | Transformer nom freq. | FLOAT | RW | 10...75
113 | S13 | GST1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
113 | I13 | GST1 | HV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I14 | GST1 | HV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I15 | GST1 | HV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I16 | GST1 | LV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I17 | GST1 | LV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I18 | GST1 | LV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I19 | GST1 | Transformer nom impedance | FLOAT | R | 0.01...250
113 | I20 | GST1 | Transformer nom Zk ohm | FLOAT | R | 0.01...250
113 | I21 | GST1 | Transformer nom SC inductance | FLOAT | R | 0.001...100
113 | I22 | GST1 | LV side max 3ph SC curr | FLOAT | R | 0.001...500
113 | I23 | GST1 | LV side 3ph SC to HV side | FLOAT | R | 0.001...500
113 | I24 | GST1 | LV side max 2ph SC curr | FLOAT | R | 0.001...500
113 | I25 | GST1 | LV side 2ph SC to HV side | FLOAT | R | 0.001...500
113 | I26 | GST1 | Trafo HV nominal current | FLOAT | R | 0.01...50000
113 | I27 | GST1 | Trafo LV nominal current | FLOAT | R | 0.01...50000
113 | O1 | GST1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
113 | O2 | GST1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O3 | GST1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O4 | GST1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
113 | O5 | GST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | O6 | GST1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | I28 | GST1 | Newest Register | UINT32 | R | 0...12
113 | I29 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I30 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I31 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I32 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I33 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I34 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I35 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I36 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I37 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I38 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I39 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I40 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I41 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I42 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I43 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I44 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I45 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I46 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I47 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I48 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I49 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I50 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I51 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I52 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I53 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I54 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I55 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I56 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I57 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I58 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I59 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I60 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I61 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I62 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I63 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I64 | GST1 | L3 Current | FLOAT | R | 0...250
113 | S14 | GST1 | EventMaskLo | UINT32 | RW | 0...4294967295
164 | S1 | PWR1 | PQS>/< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
164 | V1 | PWR1 | PQS>/< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
164 | I1 | PWR1 | Meas/Set at the moment | FLOAT | R | -1250...1250
164 | I2 | PWR1 | Meas/Nom at the moment | FLOAT | R | -1250...1250
164 | I3 | PWR1 | PQS>/< starts | UINT32 | R | 0...4294967295
164 | I4 | PWR1 | PQS>/< trips | UINT32 | R | 0...4294967295
164 | I5 | PWR1 | PQS>/< blocks | UINT32 | R | 0...4294967295
164 | S2 | PWR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
164 | S3 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S4 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S5 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S6 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S7 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S8 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S9 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S10 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S11 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S12 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S13 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S14 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S15 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S16 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S17 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S18 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | O1 | PWR1 | PQS>/< START | SIGNAL_OUT | RW | 0...4294967295
164 | O2 | PWR1 | PQS>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
164 | O3 | PWR1 | PQS>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
164 | I6 | PWR1 | Newest Register | UINT32 | R | 0...12
164 | I7 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I8 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I9 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I10 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I11 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I12 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I13 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I14 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I15 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I16 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I17 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I18 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | S19 | PWR1 | EventMaskLo | UINT32 | RW | 0...4294967295
165 | S1 | PWR2 | PQS>>/<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
165 | V1 | PWR2 | PQS>>/<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
165 | I1 | PWR2 | Meas/Set at the moment | FLOAT | R | -1250...1250
165 | I2 | PWR2 | Meas/Nom at the moment | FLOAT | R | -1250...1250
165 | I3 | PWR2 | PQS>>/<< starts | UINT32 | R | 0...4294967295
165 | I4 | PWR2 | PQS>>/<< trips | UINT32 | R | 0...4294967295
165 | I5 | PWR2 | PQS>>/<< blocks | UINT32 | R | 0...4294967295
165 | S2 | PWR2 | Clear statistics | UINT32 | W | 0=-;1=Clear
165 | S3 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S4 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S5 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S6 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S7 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S8 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S9 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S10 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S11 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S12 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S13 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S14 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S15 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S16 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S17 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S18 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | O1 | PWR2 | PQS>>/<< START | SIGNAL_OUT | RW | 0...4294967295
165 | O2 | PWR2 | PQS>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
165 | O3 | PWR2 | PQS>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
165 | I6 | PWR2 | Newest Register | UINT32 | R | 0...12
165 | I7 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I8 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I9 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I10 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I11 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I12 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I13 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I14 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I15 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I16 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I17 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I18 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | S19 | PWR2 | EventMaskLo | UINT32 | RW | 0...4294967295
166 | S1 | PWR3 | PQS>>>/<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
166 | V1 | PWR3 | PQS>>>/<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
166 | I1 | PWR3 | Meas/Set at the moment | FLOAT | R | -1250...1250
166 | I2 | PWR3 | Meas/Nom at the moment | FLOAT | R | -1250...1250
166 | I3 | PWR3 | PQS>>>/<<< starts | UINT32 | R | 0...4294967295
166 | I4 | PWR3 | PQS>>>/<<< trips | UINT32 | R | 0...4294967295
166 | I5 | PWR3 | PQS>>>/<<< blocks | UINT32 | R | 0...4294967295
166 | S2 | PWR3 | Clear statistics | UINT32 | W | 0=-;1=Clear
166 | S3 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S4 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S5 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S6 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S7 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S8 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S9 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S10 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S11 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S12 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S13 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S14 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S15 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S16 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S17 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S18 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | O1 | PWR3 | PQS>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
166 | O2 | PWR3 | PQS>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
166 | O3 | PWR3 | PQS>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
166 | I6 | PWR3 | Newest Register | UINT32 | R | 0...12
166 | I7 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I8 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I9 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I10 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I11 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I12 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I13 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I14 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I15 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I16 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I17 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I18 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | S19 | PWR3 | EventMaskLo | UINT32 | RW | 0...4294967295
167 | S1 | PWR4 | PQS>>>>/<<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
167 | V1 | PWR4 | PQS>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
167 | I1 | PWR4 | Meas/Set at the moment | FLOAT | R | -1250...1250
167 | I2 | PWR4 | Meas/Nom at the moment | FLOAT | R | -1250...1250
167 | I3 | PWR4 | PQS>>>>/<<<< starts | UINT32 | R | 0...4294967295
167 | I4 | PWR4 | PQS>>>>/<<<< trips | UINT32 | R | 0...4294967295
167 | I5 | PWR4 | PQS>>>>/<<<< blocks | UINT32 | R | 0...4294967295
167 | S2 | PWR4 | Clear statistics | UINT32 | W | 0=-;1=Clear
167 | S3 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S4 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S5 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S6 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S7 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S8 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S9 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S10 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S11 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S12 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S13 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S14 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S15 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S16 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S17 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S18 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | O1 | PWR4 | PQS>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
167 | O2 | PWR4 | PQS>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
167 | O3 | PWR4 | PQS>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
167 | I6 | PWR4 | Newest Register | UINT32 | R | 0...12
167 | I7 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I8 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I9 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I10 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I11 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I12 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I13 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I14 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I15 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I16 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I17 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I18 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | S19 | PWR4 | EventMaskLo | UINT32 | RW | 0...4294967295
100 | S1 | OPW1 | P> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
100 | V1 | OPW1 | P> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
100 | I1 | OPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
100 | I2 | OPW1 | P> starts | UINT32 | R | 0...4294967295
100 | I3 | OPW1 | P> trips | UINT32 | R | 0...4294967295
100 | I4 | OPW1 | P> blocks | UINT32 | R | 0...4294967295
100 | S2 | OPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
100 | S3 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S4 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S5 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S6 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S7 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S8 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S9 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S10 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S11 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S12 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S13 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S14 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S15 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S16 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S17 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S18 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | O1 | OPW1 | P> START | SIGNAL_OUT | RW | 0...4294967295
100 | O2 | OPW1 | P> TRIP | SIGNAL_OUT | RW | 0...4294967295
100 | O3 | OPW1 | P> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
100 | I5 | OPW1 | Newest Register | UINT32 | R | 0...12
100 | I6 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I7 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I8 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I9 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I10 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I11 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I12 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I13 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I14 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I15 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I16 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I17 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | S19 | OPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
101 | S1 | UPW1 | P< [37] mode | UINT32 | RW | 0=Disabled;1=Activated
101 | V1 | UPW1 | P< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
101 | I1 | UPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
101 | I2 | UPW1 | P< starts | UINT32 | R | 0...4294967295
101 | I3 | UPW1 | P< trips | UINT32 | R | 0...4294967295
101 | I4 | UPW1 | P< blocks | UINT32 | R | 0...4294967295
101 | S2 | UPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
101 | S3 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S4 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S5 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S6 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S7 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S8 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S9 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S10 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S11 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S12 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S13 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S14 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S15 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S16 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S17 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S18 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S19 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S20 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S21 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S22 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S23 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S24 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S25 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S26 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | O1 | UPW1 | P< START | SIGNAL_OUT | RW | 0...4294967295
101 | O2 | UPW1 | P< TRIP | SIGNAL_OUT | RW | 0...4294967295
101 | O3 | UPW1 | P< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
101 | I5 | UPW1 | Newest Register | UINT32 | R | 0...12
101 | I6 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I7 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I8 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I9 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I10 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I11 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I12 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I13 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I14 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I15 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I16 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I17 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | S27 | UPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
102 | S1 | RPW1 | Prev> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
102 | V1 | RPW1 | Prev> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
102 | I1 | RPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
102 | I2 | RPW1 | Prev> starts | UINT32 | R | 0...4294967295
102 | I3 | RPW1 | Prev> trips | UINT32 | R | 0...4294967295
102 | I4 | RPW1 | Prev> blocks | UINT32 | R | 0...4294967295
102 | S2 | RPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
102 | S3 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S4 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S5 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S6 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S7 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S8 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S9 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S10 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S11 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S12 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S13 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S14 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S15 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S16 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S17 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S18 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | O1 | RPW1 | Prev> START | SIGNAL_OUT | RW | 0...4294967295
102 | O2 | RPW1 | Prev> TRIP | SIGNAL_OUT | RW | 0...4294967295
102 | O3 | RPW1 | Prev> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
102 | I5 | RPW1 | Newest Register | UINT32 | R | 0...12
102 | I6 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I7 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I8 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I9 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I10 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I11 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I12 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I13 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I14 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I15 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I16 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I17 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | S19 | RPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
110 | S1 | SEF1 | U03rd< [64S] mode | UINT32 | RW | 0=Disabled; 1=Activated
110 | V1 | SEF1 | U03rd< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
110 | I1 | SEF1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
110 | I2 | SEF1 | Measured U0 3rd harm (%) | FLOAT | R | 0...1250
110 | I3 | SEF1 | Measured U0 3rd harm (Pri) | FLOAT | R | 0...1250
110 | I4 | SEF1 | U03rd< starts | UINT32 | R | 0...4294967295
110 | I5 | SEF1 | U03rd< trips | UINT32 | R | 0...4294967295
110 | I6 | SEF1 | U03rd< blocks | UINT32 | R | 0...4294967295
110 | S2 | SEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
110 | S3 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S4 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S5 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S6 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S7 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S8 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S9 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S10 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S11 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S12 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S13 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S14 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S15 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S16 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S17 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S18 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S19 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S20 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S21 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S22 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S23 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S24 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S25 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S26 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | O1 | SEF1 | U03rd< START | SIGNAL_OUT | RW | 0...4294967295
110 | O2 | SEF1 | U03rd< TRIP | SIGNAL_OUT | RW | 0...4294967295
110 | O3 | SEF1 | U03rd< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
110 | I7 | SEF1 | Newest Register | UINT32 | R | 0...12
110 | I8 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I9 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I10 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I11 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I12 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I13 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I14 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I15 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I16 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I17 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I18 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I19 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I20 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I21 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I22 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I23 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I24 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I25 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I26 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I27 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I28 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I29 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I30 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I31 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | S27 | SEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
109 | S1 | UEX1 | Q< [40] mode | UINT32 | RW | 0=Disabled; 1=Activated
109 | V1 | UEX1 | Q< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
109 | I1 | UEX1 | Qmeas/Qset at the moment | FLOAT | R | -1250...1250
109 | I2 | UEX1 | Q< starts | UINT32 | R | 0...4294967295
109 | I3 | UEX1 | Q< trips | UINT32 | R | 0...4294967295
109 | I4 | UEX1 | Q< blocks | UINT32 | R | 0...4294967295
109 | S2 | UEX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
109 | S3 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S4 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S5 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S6 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S7 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S8 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S9 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S10 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S11 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S12 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S13 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S14 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S15 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S16 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S17 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S18 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S19 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S20 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S21 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S22 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S23 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S24 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S25 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S26 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S27 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S28 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S29 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S30 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S31 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S32 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S33 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S34 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S35 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S36 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S37 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S38 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S39 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S40 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S41 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S42 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S43 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S44 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S45 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S46 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S47 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S48 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S49 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S50 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | O1 | UEX1 | Q< START | SIGNAL_OUT | RW | 0...4294967295
109 | O2 | UEX1 | Q< TRIP | SIGNAL_OUT | RW | 0...4294967295
109 | O3 | UEX1 | Q< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
109 | I5 | UEX1 | Newest Register | UINT32 | R | 0...12
109 | I6 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I7 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I8 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I9 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I10 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I11 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I12 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I13 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I14 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I15 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I16 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I17 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I18 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I19 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I20 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I21 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I22 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I23 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I24 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I25 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I26 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I27 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I28 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I29 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | S51 | UEX1 | EventMaskLo | UINT32 | RW | 0...4294967295
111 | S1 | UIM1 | Z< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
111 | V1 | UIM1 | Z< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
111 | I1 | UIM1 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
111 | I2 | UIM1 | Z< starts | UINT32 | R | 0...4294967295
111 | I3 | UIM1 | Z< trips | UINT32 | R | 0...4294967295
111 | I4 | UIM1 | Z< blocks | UINT32 | R | 0...4294967295
111 | S2 | UIM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
111 | S3 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S4 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S5 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S6 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S7 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S8 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S9 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S10 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S11 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S12 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S13 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S14 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S15 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S16 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S17 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S18 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | O1 | UIM1 | Z< START | SIGNAL_OUT | RW | 0...4294967295
111 | O2 | UIM1 | Z< TRIP | SIGNAL_OUT | RW | 0...4294967295
111 | O3 | UIM1 | Z< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
111 | I5 | UIM1 | Newest Register | UINT32 | R | 0...12
111 | I6 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I7 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I8 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I9 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I10 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I11 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I12 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I13 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I14 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I15 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I16 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I17 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I18 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I19 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I20 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I21 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I22 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I23 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I24 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I25 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I26 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I27 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I28 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I29 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I30 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I31 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I32 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I33 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I34 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I35 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I36 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I37 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I38 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I39 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I40 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I41 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | S19 | UIM1 | EventMaskLo | UINT32 | RW | 0...4294967295
149 | S1 | UIM2 | Z<< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
149 | V1 | UIM2 | Z<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
149 | I1 | UIM2 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
149 | I2 | UIM2 | Z<< starts | UINT32 | R | 0...4294967295
149 | I3 | UIM2 | Z<< trips | UINT32 | R | 0...4294967295
149 | I4 | UIM2 | Z<< blocks | UINT32 | R | 0...4294967295
149 | S2 | UIM2 | Clear statistics | UINT32 | W | 0=-;1=Clear
149 | S3 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S4 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S5 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S6 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S7 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S8 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S9 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S10 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S11 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S12 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S13 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S14 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S15 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S16 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S17 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S18 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | O1 | UIM2 | Z<< START | SIGNAL_OUT | RW | 0...4294967295
149 | O2 | UIM2 | Z<< TRIP | SIGNAL_OUT | RW | 0...4294967295
149 | O3 | UIM2 | Z<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
149 | I5 | UIM2 | Newest Register | UINT32 | R | 0...12
149 | I6 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I7 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I8 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I9 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I10 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I11 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I12 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I13 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I14 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I15 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I16 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I17 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I18 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I19 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I20 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I21 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I22 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I23 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I24 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I25 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I26 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I27 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I28 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I29 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I30 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I31 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I32 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I33 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I34 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I35 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I36 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I37 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I38 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I39 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I40 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I41 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | S19 | UIM2 | EventMaskLo | UINT32 | RW | 0...4294967295
112 | S1 | VOC1 | Iv> [51V] mode | UINT32 | RW | 0=Disabled; 1=Activated
112 | V1 | VOC1 | Iv> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
112 | I1 | VOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
112 | I2 | VOC1 | Iv> starts | UINT32 | R | 0...4294967295
112 | I3 | VOC1 | Iv> trips | UINT32 | R | 0...4294967295
112 | I4 | VOC1 | Iv> blocks | UINT32 | R | 0...4294967295
112 | S2 | VOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
112 | S3 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S4 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S5 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S6 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S7 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S8 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S9 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S10 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S11 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S12 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S13 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S14 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S15 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S16 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S17 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S18 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S19 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S20 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S21 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S22 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S23 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S24 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S25 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S26 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S27 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S28 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S29 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S30 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S31 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S32 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S33 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S34 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S35 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S36 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S37 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S38 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S39 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S40 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S41 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S42 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | O1 | VOC1 | Iv> START | SIGNAL_OUT | RW | 0...4294967295
112 | O2 | VOC1 | Iv> TRIP | SIGNAL_OUT | RW | 0...4294967295
112 | O3 | VOC1 | Iv> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
112 | I5 | VOC1 | Newest Register | UINT32 | R | 0...12
112 | I6 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I7 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I8 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I9 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I10 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I11 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I12 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I13 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I14 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I15 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I16 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I17 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I18 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I19 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I20 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I21 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I22 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I23 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I24 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I25 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I26 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I27 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I28 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I29 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I30 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I31 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I32 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I33 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I34 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I35 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I36 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I37 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I38 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I39 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I40 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I41 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I42 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I43 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I44 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I45 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I46 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I47 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I48 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I49 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I50 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I51 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I52 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I53 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I54 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I55 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I56 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I57 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I58 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I59 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I60 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I61 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I62 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I63 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I64 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I65 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | S43 | VOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
128 | S1 | VHZ1 | V/Hz > [24] mode | UINT32 | RW | 0=Disabled;1=Activated
128 | S2 | VHZ1 | V/Hz(1) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V1 | VHZ1 | V/Hz(1) > condition | UINT32 | R | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
128 | I1 | VHZ1 | V/Hz(1) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | S3 | VHZ1 | V/Hz(2) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V2 | VHZ1 | V/Hz(2) > condition | UINT32 | R | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
128 | I2 | VHZ1 | V/Hz(2) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | I3 | VHZ1 | U/f at the moment | FLOAT | R | -100...100
128 | I4 | VHZ1 | U/f atm to nominal U/f ratio | FLOAT | R | -100...100
128 | I5 | VHZ1 | V/Hz(1) > Starts | UINT32 | R | 0...4294967295
128 | I6 | VHZ1 | V/Hz(1) > Alarms | UINT32 | R | 0...4294967295
128 | I7 | VHZ1 | V/Hz(1) > Trips | UINT32 | R | 0...4294967295
128 | I8 | VHZ1 | V/Hz(1) > Blocks | UINT32 | R | 0...4294967295
128 | I9 | VHZ1 | V/Hz(2) > Starts | UINT32 | R | 0...4294967295
128 | I10 | VHZ1 | V/Hz(2) > Alarms | UINT32 | R | 0...4294967295
128 | I11 | VHZ1 | V/Hz(2) > Trips | UINT32 | R | 0...4294967295
128 | I12 | VHZ1 | V/Hz(2) > Blocks | UINT32 | R | 0...4294967295
128 | S4 | VHZ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
128 | S5 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S6 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S7 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S8 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S9 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S10 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S11 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S12 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S13 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S14 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S15 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S16 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S17 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S18 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S19 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S20 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S21 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S22 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S23 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S24 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S25 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S26 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S27 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S28 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S29 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S30 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S31 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S32 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S33 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S34 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S35 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S36 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S37 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S38 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S39 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S40 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S41 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S42 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S43 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S44 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S45 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S46 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S47 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S48 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S49 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S50 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S51 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S52 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | O1 | VHZ1 | V/Hz(1) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O2 | VHZ1 | V/Hz(1) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O3 | VHZ1 | V/Hz(1) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O4 | VHZ1 | V/Hz(1) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | O5 | VHZ1 | V/Hz(2) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O6 | VHZ1 | V/Hz(2) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O7 | VHZ1 | V/Hz(2) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O8 | VHZ1 | V/Hz(2) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | I13 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I14 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I15 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I16 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I17 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I18 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I19 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I20 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I21 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I22 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I23 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I24 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I25 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I26 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I27 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I28 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I29 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I30 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I31 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I32 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I33 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I34 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I35 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I36 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I37 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I38 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I39 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I40 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I41 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I42 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I43 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I44 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I45 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I46 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I47 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I48 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I49 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I50 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I51 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I52 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I53 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I54 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I55 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I56 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I57 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I58 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I59 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I60 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I61 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I62 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I63 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I64 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I65 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I66 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I67 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I68 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I69 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I70 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I71 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I72 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I73 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I74 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I75 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I76 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I77 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I78 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I79 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I80 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I81 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I82 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I83 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I84 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I85 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I86 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I87 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I88 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I89 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I90 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I91 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I92 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I93 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I94 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I95 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I96 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I97 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I98 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I99 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I100 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I101 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I102 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I103 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I104 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I105 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I106 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I107 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I108 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I109 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I110 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | S53 | VHZ1 | EventMaskLo | UINT32 | RW | 0...4294967295
129 | S1 | UPF1 | PF< [55] mode | UINT32 | RW | 0=Disabled; 1=Activated
129 | V1 | UPF1 | PF< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
129 | S2 | UPF1 | Available modes | UINT32 | RW | 0=Trip;1=Trip and Alarm
129 | I1 | UPF1 | PFmeas/PFalarm at the moment | FLOAT | R | 0...1250
129 | I2 | UPF1 | PFmeas/PFtrip at the moment | FLOAT | R | 0...1250
129 | I3 | UPF1 | PF< Alarm Starts | UINT32 | R | 0...4294967295
129 | I4 | UPF1 | PF< Alarms | UINT32 | R | 0...4294967295
129 | I5 | UPF1 | PF< Starts | UINT32 | R | 0...4294967295
129 | I6 | UPF1 | PF< Trips | UINT32 | R | 0...4294967295
129 | I7 | UPF1 | PF< Blocks | UINT32 | R | 0...4294967295
129 | S3 | UPF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
129 | S4 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S5 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S6 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S7 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S8 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S9 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S10 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S11 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S12 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S13 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S14 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S15 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S16 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S17 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S18 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S19 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S20 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S21 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S22 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S23 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S24 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S25 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S26 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S27 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S28 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S29 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S30 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S31 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S32 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S33 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S34 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S35 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | O1 | UPF1 | PF< START | SIGNAL_OUT | RW | 0...4294967295
129 | O2 | UPF1 | PF< TRIP | SIGNAL_OUT | RW | 0...4294967295
129 | O3 | UPF1 | PF< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
129 | I8 | UPF1 | Newest Register | UINT32 | R | 0...12
129 | I9 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I10 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I11 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I12 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I13 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I14 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I15 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I16 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I17 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I18 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I19 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I20 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | S36 | UPF1 | EventMaskLo | UINT32 | RW | 0...4294967295
141 | I1 | RTDIN | S1 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I2 | RTDIN | S1 Resistance | FLOAT | R | 0...4000.000
141 | I3 | RTDIN | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I4 | RTDIN | S1 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I5 | RTDIN | S2 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I6 | RTDIN | S2 Resistance | FLOAT | R | 0...4000.000
141 | I7 | RTDIN | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I8 | RTDIN | S2 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I9 | RTDIN | S3 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I10 | RTDIN | S3 Resistance | FLOAT | R | 0...4000.000
141 | I11 | RTDIN | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I12 | RTDIN | S3 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I13 | RTDIN | S4 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I14 | RTDIN | S4 Resistance | FLOAT | R | 0...4000.000
141 | I15 | RTDIN | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I16 | RTDIN | S4 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I17 | RTDIN | S5 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I18 | RTDIN | S5 Resistance | FLOAT | R | 0...4000.000
141 | I19 | RTDIN | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I20 | RTDIN | S5 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I21 | RTDIN | S6 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I22 | RTDIN | S6 Resistance | FLOAT | R | 0...4000.000
141 | I23 | RTDIN | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I24 | RTDIN | S6 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I25 | RTDIN | S7 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I26 | RTDIN | S7 Resistance | FLOAT | R | 0...4000.000
141 | I27 | RTDIN | S7 Measurement mA | FLOAT | R | 0.000...20.000
141 | I28 | RTDIN | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I29 | RTDIN | S7 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I30 | RTDIN | S8 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I31 | RTDIN | S8 Resistance | FLOAT | R | 0...4000.000
141 | I32 | RTDIN | S8 Measurement mA | FLOAT | R | 0.000...20.000
141 | I33 | RTDIN | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I34 | RTDIN | S8 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I35 | RTDIN | S9 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I36 | RTDIN | S9 Resistance | FLOAT | R | 0...4000.000
141 | I37 | RTDIN | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I38 | RTDIN | S9 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I39 | RTDIN | S10 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I40 | RTDIN | S10 Resistance | FLOAT | R | 0...4000.000
141 | I41 | RTDIN | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I42 | RTDIN | S10 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I43 | RTDIN | S11 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I44 | RTDIN | S11 Resistance | FLOAT | R | 0...4000.000
141 | I45 | RTDIN | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I46 | RTDIN | S11 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I47 | RTDIN | S12 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I48 | RTDIN | S12 Resistance | FLOAT | R | 0...4000.000
141 | I49 | RTDIN | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I50 | RTDIN | S12 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I51 | RTDIN | S13 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I52 | RTDIN | S13 Resistance | FLOAT | R | 0...4000.000
141 | I53 | RTDIN | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I54 | RTDIN | S13 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I55 | RTDIN | S14 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I56 | RTDIN | S14 Resistance | FLOAT | R | 0...4000.000
141 | I57 | RTDIN | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I58 | RTDIN | S14 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I59 | RTDIN | S15 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I60 | RTDIN | S15 Resistance | FLOAT | R | 0...4000.000
141 | I61 | RTDIN | S15 Measurement mA | FLOAT | R | 0.000...20.000
141 | I62 | RTDIN | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I63 | RTDIN | S15 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I64 | RTDIN | S16 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I65 | RTDIN | S16 Resistance | FLOAT | R | 0...4000.000
141 | I66 | RTDIN | S16 Measurement mA | FLOAT | R | 0.000...20.000
141 | I67 | RTDIN | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I68 | RTDIN | S16 Filtered measurement | FLOAT | R | -200.0...2000.0
69 | S1 | RTD1 | RTD mode | UINT32 | RW | 0=Disabled;1=Activated
69 | S2 | RTD1 | S1 enable | UINT32 | RW | 0=No;1=Yes
69 | I1 | RTD1 | S1 Measurement (Protection) | FLOAT | R | -200...2000
69 | V1 | RTD1 | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S3 | RTD1 | S1 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I2 | RTD1 | S1 Alarm1 act | UINT32 | R | 0...4294967295
69 | S4 | RTD1 | S1 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S5 | RTD1 | S1 Alarm1 | FLOAT | RW | -200...2000
69 | S6 | RTD1 | S1 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I3 | RTD1 | S1 Alarm2 act | UINT32 | R | 0...4294967295
69 | S7 | RTD1 | S1 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S8 | RTD1 | S1 Alarm2 | FLOAT | RW | -200...2000
69 | I4 | RTD1 | S2 Measurement (Protection) | FLOAT | R | -200...2000
69 | V2 | RTD1 | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S9 | RTD1 | S2 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I5 | RTD1 | S2 Alarm1 act | UINT32 | R | 0...4294967295
69 | S10 | RTD1 | S2 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S11 | RTD1 | S2 Alarm1 | FLOAT | RW | -200...2000
69 | S12 | RTD1 | S2 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I6 | RTD1 | S2 Alarm2 act | UINT32 | R | 0...4294967295
69 | S13 | RTD1 | S2 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S14 | RTD1 | S2 Alarm2 | FLOAT | RW | -200...2000
69 | I7 | RTD1 | S3 Measurement (Protection) | FLOAT | R | -200...2000
69 | V3 | RTD1 | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S15 | RTD1 | S3 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I8 | RTD1 | S3 Alarm1 act | UINT32 | R | 0...4294967295
69 | S16 | RTD1 | S3 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S17 | RTD1 | S3 Alarm1 | FLOAT | RW | -200...2000
69 | S18 | RTD1 | S3 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I9 | RTD1 | S3 Alarm2 act | UINT32 | R | 0...4294967295
69 | S19 | RTD1 | S3 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S20 | RTD1 | S3 Alarm2 | FLOAT | RW | -200...2000
69 | I10 | RTD1 | S4 Measurement (Protection) | FLOAT | R | -200...2000
69 | V4 | RTD1 | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S21 | RTD1 | S4 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I11 | RTD1 | S4 Alarm1 act | UINT32 | R | 0...4294967295
69 | S22 | RTD1 | S4 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S23 | RTD1 | S4 Alarm1 | FLOAT | RW | -200...2000
69 | S24 | RTD1 | S4 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I12 | RTD1 | S4 Alarm2 act | UINT32 | R | 0...4294967295
69 | S25 | RTD1 | S4 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S26 | RTD1 | S4 Alarm2 | FLOAT | RW | -200...2000
69 | I13 | RTD1 | S5 Measurement (Protection) | FLOAT | R | -200...2000
69 | V5 | RTD1 | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S27 | RTD1 | S5 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I14 | RTD1 | S5 Alarm1 act | UINT32 | R | 0...4294967295
69 | S28 | RTD1 | S5 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S29 | RTD1 | S5 Alarm1 | FLOAT | RW | -200...2000
69 | S30 | RTD1 | S5 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I15 | RTD1 | S5 Alarm2 act | UINT32 | R | 0...4294967295
69 | S31 | RTD1 | S5 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S32 | RTD1 | S5 Alarm2 | FLOAT | RW | -200...2000
69 | I16 | RTD1 | S6 Measurement (Protection) | FLOAT | R | -200...2000
69 | V6 | RTD1 | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S33 | RTD1 | S6 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I17 | RTD1 | S6 Alarm1 act | UINT32 | R | 0...4294967295
69 | S34 | RTD1 | S6 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S35 | RTD1 | S6 Alarm1 | FLOAT | RW | -200...2000
69 | S36 | RTD1 | S6 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I18 | RTD1 | S6 Alarm2 act | UINT32 | R | 0...4294967295
69 | S37 | RTD1 | S6 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S38 | RTD1 | S6 Alarm2 | FLOAT | RW | -200...2000
69 | I19 | RTD1 | S7 Measurement (Protection) | FLOAT | R | -200...2000
69 | V7 | RTD1 | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S39 | RTD1 | S7 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I20 | RTD1 | S7 Alarm1 act | UINT32 | R | 0...4294967295
69 | S40 | RTD1 | S7 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S41 | RTD1 | S7 Alarm1 | FLOAT | RW | -200...2000
69 | S42 | RTD1 | S7 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I21 | RTD1 | S7 Alarm2 act | UINT32 | R | 0...4294967295
69 | S43 | RTD1 | S7 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S44 | RTD1 | S7 Alarm2 | FLOAT | RW | -200...2000
69 | I22 | RTD1 | S8 Measurement (Protection) | FLOAT | R | -200...2000
69 | V8 | RTD1 | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S45 | RTD1 | S8 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I23 | RTD1 | S8 Alarm1 act | UINT32 | R | 0...4294967295
69 | S46 | RTD1 | S8 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S47 | RTD1 | S8 Alarm1 | FLOAT | RW | -200...2000
69 | S48 | RTD1 | S8 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I24 | RTD1 | S8 Alarm2 act | UINT32 | R | 0...4294967295
69 | S49 | RTD1 | S8 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S50 | RTD1 | S8 Alarm2 | FLOAT | RW | -200...2000
69 | I25 | RTD1 | S9 Measurement (Protection) | FLOAT | R | -200...2000
69 | V9 | RTD1 | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S51 | RTD1 | S9 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I26 | RTD1 | S9 Alarm1 act | UINT32 | R | 0...4294967295
69 | S52 | RTD1 | S9 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S53 | RTD1 | S9 Alarm1 | FLOAT | RW | -200...2000
69 | S54 | RTD1 | S9 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I27 | RTD1 | S9 Alarm2 act | UINT32 | R | 0...4294967295
69 | S55 | RTD1 | S9 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S56 | RTD1 | S9 Alarm2 | FLOAT | RW | -200...2000
69 | I28 | RTD1 | S10 Measurement (Protection) | FLOAT | R | -200...2000
69 | V10 | RTD1 | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S57 | RTD1 | S10 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I29 | RTD1 | S10 Alarm1 act | UINT32 | R | 0...4294967295
69 | S58 | RTD1 | S10 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S59 | RTD1 | S10 Alarm1 | FLOAT | RW | -200...2000
69 | S60 | RTD1 | S10 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I30 | RTD1 | S10 Alarm2 act | UINT32 | R | 0...4294967295
69 | S61 | RTD1 | S10 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S62 | RTD1 | S10 Alarm2 | FLOAT | RW | -200...2000
69 | I31 | RTD1 | S11 Measurement (Protection) | FLOAT | R | -200...2000
69 | V11 | RTD1 | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S63 | RTD1 | S11 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I32 | RTD1 | S11 Alarm1 act | UINT32 | R | 0...4294967295
69 | S64 | RTD1 | S11 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S65 | RTD1 | S11 Alarm1 | FLOAT | RW | -200...2000
69 | S66 | RTD1 | S11 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I33 | RTD1 | S11 Alarm2 act | UINT32 | R | 0...4294967295
69 | S67 | RTD1 | S11 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S68 | RTD1 | S11 Alarm2 | FLOAT | RW | -200...2000
69 | I34 | RTD1 | S12 Measurement (Protection) | FLOAT | R | -200...2000
69 | V12 | RTD1 | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S69 | RTD1 | S12 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I35 | RTD1 | S12 Alarm1 act | UINT32 | R | 0...4294967295
69 | S70 | RTD1 | S12 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S71 | RTD1 | S12 Alarm1 | FLOAT | RW | -200...2000
69 | S72 | RTD1 | S12 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I36 | RTD1 | S12 Alarm2 act | UINT32 | R | 0...4294967295
69 | S73 | RTD1 | S12 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S74 | RTD1 | S12 Alarm2 | FLOAT | RW | -200...2000
69 | I37 | RTD1 | S13 Measurement (Protection) | FLOAT | R | -200...2000
69 | V13 | RTD1 | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S75 | RTD1 | S13 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I38 | RTD1 | S13 Alarm1 act | UINT32 | R | 0...4294967295
69 | S76 | RTD1 | S13 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S77 | RTD1 | S13 Alarm1 | FLOAT | RW | -200...2000
69 | S78 | RTD1 | S13 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I39 | RTD1 | S13 Alarm2 act | UINT32 | R | 0...4294967295
69 | S79 | RTD1 | S13 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S80 | RTD1 | S13 Alarm2 | FLOAT | RW | -200...2000
69 | I40 | RTD1 | S14 Measurement (Protection) | FLOAT | R | -200...2000
69 | V14 | RTD1 | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S81 | RTD1 | S14 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I41 | RTD1 | S14 Alarm1 act | UINT32 | R | 0...4294967295
69 | S82 | RTD1 | S14 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S83 | RTD1 | S14 Alarm1 | FLOAT | RW | -200...2000
69 | S84 | RTD1 | S14 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I42 | RTD1 | S14 Alarm2 act | UINT32 | R | 0...4294967295
69 | S85 | RTD1 | S14 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S86 | RTD1 | S14 Alarm2 | FLOAT | RW | -200...2000
69 | I43 | RTD1 | S15 Measurement (Protection) | FLOAT | R | -200...2000
69 | V15 | RTD1 | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S87 | RTD1 | S15 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I44 | RTD1 | S15 Alarm1 act | UINT32 | R | 0...4294967295
69 | S88 | RTD1 | S15 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S89 | RTD1 | S15 Alarm1 | FLOAT | RW | -200...2000
69 | S90 | RTD1 | S15 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I45 | RTD1 | S15 Alarm2 act | UINT32 | R | 0...4294967295
69 | S91 | RTD1 | S15 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S92 | RTD1 | S15 Alarm2 | FLOAT | RW | -200...2000
69 | I46 | RTD1 | S16 Measurement (Protection) | FLOAT | R | -200...2000
69 | V16 | RTD1 | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S93 | RTD1 | S16 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I47 | RTD1 | S16 Alarm1 act | UINT32 | R | 0...4294967295
69 | S94 | RTD1 | S16 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S95 | RTD1 | S16 Alarm1 | FLOAT | RW | -200...2000
69 | S96 | RTD1 | S16 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I48 | RTD1 | S16 Alarm2 act | UINT32 | R | 0...4294967295
69 | S97 | RTD1 | S16 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S98 | RTD1 | S16 Alarm2 | FLOAT | RW | -200...2000
69 | O1 | RTD1 | S1 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O2 | RTD1 | S1 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O3 | RTD1 | S1 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O4 | RTD1 | S2 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O5 | RTD1 | S2 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O6 | RTD1 | S2 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O7 | RTD1 | S3 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O8 | RTD1 | S3 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O9 | RTD1 | S3 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O10 | RTD1 | S4 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O11 | RTD1 | S4 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O12 | RTD1 | S4 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O13 | RTD1 | S5 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O14 | RTD1 | S5 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O15 | RTD1 | S5 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O16 | RTD1 | S6 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O17 | RTD1 | S6 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O18 | RTD1 | S6 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O19 | RTD1 | S7 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O20 | RTD1 | S7 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O21 | RTD1 | S7 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O22 | RTD1 | S8 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O23 | RTD1 | S8 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O24 | RTD1 | S8 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O25 | RTD1 | S9 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O26 | RTD1 | S9 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O27 | RTD1 | S9 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O28 | RTD1 | S10 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O29 | RTD1 | S10 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O30 | RTD1 | S10 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O31 | RTD1 | S11 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O32 | RTD1 | S11 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O33 | RTD1 | S11 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O34 | RTD1 | S12 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O35 | RTD1 | S12 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O36 | RTD1 | S12 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O37 | RTD1 | S13 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O38 | RTD1 | S13 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O39 | RTD1 | S13 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O40 | RTD1 | S14 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O41 | RTD1 | S14 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O42 | RTD1 | S14 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O43 | RTD1 | S15 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O44 | RTD1 | S15 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O45 | RTD1 | S15 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O46 | RTD1 | S16 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O47 | RTD1 | S16 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O48 | RTD1 | S16 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | S99 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
69 | S100 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
70 | S1 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
70 | S2 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
74 | S1 | ARC1 | I/I0 Arc> [50ARC/50NARC] mode | UINT32 | RW | 0=Disabled;1=Activated
74 | S2 | ARC1 | I/I0 Arc> Self supervision test pulse | UINT32 | RW | 0=Disabled;1=On
74 | V1 | ARC1 | I/I0 Arc> condition | UINT32 | R | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
74 | V2 | ARC1 | Sensor status | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I1 | ARC1 | I/I0 Arc> Zone1 Trips | UINT32 | R | 0...4294967295
74 | I2 | ARC1 | I/I0 Arc> Zone1 Blocks | UINT32 | R | 0...4294967295
74 | I3 | ARC1 | I/I0 Arc> Zone2 Trips | UINT32 | R | 0...4294967295
74 | I4 | ARC1 | I/I0 Arc> Zone2 Blocks | UINT32 | R | 0...4294967295
74 | I5 | ARC1 | I/I0 Arc> Zone3 Trips | UINT32 | R | 0...4294967295
74 | I6 | ARC1 | I/I0 Arc> Zone3 Blocks | UINT32 | R | 0...4294967295
74 | I7 | ARC1 | I/I0 Arc> Zone4 Trips | UINT32 | R | 0...4294967295
74 | I8 | ARC1 | I/I0 Arc> Zone4 Blocks | UINT32 | R | 0...4294967295
74 | S3 | ARC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
74 | I9 | ARC1 | Channel 1 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I10 | ARC1 | Channel 1 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I11 | ARC1 | Channel 2 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I12 | ARC1 | Channel 2 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I13 | ARC1 | Channel 3 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I14 | ARC1 | Channel 3 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I15 | ARC1 | Channel 4 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I16 | ARC1 | Channel 4 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | S4 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S5 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S6 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S7 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S8 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S9 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S10 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S11 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S12 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S13 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S14 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S15 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S16 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S17 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S18 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S19 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S20 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S21 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S22 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S23 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S24 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S25 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S26 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S27 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S28 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S29 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S30 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S31 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S32 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S33 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S34 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S35 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S36 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S37 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S38 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S39 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S40 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S41 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S42 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S43 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S44 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S45 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S46 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S47 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S48 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S49 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S50 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S51 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S52 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S53 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S54 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S55 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S56 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S57 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S58 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S59 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S60 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S61 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S62 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S63 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S64 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S65 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S66 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S67 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S68 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S69 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S70 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S71 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S72 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S73 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S74 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S75 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S76 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S77 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S78 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S79 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S80 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S81 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S82 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S83 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S84 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S85 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S86 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S87 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S88 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S89 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S90 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S91 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S92 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S93 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S94 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S95 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S96 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S97 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S98 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S99 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S100 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S101 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S102 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S103 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S104 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S105 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S106 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S107 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S108 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S109 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S110 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S111 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S112 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S113 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S114 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S115 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S116 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S117 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S118 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S119 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S120 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S121 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S122 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S123 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S124 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S125 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S126 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S127 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S128 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S129 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S130 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S131 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S132 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S133 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S134 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S135 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S136 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S137 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S138 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S139 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S140 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S141 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S142 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S143 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S144 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S145 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S146 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S147 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S148 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S149 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S150 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S151 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S152 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S153 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S154 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S155 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S156 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S157 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S158 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S159 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S160 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S161 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S162 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S163 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S164 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S165 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S166 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S167 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S168 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S169 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S170 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S171 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S172 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S173 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S174 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S175 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S176 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S177 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S178 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S179 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S180 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S181 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S182 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S183 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S184 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S185 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S186 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S187 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S188 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S189 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S190 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S191 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S192 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S193 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S194 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S195 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S196 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S197 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S198 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S199 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S200 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S201 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S202 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S203 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S204 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S205 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S206 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S207 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S208 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S209 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S210 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S211 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S212 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S213 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S214 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S215 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S216 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S217 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S218 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S219 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S220 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S221 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S222 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S223 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S224 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S225 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S226 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S227 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S228 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S229 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S230 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S231 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S232 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S233 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S234 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S235 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S236 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S237 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S238 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S239 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S240 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S241 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S242 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S243 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S244 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S245 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S246 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S247 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S248 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S249 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S250 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S251 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S252 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S253 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S254 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S255 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S256 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S257 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S258 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S259 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S260 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S261 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S262 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S263 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S264 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S265 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S266 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S267 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S268 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S269 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S270 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S271 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S272 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S273 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S274 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S275 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S276 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S277 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S278 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S279 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S280 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S281 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S282 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S283 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S284 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S285 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S286 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S287 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S288 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S289 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S290 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S291 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S292 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S293 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S294 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S295 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S296 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S297 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S298 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S299 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S300 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S301 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S302 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S303 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S304 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S305 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S306 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S307 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S308 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S309 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S310 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S311 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S312 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S313 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S314 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S315 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S316 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S317 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S318 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S319 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S320 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S321 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S322 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S323 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S324 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S325 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S326 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S327 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S328 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S329 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S330 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S331 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S332 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S333 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S334 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S335 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S336 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S337 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S338 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S339 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S340 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S341 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S342 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S343 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S344 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S345 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S346 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S347 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S348 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S349 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S350 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S351 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S352 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S353 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S354 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S355 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S356 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S357 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S358 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S359 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S360 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S361 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S362 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S363 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S364 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S365 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S366 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S367 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S368 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S369 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S370 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S371 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S372 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S373 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S374 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S375 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S376 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S377 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S378 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S379 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S380 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S381 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S382 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S383 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S384 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S385 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S386 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S387 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S388 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S389 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S390 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S391 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S392 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S393 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S394 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S395 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S396 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S397 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S398 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S399 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S400 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S401 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S402 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S403 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S404 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S405 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S406 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S407 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S408 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S409 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S410 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S411 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | O1 | ARC1 | I/I0 Arc> Ph.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O2 | ARC1 | I/I0 Arc> Res.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O3 | ARC1 | I/I0 Arc> Zone1.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O4 | ARC1 | I/I0 Arc> Zone2.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O5 | ARC1 | I/I0 Arc> Zone3.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O6 | ARC1 | I/I0 Arc> Zone4.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O7 | ARC1 | I/I0 Arc> Ph.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O8 | ARC1 | I/I0 Arc> Res.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O9 | ARC1 | I/I0 Arc> Ph.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O10 | ARC1 | I/I0 Arc> Res.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O11 | ARC1 | I/I0 Arc> Zone1 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O12 | ARC1 | I/I0 Arc> Zone1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O13 | ARC1 | I/I0 Arc> Zone2 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O14 | ARC1 | I/I0 Arc> Zone2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O15 | ARC1 | I/I0 Arc> Zone3 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O16 | ARC1 | I/I0 Arc> Zone3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O17 | ARC1 | I/I0 Arc> Zone4 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O18 | ARC1 | I/I0 Arc> Zone4 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O19 | ARC1 | I/I0 Arc> S1 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O20 | ARC1 | I/I0 Arc> S2 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O21 | ARC1 | I/I0 Arc> S3 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O22 | ARC1 | I/I0 Arc> S4 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O23 | ARC1 | I/I0 Arc> IO unit fault | SIGNAL_OUT | RW | 0...4294967295
74 | I17 | ARC1 | Newest Register | UINT32 | R | 0...12
74 | I18 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I19 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I20 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I21 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I22 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I23 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I24 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I25 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I26 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I27 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I28 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I29 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I30 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I31 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I32 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I33 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I34 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I35 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I36 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I37 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I38 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I39 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I40 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I41 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I42 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I43 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I44 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I45 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I46 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I47 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I48 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I49 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I50 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I51 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I52 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I53 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I54 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I55 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I56 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I57 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I58 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I59 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I60 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I61 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I62 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I63 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I64 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I65 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I66 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I67 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I68 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I69 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I70 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I71 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I72 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I73 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I74 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I75 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I76 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I77 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | S412 | ARC1 | EventMaskLo | UINT32 | RW | 0...4294967295
74 | S413 | ARC1 | EventMaskHi | UINT32 | RW | 0...4294967295
52 | S1 | CTS1 | CTS1 mode | UINT32 | RW | 0=Disabled;1=Activated
52 | V1 | CTS1 | CTS1 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
52 | I1 | CTS1 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
52 | I2 | CTS1 | Natural unbalance ang | FLOAT | R | -360...360
52 | I3 | CTS1 | Measured current difference Isum, I0 | FLOAT | R | 0...50
52 | I4 | CTS1 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
52 | I5 | CTS1 | CTS1 alarms | UINT32 | R | 0...4294967295
52 | I6 | CTS1 | CTS1 blocks | UINT32 | R | 0...4294967295
52 | S2 | CTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
52 | S3 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S4 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S5 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S6 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S7 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S8 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S9 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S10 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S11 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S12 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S13 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S14 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S15 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S16 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S17 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S18 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S19 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S20 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S21 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S22 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S23 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S24 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S25 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S26 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S27 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S28 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S29 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S30 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S31 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S32 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S33 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S34 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S35 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S36 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S37 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S38 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S39 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S40 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S41 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S42 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S43 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S44 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S45 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S46 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S47 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S48 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S49 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S50 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | O1 | CTS1 | CTS1 ALARM | SIGNAL_OUT | RW | 0...4294967295
52 | O2 | CTS1 | CTS1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
52 | I7 | CTS1 | Newest Register | UINT32 | R | 0...12
52 | I8 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I9 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I10 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I11 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I12 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I13 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I14 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I15 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I16 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I17 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I18 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I19 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I20 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I21 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I22 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I23 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I24 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I25 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I26 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I27 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I28 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I29 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I30 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I31 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I32 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I33 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I34 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I35 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I36 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I37 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I38 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I39 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I40 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I41 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I42 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I43 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I44 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I45 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I46 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I47 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I48 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I49 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I50 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I51 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I52 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I53 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I54 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I55 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I56 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I57 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I58 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I59 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I60 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I61 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I62 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I63 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I64 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I65 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I66 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I67 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I68 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I69 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I70 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I71 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I72 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I73 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I74 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I75 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I76 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I77 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I78 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I79 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | S51 | CTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
52 | S52 | CTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
54 | S1 | CTS2 | CTS2 mode | UINT32 | RW | 0=Disabled;1=Activated
54 | V1 | CTS2 | CTS2 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
54 | I1 | CTS2 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
54 | I2 | CTS2 | Natural unbalance ang | FLOAT | R | -360...360
54 | I3 | CTS2 | Measured current difference Isum, I0 | FLOAT | R | 0...50
54 | I4 | CTS2 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
54 | I5 | CTS2 | CTS2 alarms | UINT32 | R | 0...4294967295
54 | I6 | CTS2 | CTS2 blocks | UINT32 | R | 0...4294967295
54 | S2 | CTS2 | Clear statistics | UINT32 | W | 0=-;1=Clear
54 | S3 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S4 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S5 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S6 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S7 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S8 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S9 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S10 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S11 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S12 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S13 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S14 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S15 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S16 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S17 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S18 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S19 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S20 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S21 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S22 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S23 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S24 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S25 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S26 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S27 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S28 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S29 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S30 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S31 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S32 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S33 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S34 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S35 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S36 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S37 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S38 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S39 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S40 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S41 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S42 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S43 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S44 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S45 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S46 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S47 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S48 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S49 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S50 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | O1 | CTS2 | CTS2 ALARM | SIGNAL_OUT | RW | 0...4294967295
54 | O2 | CTS2 | CTS2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
54 | I7 | CTS2 | Newest Register | UINT32 | R | 0...12
54 | I8 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I9 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I10 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I11 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I12 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I13 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I14 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I15 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I16 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I17 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I18 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I19 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I20 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I21 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I22 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I23 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I24 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I25 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I26 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I27 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I28 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I29 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I30 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I31 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I32 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I33 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I34 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I35 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I36 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I37 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I38 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I39 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I40 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I41 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I42 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I43 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I44 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I45 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I46 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I47 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I48 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I49 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I50 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I51 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I52 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I53 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I54 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I55 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I56 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I57 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I58 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I59 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I60 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I61 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I62 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I63 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I64 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I65 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I66 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I67 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I68 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I69 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I70 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I71 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I72 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I73 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I74 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I75 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I76 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I77 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I78 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I79 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | S51 | CTS2 | EventMaskLo | UINT32 | RW | 0...4294967295
54 | S52 | CTS2 | EventMaskHi | UINT32 | RW | 0...4294967295
53 | S1 | VTS1 | VTS [60] mode | UINT32 | RW | 0=Disabled;1=Activated
53 | V1 | VTS1 | VTS condition | UINT32 | R | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
53 | V2 | VTS1 | Bus voltages | UINT32 | R | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
53 | I1 | VTS1 | VTS Starts | UINT32 | R | 0...4294967295
53 | I2 | VTS1 | Line fuse fails | UINT32 | R | 0...4294967295
53 | I3 | VTS1 | Bus fuse fails | UINT32 | R | 0...4294967295
53 | I4 | VTS1 | VTS Blocks | UINT32 | R | 0...4294967295
53 | S2 | VTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
53 | S3 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S4 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S5 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S6 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S7 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S8 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S9 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S10 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S11 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S12 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S13 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S14 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S15 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S16 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S17 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S18 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S19 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S20 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S21 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S22 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S23 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S24 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S25 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S26 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S27 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S28 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S29 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S30 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S31 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S32 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S33 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S34 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S35 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S36 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S37 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S38 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S39 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S40 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S41 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S42 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S43 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S44 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S45 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S46 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S47 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S48 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S49 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S50 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | O1 | VTS1 | VTS Start | SIGNAL_OUT | RW | 0...4294967295
53 | O2 | VTS1 | VTS Fail Alarm Bus | SIGNAL_OUT | RW | 0...4294967295
53 | O3 | VTS1 | VTS Fail Alarm Line | SIGNAL_OUT | RW | 0...4294967295
53 | O4 | VTS1 | VTS Blocked(time delay) | SIGNAL_OUT | RW | 0...4294967295
53 | I5 | VTS1 | Newest Register | UINT32 | R | 0...12
53 | I6 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I7 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I8 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I9 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I10 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I11 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I12 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I13 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I14 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I15 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I16 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I17 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I18 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I19 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I20 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I21 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I22 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I23 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I24 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I25 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I26 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I27 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I28 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I29 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I30 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I31 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I32 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I33 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I34 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I35 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I36 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I37 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I38 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I39 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I40 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I41 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I42 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I43 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I44 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I45 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I46 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I47 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I48 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I49 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I50 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I51 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I52 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I53 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I54 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I55 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I56 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I57 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I58 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I59 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I60 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I61 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I62 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I63 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I64 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I65 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | S51 | VTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
53 | S52 | VTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
43 | S1 | FLX1 | Fault locator mode | UINT32 | RW | 0=Disabled;1=Activated
43 | V1 | FLX1 | Fault locator condition | UINT32 | R | 0=Idle;1=Triggered;2=Calc ready
43 | I1 | FLX1 | Times Flocator triggered | UINT32 | R | 0...4294967295
43 | I2 | FLX1 | Last fault reactance | FLOAT | R | -1800...1800
43 | I3 | FLX1 | Last fault distance | FLOAT | R | -1800...1800
43 | V2 | FLX1 | Last fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I4 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I5 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I6 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | I7 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I8 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I9 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | V3 | FLX1 | Last fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | S2 | FLX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
43 | S3 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S4 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S5 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S6 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S7 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S8 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S9 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S10 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S11 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S12 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S13 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S14 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S15 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S16 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S17 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S18 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | I10 | FLX1 | Newest Register | UINT32 | R | 0...12
43 | I11 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I12 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I13 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I14 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I15 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I16 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I17 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I18 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I19 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I20 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I21 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I22 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I23 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I24 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I25 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I26 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I27 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I28 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I29 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I30 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I31 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I32 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I33 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I34 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I35 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I36 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I37 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I38 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I39 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I40 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I41 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I42 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I43 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I44 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I45 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I46 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I47 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I48 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I49 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I50 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I51 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I52 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I53 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I54 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I55 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I56 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I57 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I58 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I59 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I60 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I61 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I62 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I63 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I64 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I65 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I66 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I67 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I68 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I69 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I70 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I71 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I72 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I73 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I74 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I75 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I76 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I77 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I78 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I79 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I80 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I81 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I82 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I83 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I84 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I85 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I86 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I87 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I88 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I89 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I90 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I91 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I92 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I93 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I94 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I95 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I96 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I97 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I98 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I99 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I100 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I101 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I102 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I103 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I104 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I105 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I106 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I107 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I108 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I109 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I110 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I111 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I112 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I113 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I114 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I115 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I116 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I117 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I118 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I119 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I120 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I121 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I122 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I123 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I124 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I125 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I126 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I127 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I128 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I129 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I130 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | S19 | FLX1 | EventMaskLo | UINT32 | RW | 0...4294967295
55 | S1 | THD1 | THD mode | UINT32 | RW | 0=Disabled;1=Activated
55 | V1 | THD1 | THD condition | UINT32 | R | 0=Normal;1=Start;2=Alarm;3=Blocked
55 | S2 | THD1 | Measurement magnitude | UINT32 | RW | 0=Amplitude;1=Power
55 | I1 | THD1 | THD starts | UINT32 | R | 0...4294967295
55 | I2 | THD1 | THD alarms | UINT32 | R | 0...4294967295
55 | I3 | THD1 | THD blocks | UINT32 | R | 0...4294967295
55 | S3 | THD1 | Clear statistics | UINT32 | W | 0=-;1=Clear
55 | S4 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S5 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S6 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S7 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S8 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S9 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S10 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S11 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S12 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S13 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S14 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S15 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S16 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S17 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S18 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S19 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S20 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S21 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S22 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S23 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S24 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S25 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S26 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S27 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S28 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S29 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S30 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S31 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S32 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S33 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S34 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S35 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S36 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S37 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S38 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S39 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S40 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S41 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S42 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S43 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S44 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S45 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S46 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S47 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S48 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S49 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S50 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S51 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S52 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S53 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S54 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S55 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S56 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S57 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S58 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S59 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S60 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S61 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S62 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S63 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S64 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S65 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S66 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S67 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S68 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S69 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S70 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S71 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S72 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S73 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S74 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S75 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | O1 | THD1 | THDPH> START | SIGNAL_OUT | RW | 0...4294967295
55 | O2 | THD1 | THDPH> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O3 | THD1 | THDI01> START | SIGNAL_OUT | RW | 0...4294967295
55 | O4 | THD1 | THDI01> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O5 | THD1 | THDI02> START | SIGNAL_OUT | RW | 0...4294967295
55 | O6 | THD1 | THDI02> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O7 | THD1 | THD> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
55 | I4 | THD1 | Newest Register | UINT32 | R | 0...12
55 | I5 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I6 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I7 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I8 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I9 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I10 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I11 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I12 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I13 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I14 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I15 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I16 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I17 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I18 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I19 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I20 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I21 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I22 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I23 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I24 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I25 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I26 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I27 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I28 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I29 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I30 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I31 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I32 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I33 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I34 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I35 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I36 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I37 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I38 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I39 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I40 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | S76 | THD1 | EventMaskLo | UINT32 | RW | 0...4294967295
58 | S1 | CBW1 | CBW mode | UINT32 | RW | 0=Disabled;1=Activated
58 | V1 | CBW1 | CBW condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On
58 | I1 | CBW1 | Breaker operations | UINT32 | R | 0...4294967295
58 | I2 | CBW1 | Alarm 1 counter | UINT32 | R | 0...4294967295
58 | I3 | CBW1 | Alarm 2 counter | UINT32 | R | 0...4294967295
58 | I4 | CBW1 | L1 Operations Left | FLOAT | R | 0...4294967295
58 | I5 | CBW1 | L2 Operations Left | FLOAT | R | 0...4294967295
58 | I6 | CBW1 | L3 Operations Left | FLOAT | R | 0...4294967295
58 | S2 | CBW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
58 | S3 | CBW1 | Alarm 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S4 | CBW1 | Alarm 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S5 | CBW1 | Alarm 1 Set | UINT32 | RW | 0...200000
58 | S6 | CBW1 | Alarm 2 Set | UINT32 | RW | 0...200000
58 | S7 | CBW1 | Operations 1 | FLOAT | RW | 0...200000
58 | S8 | CBW1 | Operations 2 | FLOAT | RW | 0...200000
58 | S9 | CBW1 | Current 1 | FLOAT | RW | 0...100
58 | S10 | CBW1 | Current 2 | FLOAT | RW | 0...100
58 | O1 | CBW1 | CBW Alarm 1 act | SIGNAL_OUT | RW | 0...4294967295
58 | I7 | CBW1 | Newest Register | UINT32 | R | 0...12
58 | I8 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I9 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I10 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I11 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I12 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I13 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I14 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I15 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I16 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I17 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I18 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I19 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I20 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I21 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I22 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I23 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I24 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I25 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I26 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I27 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I28 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I29 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I30 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I31 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I32 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I33 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I34 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I35 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I36 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I37 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I38 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I39 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I40 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I41 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I42 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I43 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | S11 | CBW1 | EventMaskLo | UINT32 | RW | 0...4294967295
97 | S1 | NJK1 | U0> RECL [79] mode | UINT32 | RW | 0=Disabled;1=Activated
97 | V1 | NJK1 | U0> RECL condition | UINT32 | R | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
97 | I1 | NJK1 | Requests | UINT32 | R | 0...4294967295
97 | I2 | NJK1 | Blocks | UINT32 | R | 0...4294967295
97 | I3 | NJK1 | Starts | UINT32 | R | 0...4294967295
97 | I4 | NJK1 | Breaker closes | UINT32 | R | 0...4294967295
97 | S2 | NJK1 | Clear statistics | UINT32 | W | 0=-;1=Clear
97 | S3 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S4 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S5 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S6 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S7 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S8 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S9 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S10 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | O1 | NJK1 | U0> RECL Blocked | SIGNAL_OUT | RW | 0...4294967295
97 | O2 | NJK1 | U0> RECL Active | SIGNAL_OUT | RW | 0...4294967295
97 | O3 | NJK1 | U0> RECL CLOSE | SIGNAL_OUT | RW | 0...4294967295
97 | O4 | NJK1 | U0> RECL BLKU0 | SIGNAL_OUT | RW | 0...4294967295
97 | I5 | NJK1 | Newest Register | UINT32 | R | 0...12
97 | I6 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I7 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I8 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I9 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I10 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I11 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I12 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I13 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I14 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I15 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I16 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I17 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I18 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I19 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I20 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I21 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I22 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I23 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I24 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I25 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I26 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I27 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I28 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I29 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | S11 | NJK1 | EventMaskLo | UINT32 | RW | 0...4294967295
61 | S1 | SOF1 | SOTF mode | UINT32 | RW | 0=Disabled;1=Activated
61 | V1 | SOF1 | SOTF condition | UINT32 | R | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
61 | I1 | SOF1 | Inits | UINT32 | R | 0...4294967295
61 | I2 | SOF1 | Starts | UINT32 | R | 0...4294967295
61 | I3 | SOF1 | Trips | UINT32 | R | 0...4294967295
61 | I4 | SOF1 | Blocks | UINT32 | R | 0...4294967295
61 | S2 | SOF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
61 | S3 | SOF1 | SG in use | UINT32 | RW | 0...255
61 | S4 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S5 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S6 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S7 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S8 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S9 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S10 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S11 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | O1 | SOF1 | SOTF Blocked | SIGNAL_OUT | RW | 0...4294967295
61 | O2 | SOF1 | SOTF Active | SIGNAL_OUT | RW | 0...4294967295
61 | O3 | SOF1 | SOTF Trip | SIGNAL_OUT | RW | 0...4294967295
61 | I5 | SOF1 | Newest Register | UINT32 | R | 0...12
61 | I6 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I7 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I8 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I9 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I10 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I11 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I12 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I13 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I14 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I15 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I16 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I17 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I18 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I19 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I20 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I21 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I22 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I23 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I24 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I25 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I26 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I27 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I28 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I29 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | S12 | SOF1 | EventMaskLo | UINT32 | RW | 0...4294967295
142 | S1 | DOS1 | Energy dose counter mode | UINT32 | RW | 0=Disabled;1=Activated
142 | S2 | DOS1 | Clear pulsecounters | UINT32 | W | 0=-;1=Clear
142 | S3 | DOS1 | DC 1 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S4 | DOS1 | DC 1 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I1 | DOS1 | DC 1 Input signal | FLOAT | R | -1000000...1000000
142 | S5 | DOS1 | DC 1 Pulse magnitude | FLOAT | RW | 0...1800
142 | S6 | DOS1 | DC 1 Pulse Lenght | FLOAT | RW | 0...1800
142 | I2 | DOS1 | DC 1 Pulses sent | UINT32 | R | 0...4294967295
142 | S7 | DOS1 | DC 2 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S8 | DOS1 | DC 2 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I3 | DOS1 | DC 2 Input signal | FLOAT | R | -1000000...1000000
142 | S9 | DOS1 | DC 2 Pulse magnitude | FLOAT | RW | 0...1800
142 | S10 | DOS1 | DC 2 Pulse Lenght | FLOAT | RW | 0...1800
142 | I4 | DOS1 | DC 2 Pulses sent | UINT32 | R | 0...4294967295
142 | S11 | DOS1 | DC 3 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S12 | DOS1 | DC 3 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I5 | DOS1 | DC 3 Input signal | FLOAT | R | -1000000...1000000
142 | S13 | DOS1 | DC 3 Pulse magnitude | FLOAT | RW | 0...1800
142 | S14 | DOS1 | DC 3 Pulse Lenght | FLOAT | RW | 0...1800
142 | I6 | DOS1 | DC 3 Pulses sent | UINT32 | R | 0...4294967295
142 | S15 | DOS1 | DC 4 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S16 | DOS1 | DC 4 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I7 | DOS1 | DC 4 Input signal | FLOAT | R | -1000000...1000000
142 | S17 | DOS1 | DC 4 Pulse magnitude | FLOAT | RW | 0...1800
142 | S18 | DOS1 | DC 4 Pulse Lenght | FLOAT | RW | 0...1800
142 | I8 | DOS1 | DC 4 Pulses sent | UINT32 | R | 0...4294967295
142 | O1 | DOS1 | DC 1 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O2 | DOS1 | DC 2 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O3 | DOS1 | DC 3 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O4 | DOS1 | DC 4 Pulse out | SIGNAL_OUT | RW | 0...4294967295
144 | V1 | PCS1 | PCS1 Switch Status | SIGNAL_OUT | RW | 0...4294967295
145 | V1 | PCS2 | PCS2 Switch Status | SIGNAL_OUT | RW | 0...4294967295
146 | V1 | PCS3 | PCS3 Switch Status | SIGNAL_OUT | RW | 0...4294967295
147 | V1 | PCS4 | PCS4 Switch Status | SIGNAL_OUT | RW | 0...4294967295
148 | V1 | PCS5 | PCS5 Switch Status | SIGNAL_OUT | RW | 0...4294967295
45 | S1 | SYN1 | Synchrocheck (SYN1,2,3) [25] mode | UINT32 | RW | 0=Disabled;1=Activated
45 | V1 | SYN1 | SYN1 Condition | UINT32 | R | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok
45 | V2 | SYN1 | SYN2 Condition | UINT32 | R | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok
45 | V3 | SYN1 | SYN3 Condition | UINT32 | R | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok
45 | I1 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I2 | SYN1 | SYN1 Mag diff | FLOAT | R | -120...120
45 | I3 | SYN1 | SYN1 Ang diff | FLOAT | R | -360...360
45 | I4 | SYN1 | SYN1 freq diff | FLOAT | R | -75...75
45 | I5 | SYN1 | SYN1 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S2 | SYN1 | Estimated BRK Closing time | FLOAT | R | 0...360
45 | S3 | SYN1 | Networks rotating time | FLOAT | R | 0...360
45 | S4 | SYN1 | Networks placement atm | FLOAT | R | -360...360
45 | I6 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I7 | SYN1 | SYN2 Mag diff | FLOAT | R | -120...120
45 | I8 | SYN1 | SYN2 Ang diff | FLOAT | R | -360...360
45 | I9 | SYN1 | SYN2 freq diff | FLOAT | R | -75...75
45 | I10 | SYN1 | SYN2 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S5 | SYN1 | SYN2 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S6 | SYN1 | SYN2 Networks rotating time | FLOAT | R | 0...360.000
45 | S7 | SYN1 | SYN2 Networks placement atm | FLOAT | R | -360.000...360.000
45 | I11 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I12 | SYN1 | SYN3 Mag diff | FLOAT | R | -120...120
45 | I13 | SYN1 | SYN3 Ang diff | FLOAT | R | -360...360
45 | I14 | SYN1 | SYN3 freq diff | FLOAT | R | -75...75
45 | I15 | SYN1 | SYN3 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S8 | SYN1 | SYN3 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S9 | SYN1 | SYN3 Networks rotating time | FLOAT | R | 0...360.000
45 | S10 | SYN1 | SYN3 Networks placement atm | FLOAT | R | -360.000...360.000
45 | S11 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S12 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S13 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S14 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S15 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S16 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S17 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S18 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S19 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S20 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S21 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S22 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S23 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S24 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S25 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S26 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S27 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S28 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S29 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S30 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S31 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S32 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S33 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S34 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S35 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S36 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S37 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S38 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S39 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S40 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S41 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S42 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S43 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S44 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S45 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S46 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S47 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S48 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S49 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S50 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S51 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S52 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S53 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S54 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S55 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S56 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S57 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S58 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S59 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S60 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S61 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S62 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S63 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S64 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S65 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S66 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S67 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S68 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S69 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S70 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S71 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S72 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S73 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S74 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S75 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S76 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S77 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S78 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S79 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S80 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S81 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S82 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S83 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S84 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S85 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S86 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S87 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S88 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S89 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S90 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S91 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S92 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S93 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S94 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S95 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S96 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S97 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S98 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S99 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S100 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S101 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S102 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S103 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S104 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S105 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S106 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S107 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S108 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S109 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S110 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S111 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S112 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S113 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S114 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S115 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S116 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S117 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S118 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S119 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S120 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S121 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S122 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S123 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S124 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S125 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S126 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S127 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S128 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S129 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S130 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S131 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S132 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S133 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S134 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S135 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S136 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S137 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S138 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S139 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S140 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S141 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S142 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S143 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S144 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S145 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S146 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S147 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S148 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S149 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S150 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S151 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S152 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S153 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S154 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S155 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S156 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S157 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S158 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S159 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S160 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S161 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S162 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S163 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S164 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S165 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S166 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S167 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S168 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S169 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S170 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S171 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S172 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S173 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S174 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S175 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S176 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S177 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S178 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S179 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S180 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S181 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S182 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S183 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S184 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S185 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S186 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S187 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S188 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S189 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S190 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S191 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S192 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S193 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S194 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S195 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S196 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S197 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S198 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S199 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S200 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S201 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S202 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S203 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S204 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S205 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S206 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S207 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S208 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S209 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S210 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S211 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S212 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S213 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S214 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S215 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S216 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S217 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S218 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S219 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S220 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S221 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S222 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S223 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S224 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S225 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S226 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S227 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S228 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S229 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S230 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S231 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S232 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S233 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S234 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S235 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S236 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S237 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S238 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S239 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S240 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S241 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S242 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S243 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S244 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S245 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S246 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S247 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S248 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S249 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S250 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S251 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S252 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S253 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S254 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S255 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S256 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S257 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S258 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S259 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S260 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S261 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S262 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S263 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S264 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S265 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S266 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S267 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S268 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S269 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S270 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S271 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S272 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S273 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S274 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | O1 | SYN1 | SYN1 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O2 | SYN1 | SYN1 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O3 | SYN1 | SYN1 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O4 | SYN1 | SYN1 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O5 | SYN1 | SYN1 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O6 | SYN1 | SYN1 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O7 | SYN1 | SYN1 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O8 | SYN1 | SYN1 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O9 | SYN1 | SYN1 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O10 | SYN1 | SYN1 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O11 | SYN1 | SYN1 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O12 | SYN1 | SYN1 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O13 | SYN1 | SYN1 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O14 | SYN1 | SYN1 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O15 | SYN1 | SYN1 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O16 | SYN1 | SYN1 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O17 | SYN1 | SYN1 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O18 | SYN1 | SYN1 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O19 | SYN1 | SYN1 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O20 | SYN1 | SYN1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O21 | SYN1 | SYN2 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O22 | SYN1 | SYN2 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O23 | SYN1 | SYN2 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O24 | SYN1 | SYN2 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O25 | SYN1 | SYN2 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O26 | SYN1 | SYN2 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O27 | SYN1 | SYN2 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O28 | SYN1 | SYN2 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O29 | SYN1 | SYN2 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O30 | SYN1 | SYN2 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O31 | SYN1 | SYN2 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O32 | SYN1 | SYN2 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O33 | SYN1 | SYN2 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O34 | SYN1 | SYN2 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O35 | SYN1 | SYN2 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O36 | SYN1 | SYN2 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O37 | SYN1 | SYN2 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O38 | SYN1 | SYN2 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O39 | SYN1 | SYN2 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O40 | SYN1 | SYN2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O41 | SYN1 | SYN3 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O42 | SYN1 | SYN3 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O43 | SYN1 | SYN3 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O44 | SYN1 | SYN3 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O45 | SYN1 | SYN3 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O46 | SYN1 | SYN3 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O47 | SYN1 | SYN3 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O48 | SYN1 | SYN3 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O49 | SYN1 | SYN3 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O50 | SYN1 | SYN3 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O51 | SYN1 | SYN3 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O52 | SYN1 | SYN3 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O53 | SYN1 | SYN3 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O54 | SYN1 | SYN3 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O55 | SYN1 | SYN3 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O56 | SYN1 | SYN3 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O57 | SYN1 | SYN3 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O58 | SYN1 | SYN3 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O59 | SYN1 | SYN3 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O60 | SYN1 | SYN3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | I16 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I17 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I18 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I19 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I20 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I21 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I22 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I23 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I24 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I25 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I26 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I27 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I28 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I29 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I30 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I31 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I32 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I33 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I34 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I35 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I36 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I37 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I38 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I39 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I40 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I41 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I42 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I43 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I44 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I45 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I46 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I47 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I48 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I49 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I50 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I51 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I52 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I53 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I54 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I55 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I56 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I57 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I58 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I59 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I60 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I61 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I62 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I63 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I64 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I65 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I66 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I67 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I68 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I69 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I70 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I71 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I72 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I73 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I74 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I75 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I76 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I77 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I78 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I79 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I80 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I81 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I82 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I83 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I84 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I85 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I86 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I87 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I88 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I89 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I90 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I91 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I92 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I93 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I94 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I95 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I96 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I97 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I98 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I99 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I100 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I101 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I102 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I103 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I104 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I105 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I106 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I107 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I108 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I109 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I110 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I111 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I112 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I113 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I114 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I115 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I116 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I117 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I118 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I119 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I120 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I121 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I122 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I123 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I124 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I125 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I126 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I127 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I128 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I129 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I130 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I131 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I132 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I133 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I134 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I135 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I136 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I137 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I138 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I139 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I140 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I141 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I142 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I143 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I144 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I145 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I146 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I147 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I148 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I149 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I150 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I151 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I152 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I153 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I154 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I155 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I156 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I157 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I158 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I159 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I160 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I161 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I162 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I163 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I164 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I165 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I166 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I167 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I168 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I169 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I170 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I171 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I172 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I173 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I174 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I175 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I176 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I177 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I178 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I179 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I180 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I181 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I182 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I183 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I184 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I185 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I186 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I187 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I188 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I189 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I190 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I191 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I192 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I193 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I194 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I195 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I196 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I197 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I198 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I199 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I200 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I201 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I202 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I203 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I204 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I205 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I206 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I207 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I208 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I209 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I210 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I211 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I212 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I213 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I214 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I215 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I216 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I217 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I218 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I219 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I220 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I221 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I222 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I223 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I224 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I225 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I226 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I227 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I228 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I229 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I230 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I231 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I232 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I233 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I234 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I235 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I236 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I237 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I238 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I239 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I240 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I241 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I242 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I243 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I244 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I245 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I246 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I247 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I248 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I249 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I250 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I251 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I252 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I253 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I254 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I255 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I256 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I257 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I258 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I259 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I260 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I261 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I262 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I263 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I264 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I265 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I266 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I267 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I268 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I269 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I270 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I271 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I272 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I273 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I274 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I275 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I276 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I277 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I278 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I279 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I280 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I281 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I282 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I283 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I284 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I285 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I286 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I287 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I288 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I289 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I290 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I291 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I292 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I293 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I294 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I295 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I296 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I297 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I298 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I299 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I300 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I301 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I302 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I303 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I304 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I305 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I306 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I307 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I308 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I309 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I310 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I311 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I312 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I313 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I314 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I315 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I316 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I317 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I318 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I319 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I320 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I321 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I322 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I323 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I324 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I325 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I326 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I327 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I328 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I329 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I330 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I331 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I332 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I333 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I334 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I335 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I336 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I337 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I338 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I339 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I340 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I341 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I342 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I343 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I344 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I345 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I346 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I347 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I348 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I349 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I350 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I351 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I352 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I353 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I354 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I355 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I356 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I357 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I358 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I359 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I360 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I361 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I362 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I363 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I364 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I365 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I366 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I367 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I368 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I369 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I370 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I371 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I372 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I373 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I374 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I375 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I376 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I377 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I378 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | S275 | SYN1 | EventMaskLo | UINT32 | RW | 0...4294967295
45 | S276 | SYN1 | EventMaskHi | UINT32 | RW | 0...4294967295
219 | S1 | SYNX1 | SYN1 Extra EventMaskLo | UINT32 | RW | 0...4294967295
219 | S2 | SYNX1 | SYN1 Extra EventMaskHi | UINT32 | RW | 0...4294967295
220 | S1 | SYNX2 | SYN2 Extra EventMaskLo | UINT32 | RW | 0...4294967295
220 | S2 | SYNX2 | SYN2 Extra EventMaskHi | UINT32 | RW | 0...4294967295
221 | S1 | SYNX3 | SYN3 Extra EventMaskLo | UINT32 | RW | 0...4294967295
221 | S2 | SYNX3 | SYN3 Extra EventMaskHi | UINT32 | RW | 0...4294967295
155 | S1 | VJP1 | <DELTA><alpha> > mode | UINT32 | RW | 0=Disabled;1=Activated
155 | V1 | VJP1 | <DELTA><alpha> > condition | UINT32 | R | 0=Normal;1=Blocked:2=Trip;3=Alarm
155 | S2 | VJP1 | Available stages | UINT32 | RW | 0=Trip;1=Trip and Alarm
155 | S3 | VJP1 | Monitored voltages | UINT32 | RW | 0=System all P-P Voltages;1=System any P-P Voltage;2=System L12 Voltage;3=System L23 Voltage;4=System L31 Voltage;5=System all P-E voltages;6=System any P-E voltage;7=System L1 Voltage;8=System L2 Voltage;9=System L3 Voltage;10=U3 Voltage;11=U4 Voltage
155 | V2 | VJP1 | Voltage meas selected | UINT32 | R | 0=Selection Ok;1=Selection not available
155 | I1 | VJP1 | <DELTA><alpha> > U1 Angle difference | FLOAT | R | -360...360
155 | I2 | VJP1 | <DELTA><alpha> U1meas/Set | FLOAT | R | -360...360
155 | I3 | VJP1 | <DELTA><alpha> U2 Angle difference | FLOAT | R | -360...360
155 | I4 | VJP1 | <DELTA><alpha> U2meas/Set | FLOAT | R | -360...360
155 | I5 | VJP1 | <DELTA><alpha> U3 Angle difference | FLOAT | R | -360...360
155 | I6 | VJP1 | <DELTA><alpha> U3meas/Set | FLOAT | R | -360...360
155 | I7 | VJP1 | <DELTA><alpha> > Alarms | UINT32 | R | 0...4294967295
155 | I8 | VJP1 | <DELTA><alpha> > Trips | UINT32 | R | 0...4294967295
155 | I9 | VJP1 | <DELTA><alpha> > Blocks | UINT32 | R | 0...4294967295
155 | S4 | VJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
155 | S5 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S6 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S7 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S8 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S9 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S10 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S11 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S12 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S13 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S14 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S15 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S16 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S17 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S18 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S19 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S20 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S21 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S22 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S23 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S24 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S25 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S26 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S27 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S28 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | O1 | VJP1 | <DELTA><alpha> > TRIP | SIGNAL_OUT | RW | 0...4294967295
155 | O2 | VJP1 | <DELTA><alpha> > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
155 | I10 | VJP1 | Newest Register | UINT32 | R | 0...12
155 | I11 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I12 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I13 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I14 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I15 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I16 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I17 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I18 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I19 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I20 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I21 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I22 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I23 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I24 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I25 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I26 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I27 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I28 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I29 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I30 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I31 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I32 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I33 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I34 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I35 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I36 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I37 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I38 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I39 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I40 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I41 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I42 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I43 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I44 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I45 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I46 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | S29 | VJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S1 | OBJ1 | Object1 mode | UINT32 | RW | 0=Disabled;1=Activated
46 | I1 | OBJ1 | Object1 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I2 | OBJ1 | Object1 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
46 | I3 | OBJ1 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | S2 | OBJ1 | Breaker traverse time | FLOAT | RW | 0.02...500
46 | S3 | OBJ1 | WD Cart traverse time | FLOAT | RW | 0.02...500
46 | S4 | OBJ1 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
46 | S5 | OBJ1 | Sync wait timeout | FLOAT | RW | 0.02...500
46 | S6 | OBJ1 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
46 | S7 | OBJ1 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
46 | S8 | OBJ1 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
46 | S9 | OBJ1 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
46 | S10 | OBJ1 | Control Termination Timeout | FLOAT | RW | 0.02...500
46 | O1 | OBJ1 | Object1 Status Open | SIGNAL_OUT | RW | 0...4294967295
46 | O2 | OBJ1 | Object1 Status Closed | SIGNAL_OUT | RW | 0...4294967295
46 | O3 | OBJ1 | Object1 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
46 | O4 | OBJ1 | Object1 Status Bad | SIGNAL_OUT | RW | 0...4294967295
46 | O5 | OBJ1 | Object1 Open Command | SIGNAL_OUT | RW | 0...4294967295
46 | O6 | OBJ1 | Object1 Close Command | SIGNAL_OUT | RW | 0...4294967295
46 | O7 | OBJ1 | Object1 Open Request | SIGNAL_OUT | RW | 0...4294967295
46 | O8 | OBJ1 | Object1 Close Request | SIGNAL_OUT | RW | 0...4294967295
46 | O9 | OBJ1 | Object1 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
46 | O10 | OBJ1 | Object1 No sync wait | SIGNAL_OUT | RW | 0...4294967295
46 | O11 | OBJ1 | Object1 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
46 | O12 | OBJ1 | Object1 No sync fail | SIGNAL_OUT | RW | 0...4294967295
46 | O13 | OBJ1 | Object1 Open timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O14 | OBJ1 | Object1 Close timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O15 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O16 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O17 | OBJ1 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
46 | S11 | OBJ1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S12 | OBJ1 | EventMaskHi | UINT32 | RW | 0...4294967295
46 | I4 | OBJ1 | Newest Register | UINT32 | R | 0...12
46 | I5 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I6 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I7 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I8 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I9 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I10 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I11 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I12 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I13 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I14 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I15 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I16 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I17 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I18 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I19 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I20 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I21 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I22 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I23 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I24 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I25 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I26 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I27 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I28 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I29 | OBJ1 | Open requests | UINT32 | R | 0...4294967295
46 | I30 | OBJ1 | Close requests | UINT32 | R | 0...4294967295
46 | I31 | OBJ1 | Open requests failed | UINT32 | R | 0...4294967295
46 | I32 | OBJ1 | Close requests failed | UINT32 | R | 0...4294967295
46 | S13 | OBJ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
47 | S1 | OBJ2 | Object2 mode | UINT32 | RW | 0=Disabled;1=Activated
47 | I1 | OBJ2 | Object2 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I2 | OBJ2 | Object2 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
47 | I3 | OBJ2 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | S2 | OBJ2 | Breaker traverse time | FLOAT | RW | 0.02...500
47 | S3 | OBJ2 | WD Cart traverse time | FLOAT | RW | 0.02...500
47 | S4 | OBJ2 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
47 | S5 | OBJ2 | Sync wait timeout | FLOAT | RW | 0.02...500
47 | S6 | OBJ2 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
47 | S7 | OBJ2 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
47 | S8 | OBJ2 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
47 | S9 | OBJ2 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
47 | S10 | OBJ2 | Control Termination Timeout | FLOAT | RW | 0.02...500
47 | O1 | OBJ2 | Object2 Status Open | SIGNAL_OUT | RW | 0...4294967295
47 | O2 | OBJ2 | Object2 Status Closed | SIGNAL_OUT | RW | 0...4294967295
47 | O3 | OBJ2 | Object2 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
47 | O4 | OBJ2 | Object2 Status Bad | SIGNAL_OUT | RW | 0...4294967295
47 | O5 | OBJ2 | Object2 Open Command | SIGNAL_OUT | RW | 0...4294967295
47 | O6 | OBJ2 | Object2 Close Command | SIGNAL_OUT | RW | 0...4294967295
47 | O7 | OBJ2 | Object2 Open Request | SIGNAL_OUT | RW | 0...4294967295
47 | O8 | OBJ2 | Object2 Close Request | SIGNAL_OUT | RW | 0...4294967295
47 | O9 | OBJ2 | Object2 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
47 | O10 | OBJ2 | Object2 No sync wait | SIGNAL_OUT | RW | 0...4294967295
47 | O11 | OBJ2 | Object2 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
47 | O12 | OBJ2 | Object2 No sync fail | SIGNAL_OUT | RW | 0...4294967295
47 | O13 | OBJ2 | Object2 Open timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O14 | OBJ2 | Object2 Close timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O15 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O16 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O17 | OBJ2 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
47 | S11 | OBJ2 | EventMaskLo | UINT32 | RW | 0...4294967295
47 | S12 | OBJ2 | EventMaskHi | UINT32 | RW | 0...4294967295
47 | I4 | OBJ2 | Newest Register | UINT32 | R | 0...12
47 | I5 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I6 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I7 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I8 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I9 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I10 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I11 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I12 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I13 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I14 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I15 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I16 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I17 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I18 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I19 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I20 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I21 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I22 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I23 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I24 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I25 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I26 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I27 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I28 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I29 | OBJ2 | Open requests | UINT32 | R | 0...4294967295
47 | I30 | OBJ2 | Close requests | UINT32 | R | 0...4294967295
47 | I31 | OBJ2 | Open requests failed | UINT32 | R | 0...4294967295
47 | I32 | OBJ2 | Close requests failed | UINT32 | R | 0...4294967295
47 | S13 | OBJ2 | Clear statistics | UINT32 | W | 0=-;1=Clear
48 | S1 | OBJ3 | Object3 mode | UINT32 | RW | 0=Disabled;1=Activated
48 | I1 | OBJ3 | Object3 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I2 | OBJ3 | Object3 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
48 | I3 | OBJ3 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | S2 | OBJ3 | Breaker traverse time | FLOAT | RW | 0.02...500
48 | S3 | OBJ3 | WD Cart traverse time | FLOAT | RW | 0.02...500
48 | S4 | OBJ3 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
48 | S5 | OBJ3 | Sync wait timeout | FLOAT | RW | 0.02...500
48 | S6 | OBJ3 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
48 | S7 | OBJ3 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
48 | S8 | OBJ3 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
48 | S9 | OBJ3 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
48 | S10 | OBJ3 | Control Termination Timeout | FLOAT | RW | 0.02...500
48 | O1 | OBJ3 | Object3 Status Open | SIGNAL_OUT | RW | 0...4294967295
48 | O2 | OBJ3 | Object3 Status Closed | SIGNAL_OUT | RW | 0...4294967295
48 | O3 | OBJ3 | Object3 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
48 | O4 | OBJ3 | Object3 Status Bad | SIGNAL_OUT | RW | 0...4294967295
48 | O5 | OBJ3 | Object3 Open Command | SIGNAL_OUT | RW | 0...4294967295
48 | O6 | OBJ3 | Object3 Close Command | SIGNAL_OUT | RW | 0...4294967295
48 | O7 | OBJ3 | Object3 Open Request | SIGNAL_OUT | RW | 0...4294967295
48 | O8 | OBJ3 | Object3 Close Request | SIGNAL_OUT | RW | 0...4294967295
48 | O9 | OBJ3 | Object3 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
48 | O10 | OBJ3 | Object3 No sync wait | SIGNAL_OUT | RW | 0...4294967295
48 | O11 | OBJ3 | Object3 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
48 | O12 | OBJ3 | Object3 No sync fail | SIGNAL_OUT | RW | 0...4294967295
48 | O13 | OBJ3 | Object3 Open timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O14 | OBJ3 | Object3 Close timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O15 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O16 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O17 | OBJ3 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
48 | S11 | OBJ3 | EventMaskLo | UINT32 | RW | 0...4294967295
48 | S12 | OBJ3 | EventMaskHi | UINT32 | RW | 0...4294967295
48 | I4 | OBJ3 | Newest Register | UINT32 | R | 0...12
48 | I5 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I6 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I7 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I8 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I9 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I10 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I11 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I12 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I13 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I14 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I15 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I16 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I17 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I18 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I19 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I20 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I21 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I22 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I23 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I24 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I25 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I26 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I27 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I28 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I29 | OBJ3 | Open requests | UINT32 | R | 0...4294967295
48 | I30 | OBJ3 | Close requests | UINT32 | R | 0...4294967295
48 | I31 | OBJ3 | Open requests failed | UINT32 | R | 0...4294967295
48 | I32 | OBJ3 | Close requests failed | UINT32 | R | 0...4294967295
48 | S13 | OBJ3 | Clear statistics | UINT32 | W | 0=-;1=Clear
49 | S1 | OBJ4 | Object4 mode | UINT32 | RW | 0=Disabled;1=Activated
49 | I1 | OBJ4 | Object4 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I2 | OBJ4 | Object4 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
49 | I3 | OBJ4 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | S2 | OBJ4 | Breaker traverse time | FLOAT | RW | 0.02...500
49 | S3 | OBJ4 | WD Cart traverse time | FLOAT | RW | 0.02...500
49 | S4 | OBJ4 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
49 | S5 | OBJ4 | Sync wait timeout | FLOAT | RW | 0.02...500
49 | S6 | OBJ4 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
49 | S7 | OBJ4 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
49 | S8 | OBJ4 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
49 | S9 | OBJ4 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
49 | S10 | OBJ4 | Control Termination Timeout | FLOAT | RW | 0.02...500
49 | O1 | OBJ4 | Object4 Status Open | SIGNAL_OUT | RW | 0...4294967295
49 | O2 | OBJ4 | Object4 Status Closed | SIGNAL_OUT | RW | 0...4294967295
49 | O3 | OBJ4 | Object4 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
49 | O4 | OBJ4 | Object4 Status Bad | SIGNAL_OUT | RW | 0...4294967295
49 | O5 | OBJ4 | Object4 Open Command | SIGNAL_OUT | RW | 0...4294967295
49 | O6 | OBJ4 | Object4 Close Command | SIGNAL_OUT | RW | 0...4294967295
49 | O7 | OBJ4 | Object4 Open Request | SIGNAL_OUT | RW | 0...4294967295
49 | O8 | OBJ4 | Object4 Close Request | SIGNAL_OUT | RW | 0...4294967295
49 | O9 | OBJ4 | Object4 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
49 | O10 | OBJ4 | Object4 No sync wait | SIGNAL_OUT | RW | 0...4294967295
49 | O11 | OBJ4 | Object4 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
49 | O12 | OBJ4 | Object4 No sync fail | SIGNAL_OUT | RW | 0...4294967295
49 | O13 | OBJ4 | Object4 Open timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O14 | OBJ4 | Object4 Close timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O15 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O16 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O17 | OBJ4 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
49 | S11 | OBJ4 | EventMaskLo | UINT32 | RW | 0...4294967295
49 | S12 | OBJ4 | EventMaskHi | UINT32 | RW | 0...4294967295
49 | I4 | OBJ4 | Newest Register | UINT32 | R | 0...12
49 | I5 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I6 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I7 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I8 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I9 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I10 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I11 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I12 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I13 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I14 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I15 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I16 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I17 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I18 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I19 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I20 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I21 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I22 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I23 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I24 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I25 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I26 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I27 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I28 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I29 | OBJ4 | Open requests | UINT32 | R | 0...4294967295
49 | I30 | OBJ4 | Close requests | UINT32 | R | 0...4294967295
49 | I31 | OBJ4 | Open requests failed | UINT32 | R | 0...4294967295
49 | I32 | OBJ4 | Close requests failed | UINT32 | R | 0...4294967295
49 | S13 | OBJ4 | Clear statistics | UINT32 | W | 0=-;1=Clear
50 | S1 | OBJ5 | Object5 mode | UINT32 | RW | 0=Disabled;1=Activated
50 | I1 | OBJ5 | Object5 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I2 | OBJ5 | Object5 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
50 | I3 | OBJ5 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | S2 | OBJ5 | Breaker traverse time | FLOAT | RW | 0.02...500
50 | S3 | OBJ5 | WD Cart traverse time | FLOAT | RW | 0.02...500
50 | S4 | OBJ5 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
50 | S5 | OBJ5 | Sync wait timeout | FLOAT | RW | 0.02...500
50 | S6 | OBJ5 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
50 | S7 | OBJ5 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
50 | S8 | OBJ5 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
50 | S9 | OBJ5 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
50 | S10 | OBJ5 | Control Termination Timeout | FLOAT | RW | 0.02...500
50 | O1 | OBJ5 | Object5 Status Open | SIGNAL_OUT | RW | 0...4294967295
50 | O2 | OBJ5 | Object5 Status Closed | SIGNAL_OUT | RW | 0...4294967295
50 | O3 | OBJ5 | Object5 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
50 | O4 | OBJ5 | Object5 Status Bad | SIGNAL_OUT | RW | 0...4294967295
50 | O5 | OBJ5 | Object5 Open Command | SIGNAL_OUT | RW | 0...4294967295
50 | O6 | OBJ5 | Object5 Close Command | SIGNAL_OUT | RW | 0...4294967295
50 | O7 | OBJ5 | Object5 Open Request | SIGNAL_OUT | RW | 0...4294967295
50 | O8 | OBJ5 | Object5 Close Request | SIGNAL_OUT | RW | 0...4294967295
50 | O9 | OBJ5 | Object5 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
50 | O10 | OBJ5 | Object5 No sync wait | SIGNAL_OUT | RW | 0...4294967295
50 | O11 | OBJ5 | Object5 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
50 | O12 | OBJ5 | Object5 No sync fail | SIGNAL_OUT | RW | 0...4294967295
50 | O13 | OBJ5 | Object5 Open timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O14 | OBJ5 | Object5 Close timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O15 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O16 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O17 | OBJ5 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
50 | S11 | OBJ5 | EventMaskLo | UINT32 | RW | 0...4294967295
50 | S12 | OBJ5 | EventMaskHi | UINT32 | RW | 0...4294967295
50 | I4 | OBJ5 | Newest Register | UINT32 | R | 0...12
50 | I5 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I6 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I7 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I8 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I9 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I10 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I11 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I12 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I13 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I14 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I15 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I16 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I17 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I18 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I19 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I20 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I21 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I22 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I23 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I24 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I25 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I26 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I27 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I28 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I29 | OBJ5 | Open requests | UINT32 | R | 0...4294967295
50 | I30 | OBJ5 | Close requests | UINT32 | R | 0...4294967295
50 | I31 | OBJ5 | Open requests failed | UINT32 | R | 0...4294967295
50 | I32 | OBJ5 | Close requests failed | UINT32 | R | 0...4294967295
50 | S13 | OBJ5 | Clear statistics | UINT32 | W | 0=-;1=Clear
150 | S1 | OBJ6 | Object6 mode | UINT32 | RW | 0=Disabled;1=Activated
150 | I1 | OBJ6 | Object6 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I2 | OBJ6 | Object6 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
150 | I3 | OBJ6 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | S2 | OBJ6 | Breaker traverse time | FLOAT | RW | 0.02...500
150 | S3 | OBJ6 | WD Cart traverse time | FLOAT | RW | 0.02...500
150 | S4 | OBJ6 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
150 | S5 | OBJ6 | Sync wait timeout | FLOAT | RW | 0.02...500
150 | S6 | OBJ6 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
150 | S7 | OBJ6 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
150 | S8 | OBJ6 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
150 | S9 | OBJ6 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
150 | S10 | OBJ6 | Control Termination Timeout | FLOAT | RW | 0.02...500
150 | O1 | OBJ6 | Object6 Status Open | SIGNAL_OUT | RW | 0...4294967295
150 | O2 | OBJ6 | Object6 Status Closed | SIGNAL_OUT | RW | 0...4294967295
150 | O3 | OBJ6 | Object6 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
150 | O4 | OBJ6 | Object6 Status Bad | SIGNAL_OUT | RW | 0...4294967295
150 | O5 | OBJ6 | Object6 Open Command | SIGNAL_OUT | RW | 0...4294967295
150 | O6 | OBJ6 | Object6 Close Command | SIGNAL_OUT | RW | 0...4294967295
150 | O7 | OBJ6 | Object6 Open Request | SIGNAL_OUT | RW | 0...4294967295
150 | O8 | OBJ6 | Object6 Close Request | SIGNAL_OUT | RW | 0...4294967295
150 | O9 | OBJ6 | Object6 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
150 | O10 | OBJ6 | Object6 No sync wait | SIGNAL_OUT | RW | 0...4294967295
150 | O11 | OBJ6 | Object6 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
150 | O12 | OBJ6 | Object6 No sync fail | SIGNAL_OUT | RW | 0...4294967295
150 | O13 | OBJ6 | Object6 Open timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O14 | OBJ6 | Object6 Close timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O15 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O16 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O17 | OBJ6 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
150 | S11 | OBJ6 | EventMaskLo | UINT32 | RW | 0...4294967295
150 | S12 | OBJ6 | EventMaskHi | UINT32 | RW | 0...4294967295
150 | I4 | OBJ6 | Newest Register | UINT32 | R | 0...12
150 | I5 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I6 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I7 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I8 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I9 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I10 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I11 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I12 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I13 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I14 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I15 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I16 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I17 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I18 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I19 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I20 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I21 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I22 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I23 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I24 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I25 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I26 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I27 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I28 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I29 | OBJ6 | Open requests | UINT32 | R | 0...4294967295
150 | I30 | OBJ6 | Close requests | UINT32 | R | 0...4294967295
150 | I31 | OBJ6 | Open requests failed | UINT32 | R | 0...4294967295
150 | I32 | OBJ6 | Close requests failed | UINT32 | R | 0...4294967295
150 | S13 | OBJ6 | Clear statistics | UINT32 | W | 0=-;1=Clear
151 | S1 | OBJ7 | Object7 mode | UINT32 | RW | 0=Disabled;1=Activated
151 | I1 | OBJ7 | Object7 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I2 | OBJ7 | Object7 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
151 | I3 | OBJ7 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | S2 | OBJ7 | Breaker traverse time | FLOAT | RW | 0.02...500
151 | S3 | OBJ7 | WD Cart traverse time | FLOAT | RW | 0.02...500
151 | S4 | OBJ7 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
151 | S5 | OBJ7 | Sync wait timeout | FLOAT | RW | 0.02...500
151 | S6 | OBJ7 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
151 | S7 | OBJ7 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
151 | S8 | OBJ7 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
151 | S9 | OBJ7 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
151 | S10 | OBJ7 | Control Termination Timeout | FLOAT | RW | 0.02...500
151 | O1 | OBJ7 | Object7 Status Open | SIGNAL_OUT | RW | 0...4294967295
151 | O2 | OBJ7 | Object7 Status Closed | SIGNAL_OUT | RW | 0...4294967295
151 | O3 | OBJ7 | Object7 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
151 | O4 | OBJ7 | Object7 Status Bad | SIGNAL_OUT | RW | 0...4294967295
151 | O5 | OBJ7 | Object7 Open Command | SIGNAL_OUT | RW | 0...4294967295
151 | O6 | OBJ7 | Object7 Close Command | SIGNAL_OUT | RW | 0...4294967295
151 | O7 | OBJ7 | Object7 Open Request | SIGNAL_OUT | RW | 0...4294967295
151 | O8 | OBJ7 | Object7 Close Request | SIGNAL_OUT | RW | 0...4294967295
151 | O9 | OBJ7 | Object7 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
151 | O10 | OBJ7 | Object7 No sync wait | SIGNAL_OUT | RW | 0...4294967295
151 | O11 | OBJ7 | Object7 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
151 | O12 | OBJ7 | Object7 No sync fail | SIGNAL_OUT | RW | 0...4294967295
151 | O13 | OBJ7 | Object7 Open timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O14 | OBJ7 | Object7 Close timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O15 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O16 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O17 | OBJ7 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
151 | S11 | OBJ7 | EventMaskLo | UINT32 | RW | 0...4294967295
151 | S12 | OBJ7 | EventMaskHi | UINT32 | RW | 0...4294967295
151 | I4 | OBJ7 | Newest Register | UINT32 | R | 0...12
151 | I5 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I6 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I7 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I8 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I9 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I10 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I11 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I12 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I13 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I14 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I15 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I16 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I17 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I18 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I19 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I20 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I21 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I22 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I23 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I24 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I25 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I26 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I27 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I28 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I29 | OBJ7 | Open requests | UINT32 | R | 0...4294967295
151 | I30 | OBJ7 | Close requests | UINT32 | R | 0...4294967295
151 | I31 | OBJ7 | Open requests failed | UINT32 | R | 0...4294967295
151 | I32 | OBJ7 | Close requests failed | UINT32 | R | 0...4294967295
151 | S13 | OBJ7 | Clear statistics | UINT32 | W | 0=-;1=Clear
152 | S1 | OBJ8 | Object8 mode | UINT32 | RW | 0=Disabled;1=Activated
152 | I1 | OBJ8 | Object8 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I2 | OBJ8 | Object8 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
152 | I3 | OBJ8 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | S2 | OBJ8 | Breaker traverse time | FLOAT | RW | 0.02...500
152 | S3 | OBJ8 | WD Cart traverse time | FLOAT | RW | 0.02...500
152 | S4 | OBJ8 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
152 | S5 | OBJ8 | Sync wait timeout | FLOAT | RW | 0.02...500
152 | S6 | OBJ8 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
152 | S7 | OBJ8 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
152 | S8 | OBJ8 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
152 | S9 | OBJ8 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
152 | S10 | OBJ8 | Control Termination Timeout | FLOAT | RW | 0.02...500
152 | O1 | OBJ8 | Object8 Status Open | SIGNAL_OUT | RW | 0...4294967295
152 | O2 | OBJ8 | Object8 Status Closed | SIGNAL_OUT | RW | 0...4294967295
152 | O3 | OBJ8 | Object8 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
152 | O4 | OBJ8 | Object8 Status Bad | SIGNAL_OUT | RW | 0...4294967295
152 | O5 | OBJ8 | Object8 Open Command | SIGNAL_OUT | RW | 0...4294967295
152 | O6 | OBJ8 | Object8 Close Command | SIGNAL_OUT | RW | 0...4294967295
152 | O7 | OBJ8 | Object8 Open Request | SIGNAL_OUT | RW | 0...4294967295
152 | O8 | OBJ8 | Object8 Close Request | SIGNAL_OUT | RW | 0...4294967295
152 | O9 | OBJ8 | Object8 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
152 | O10 | OBJ8 | Object8 No sync wait | SIGNAL_OUT | RW | 0...4294967295
152 | O11 | OBJ8 | Object8 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
152 | O12 | OBJ8 | Object8 No sync fail | SIGNAL_OUT | RW | 0...4294967295
152 | O13 | OBJ8 | Object8 Open timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O14 | OBJ8 | Object8 Close timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O15 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O16 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O17 | OBJ8 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
152 | S11 | OBJ8 | EventMaskLo | UINT32 | RW | 0...4294967295
152 | S12 | OBJ8 | EventMaskHi | UINT32 | RW | 0...4294967295
152 | I4 | OBJ8 | Newest Register | UINT32 | R | 0...12
152 | I5 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I6 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I7 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I8 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I9 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I10 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I11 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I12 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I13 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I14 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I15 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I16 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I17 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I18 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I19 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I20 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I21 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I22 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I23 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I24 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I25 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I26 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I27 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I28 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I29 | OBJ8 | Open requests | UINT32 | R | 0...4294967295
152 | I30 | OBJ8 | Close requests | UINT32 | R | 0...4294967295
152 | I31 | OBJ8 | Open requests failed | UINT32 | R | 0...4294967295
152 | I32 | OBJ8 | Close requests failed | UINT32 | R | 0...4294967295
152 | S13 | OBJ8 | Clear statistics | UINT32 | W | 0=-;1=Clear
153 | S1 | OBJ9 | Object9 mode | UINT32 | RW | 0=Disabled;1=Activated
153 | I1 | OBJ9 | Object9 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I2 | OBJ9 | Object9 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
153 | I3 | OBJ9 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | S2 | OBJ9 | Breaker traverse time | FLOAT | RW | 0.02...500
153 | S3 | OBJ9 | WD Cart traverse time | FLOAT | RW | 0.02...500
153 | S4 | OBJ9 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
153 | S5 | OBJ9 | Sync wait timeout | FLOAT | RW | 0.02...500
153 | S6 | OBJ9 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
153 | S7 | OBJ9 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
153 | S8 | OBJ9 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
153 | S9 | OBJ9 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
153 | S10 | OBJ9 | Control Termination Timeout | FLOAT | RW | 0.02...500
153 | O1 | OBJ9 | Object9 Status Open | SIGNAL_OUT | RW | 0...4294967295
153 | O2 | OBJ9 | Object9 Status Closed | SIGNAL_OUT | RW | 0...4294967295
153 | O3 | OBJ9 | Object9 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
153 | O4 | OBJ9 | Object9 Status Bad | SIGNAL_OUT | RW | 0...4294967295
153 | O5 | OBJ9 | Object9 Open Command | SIGNAL_OUT | RW | 0...4294967295
153 | O6 | OBJ9 | Object9 Close Command | SIGNAL_OUT | RW | 0...4294967295
153 | O7 | OBJ9 | Object9 Open Request | SIGNAL_OUT | RW | 0...4294967295
153 | O8 | OBJ9 | Object9 Close Request | SIGNAL_OUT | RW | 0...4294967295
153 | O9 | OBJ9 | Object9 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
153 | O10 | OBJ9 | Object9 No sync wait | SIGNAL_OUT | RW | 0...4294967295
153 | O11 | OBJ9 | Object9 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
153 | O12 | OBJ9 | Object9 No sync fail | SIGNAL_OUT | RW | 0...4294967295
153 | O13 | OBJ9 | Object9 Open timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O14 | OBJ9 | Object9 Close timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O15 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O16 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O17 | OBJ9 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
153 | S11 | OBJ9 | EventMaskLo | UINT32 | RW | 0...4294967295
153 | S12 | OBJ9 | EventMaskHi | UINT32 | RW | 0...4294967295
153 | I4 | OBJ9 | Newest Register | UINT32 | R | 0...12
153 | I5 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I6 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I7 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I8 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I9 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I10 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I11 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I12 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I13 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I14 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I15 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I16 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I17 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I18 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I19 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I20 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I21 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I22 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I23 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I24 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I25 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I26 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I27 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I28 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I29 | OBJ9 | Open requests | UINT32 | R | 0...4294967295
153 | I30 | OBJ9 | Close requests | UINT32 | R | 0...4294967295
153 | I31 | OBJ9 | Open requests failed | UINT32 | R | 0...4294967295
153 | I32 | OBJ9 | Close requests failed | UINT32 | R | 0...4294967295
153 | S13 | OBJ9 | Clear statistics | UINT32 | W | 0=-;1=Clear
154 | S1 | OBJ10 | Object10 mode | UINT32 | RW | 0=Disabled;1=Activated
154 | I1 | OBJ10 | Object10 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I2 | OBJ10 | Object10 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
154 | I3 | OBJ10 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | S2 | OBJ10 | Breaker traverse time | FLOAT | RW | 0.02...500
154 | S3 | OBJ10 | WD Cart traverse time | FLOAT | RW | 0.02...500
154 | S4 | OBJ10 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
154 | S5 | OBJ10 | Sync wait timeout | FLOAT | RW | 0.02...500
154 | S6 | OBJ10 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
154 | S7 | OBJ10 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
154 | S8 | OBJ10 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
154 | S9 | OBJ10 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
154 | S10 | OBJ10 | Control Termination Timeout | FLOAT | RW | 0.02...500
154 | O1 | OBJ10 | Object10 Status Open | SIGNAL_OUT | RW | 0...4294967295
154 | O2 | OBJ10 | Object10 Status Closed | SIGNAL_OUT | RW | 0...4294967295
154 | O3 | OBJ10 | Object10 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
154 | O4 | OBJ10 | Object10 Status Bad | SIGNAL_OUT | RW | 0...4294967295
154 | O5 | OBJ10 | Object10 Open Command | SIGNAL_OUT | RW | 0...4294967295
154 | O6 | OBJ10 | Object10 Close Command | SIGNAL_OUT | RW | 0...4294967295
154 | O7 | OBJ10 | Object10 Open Request | SIGNAL_OUT | RW | 0...4294967295
154 | O8 | OBJ10 | Object10 Close Request | SIGNAL_OUT | RW | 0...4294967295
154 | O9 | OBJ10 | Object10 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
154 | O10 | OBJ10 | Object10 No sync wait | SIGNAL_OUT | RW | 0...4294967295
154 | O11 | OBJ10 | Object10 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
154 | O12 | OBJ10 | Object10 No sync fail | SIGNAL_OUT | RW | 0...4294967295
154 | O13 | OBJ10 | Object10 Open timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O14 | OBJ10 | Object10 Close timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O15 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O16 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O17 | OBJ10 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
154 | S11 | OBJ10 | EventMaskLo | UINT32 | RW | 0...4294967295
154 | S12 | OBJ10 | EventMaskHi | UINT32 | RW | 0...4294967295
154 | I4 | OBJ10 | Newest Register | UINT32 | R | 0...12
154 | I5 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I6 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I7 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I8 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I9 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I10 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I11 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I12 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I13 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I14 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I15 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I16 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I17 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I18 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I19 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I20 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I21 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I22 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I23 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I24 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I25 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I26 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I27 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I28 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I29 | OBJ10 | Open requests | UINT32 | R | 0...4294967295
154 | I30 | OBJ10 | Close requests | UINT32 | R | 0...4294967295
154 | I31 | OBJ10 | Open requests failed | UINT32 | R | 0...4294967295
154 | I32 | OBJ10 | Close requests failed | UINT32 | R | 0...4294967295
154 | S13 | OBJ10 | Clear statistics | UINT32 | W | 0=-;1=Clear
104 | S1 | CIN1 | Indicator 1 mode | UINT32 | RW | 0=Disabled;1=Activated
104 | S2 | CIN1 | Ind.1 traverse time | FLOAT | RW | 0.02...500
104 | I1 | CIN1 | Ind.1 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
105 | S1 | CIN2 | Indicator 2 mode | UINT32 | RW | 0=Disabled;1=Activated
105 | S2 | CIN2 | Ind.2 traverse time | FLOAT | RW | 0.02...500
105 | I1 | CIN2 | Ind.2 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
106 | S1 | CIN3 | Indicator 3 mode | UINT32 | RW | 0=Disabled;1=Activated
106 | S2 | CIN3 | Ind.3 traverse time | FLOAT | RW | 0.02...500
106 | I1 | CIN3 | Ind.3 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
107 | S1 | CIN4 | Indicator 4 mode | UINT32 | RW | 0=Disabled;1=Activated
107 | S2 | CIN4 | Ind.4 traverse time | FLOAT | RW | 0.02...500
107 | I1 | CIN4 | Ind.4 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
108 | S1 | CIN5 | Indicator 5 mode | UINT32 | RW | 0=Disabled;1=Activated
108 | S2 | CIN5 | Ind.5 traverse time | FLOAT | RW | 0.02...500
108 | I1 | CIN5 | Ind.5 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
63 | S1 | AR1 | Auto-recloser [79] Mode | UINT32 | RW | 0=Disabled;1=Activated
63 | V1 | AR1 | AR Status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear
63 | V2 | AR1 | Timer active | UINT32 | R | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
63 | I1 | AR1 | AR Timer value | FLOAT | R | 0...1800
63 | I2 | AR1 | AR Started | UINT32 | R | 0...4294967295
63 | I3 | AR1 | Shot 1 Started | UINT32 | R | 0...4294967295
63 | I4 | AR1 | Shot 2 Started | UINT32 | R | 0...4294967295
63 | I5 | AR1 | Shot 3 Started | UINT32 | R | 0...4294967295
63 | I6 | AR1 | Shot 4 Started | UINT32 | R | 0...4294967295
63 | I7 | AR1 | Shot 5 Started | UINT32 | R | 0...4294967295
63 | I8 | AR1 | Shot 1 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I9 | AR1 | Shot 2 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I10 | AR1 | Shot 3 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I11 | AR1 | Shot 4 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I12 | AR1 | Shot 5 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I13 | AR1 | Shot 1 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I14 | AR1 | Shot 2 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I15 | AR1 | Shot 3 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I16 | AR1 | Shot 4 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I17 | AR1 | Shot 5 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I18 | AR1 | Shot 1 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I19 | AR1 | Shot 2 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I20 | AR1 | Shot 3 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I21 | AR1 | Shot 4 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I22 | AR1 | Shot 5 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I23 | AR1 | Shot 1 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I24 | AR1 | Shot 2 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I25 | AR1 | Shot 3 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I26 | AR1 | Shot 4 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I27 | AR1 | Shot 5 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I28 | AR1 | Shot 1 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I29 | AR1 | Shot 2 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I30 | AR1 | Shot 3 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I31 | AR1 | Shot 4 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I32 | AR1 | Shot 5 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I33 | AR1 | Shots failed | UINT32 | R | 0...4294967295
63 | I34 | AR1 | Shots cleared | UINT32 | R | 0...4294967295
63 | I35 | AR1 | Final trips | UINT32 | R | 0...4294967295
63 | S2 | AR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
63 | S3 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S4 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S5 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S6 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S7 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S8 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S9 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S10 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S11 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S12 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S13 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S14 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S15 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S16 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S17 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S18 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S19 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S20 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S21 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S22 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S23 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S24 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S25 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S26 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S27 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S28 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S29 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S30 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S31 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S32 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S33 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S34 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S35 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S36 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S37 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S38 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S39 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S40 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S41 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S42 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S43 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S44 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S45 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S46 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S47 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S48 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S49 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S50 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S51 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S52 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S53 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S54 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S55 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S56 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S57 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S58 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S59 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S60 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S61 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S62 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S63 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S64 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S65 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S66 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S67 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S68 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S69 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S70 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S71 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S72 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S73 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S74 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S75 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S76 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S77 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S78 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S79 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S80 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S81 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S82 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S83 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S84 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S85 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S86 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S87 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S88 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S89 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S90 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S91 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S92 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S93 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S94 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S95 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S96 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S97 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S98 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S99 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S100 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S101 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S102 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S103 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S104 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S105 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S106 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S107 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S108 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S109 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S110 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S111 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S112 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S113 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S114 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S115 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S116 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S117 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S118 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S119 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S120 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S121 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S122 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S123 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S124 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S125 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S126 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S127 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S128 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S129 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S130 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S131 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S132 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S133 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S134 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S135 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S136 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S137 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S138 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S139 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S140 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S141 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S142 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S143 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S144 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S145 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S146 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S147 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S148 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S149 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S150 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S151 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S152 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S153 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S154 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S155 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S156 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S157 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S158 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S159 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S160 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S161 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S162 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S163 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S164 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S165 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S166 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S167 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S168 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S169 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S170 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S171 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S172 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S173 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S174 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S175 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S176 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S177 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S178 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S179 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S180 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S181 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S182 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S183 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S184 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S185 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S186 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S187 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S188 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S189 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S190 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S191 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S192 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S193 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S194 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S195 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S196 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S197 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S198 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S199 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S200 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S201 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S202 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S203 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S204 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S205 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S206 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S207 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S208 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S209 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S210 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S211 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S212 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S213 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S214 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S215 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S216 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S217 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S218 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S219 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S220 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S221 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S222 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S223 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S224 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S225 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S226 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S227 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S228 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S229 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S230 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S231 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S232 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S233 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S234 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S235 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S236 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S237 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S238 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S239 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S240 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S241 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S242 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S243 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S244 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S245 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S246 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S247 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S248 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S249 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S250 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S251 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S252 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S253 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S254 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S255 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S256 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S257 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S258 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S259 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S260 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S261 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S262 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S263 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S264 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S265 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S266 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S267 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S268 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S269 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S270 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S271 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S272 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S273 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S274 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S275 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S276 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S277 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S278 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S279 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S280 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S281 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S282 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S283 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S284 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S285 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S286 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S287 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S288 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S289 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S290 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S291 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S292 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S293 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S294 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S295 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S296 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S297 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S298 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S299 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S300 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S301 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S302 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S303 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S304 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S305 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S306 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S307 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S308 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S309 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S310 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S311 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S312 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S313 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S314 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S315 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S316 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S317 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S318 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S319 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S320 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S321 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S322 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S323 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S324 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S325 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S326 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S327 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S328 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S329 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S330 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S331 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S332 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S333 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S334 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S335 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S336 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S337 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S338 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S339 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S340 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S341 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S342 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S343 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S344 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S345 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S346 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S347 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S348 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S349 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S350 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S351 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S352 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S353 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S354 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S355 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S356 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S357 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S358 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S359 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S360 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S361 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S362 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S363 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S364 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S365 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S366 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S367 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S368 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S369 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S370 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S371 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S372 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S373 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S374 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S375 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S376 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S377 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S378 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S379 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S380 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S381 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S382 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S383 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S384 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S385 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S386 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S387 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S388 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S389 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S390 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S391 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S392 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S393 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S394 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S395 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S396 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S397 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S398 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S399 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S400 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S401 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S402 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S403 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S404 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S405 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S406 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S407 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S408 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S409 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S410 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S411 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S412 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S413 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S414 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S415 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S416 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S417 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S418 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S419 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S420 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S421 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S422 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S423 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S424 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S425 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S426 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S427 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S428 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S429 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S430 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S431 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S432 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S433 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S434 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S435 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S436 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S437 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S438 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S439 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S440 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S441 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S442 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S443 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S444 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S445 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S446 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S447 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S448 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S449 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S450 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S451 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S452 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S453 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S454 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S455 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S456 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S457 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S458 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S459 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S460 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S461 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S462 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S463 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S464 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S465 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S466 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S467 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S468 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S469 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S470 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S471 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S472 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S473 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S474 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S475 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S476 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S477 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S478 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S479 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S480 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S481 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S482 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S483 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S484 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S485 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S486 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S487 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S488 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S489 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S490 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S491 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S492 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S493 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S494 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S495 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S496 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S497 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S498 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S499 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S500 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S501 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S502 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S503 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S504 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S505 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S506 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S507 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S508 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S509 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S510 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S511 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S512 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S513 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S514 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S515 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S516 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S517 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S518 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S519 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S520 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S521 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S522 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S523 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S524 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S525 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S526 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S527 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S528 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S529 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S530 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S531 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S532 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S533 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S534 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S535 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S536 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S537 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S538 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S539 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S540 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S541 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S542 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S543 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S544 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S545 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S546 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S547 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S548 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S549 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S550 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S551 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S552 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S553 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S554 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S555 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S556 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S557 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S558 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S559 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S560 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S561 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S562 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S563 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S564 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S565 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S566 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S567 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S568 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S569 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S570 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S571 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S572 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S573 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S574 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S575 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S576 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S577 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S578 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S579 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S580 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S581 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S582 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S583 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S584 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S585 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S586 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S587 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S588 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S589 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S590 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S591 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S592 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S593 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S594 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S595 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S596 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S597 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S598 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S599 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S600 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S601 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S602 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S603 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S604 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S605 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S606 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S607 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S608 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S609 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S610 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S611 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S612 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S613 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S614 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S615 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S616 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S617 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S618 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S619 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S620 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S621 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S622 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S623 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S624 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S625 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S626 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S627 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S628 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S629 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S630 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S631 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S632 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S633 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S634 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S635 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S636 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S637 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S638 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S639 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S640 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S641 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S642 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S643 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S644 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S645 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S646 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S647 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S648 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S649 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S650 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S651 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S652 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S653 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S654 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S655 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S656 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S657 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S658 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S659 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S660 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S661 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S662 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S663 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S664 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S665 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S666 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S667 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S668 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S669 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S670 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S671 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S672 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S673 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S674 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S675 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S676 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S677 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S678 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S679 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S680 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S681 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S682 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S683 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S684 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S685 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S686 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S687 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S688 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S689 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S690 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S691 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S692 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S693 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S694 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S695 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S696 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S697 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S698 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S699 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S700 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S701 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S702 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S703 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S704 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S705 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S706 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S707 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S708 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S709 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S710 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S711 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S712 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S713 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S714 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S715 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S716 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S717 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S718 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S719 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S720 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S721 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S722 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S723 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S724 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S725 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S726 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S727 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S728 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S729 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S730 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S731 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S732 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S733 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S734 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S735 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S736 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S737 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S738 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S739 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S740 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S741 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S742 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S743 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S744 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S745 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S746 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S747 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S748 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S749 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S750 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S751 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S752 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S753 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S754 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S755 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S756 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S757 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S758 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S759 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S760 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S761 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S762 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S763 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S764 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S765 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S766 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S767 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S768 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S769 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S770 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S771 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S772 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S773 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S774 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S775 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S776 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S777 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S778 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S779 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S780 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S781 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S782 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S783 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S784 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S785 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S786 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S787 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S788 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S789 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S790 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S791 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S792 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S793 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S794 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S795 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S796 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S797 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S798 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S799 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S800 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S801 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S802 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S803 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S804 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S805 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S806 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S807 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S808 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S809 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S810 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S811 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S812 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S813 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S814 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S815 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S816 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S817 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S818 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S819 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S820 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S821 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S822 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S823 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S824 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S825 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S826 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S827 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S828 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S829 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S830 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S831 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S832 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S833 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S834 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S835 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S836 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S837 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S838 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S839 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S840 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S841 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S842 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S843 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S844 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S845 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S846 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S847 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S848 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S849 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S850 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S851 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S852 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S853 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S854 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S855 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S856 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S857 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S858 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S859 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S860 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S861 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S862 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S863 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S864 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S865 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S866 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S867 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S868 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S869 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S870 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S871 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S872 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S873 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S874 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S875 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S876 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S877 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S878 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S879 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S880 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S881 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S882 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S883 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S884 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S885 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S886 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S887 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S888 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S889 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S890 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S891 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S892 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S893 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S894 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S895 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S896 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S897 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S898 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S899 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S900 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S901 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S902 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S903 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S904 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S905 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S906 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S907 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S908 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S909 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S910 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S911 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S912 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S913 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S914 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S915 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S916 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S917 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S918 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S919 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S920 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S921 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S922 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S923 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S924 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S925 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S926 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S927 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S928 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S929 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S930 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S931 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S932 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S933 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S934 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S935 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S936 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S937 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S938 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S939 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S940 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S941 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S942 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S943 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S944 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S945 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S946 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S947 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S948 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S949 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S950 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S951 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S952 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S953 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S954 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S955 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S956 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S957 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S958 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S959 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S960 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S961 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S962 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S963 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S964 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S965 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S966 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S967 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S968 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S969 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S970 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S971 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S972 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S973 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S974 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S975 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S976 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S977 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S978 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S979 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S980 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S981 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S982 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S983 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S984 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S985 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S986 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S987 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S988 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S989 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S990 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S991 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S992 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S993 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S994 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S995 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S996 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S997 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S998 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S999 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1000 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1001 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1002 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1003 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1004 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1005 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1006 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1007 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1008 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1009 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1010 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1011 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1012 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1013 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1014 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1015 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1016 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1017 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1018 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1019 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1020 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1021 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1022 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1023 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1024 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1025 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1026 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1027 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1028 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1029 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1030 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1031 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1032 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1033 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1034 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1035 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1036 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1037 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1038 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1039 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1040 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1041 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1042 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1043 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1044 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1045 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1046 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1047 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1048 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1049 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1050 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1051 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1052 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1053 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1054 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1055 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1056 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1057 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1058 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1059 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1060 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1061 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1062 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1063 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1064 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1065 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1066 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1067 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1068 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1069 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1070 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1071 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1072 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1073 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1074 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1075 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1076 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1077 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1078 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1079 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1080 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1081 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1082 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1083 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1084 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1085 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1086 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1087 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1088 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1089 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1090 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1091 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1092 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1093 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1094 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1095 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1096 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1097 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1098 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1099 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1100 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1101 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1102 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1103 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1104 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1105 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1106 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1107 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1108 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1109 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1110 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1111 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1112 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1113 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1114 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1115 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1116 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1117 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1118 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1119 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1120 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1121 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1122 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1123 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1124 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1125 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1126 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1127 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1128 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1129 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1130 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1131 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1132 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1133 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1134 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1135 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1136 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1137 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1138 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1139 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1140 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1141 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1142 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1143 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1144 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1145 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1146 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1147 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1148 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1149 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1150 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1151 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1152 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1153 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1154 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1155 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1156 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1157 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1158 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1159 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1160 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1161 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1162 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1163 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1164 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1165 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1166 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1167 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1168 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1169 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1170 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1171 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1172 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1173 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1174 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1175 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1176 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1177 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1178 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1179 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1180 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1181 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1182 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1183 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1184 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1185 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1186 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1187 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1188 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1189 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1190 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1191 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1192 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1193 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1194 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1195 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1196 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1197 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1198 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1199 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1200 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1201 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1202 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1203 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1204 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1205 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1206 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1207 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1208 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1209 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1210 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1211 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1212 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1213 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1214 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1215 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1216 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1217 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1218 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1219 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1220 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1221 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1222 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1223 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1224 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1225 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1226 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1227 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1228 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1229 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1230 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1231 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1232 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1233 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1234 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1235 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1236 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1237 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1238 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1239 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1240 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1241 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1242 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1243 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1244 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1245 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1246 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1247 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1248 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1249 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1250 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | O1 | AR1 | AR On | SIGNAL_OUT | RW | 0...4294967295
63 | O2 | AR1 | AR Off | SIGNAL_OUT | RW | 0...4294967295
63 | O3 | AR1 | AR In Progress | SIGNAL_OUT | RW | 0...4294967295
63 | O4 | AR1 | AR1 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O5 | AR1 | AR2 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O6 | AR1 | AR3 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O7 | AR1 | AR4 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O8 | AR1 | AR5 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O9 | AR1 | AR Running | SIGNAL_OUT | RW | 0...4294967295
63 | O10 | AR1 | AR Shot 1 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O11 | AR1 | AR Shot 2 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O12 | AR1 | AR Shot 3 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O13 | AR1 | AR Shot 4 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O14 | AR1 | AR Shot 5 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O15 | AR1 | AR Sequence finished | SIGNAL_OUT | RW | 0...4294967295
63 | O16 | AR1 | AR Final Trip | SIGNAL_OUT | RW | 0...4294967295
63 | O17 | AR1 | Dead time on | SIGNAL_OUT | RW | 0...4294967295
63 | O18 | AR1 | ARC time on | SIGNAL_OUT | RW | 0...4294967295
63 | O19 | AR1 | Reclaim time on | SIGNAL_OUT | RW | 0...4294967295
63 | O20 | AR1 | AR Ready | SIGNAL_OUT | RW | 0...4294967295
63 | O21 | AR1 | AR Lockout after successfull sequence | SIGNAL_OUT | RW | 0...4294967295
63 | O22 | AR1 | AR Operation Inhibit | SIGNAL_OUT | RW | 0...4294967295
63 | O23 | AR1 | AR Locked | SIGNAL_OUT | RW | 0...4294967295
63 | I36 | AR1 | Newest Register | UINT32 | R | 0...12
63 | I37 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I38 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I39 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I40 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I41 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I42 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I43 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I44 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I45 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I46 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I47 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I48 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I49 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I50 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I51 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I52 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I53 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I54 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I55 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I56 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I57 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I58 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I59 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I60 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I61 | AR1 | Active time | FLOAT | R | 0...1800
63 | I62 | AR1 | Active time | FLOAT | R | 0...1800
63 | I63 | AR1 | Active time | FLOAT | R | 0...1800
63 | I64 | AR1 | Active time | FLOAT | R | 0...1800
63 | I65 | AR1 | Active time | FLOAT | R | 0...1800
63 | I66 | AR1 | Active time | FLOAT | R | 0...1800
63 | I67 | AR1 | Active time | FLOAT | R | 0...1800
63 | I68 | AR1 | Active time | FLOAT | R | 0...1800
63 | I69 | AR1 | Active time | FLOAT | R | 0...1800
63 | I70 | AR1 | Active time | FLOAT | R | 0...1800
63 | I71 | AR1 | Active time | FLOAT | R | 0...1800
63 | I72 | AR1 | Active time | FLOAT | R | 0...1800
63 | S1251 | AR1 | EventMaskLo | UINT32 | RW | 0...4294967295
63 | S1252 | AR1 | EventMaskHi | UINT32 | RW | 0...4294967295
115 | S1 | VRG1 | Vreg [AVR/90] mode | UINT32 | RW | 0=Disabled;1=Activated
115 | V1 | VRG1 | Vreg settings condition | UINT32 | R | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok
115 | V2 | VRG1 | Vreg condition | UINT32 | R | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on
115 | V3 | VRG1 | Vreg timer active | UINT32 | R | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
115 | I1 | VRG1 | Time left to operation | FLOAT | R | 0...1800
115 | I2 | VRG1 | Voltage now | FLOAT | R | 0...140
115 | I3 | VRG1 | Voltage difference to set target | FLOAT | R | -140...140
115 | I4 | VRG1 | Voltage set now to | FLOAT | R | -50000...50000
115 | I5 | VRG1 | Tap location now (- 0 +) | FLOAT | R | -30...30
115 | I6 | VRG1 | Absolute tap location | FLOAT | R | 0...50
115 | V4 | VRG1 | Tap changer on high border | UINT32 | R | 0=No;1=Yes
115 | V5 | VRG1 | Tap changer on low border | UINT32 | R | 0=No;1=Yes
115 | I7 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual (loc&rem)
115 | V6 | VRG1 | Remote tap control input | UINT32 | RW | 0=Stop;1=Lower;2=Higher
115 | S2 | VRG1 | Control pulselength max | FLOAT | RW | 0...1800
115 | S3 | VRG1 | Control pulselength min | FLOAT | RW | 0...1800
115 | S4 | VRG1 | Min time between pulses | FLOAT | RW | 0...1800
115 | V7 | VRG1 | Tap position ind. Setting | UINT32 | R | 0=Not selected;1=Set Ok;2=Wrong setting;3=Meas.Quality Fault.
115 | I8 | VRG1 | AVR rised voltage | UINT32 | R | 0...4294967295
115 | I9 | VRG1 | AVR reduced voltage | UINT32 | R | 0...4294967295
115 | I10 | VRG1 | AVR control blocked | UINT32 | R | 0...4294967295
115 | I11 | VRG1 | AVR Undervoltage blocked | UINT32 | R | 0...4294967295
115 | I12 | VRG1 | AVR Overcurrent blocked | UINT32 | R | 0...4294967295
115 | S5 | VRG1 | Clear statistics | UINT32 | W | 0=-;1=Clear
115 | S6 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S7 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S8 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S9 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S10 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S11 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S12 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S13 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S14 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S15 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S16 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S17 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S18 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S19 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S20 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S21 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S22 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S23 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S24 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S25 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S26 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S27 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S28 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S29 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S30 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S31 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S32 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S33 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S34 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S35 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S36 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S37 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S38 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S39 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S40 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S41 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S42 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S43 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S44 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S45 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S46 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S47 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S48 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S49 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S50 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S51 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S52 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S53 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S54 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S55 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S56 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S57 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S58 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S59 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S60 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S61 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S62 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S63 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S64 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S65 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S66 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S67 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S68 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S69 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S70 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S71 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S72 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S73 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S74 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S75 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S76 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S77 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S78 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S79 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S80 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S81 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S82 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S83 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S84 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S85 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S86 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S87 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S88 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S89 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S90 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S91 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S92 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S93 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S94 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S95 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S96 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S97 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S98 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S99 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S100 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S101 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S102 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S103 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S104 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S105 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S106 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S107 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S108 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S109 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S110 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S111 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S112 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S113 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S114 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S115 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S116 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S117 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S118 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S119 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S120 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S121 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S122 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S123 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S124 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S125 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S126 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S127 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S128 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S129 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S130 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S131 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S132 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S133 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | I13 | VRG1 | AVR to Manual control | SIGNAL_IN | RW | 0...4294967295
115 | O1 | VRG1 | AVR Raise Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O2 | VRG1 | AVR Lower Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O3 | VRG1 | AVR In manual control | SIGNAL_OUT | RW | 0...4294967295
115 | O4 | VRG1 | AVR U>/< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O5 | VRG1 | AVR U>>/<< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O6 | VRG1 | AVR Outputs blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O7 | VRG1 | AVR Operation blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O8 | VRG1 | AVR Control wait on | SIGNAL_OUT | RW | 0...4294967295
115 | O9 | VRG1 | AVR U< block active | SIGNAL_OUT | RW | 0...4294967295
115 | O10 | VRG1 | AVR I> block active | SIGNAL_OUT | RW | 0...4294967295
115 | O11 | VRG1 | AVR Tap in highlimit | SIGNAL_OUT | RW | 0...4294967295
115 | O12 | VRG1 | AVR Tap in lowlimit | SIGNAL_OUT | RW | 0...4294967295
115 | I14 | VRG1 | Newest Register | UINT32 | R | 0...12
115 | I15 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I16 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I17 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I18 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I19 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I20 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I21 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I22 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I23 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I24 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I25 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I26 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I27 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I28 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I29 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I30 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I31 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I32 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I33 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I34 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I35 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I36 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I37 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I38 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I39 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I40 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I41 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I42 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I43 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I44 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I45 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I46 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I47 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I48 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I49 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I50 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I51 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I52 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I53 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I54 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I55 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I56 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I57 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I58 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I59 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I60 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I61 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I62 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | S134 | VRG1 | EventMaskLo | UINT32 | RW | 0...4294967295
115 | S135 | VRG1 | EventMaskHi | UINT32 | RW | 0...4294967295
135 | S1 | EMON1 | Monitor mode | UINT32 | RW | 0=Disabled;1=Activated
135 | S2 | EMON1 | I> (50) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V1 | EMON1 | I> (50) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S3 | EMON1 | I0> (50N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S4 | EMON1 | I0> (50N) I0input | UINT32 | RW | 0=I01;1=I02;2=I0Calc
135 | V2 | EMON1 | I0> (50N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S5 | EMON1 | Idir> (67) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V3 | EMON1 | Idir> (67) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S6 | EMON1 | I0dir> (67N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S7 | EMON1 | I0dir> (67N) I0input | UINT32 | RW | 0=I01;1=I02
135 | S8 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=select
135 | S9 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V4 | EMON1 | I0dir> (67N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S10 | EMON1 | I0Int> (67NT) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S11 | EMON1 | I0Int> (67NT) I0input | UINT32 | RW | 0=I01;1=I02
135 | V5 | EMON1 | I0Int> (67NT) Monitor condition | UINT32 | R | 0=Normal;1=FLT FW;2=FLT REV
135 | S12 | EMON1 | U< (27) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S13 | EMON1 | U< (27) Measured magnitude | UINT32 | RW | 0=P-P Voltages;1=P-E Voltages
135 | S14 | EMON1 | U< (27) Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
135 | V6 | EMON1 | U< (27) Monitor condition | UINT32 | R | 0=Normal;1=Undervoltage;2=No voltage
135 | S15 | EMON1 | U0> (59N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S16 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=Select
135 | S17 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V7 | EMON1 | U0> (59N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S18 | EMON1 | FL (21FL) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V8 | EMON1 | FL (21FL) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | I1 | EMON1 | I> (50) Alarms | UINT32 | R | 0...4294967295
135 | I2 | EMON1 | I0> (50N) Alarms | UINT32 | R | 0...4294967295
135 | I3 | EMON1 | Idir> (67) Alarms | UINT32 | R | 0...4294967295
135 | I4 | EMON1 | I0dir> (67N) Alarms | UINT32 | R | 0...4294967295
135 | I5 | EMON1 | I0Int> (67) Alarms FWD | UINT32 | R | 0...4294967295
135 | I6 | EMON1 | I0Int> (67) Alarms REV | UINT32 | R | 0...4294967295
135 | I7 | EMON1 | U< (27) Undervoltage Alarms | UINT32 | R | 0...4294967295
135 | I8 | EMON1 | U< (27) No voltage Alarms | UINT32 | R | 0...4294967295
135 | I9 | EMON1 | U0> (59N) Alarms | UINT32 | R | 0...4294967295
135 | I10 | EMON1 | FL (21FL) Triggered | UINT32 | R | 0...4294967295
135 | S19 | EMON1 | Clear statistics | UINT32 | W | 0=-;1=Clear
135 | S20 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S21 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S22 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S23 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S24 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S25 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S26 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S27 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S28 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S29 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S30 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S31 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S32 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S33 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S34 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S35 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S36 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S37 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S38 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S39 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S40 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S41 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S42 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S43 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S44 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S45 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S46 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S47 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S48 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S49 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S50 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S51 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S52 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S53 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S54 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S55 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S56 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S57 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S58 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S59 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S60 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S61 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S62 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S63 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S64 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S65 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S66 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S67 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S68 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S69 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S70 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S71 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S72 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S73 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S74 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S75 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S76 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S77 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S78 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S79 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S80 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S81 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S82 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S83 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S84 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S85 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S86 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S87 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S88 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S89 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S90 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S91 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S92 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S93 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S94 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S95 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S96 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S97 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S98 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S99 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S100 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S101 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S102 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S103 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S104 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S105 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S106 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S107 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S108 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S109 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S110 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S111 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S112 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S113 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S114 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S115 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S116 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S117 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S118 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S119 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S120 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S121 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S122 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S123 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S124 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S125 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S126 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S127 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S128 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S129 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S130 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S131 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S132 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S133 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S134 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S135 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S136 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S137 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S138 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S139 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S140 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S141 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S142 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S143 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S144 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S145 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S146 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S147 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S148 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S149 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S150 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S151 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S152 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S153 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S154 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S155 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S156 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S157 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S158 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S159 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S160 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S161 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S162 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S163 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S164 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S165 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S166 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S167 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S168 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S169 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S170 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S171 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S172 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S173 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S174 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S175 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S176 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S177 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S178 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S179 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S180 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S181 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S182 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S183 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S184 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S185 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S186 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S187 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S188 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S189 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S190 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S191 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S192 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S193 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S194 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S195 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S196 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S197 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S198 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S199 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S200 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S201 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S202 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S203 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S204 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S205 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S206 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S207 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S208 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S209 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S210 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S211 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S212 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S213 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S214 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S215 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S216 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S217 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S218 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S219 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S220 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S221 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S222 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S223 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S224 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S225 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S226 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S227 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | O1 | EMON1 | I> (50) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O2 | EMON1 | I0> (50N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O3 | EMON1 | Idir> (67) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O4 | EMON1 | I0dir> (67N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O5 | EMON1 | I0int> (67NT) Alarm FWD | SIGNAL_OUT | RW | 0...4294967295
135 | O6 | EMON1 | I0int> (67NT) Alarm REV | SIGNAL_OUT | RW | 0...4294967295
135 | O7 | EMON1 | U< (27) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O8 | EMON1 | U< (27) No voltage | SIGNAL_OUT | RW | 0...4294967295
135 | O9 | EMON1 | U0> (59N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O10 | EMON1 | FL (21FL) Triggered | SIGNAL_OUT | RW | 0...4294967295
135 | I11 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I12 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I13 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I14 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I15 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I16 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I17 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I18 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I19 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I20 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I21 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I22 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I23 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I24 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I25 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I26 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I27 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I28 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I29 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I30 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I31 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I32 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I33 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I34 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I35 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I36 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I37 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I38 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I39 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I40 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I41 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I42 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I43 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I44 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I45 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I46 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I47 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I48 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I49 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I50 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I51 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I52 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I53 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I54 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I55 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I56 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I57 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I58 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I59 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I60 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I61 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I62 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I63 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I64 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I65 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I66 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I67 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I68 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I69 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I70 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I71 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I72 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I73 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I74 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I75 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I76 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I77 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I78 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I79 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I80 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I81 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I82 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I83 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I84 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I85 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I86 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I87 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I88 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I89 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I90 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I91 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I92 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I93 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I94 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I95 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I96 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I97 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I98 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I99 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I100 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I101 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I102 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I103 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I104 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I105 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I106 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I107 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I108 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I109 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I110 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I111 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I112 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I113 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I114 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I115 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I116 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I117 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I118 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I119 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I120 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I121 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I122 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I123 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I124 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I125 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I126 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I127 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I128 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I129 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I130 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I131 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I132 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I133 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I134 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I135 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I136 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I137 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I138 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I139 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I140 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I141 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I142 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I143 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I144 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I145 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I146 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I147 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I148 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I149 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I150 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I151 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I152 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I153 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I154 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I155 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I156 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I157 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I158 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I159 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I160 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I161 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I162 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I163 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I164 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I165 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I166 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I167 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I168 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I169 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I170 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I171 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I172 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I173 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I174 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I175 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I176 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I177 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I178 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I179 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I180 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I181 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I182 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I183 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I184 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I185 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I186 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I187 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I188 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I189 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I190 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I191 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I192 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I193 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I194 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I195 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I196 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I197 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I198 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I199 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I200 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I201 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I202 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I203 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I204 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I205 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I206 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I207 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I208 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I209 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I210 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I211 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I212 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I213 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I214 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I215 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I216 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I217 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I218 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I219 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I220 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I221 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I222 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I223 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I224 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I225 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I226 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I227 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I228 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I229 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I230 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I231 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I232 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I233 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I234 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I235 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I236 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I237 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I238 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I239 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I240 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I241 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I242 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I243 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I244 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I245 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I246 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I247 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I248 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I249 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I250 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I251 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I252 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I253 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I254 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I255 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I256 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I257 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I258 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | S228 | EMON1 | EventMaskLo | UINT32 | RW | 0...4294967295
135 | S229 | EMON1 | EventMaskHi | UINT32 | RW | 0...4294967295
143 | O1 | ALARM | ALARM 1 | SIGNAL_IN | RW | 0...4294967295
143 | O2 | ALARM | ALARM 2 | SIGNAL_IN | RW | 0...4294967295
143 | O3 | ALARM | ALARM 3 | SIGNAL_IN | RW | 0...4294967295
143 | O4 | ALARM | ALARM 4 | SIGNAL_IN | RW | 0...4294967295
143 | O5 | ALARM | ALARM 5 | SIGNAL_IN | RW | 0...4294967295
143 | O6 | ALARM | ALARM 6 | SIGNAL_IN | RW | 0...4294967295
143 | O7 | ALARM | ALARM 7 | SIGNAL_IN | RW | 0...4294967295
143 | O8 | ALARM | ALARM 8 | SIGNAL_IN | RW | 0...4294967295
143 | O9 | ALARM | ALARM 9 | SIGNAL_IN | RW | 0...4294967295
143 | O10 | ALARM | ALARM 10 | SIGNAL_IN | RW | 0...4294967295
143 | O11 | ALARM | ALARM 11 | SIGNAL_IN | RW | 0...4294967295
143 | O12 | ALARM | ALARM 12 | SIGNAL_IN | RW | 0...4294967295
143 | O13 | ALARM | ALARM 13 | SIGNAL_IN | RW | 0...4294967295
143 | O14 | ALARM | ALARM 14 | SIGNAL_IN | RW | 0...4294967295
143 | O15 | ALARM | ALARM 15 | SIGNAL_IN | RW | 0...4294967295
143 | O16 | ALARM | ALARM 16 | SIGNAL_IN | RW | 0...4294967295
143 | O17 | ALARM | ALARM 17 | SIGNAL_IN | RW | 0...4294967295
143 | O18 | ALARM | ALARM 18 | SIGNAL_IN | RW | 0...4294967295
143 | O19 | ALARM | ALARM 19 | SIGNAL_IN | RW | 0...4294967295
143 | O20 | ALARM | ALARM 20 | SIGNAL_IN | RW | 0...4294967295
143 | O21 | ALARM | ALARM 21 | SIGNAL_IN | RW | 0...4294967295
143 | O22 | ALARM | ALARM 22 | SIGNAL_IN | RW | 0...4294967295
143 | O23 | ALARM | ALARM 23 | SIGNAL_IN | RW | 0...4294967295
143 | O24 | ALARM | ALARM 24 | SIGNAL_IN | RW | 0...4294967295
143 | O25 | ALARM | ALARM 25 | SIGNAL_IN | RW | 0...4294967295
143 | O26 | ALARM | ALARM 26 | SIGNAL_IN | RW | 0...4294967295
143 | O27 | ALARM | ALARM 27 | SIGNAL_IN | RW | 0...4294967295
143 | O28 | ALARM | ALARM 28 | SIGNAL_IN | RW | 0...4294967295
143 | O29 | ALARM | ALARM 29 | SIGNAL_IN | RW | 0...4294967295
143 | O30 | ALARM | ALARM 30 | SIGNAL_IN | RW | 0...4294967295
143 | O31 | ALARM | ALARM 31 | SIGNAL_IN | RW | 0...4294967295
143 | O32 | ALARM | ALARM 32 | SIGNAL_IN | RW | 0...4294967295
143 | O33 | ALARM | ALARM 33 | SIGNAL_IN | RW | 0...4294967295
143 | O34 | ALARM | ALARM 34 | SIGNAL_IN | RW | 0...4294967295
143 | O35 | ALARM | ALARM 35 | SIGNAL_IN | RW | 0...4294967295
143 | O36 | ALARM | ALARM 36 | SIGNAL_IN | RW | 0...4294967295
143 | O37 | ALARM | ALARM 37 | SIGNAL_IN | RW | 0...4294967295
143 | O38 | ALARM | ALARM 38 | SIGNAL_IN | RW | 0...4294967295
143 | O39 | ALARM | ALARM 39 | SIGNAL_IN | RW | 0...4294967295
143 | O40 | ALARM | ALARM 40 | SIGNAL_IN | RW | 0...4294967295
143 | O41 | ALARM | ALARM 41 | SIGNAL_IN | RW | 0...4294967295
143 | O42 | ALARM | ALARM 42 | SIGNAL_IN | RW | 0...4294967295
143 | O43 | ALARM | ALARM 43 | SIGNAL_IN | RW | 0...4294967295
143 | O44 | ALARM | ALARM 44 | SIGNAL_IN | RW | 0...4294967295
143 | O45 | ALARM | ALARM 45 | SIGNAL_IN | RW | 0...4294967295
143 | O46 | ALARM | ALARM 46 | SIGNAL_IN | RW | 0...4294967295
143 | O47 | ALARM | ALARM 47 | SIGNAL_IN | RW | 0...4294967295
143 | O48 | ALARM | ALARM 48 | SIGNAL_IN | RW | 0...4294967295
143 | O49 | ALARM | ALARM 49 | SIGNAL_IN | RW | 0...4294967295
143 | O50 | ALARM | ALARM 50 | SIGNAL_IN | RW | 0...4294967295
143 | O51 | ALARM | ALARM 51 | SIGNAL_IN | RW | 0...4294967295
143 | O52 | ALARM | ALARM 52 | SIGNAL_IN | RW | 0...4294967295
143 | O53 | ALARM | ALARM 53 | SIGNAL_IN | RW | 0...4294967295
143 | O54 | ALARM | ALARM 54 | SIGNAL_IN | RW | 0...4294967295
143 | O55 | ALARM | ALARM 55 | SIGNAL_IN | RW | 0...4294967295
143 | O56 | ALARM | ALARM 56 | SIGNAL_IN | RW | 0...4294967295
143 | O57 | ALARM | ALARM 57 | SIGNAL_IN | RW | 0...4294967295
143 | O58 | ALARM | ALARM 58 | SIGNAL_IN | RW | 0...4294967295
143 | O59 | ALARM | ALARM 59 | SIGNAL_IN | RW | 0...4294967295
143 | O60 | ALARM | ALARM 60 | SIGNAL_IN | RW | 0...4294967295
143 | O61 | ALARM | ALARM 61 | SIGNAL_IN | RW | 0...4294967295
143 | O62 | ALARM | ALARM 62 | SIGNAL_IN | RW | 0...4294967295
143 | O63 | ALARM | ALARM 63 | SIGNAL_IN | RW | 0...4294967295
143 | O64 | ALARM | ALARM 64 | SIGNAL_IN | RW | 0...4294967295
159 | S1 | ALARM1 | EventMaskLo | UINT32 | RW | 0...4294967295
159 | S2 | ALARM1 | EventMaskHi | UINT32 | RW | 0...4294967295
160 | S1 | ALARM2 | EventMaskLo | UINT32 | RW | 0...4294967295
160 | S2 | ALARM2 | EventMaskHi | UINT32 | RW | 0...4294967295
162 | S1 | GSYN | Synchronizer mode | UINT32 | RW | 0=Disabled;1=Activated
162 | S2 | GSYN | Synchronizer reference voltage input | UINT32 | RW | 0=U4 Input;1=U3 Input
162 | S3 | GSYN | Voltage difference calculation mode | UINT32 | RW | 0=System is reference;1=U3/U4 Input is reference
162 | S4 | GSYN | Synchronizer voltage reference | UINT32 | RW | 0=UL12;1=UL23;2=UL31;3=UL1;4=UL2;5=UL3
162 | S5 | GSYN | Synchronizer measurement settings | UINT32 | R | 0=Meas.Conf.Incorrect;1=PP and PE voltages;2=PP Voltages;
162 | S6 | GSYN | Synchronizer status | UINT32 | R | 0=Conf.Error;1=Idle Ready;2=Synchronizing;3=Blocked
162 | S7 | GSYN | Force control signals on | UINT32 | RW | 0=None;1=Blocked On;2=Running On;3=Increase U On;4=Decrease U On;5=Increase F On;6=Decrease F On;7=CB Close On;8=LongSyncTime On
162 | S8 | GSYN | Synchronizing by | UINT32 | RW | 0=Autosynchronizer;1=Manual commands
162 | S9 | GSYN | Manual switching mode | UINT32 | RW | 0=Assisted synchroswitch;1=I know what I am doing
162 | S10 | GSYN | Synchroswitch status | UINT32 | R | 0=Standstill;1=Departing;2=Enclosing
162 | S11 | GSYN | Magnitude side A | FLOAT | R | 0.000...200.000
162 | S12 | GSYN | Magnitude side B | FLOAT | R | 0.000...200.000
162 | S13 | GSYN | Frequency side A | FLOAT | R | 0.000...75.000
162 | S14 | GSYN | Frequency side B | FLOAT | R | 0.000...75.000
162 | S15 | GSYN | Magnitude difference | FLOAT | R | -200...200
162 | S16 | GSYN | Frequency difference | FLOAT | R | -100...100
162 | S17 | GSYN | Angle difference | FLOAT | R | -360...360
162 | S18 | GSYN | Magnitude difference on closing BRK | FLOAT | R | -200...200
162 | S19 | GSYN | Frequency difference on closing BRK | FLOAT | R | -100...100
162 | S20 | GSYN | Angle difference on closing BRK | FLOAT | R | -360...360
162 | S21 | GSYN | Estimated BRK Closing time | FLOAT | R | 0...360
162 | S22 | GSYN | Networks rotating time | FLOAT | R | 0...360
162 | S23 | GSYN | Networks placement atm | FLOAT | R | -360...360
162 | S24 | GSYN | Synchronizing time left | FLOAT | R | 0...1800
162 | S25 | GSYN | Get measurement errors for fine tuning | UINT32 | RW | 0=-;1=Get errors
162 | S26 | GSYN | Magnitude difference fine tune | FLOAT | RW | -200...200
162 | S27 | GSYN | Frequency difference fine tune | FLOAT | RW | -100...100
162 | S28 | GSYN | Angle difference fine tune | FLOAT | RW | -360...360
162 | S29 | GSYN | Minimum voltage allowed for synchronizing | FLOAT | RW | 0...105
162 | S30 | GSYN | Maximum voltage allowed for synchronizing | FLOAT | RW | 0...200
162 | S31 | GSYN | Maximum zero voltage allowed for synchronizing (100% disabled) | FLOAT | RW | 0...100
162 | S32 | GSYN | Maximum allowed voltage difference | FLOAT | RW | 0.1...50
162 | S33 | GSYN | Maximum allowed overfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S34 | GSYN | Maximum allowed underfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S35 | GSYN | Max.Time for synchronizing | FLOAT | RW | 0...1800
162 | S36 | GSYN | Maximum allowed angular disposition to allow synchronizing | FLOAT | RW | 0.01...25
162 | S37 | GSYN | Adjustment for measurement inaccuracy or set of desired volt. offset | FLOAT | RW | -95...95
162 | S38 | GSYN | Adjustment for measurement inaccuracy or set of desired angular offset | FLOAT | RW | -60...60
162 | S39 | GSYN | Adjustment for measurement inaccuracy or set of desired freq. offset | FLOAT | RW | -0.5...2
162 | S40 | GSYN | Voltage adjustment slope | FLOAT | RW | 0...25
162 | S41 | GSYN | Volt. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S42 | GSYN | Volt. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S43 | GSYN | Volt. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S44 | GSYN | Freq. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S45 | GSYN | Freq. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S46 | GSYN | Freq. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S47 | GSYN | Maximum allowed voltage difference to start synchronizing | FLOAT | RW | 0...50
162 | S48 | GSYN | Integrator sum when voltage adjustment pulse is generated | FLOAT | RW | 0...50
162 | S49 | GSYN | Voltage adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S50 | GSYN | Frequency adjustment slope when increasing | FLOAT | RW | 0...10
162 | S51 | GSYN | Frequency adjustment slope when decreasing | FLOAT | RW | -10...0
162 | S52 | GSYN | Maximum allowed frequency difference to start synchronizing | FLOAT | RW | 0...25
162 | S53 | GSYN | Integrator sum when frequency adjustment pulse is generated | FLOAT | RW | 0...50
162 | S54 | GSYN | Frequency adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S55 | GSYN | Filter time for angle derivative | FLOAT | RW | 0...1800
162 | S56 | GSYN | Circuit breaker pre-closing adjustment constant | FLOAT | RW | 0...10
162 | S57 | GSYN | Circuit breaker pre-closing time incl auxiliary relays | FLOAT | RW | 0...1800
162 | S58 | GSYN | Lenght of circuit breaker closing pulse | FLOAT | RW | 0...1800
162 | I1 | GSYN | Start Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I2 | GSYN | Stop Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I3 | GSYN | Block and Interrupt Synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I4 | GSYN | Breaker Closed | SIGNAL_IN | RW | 0...4294967295
162 | I5 | GSYN | Manual increase voltage | SIGNAL_IN | RW | 0...4294967295
162 | I6 | GSYN | Manual decrease voltage | SIGNAL_IN | RW | 0...4294967295
162 | I7 | GSYN | Manual increase frequency | SIGNAL_IN | RW | 0...4294967295
162 | I8 | GSYN | Manual decrease frequency | SIGNAL_IN | RW | 0...4294967295
162 | I9 | GSYN | Manual Close Breaker | SIGNAL_IN | RW | 0...4294967295
162 | O1 | GSYN | GSYN Voltage Mag.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O2 | GSYN | GSYN Voltage Freq.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O3 | GSYN | GSYN Voltage Ang.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O4 | GSYN | GSYN Blocked | SIGNAL_OUT | RW | 0...4294967295
162 | O5 | GSYN | GSYN Running | SIGNAL_OUT | RW | 0...4294967295
162 | O6 | GSYN | GSYN Increase Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O7 | GSYN | GSYN Decrease Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O8 | GSYN | GSYN Increase Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O9 | GSYN | GSYN Decrease Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O10 | GSYN | GSYN Breaker Close Pulse | SIGNAL_OUT | RW | 0...4294967295
162 | O11 | GSYN | GSYN Long Sync Time | SIGNAL_OUT | RW | 0...4294967295
162 | O12 | GSYN | GSYN Nets Standstill | SIGNAL_OUT | RW | 0...4294967295
162 | O13 | GSYN | GSYN Nets Departing | SIGNAL_OUT | RW | 0...4294967295
162 | O14 | GSYN | GSYN Nets Enclosing | SIGNAL_OUT | RW | 0...4294967295
162 | S59 | GSYN | Control EventMaskLo | UINT32 | RW | 0...4294967295
162 | S60 | GSYN | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | S1 | VREC | Measurement value recorder mode | UINT32 | RW | 0=Disabled;1=Activated
163 | S2 | VREC | Scale current values to primary | UINT32 | RW | 0=No;1=Yes
163 | S3 | VREC | Record fault types (Overcurrrent & Voltage Over/Under) faults | UINT32 | RW | 0=No;1=Yes
163 | I1 | VREC | Trigger register to memory | SIGNAL_IN | RW | 0...4294967295
163 | I2 | VREC | Tripped stage | UINT32 | R | 0=-;1=I> Trip;2=I>> Trip;3=I>>> Trip;4=I>>>> Trip;5=IDir> Trip;6=IDir>> Trip;7=IDir>>> Trip;8=IDir>>>> Trip;9=U> Trip;10=U>> Trip;11=U>>> Trip;12=U>>>> Trip;13=U< Trip;14=U<< Trip;15=U<<< Trip;16=U<<<< Trip;17=I0> TRIP;18=I0>> Trip;19=I0>>> Trip;20=I0>>>> Trip;21=I0Dir> Trip;22=I0Dir>> Trip;23=I0Dir>>> Trip;24=I0Dir>>>> Trip;25=f> Trip;26=f>> Trip;27=f>>> Trip;28=f>>>> Trip;29=f< Trip;30=f<< Trip;31=f<<< Trip;32=f<<<< Trip;33=P> Trip;34=P< Trip;35=Prev> Trip;36=T> Trip;37=I2> Trip;38=I2>> Trip;39=I2>>> Trip;40=I2>>>> Trip;41=U1/2 > Trip;42=U1/2 >> Trip;43=U1/2 >>> Trip;44=U1/2 >>>> Trip;45=U0> Trip;46=U0>> Trip;47=U0>>> Trip;48=U0>>>> Trip
163 | I3 | VREC | Overcurrent fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;
163 | I4 | VREC | Voltage fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C;8=-;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I5 | VREC | VREC Magnitude 1 | FLOAT | R | 0...1800
163 | I6 | VREC | VREC Magnitude 2 | FLOAT | R | 0...1800
163 | I7 | VREC | VREC Magnitude 3 | FLOAT | R | 0...1800
163 | I8 | VREC | VREC Magnitude 4 | FLOAT | R | 0...1800
163 | I9 | VREC | VREC Magnitude 5 | FLOAT | R | 0...1800
163 | I10 | VREC | VREC Magnitude 6 | FLOAT | R | 0...1800
163 | I11 | VREC | VREC Magnitude 7 | FLOAT | R | 0...1800
163 | I12 | VREC | VREC Magnitude 8 | FLOAT | R | 0...1800
163 | I13 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I14 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I15 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I16 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I17 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I18 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I19 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I20 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I21 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I22 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I23 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I24 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295

## T SPA map AQ-210 v2.1.1.3-233
SPA Ch | SPA Data | Ch Name | Description | Type | Access | Range
46 | V1 | OBJ1 | Open Select | UINT32 | W | 1=Select
46 | V2 | OBJ1 | Close Select | UINT32 | W | 1=Select
46 | V3 | OBJ1 | Execute | UINT32 | W | 1=Execute
46 | V4 | OBJ1 | Cancel | UINT32 | W | 1=Cancel
46 | V5 | OBJ1 | Direct Open | UINT32 | W | 1=Open
46 | V6 | OBJ1 | Direct Close | UINT32 | W | 1=Close
47 | V1 | OBJ2 | Open Select | UINT32 | W | 1=Select
47 | V2 | OBJ2 | Close Select | UINT32 | W | 1=Select
47 | V3 | OBJ2 | Execute | UINT32 | W | 1=Execute
47 | V4 | OBJ2 | Cancel | UINT32 | W | 1=Cancel
47 | V5 | OBJ2 | Direct Open | UINT32 | W | 1=Open
47 | V6 | OBJ2 | Direct Close | UINT32 | W | 1=Close
48 | V1 | OBJ3 | Open Select | UINT32 | W | 1=Select
48 | V2 | OBJ3 | Close Select | UINT32 | W | 1=Select
48 | V3 | OBJ3 | Execute | UINT32 | W | 1=Execute
48 | V4 | OBJ3 | Cancel | UINT32 | W | 1=Cancel
48 | V5 | OBJ3 | Direct Open | UINT32 | W | 1=Open
48 | V6 | OBJ3 | Direct Close | UINT32 | W | 1=Close
49 | V1 | OBJ4 | Open Select | UINT32 | W | 1=Select
49 | V2 | OBJ4 | Close Select | UINT32 | W | 1=Select
49 | V3 | OBJ4 | Execute | UINT32 | W | 1=Execute
49 | V4 | OBJ4 | Cancel | UINT32 | W | 1=Cancel
49 | V5 | OBJ4 | Direct Open | UINT32 | W | 1=Open
49 | V6 | OBJ4 | Direct Close | UINT32 | W | 1=Close
50 | V1 | OBJ5 | Open Select | UINT32 | W | 1=Select
50 | V2 | OBJ5 | Close Select | UINT32 | W | 1=Select
50 | V3 | OBJ5 | Execute | UINT32 | W | 1=Execute
50 | V4 | OBJ5 | Cancel | UINT32 | W | 1=Cancel
50 | V5 | OBJ5 | Direct Open | UINT32 | W | 1=Open
50 | V6 | OBJ5 | Direct Close | UINT32 | W | 1=Close
150 | V1 | OBJ6 | Open Select | UINT32 | W | 1=Select
150 | V2 | OBJ6 | Close Select | UINT32 | W | 1=Select
150 | V3 | OBJ6 | Execute | UINT32 | W | 1=Execute
150 | V4 | OBJ6 | Cancel | UINT32 | W | 1=Cancel
150 | V5 | OBJ6 | Direct Open | UINT32 | W | 1=Open
150 | V6 | OBJ6 | Direct Close | UINT32 | W | 1=Close
151 | V1 | OBJ7 | Open Select | UINT32 | W | 1=Select
151 | V2 | OBJ7 | Close Select | UINT32 | W | 1=Select
151 | V3 | OBJ7 | Execute | UINT32 | W | 1=Execute
151 | V4 | OBJ7 | Cancel | UINT32 | W | 1=Cancel
151 | V5 | OBJ7 | Direct Open | UINT32 | W | 1=Open
151 | V6 | OBJ7 | Direct Close | UINT32 | W | 1=Close
152 | V1 | OBJ8 | Open Select | UINT32 | W | 1=Select
152 | V2 | OBJ8 | Close Select | UINT32 | W | 1=Select
152 | V3 | OBJ8 | Execute | UINT32 | W | 1=Execute
152 | V4 | OBJ8 | Cancel | UINT32 | W | 1=Cancel
152 | V5 | OBJ8 | Direct Open | UINT32 | W | 1=Open
152 | V6 | OBJ8 | Direct Close | UINT32 | W | 1=Close
153 | V1 | OBJ9 | Open Select | UINT32 | W | 1=Select
153 | V2 | OBJ9 | Close Select | UINT32 | W | 1=Select
153 | V3 | OBJ9 | Execute | UINT32 | W | 1=Execute
153 | V4 | OBJ9 | Cancel | UINT32 | W | 1=Cancel
153 | V5 | OBJ9 | Direct Open | UINT32 | W | 1=Open
153 | V6 | OBJ9 | Direct Close | UINT32 | W | 1=Close
154 | V1 | OBJ10 | Open Select | UINT32 | W | 1=Select
154 | V2 | OBJ10 | Close Select | UINT32 | W | 1=Select
154 | V3 | OBJ10 | Execute | UINT32 | W | 1=Execute
154 | V4 | OBJ10 | Cancel | UINT32 | W | 1=Cancel
154 | V5 | OBJ10 | Direct Open | UINT32 | W | 1=Open
154 | V6 | OBJ10 | Direct Close | UINT32 | W | 1=Close
116 | S1 | MEAS1 | Side 1 Current meas update interval | UINT32 | RW | 5...10000
116 | I1 | MEAS1 | Pri.Pha.curr.IL1 | FLOAT | R | 0...100000
116 | I2 | MEAS1 | Pri.Pha.curr.IL2 | FLOAT | R | 0...100000
116 | I3 | MEAS1 | Pri.Pha.curr.IL3 | FLOAT | R | 0...100000
116 | I4 | MEAS1 | Pri.Res.curr.I01 | FLOAT | R | 0...100000
116 | I5 | MEAS1 | Pri.Res.curr.I02 | FLOAT | R | 0...100000
116 | I6 | MEAS1 | Pha.angle IL1 | FLOAT | R | -360...360
116 | I7 | MEAS1 | Pha.angle IL2 | FLOAT | R | -360...360
116 | I8 | MEAS1 | Pha.angle IL3 | FLOAT | R | -360...360
116 | I9 | MEAS1 | Res.curr.angle I01 | FLOAT | R | -360...360
116 | I10 | MEAS1 | Res.curr.angle I02 | FLOAT | R | -360...360
116 | I11 | MEAS1 | Pri.calc.I0 | FLOAT | R | 0...100000
116 | I12 | MEAS1 | calc.I0 Pha.angle | FLOAT | R | -360...360
116 | I13 | MEAS1 | Pha.curr.IL1 TRMS Pri | FLOAT | R | 0...100000
116 | I14 | MEAS1 | Pha.curr.IL2 TRMS Pri | FLOAT | R | 0...100000
116 | I15 | MEAS1 | Pha.curr.IL3 TRMS Pri | FLOAT | R | 0...100000
116 | I16 | MEAS1 | Pri.Pos.seq.curr. | FLOAT | R | 0...100000
116 | I17 | MEAS1 | Pri.Neg.seq.curr. | FLOAT | R | 0...100000
116 | I18 | MEAS1 | Pri.Zero seq.curr. | FLOAT | R | 0...100000
116 | I19 | MEAS1 | Pos.seq.curr.angle | FLOAT | R | -360...360
116 | I20 | MEAS1 | Neg.seq.curr.angle | FLOAT | R | -360...360
116 | I21 | MEAS1 | Zero seq.curr.angle | FLOAT | R | -360...360
116 | I22 | MEAS1 | Res.curr.I01 TRMS Pri | FLOAT | R | 0...100000
116 | I23 | MEAS1 | Res.curr.I02 TRMS Pri | FLOAT | R | 0...100000
116 | I24 | MEAS1 | Pha.L1 ampl. THD | FLOAT | R | 0...100
116 | I25 | MEAS1 | Pha.L1 pow. THD | FLOAT | R | 0...100
116 | I26 | MEAS1 | Pha.L2 ampl. THD | FLOAT | R | 0...100
116 | I27 | MEAS1 | Pha.L2 pow. THD | FLOAT | R | 0...100
116 | I28 | MEAS1 | Pha.L3 ampl. THD | FLOAT | R | 0...100
116 | I29 | MEAS1 | Pha.L3 pow. THD | FLOAT | R | 0...100
116 | I30 | MEAS1 | Res.I01 ampl. THD | FLOAT | R | 0...100
116 | I31 | MEAS1 | Res.I01 pow. THD | FLOAT | R | 0...100
116 | I32 | MEAS1 | Res.I02 ampl. THD | FLOAT | R | 0...100
116 | I33 | MEAS1 | Res.I02 pow. THD | FLOAT | R | 0...100
116 | I34 | MEAS1 | Meas1 IL ang. Ref | FLOAT | R | -360...360
117 | S1 | MEAS2 | Side 2 Current meas update interval | UINT32 | RW | 5...10000
117 | I1 | MEAS2 | Pri.Pha.curr.I''L1 | FLOAT | R | 0...100000
117 | I2 | MEAS2 | Pri.Pha.curr.I''L2 | FLOAT | R | 0...100000
117 | I3 | MEAS2 | Pri.Pha.curr.I''L3 | FLOAT | R | 0...100000
117 | I4 | MEAS2 | Pha.angle I''L1 | FLOAT | R | -360...360
117 | I5 | MEAS2 | Pha.angle I''L2 | FLOAT | R | -360...360
117 | I6 | MEAS2 | Pha.angle I''L3 | FLOAT | R | -360...360
117 | I7 | MEAS2 | Pri.Res.curr.I''01 | FLOAT | R | 0...100000
117 | I8 | MEAS2 | Res.curr.angle I''01 | FLOAT | R | -360...360
117 | I9 | MEAS2 | Pri.Res.curr.I''02 | FLOAT | R | 0...100000
117 | I10 | MEAS2 | Res.curr.angle I''02 | FLOAT | R | -360...360
117 | I11 | MEAS2 | Pri.calc.I''0 | FLOAT | R | 0...100000
117 | I12 | MEAS2 | calc.I''0 Pha.angle | FLOAT | R | -360...360
117 | I13 | MEAS2 | Pha.curr.I''L1 TRMS Pri | FLOAT | R | 0...100000
117 | I14 | MEAS2 | Pha.curr.I''L2 TRMS Pri | FLOAT | R | 0...100000
117 | I15 | MEAS2 | Pha.curr.I''L3 TRMS Pri | FLOAT | R | 0...100000
117 | I16 | MEAS2 | I'' Pri.Pos.seq.curr. | FLOAT | R | 0...100000
117 | I17 | MEAS2 | I'' Pri.Neg.seq.curr. | FLOAT | R | 0...100000
117 | I18 | MEAS2 | I'' Pri.Zero seq.curr. | FLOAT | R | 0...100000
117 | I19 | MEAS2 | I'' Pos.seq.curr.angle | FLOAT | R | -360...360
117 | I20 | MEAS2 | I'' Neg.seq.curr.angle | FLOAT | R | -360...360
117 | I21 | MEAS2 | I'' Zero seq.curr.angle | FLOAT | R | -360...360
117 | I22 | MEAS2 | Res.curr.I''01 TRMS Pri | FLOAT | R | 0...100000
117 | I23 | MEAS2 | Res.curr.I''02 TRMS Pri | FLOAT | R | 0...100000
117 | I24 | MEAS2 | Pha.I''L1 ampl. THD | FLOAT | R | 0...100
117 | I25 | MEAS2 | Pha.I''L1 pow. THD | FLOAT | R | 0...100
117 | I26 | MEAS2 | Pha.I''L2 ampl. THD | FLOAT | R | 0...100
117 | I27 | MEAS2 | Pha.I''L2 pow. THD | FLOAT | R | 0...100
117 | I28 | MEAS2 | Pha.I''L3 ampl. THD | FLOAT | R | 0...100
117 | I29 | MEAS2 | Pha.I''L3 pow. THD | FLOAT | R | 0...100
117 | I30 | MEAS2 | Res.I''01 ampl. THD | FLOAT | R | 0...100
117 | I31 | MEAS2 | Res.I''01 pow. THD | FLOAT | R | 0...100
117 | I32 | MEAS2 | Res.I''02 ampl. THD | FLOAT | R | 0...100
117 | I33 | MEAS2 | Res.I''02 pow. THD | FLOAT | R | 0...100
117 | I34 | MEAS2 | MEAS2 IL ang. Ref | FLOAT | R | -360...360
118 | S1 | MEAS3 | Voltage meas update interval | UINT32 | RW | 5...10000
118 | I1 | MEAS3 | Pos.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I2 | MEAS3 | Neg.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I3 | MEAS3 | Zero.seq.Volt.pri | FLOAT | R | 0...1000000
118 | I4 | MEAS3 | Pos.Seq volt.Angle | FLOAT | R | -360...360
118 | I5 | MEAS3 | Neg.Seq.volt.Angle | FLOAT | R | -360...360
118 | I6 | MEAS3 | Zero.Seq.volt.Angle | FLOAT | R | -360...360
118 | I7 | MEAS3 | System volt UL12 mag | FLOAT | R | 0...1000000
118 | I8 | MEAS3 | System volt UL12 mag(kV) | FLOAT | R | 0...1000
118 | I9 | MEAS3 | System volt UL12 ang | FLOAT | R | -360...360
118 | I10 | MEAS3 | System volt UL23 mag | FLOAT | R | 0...1000000
118 | I11 | MEAS3 | System volt UL23 mag(kV) | FLOAT | R | 0...1000
118 | I12 | MEAS3 | System volt UL23 ang | FLOAT | R | -360...360
118 | I13 | MEAS3 | System volt UL31 mag | FLOAT | R | 0...1000000
118 | I14 | MEAS3 | System volt UL31 mag(kV) | FLOAT | R | 0...1000
118 | I15 | MEAS3 | System volt UL31 ang | FLOAT | R | -360...360
118 | I16 | MEAS3 | System volt UL1 mag | FLOAT | R | 0...1000000
118 | I17 | MEAS3 | System volt UL1 mag(kV) | FLOAT | R | 0...1000
118 | I18 | MEAS3 | System volt UL1 ang | FLOAT | R | -360...360
118 | I19 | MEAS3 | System volt UL2 mag | FLOAT | R | 0...1000000
118 | I20 | MEAS3 | System volt UL2 mag(kV) | FLOAT | R | 0...1000
118 | I21 | MEAS3 | System volt UL2 ang | FLOAT | R | -360...360
118 | I22 | MEAS3 | System volt UL3 mag | FLOAT | R | 0...1000000
118 | I23 | MEAS3 | System volt UL3 mag(kV) | FLOAT | R | 0...1000
118 | I24 | MEAS3 | System volt UL3 ang | FLOAT | R | -360...360
118 | I25 | MEAS3 | System volt U0 mag | FLOAT | R | 0...1000000
118 | I26 | MEAS3 | System volt U0 mag(kV) | FLOAT | R | 0...1000
118 | I27 | MEAS3 | System volt U0 mag(%) | FLOAT | R | 0...120
118 | I28 | MEAS3 | System volt U0 ang | FLOAT | R | -360...360
118 | I29 | MEAS3 | System volt U3 mag | FLOAT | R | 0...1000000
118 | I30 | MEAS3 | System volt U3 mag(kV) | FLOAT | R | 0...1000
118 | I31 | MEAS3 | System volt U3 ang | FLOAT | R | -360...360
118 | I32 | MEAS3 | System volt U4 mag | FLOAT | R | 0...1000000
118 | I33 | MEAS3 | System volt U4 mag(kV) | FLOAT | R | 0...1000
118 | I34 | MEAS3 | System volt U4 ang | FLOAT | R | -360...360
188 | I1 | IMERX | IL1 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I2 | IMERX | IL1 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I3 | IMERX | IL2 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I4 | IMERX | IL2 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I5 | IMERX | IL3 Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I6 | IMERX | IL3 Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I7 | IMERX | Pos.seq. Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I8 | IMERX | Pos.Seq. Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I9 | IMERX | I01 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I10 | IMERX | I01 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I11 | IMERX | I02 Residual Resistive Current Pri. | FLOAT | R | -100000...100000
188 | I12 | IMERX | I02 Residual Reactive Current Pri. | FLOAT | R | -100000...100000
188 | I13 | IMERX | I01 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I14 | IMERX | I01 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
188 | I15 | IMERX | I02 Residual Resistive Current Sec. | FLOAT | R | -100000...100000
188 | I16 | IMERX | I02 Residual Reactive Current Sec. | FLOAT | R | -100000...100000
119 | S1 | POW1 | Power meas update interval | UINT32 | RW | 5...10000
119 | S2 | POW1 | Nominal Power kVA | FLOAT | RW | 0.1...500000
119 | I1 | POW1 | PQ Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Ind;2=Q2 Rev Cap;3=Q3 Rev Ind;4=Q4 Fwd Cap
119 | I2 | POW1 | VA Quadrant | UINT32 | R | 0=Undefined;1=Q1 Fwd Cap, AV;2=Q2 Rev Ind AV;3=Q3 Rev Cap VA;4=Q4 Fwd Ind VA
119 | I3 | POW1 | Export Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I4 | POW1 | Export Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I5 | POW1 | Import Active Energy (P) MWh | INT32 | R | -2147483647...2147483647
119 | I6 | POW1 | Import Active Energy (P) kWh | INT32 | RW | -2147483647...2147483647
119 | I7 | POW1 | Active Energy (P) Export/Import balance MWh | INT32 | R | -2147483647...2147483647
119 | I8 | POW1 | Active Energy (P) Export/Import balance kWh | INT32 | R | -2147483647...2147483647
119 | I9 | POW1 | Exported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I10 | POW1 | Exported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I11 | POW1 | Imported (Q) while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I12 | POW1 | Imported (Q) while Export (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I13 | POW1 | Reactive Energy (Q) balance while Export (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I14 | POW1 | Reactive Energy (Q) balance while Export (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I15 | POW1 | Exported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I16 | POW1 | Exported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I17 | POW1 | Imported (Q) while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I18 | POW1 | Imported (Q) while Import (P) kVarh | INT32 | RW | -2147483647...2147483647
119 | I19 | POW1 | Reactive Energy (Q) balance while Import (P) MVarh | INT32 | R | -2147483647...2147483647
119 | I20 | POW1 | Reactive Energy (Q) balance while Import (P) kVarh | INT32 | R | -2147483647...2147483647
119 | I21 | POW1 | Apparent Energy (S) while Export (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I22 | POW1 | Apparent Energy (S) while Export (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I23 | POW1 | Apparent Energy (S) while Import (P) MVAh | INT32 | R | -2147483647...2147483647
119 | I24 | POW1 | Apparent Energy (S) while Import (P) kVAh | INT32 | RW | -2147483647...2147483647
119 | I25 | POW1 | Apparent Energy (S) Net | INT32 | R | -2147483647...2147483647
119 | I26 | POW1 | Real Energy (P) Net | INT32 | RW | -2147483647...2147483647
119 | I27 | POW1 | Reactive Energy (Q) Net | INT32 | RW | -2147483647...2147483647
119 | I28 | POW1 | Real Energy (P) Supply (Default supply direction towards busbar) | INT32 | RW | -2147483647...2147483647
119 | I29 | POW1 | Reactive Energy (Q) Supply (Default supply direction towards busbar) | INT32 | R | -2147483647...2147483647
119 | I30 | POW1 | Real Energy (P) Demand (Default demand direction from busbar) | INT32 | RW | -2147483647...2147483647
119 | I31 | POW1 | Reactive Energy (Q) Demand (Default demand direction from busbar) | INT32 | R | -2147483647...2147483647
119 | S3 | POW1 | Reset 3ph Energies | UINT32 | RW | 0=-;1=Reset
119 | I32 | POW1 | POW1 L1 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I33 | POW1 | POW1 L1 Active power (P) | FLOAT | R | -1000000...1000000
119 | I34 | POW1 | POW1 L1 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I35 | POW1 | POW1 L1 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I36 | POW1 | POW1 L1 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I37 | POW1 | L1 PF | FLOAT | R | -1000000...1000000
119 | I38 | POW1 | POW1 L2 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I39 | POW1 | POW1 L2 Active power (P) | FLOAT | R | -1000000...1000000
119 | I40 | POW1 | POW1 L2 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I41 | POW1 | POW1 L2 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I42 | POW1 | POW1 L2 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I43 | POW1 | L2 PF | FLOAT | R | -1000000...1000000
119 | I44 | POW1 | POW1 L3 Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I45 | POW1 | POW1 L3 Active power (P) | FLOAT | R | -1000000...1000000
119 | I46 | POW1 | POW1 L3 Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I47 | POW1 | POW1 L3 Tan(phi) | FLOAT | R | -1000000...1000000
119 | I48 | POW1 | POW1 L3 Cos(phi) | FLOAT | R | -1000000...1000000
119 | I49 | POW1 | L3 PF | FLOAT | R | -1000000...1000000
119 | I50 | POW1 | POW1 3PH Apparent power (S) | FLOAT | R | -1000000...1000000
119 | I51 | POW1 | POW1 3PH Apparent power (S MVA) | FLOAT | R | -1000000...1000000
119 | I52 | POW1 | POW1 3PH Active power (P) | FLOAT | R | -1000000...1000000
119 | I53 | POW1 | POW1 3PH Active power (P MW) | FLOAT | R | -1000000...1000000
119 | I54 | POW1 | POW1 3PH Reactive power (Q) | FLOAT | R | -1000000...1000000
119 | I55 | POW1 | POW1 3PH Reactive power (QMVar) | FLOAT | R | -1000000...1000000
119 | I56 | POW1 | POW1 3PH Tan(phi) | FLOAT | R | -1000000...1000000
119 | I57 | POW1 | POW1 3PH Cos(phi) | FLOAT | R | -1000000...1000000
119 | I58 | POW1 | 3PH PF | FLOAT | R | -1000000...1000000
136 | S1 | IMP1 | Impedance meas. update interval | UINT32 | RW | 500...10000
136 | I1 | IMP1 | Primary L12 R | FLOAT | R | -1000000...1000000
136 | I2 | IMP1 | Primary L12 X | FLOAT | R | -1000000...1000000
136 | I3 | IMP1 | Primary L23 R | FLOAT | R | -1000000...1000000
136 | I4 | IMP1 | Primary L23 X | FLOAT | R | -1000000...1000000
136 | I5 | IMP1 | Primary L31 R | FLOAT | R | -1000000...1000000
136 | I6 | IMP1 | Primary L31 X | FLOAT | R | -1000000...1000000
136 | I7 | IMP1 | Primary Z12 | FLOAT | R | -1000000...1000000
136 | I8 | IMP1 | Primary Z23 | FLOAT | R | -1000000...1000000
136 | I9 | IMP1 | Primary Z31 | FLOAT | R | -1000000...1000000
136 | I10 | IMP1 | Angle Z12 | FLOAT | R | -360...360
136 | I11 | IMP1 | Angle Z23 | FLOAT | R | -360...360
136 | I12 | IMP1 | Angle Z31 | FLOAT | R | -360...360
136 | I13 | IMP1 | Primary L1 R | FLOAT | R | -1000000...1000000
136 | I14 | IMP1 | Primary L1 X | FLOAT | R | -1000000...1000000
136 | I15 | IMP1 | Primary L2 R | FLOAT | R | -1000000...1000000
136 | I16 | IMP1 | Primary L2 X | FLOAT | R | -1000000...1000000
136 | I17 | IMP1 | Primary L3 R | FLOAT | R | -1000000...1000000
136 | I18 | IMP1 | Primary L3 X | FLOAT | R | -1000000...1000000
136 | I19 | IMP1 | Primary Z1 | FLOAT | R | -1000000...1000000
136 | I20 | IMP1 | Primary Z2 | FLOAT | R | -1000000...1000000
136 | I21 | IMP1 | Primary Z3 | FLOAT | R | -1000000...1000000
136 | I22 | IMP1 | Angle Z1 | FLOAT | R | -360...360
136 | I23 | IMP1 | Angle Z2 | FLOAT | R | -360...360
136 | I24 | IMP1 | Angle Z3 | FLOAT | R | -360...360
137 | I1 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I2 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I3 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I4 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I5 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I6 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I7 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I8 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I9 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I10 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I11 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
137 | I12 | FLTREG | Recorded fault value | FLOAT | R | -1000000...1000000
120 | S1 | FREQS | Smpl mode | UINT32 | RW | 0=Fixed;1=Tracking
120 | S2 | FREQS | Max. Tracking freq. allowed (+Nom f) | FLOAT | RW | 0.001...75
120 | S3 | FREQS | Sys.nom.f | FLOAT | RW | 7...75
120 | S4 | FREQS | Min. Tracking freq. allowed (- Nom f) | FLOAT | RW | 0.001...75
120 | I1 | FREQS | Track.sys.f | FLOAT | R | 0...75
120 | I2 | FREQS | f atm. Protections (when not measurable returns to nominal) | FLOAT | R | 0...75
120 | I3 | FREQS | f atm. Display (when not measurable is 0Hz) | FLOAT | R | 0...75
10 | I1 | DIGI | Dis 1-32 | UINT32 | R | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32
10 | I2 | DIGI | Dis 33-64 | UINT32 | R | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51
10 | I3 | DIGI | DI1 | SIGNAL_OUT | R | 0...4294967295
10 | V1 | DIGI | DI1 Counter | UINT32 | R | 0...4294967295
10 | V2 | DIGI | DI1 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I4 | DIGI | DI2 | SIGNAL_OUT | R | 0...4294967295
10 | V3 | DIGI | DI2 Counter | UINT32 | R | 0...4294967295
10 | V4 | DIGI | DI2 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I5 | DIGI | DI3 | SIGNAL_OUT | R | 0...4294967295
10 | V5 | DIGI | DI3 Counter | UINT32 | R | 0...4294967295
10 | V6 | DIGI | DI3 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I6 | DIGI | DI4 | SIGNAL_OUT | R | 0...4294967295
10 | V7 | DIGI | DI4 Counter | UINT32 | R | 0...4294967295
10 | V8 | DIGI | DI4 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I7 | DIGI | DI5 | SIGNAL_OUT | R | 0...4294967295
10 | V9 | DIGI | DI5 Counter | UINT32 | R | 0...4294967295
10 | V10 | DIGI | DI5 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I8 | DIGI | DI6 | SIGNAL_OUT | R | 0...4294967295
10 | V11 | DIGI | DI6 Counter | UINT32 | R | 0...4294967295
10 | V12 | DIGI | DI6 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I9 | DIGI | DI7 | SIGNAL_OUT | R | 0...4294967295
10 | V13 | DIGI | DI7 Counter | UINT32 | R | 0...4294967295
10 | V14 | DIGI | DI7 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I10 | DIGI | DI8 | SIGNAL_OUT | R | 0...4294967295
10 | V15 | DIGI | DI8 Counter | UINT32 | R | 0...4294967295
10 | V16 | DIGI | DI8 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I11 | DIGI | DI9 | SIGNAL_OUT | R | 0...4294967295
10 | V17 | DIGI | DI9 Counter | UINT32 | R | 0...4294967295
10 | V18 | DIGI | DI9 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I12 | DIGI | DI10 | SIGNAL_OUT | R | 0...4294967295
10 | V19 | DIGI | DI10 Counter | UINT32 | R | 0...4294967295
10 | V20 | DIGI | DI10 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I13 | DIGI | DI11 | SIGNAL_OUT | R | 0...4294967295
10 | V21 | DIGI | DI11 Counter | UINT32 | R | 0...4294967295
10 | V22 | DIGI | DI11 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I14 | DIGI | DI12 | SIGNAL_OUT | R | 0...4294967295
10 | V23 | DIGI | DI12 Counter | UINT32 | R | 0...4294967295
10 | V24 | DIGI | DI12 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I15 | DIGI | DI13 | SIGNAL_OUT | R | 0...4294967295
10 | V25 | DIGI | DI13 Counter | UINT32 | R | 0...4294967295
10 | V26 | DIGI | DI13 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I16 | DIGI | DI14 | SIGNAL_OUT | R | 0...4294967295
10 | V27 | DIGI | DI14 Counter | UINT32 | R | 0...4294967295
10 | V28 | DIGI | DI14 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I17 | DIGI | DI15 | SIGNAL_OUT | R | 0...4294967295
10 | V29 | DIGI | DI15 Counter | UINT32 | R | 0...4294967295
10 | V30 | DIGI | DI15 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I18 | DIGI | DI16 | SIGNAL_OUT | R | 0...4294967295
10 | V31 | DIGI | DI16 Counter | UINT32 | R | 0...4294967295
10 | V32 | DIGI | DI16 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I19 | DIGI | DI17 | SIGNAL_OUT | R | 0...4294967295
10 | V33 | DIGI | DI17 Counter | UINT32 | R | 0...4294967295
10 | V34 | DIGI | DI17 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I20 | DIGI | DI18 | SIGNAL_OUT | R | 0...4294967295
10 | V35 | DIGI | DI18 Counter | UINT32 | R | 0...4294967295
10 | V36 | DIGI | DI18 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I21 | DIGI | DI19 | SIGNAL_OUT | R | 0...4294967295
10 | V37 | DIGI | DI19 Counter | UINT32 | R | 0...4294967295
10 | V38 | DIGI | DI19 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I22 | DIGI | DI20 | SIGNAL_OUT | R | 0...4294967295
10 | V39 | DIGI | DI20 Counter | UINT32 | R | 0...4294967295
10 | V40 | DIGI | DI20 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I23 | DIGI | DI21 | SIGNAL_OUT | R | 0...4294967295
10 | V41 | DIGI | DI21 Counter | UINT32 | R | 0...4294967295
10 | V42 | DIGI | DI21 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I24 | DIGI | DI22 | SIGNAL_OUT | R | 0...4294967295
10 | V43 | DIGI | DI22 Counter | UINT32 | R | 0...4294967295
10 | V44 | DIGI | DI22 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I25 | DIGI | DI23 | SIGNAL_OUT | R | 0...4294967295
10 | V45 | DIGI | DI23 Counter | UINT32 | R | 0...4294967295
10 | V46 | DIGI | DI23 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I26 | DIGI | DI24 | SIGNAL_OUT | R | 0...4294967295
10 | V47 | DIGI | DI24 Counter | UINT32 | R | 0...4294967295
10 | V48 | DIGI | DI24 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I27 | DIGI | DI25 | SIGNAL_OUT | R | 0...4294967295
10 | V49 | DIGI | DI25 Counter | UINT32 | R | 0...4294967295
10 | V50 | DIGI | DI25 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I28 | DIGI | DI26 | SIGNAL_OUT | R | 0...4294967295
10 | V51 | DIGI | DI26 Counter | UINT32 | R | 0...4294967295
10 | V52 | DIGI | DI26 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I29 | DIGI | DI27 | SIGNAL_OUT | R | 0...4294967295
10 | V53 | DIGI | DI27 Counter | UINT32 | R | 0...4294967295
10 | V54 | DIGI | DI27 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I30 | DIGI | DI28 | SIGNAL_OUT | R | 0...4294967295
10 | V55 | DIGI | DI28 Counter | UINT32 | R | 0...4294967295
10 | V56 | DIGI | DI28 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I31 | DIGI | DI29 | SIGNAL_OUT | R | 0...4294967295
10 | V57 | DIGI | DI29 Counter | UINT32 | R | 0...4294967295
10 | V58 | DIGI | DI29 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I32 | DIGI | DI30 | SIGNAL_OUT | R | 0...4294967295
10 | V59 | DIGI | DI30 Counter | UINT32 | R | 0...4294967295
10 | V60 | DIGI | DI30 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I33 | DIGI | DI31 | SIGNAL_OUT | R | 0...4294967295
10 | V61 | DIGI | DI31 Counter | UINT32 | R | 0...4294967295
10 | V62 | DIGI | DI31 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I34 | DIGI | DI32 | SIGNAL_OUT | R | 0...4294967295
10 | V63 | DIGI | DI32 Counter | UINT32 | R | 0...4294967295
10 | V64 | DIGI | DI32 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I35 | DIGI | DI33 | SIGNAL_OUT | R | 0...4294967295
10 | V65 | DIGI | DI33 Counter | UINT32 | R | 0...4294967295
10 | V66 | DIGI | DI33 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I36 | DIGI | DI34 | SIGNAL_OUT | R | 0...4294967295
10 | V67 | DIGI | DI34 Counter | UINT32 | R | 0...4294967295
10 | V68 | DIGI | DI34 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I37 | DIGI | DI35 | SIGNAL_OUT | R | 0...4294967295
10 | V69 | DIGI | DI35 Counter | UINT32 | R | 0...4294967295
10 | V70 | DIGI | DI35 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I38 | DIGI | DI36 | SIGNAL_OUT | R | 0...4294967295
10 | V71 | DIGI | DI36 Counter | UINT32 | R | 0...4294967295
10 | V72 | DIGI | DI36 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I39 | DIGI | DI37 | SIGNAL_OUT | R | 0...4294967295
10 | V73 | DIGI | DI37 Counter | UINT32 | R | 0...4294967295
10 | V74 | DIGI | DI37 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I40 | DIGI | DI38 | SIGNAL_OUT | R | 0...4294967295
10 | V75 | DIGI | DI38 Counter | UINT32 | R | 0...4294967295
10 | V76 | DIGI | DI38 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I41 | DIGI | DI39 | SIGNAL_OUT | R | 0...4294967295
10 | V77 | DIGI | DI39 Counter | UINT32 | R | 0...4294967295
10 | V78 | DIGI | DI39 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I42 | DIGI | DI40 | SIGNAL_OUT | R | 0...4294967295
10 | V79 | DIGI | DI40 Counter | UINT32 | R | 0...4294967295
10 | V80 | DIGI | DI40 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I43 | DIGI | DI41 | SIGNAL_OUT | R | 0...4294967295
10 | V81 | DIGI | DI41 Counter | UINT32 | R | 0...4294967295
10 | V82 | DIGI | DI41 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I44 | DIGI | DI42 | SIGNAL_OUT | R | 0...4294967295
10 | V83 | DIGI | DI42 Counter | UINT32 | R | 0...4294967295
10 | V84 | DIGI | DI42 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I45 | DIGI | DI43 | SIGNAL_OUT | R | 0...4294967295
10 | V85 | DIGI | DI43 Counter | UINT32 | R | 0...4294967295
10 | V86 | DIGI | DI43 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I46 | DIGI | DI44 | SIGNAL_OUT | R | 0...4294967295
10 | V87 | DIGI | DI44 Counter | UINT32 | R | 0...4294967295
10 | V88 | DIGI | DI44 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I47 | DIGI | DI45 | SIGNAL_OUT | R | 0...4294967295
10 | V89 | DIGI | DI45 Counter | UINT32 | R | 0...4294967295
10 | V90 | DIGI | DI45 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I48 | DIGI | DI46 | SIGNAL_OUT | R | 0...4294967295
10 | V91 | DIGI | DI46 Counter | UINT32 | R | 0...4294967295
10 | V92 | DIGI | DI46 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I49 | DIGI | DI47 | SIGNAL_OUT | R | 0...4294967295
10 | V93 | DIGI | DI47 Counter | UINT32 | R | 0...4294967295
10 | V94 | DIGI | DI47 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I50 | DIGI | DI48 | SIGNAL_OUT | R | 0...4294967295
10 | V95 | DIGI | DI48 Counter | UINT32 | R | 0...4294967295
10 | V96 | DIGI | DI48 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I51 | DIGI | DI49 | SIGNAL_OUT | R | 0...4294967295
10 | V97 | DIGI | DI49 Counter | UINT32 | R | 0...4294967295
10 | V98 | DIGI | DI49 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I52 | DIGI | DI50 | SIGNAL_OUT | R | 0...4294967295
10 | V99 | DIGI | DI50 Counter | UINT32 | R | 0...4294967295
10 | V100 | DIGI | DI50 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | I53 | DIGI | DI51 | SIGNAL_OUT | R | 0...4294967295
10 | V101 | DIGI | DI51 Counter | UINT32 | R | 0...4294967295
10 | V102 | DIGI | DI51 Counter Clear | UINT32 | RW | 0=-;1=Clear
10 | S1 | DIGI | EventMaskLo | UINT32 | RW | 0...4294967295
10 | S2 | DIGI | EventMaskHi | UINT32 | RW | 0...4294967295
11 | S1 | DIGI2 | EventMaskLo | UINT32 | RW | 0...4294967295
11 | S2 | DIGI2 | EventMaskHi | UINT32 | RW | 0...4294967295
15 | O1 | RELE | Outputs status | UINT32 | R | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15
15 | O2 | RELE | OUT1 | SIGNAL_IN | RW | 0...4294967295
15 | O3 | RELE | OUT2 | SIGNAL_IN | RW | 0...4294967295
15 | O4 | RELE | OUT3 | SIGNAL_IN | RW | 0...4294967295
15 | O5 | RELE | OUT4 | SIGNAL_IN | RW | 0...4294967295
15 | O6 | RELE | OUT5 | SIGNAL_IN | RW | 0...4294967295
15 | O7 | RELE | OUT6 | SIGNAL_IN | RW | 0...4294967295
15 | O8 | RELE | OUT7 | SIGNAL_IN | RW | 0...4294967295
15 | O9 | RELE | OUT8 | SIGNAL_IN | RW | 0...4294967295
15 | O10 | RELE | OUT9 | SIGNAL_IN | RW | 0...4294967295
15 | O11 | RELE | OUT10 | SIGNAL_IN | RW | 0...4294967295
15 | O12 | RELE | OUT11 | SIGNAL_IN | RW | 0...4294967295
15 | O13 | RELE | OUT12 | SIGNAL_IN | RW | 0...4294967295
15 | O14 | RELE | OUT13 | SIGNAL_IN | RW | 0...4294967295
15 | O15 | RELE | OUT14 | SIGNAL_IN | RW | 0...4294967295
15 | O16 | RELE | OUT15 | SIGNAL_IN | RW | 0...4294967295
121 | O1 | LED | LED START | SIGNAL_IN | RW | 0...4294967295
121 | O2 | LED | LED TRIP | SIGNAL_IN | RW | 0...4294967295
121 | O3 | LED | User LED 1 | SIGNAL_IN | RW | 0...4294967295
121 | O4 | LED | User LED 2 | SIGNAL_IN | RW | 0...4294967295
121 | O5 | LED | User LED 3 | SIGNAL_IN | RW | 0...4294967295
121 | O6 | LED | User LED 4 | SIGNAL_IN | RW | 0...4294967295
121 | O7 | LED | User LED 5 | SIGNAL_IN | RW | 0...4294967295
121 | O8 | LED | User LED 6 | SIGNAL_IN | RW | 0...4294967295
121 | O9 | LED | User LED 7 | SIGNAL_IN | RW | 0...4294967295
121 | O10 | LED | User LED 8 | SIGNAL_IN | RW | 0...4294967295
121 | O11 | LED | User LED 9 | SIGNAL_IN | RW | 0...4294967295
121 | O12 | LED | User LED 10 | SIGNAL_IN | RW | 0...4294967295
121 | O13 | LED | User LED 11 | SIGNAL_IN | RW | 0...4294967295
121 | O14 | LED | User LED 12 | SIGNAL_IN | RW | 0...4294967295
121 | O15 | LED | User LED 13 | SIGNAL_IN | RW | 0...4294967295
121 | O16 | LED | User LED 14 | SIGNAL_IN | RW | 0...4294967295
121 | O17 | LED | User LED 15 | SIGNAL_IN | RW | 0...4294967295
121 | O18 | LED | User LED 16 | SIGNAL_IN | RW | 0...4294967295
122 | O1 | LEDX | User LED 17 | SIGNAL_IN | RW | 0...4294967295
122 | O2 | LEDX | User LED 18 | SIGNAL_IN | RW | 0...4294967295
122 | O3 | LEDX | User LED 19 | SIGNAL_IN | RW | 0...4294967295
122 | O4 | LEDX | User LED 20 | SIGNAL_IN | RW | 0...4294967295
122 | O5 | LEDX | User LED 21 | SIGNAL_IN | RW | 0...4294967295
122 | O6 | LEDX | User LED 22 | SIGNAL_IN | RW | 0...4294967295
122 | O7 | LEDX | User LED 23 | SIGNAL_IN | RW | 0...4294967295
122 | O8 | LEDX | User LED 24 | SIGNAL_IN | RW | 0...4294967295
122 | O9 | LEDX | User LED 25 | SIGNAL_IN | RW | 0...4294967295
122 | O10 | LEDX | User LED 26 | SIGNAL_IN | RW | 0...4294967295
122 | O11 | LEDX | User LED 27 | SIGNAL_IN | RW | 0...4294967295
122 | O12 | LEDX | User LED 28 | SIGNAL_IN | RW | 0...4294967295
122 | O13 | LEDX | User LED 29 | SIGNAL_IN | RW | 0...4294967295
122 | O14 | LEDX | User LED 30 | SIGNAL_IN | RW | 0...4294967295
122 | O15 | LEDX | User LED 31 | SIGNAL_IN | RW | 0...4294967295
122 | O16 | LEDX | User LED 32 | SIGNAL_IN | RW | 0...4294967295
122 | O17 | LEDX | User LED 33 | SIGNAL_IN | RW | 0...4294967295
122 | O18 | LEDX | User LED 34 | SIGNAL_IN | RW | 0...4294967295
122 | O19 | LEDX | User LED 35 | SIGNAL_IN | RW | 0...4294967295
122 | O20 | LEDX | User LED 36 | SIGNAL_IN | RW | 0...4294967295
122 | O21 | LEDX | User LED 37 | SIGNAL_IN | RW | 0...4294967295
122 | O22 | LEDX | User LED 38 | SIGNAL_IN | RW | 0...4294967295
122 | O23 | LEDX | User LED 39 | SIGNAL_IN | RW | 0...4294967295
122 | O24 | LEDX | User LED 40 | SIGNAL_IN | RW | 0...4294967295
122 | O25 | LEDX | User LED 41 | SIGNAL_IN | RW | 0...4294967295
122 | O26 | LEDX | User LED 42 | SIGNAL_IN | RW | 0...4294967295
122 | O27 | LEDX | User LED 43 | SIGNAL_IN | RW | 0...4294967295
122 | O28 | LEDX | User LED 44 | SIGNAL_IN | RW | 0...4294967295
122 | O29 | LEDX | User LED 45 | SIGNAL_IN | RW | 0...4294967295
122 | O30 | LEDX | User LED 46 | SIGNAL_IN | RW | 0...4294967295
122 | O31 | LEDX | User LED 47 | SIGNAL_IN | RW | 0...4294967295
122 | O32 | LEDX | User LED 48 | SIGNAL_IN | RW | 0...4294967295
65 | V1 | SGS | Active setting group | UINT32 | R | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
65 | S1 | SGS | Force SG | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | S2 | SGS | Force SG change | UINT32 | RW | 0=Disabled;1=Enabled
65 | S3 | SGS | Used setting groups | UINT32 | RW | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
65 | S4 | SGS | Remote SG change | UINT32 | RW | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
65 | O1 | SGS | Forced SG in use | SIGNAL_OUT | RW | 0...4294967295
65 | O2 | SGS | SG1 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O3 | SGS | SG2 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O4 | SGS | SG3 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O5 | SGS | SG4 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O6 | SGS | SG5 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O7 | SGS | SG6 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O8 | SGS | SG7 Active | SIGNAL_OUT | RW | 0...4294967295
65 | O9 | SGS | SG8 Active | SIGNAL_OUT | RW | 0...4294967295
7 | I1 | CTRL | Local/Remote status | UINT32 | R | 0=Remote;1=Local
123 | V1 | DEV | Serial number | UINT32 | R | 0...4294967295
123 | V2 | DEV | SW version | STRING | R | ...32
124 | S1 | EVENT | Clear Events | UINT32 | RW | 0=-;1=Clear
125 | I1 | DIAG | Diagnostic alarm status | UINT32 | R | 0b=Temp. out of range;1b=Voltage out of range;2b=HW configuration invalid;3b=Relay output failure;4b=Option card A alarm;5b=Option card B alarm;6b=Option card C alarm;7b=Option card D alarm;8b=Option card E alarm;9b=Option card F alarm;10b=GOOSE invalid;
125 | S1 | DIAG | Clear diagnostic alarm | UINT32 | W | 0=-;1=Clear
125 | I2 | DIAG | Internal temperature | FLOAT | R | 0...200
125 | I3 | DIAG | Internal voltage 24V | FLOAT | R | 0...50
125 | I4 | DIAG | Internal voltage 24V max | FLOAT | R | 0...50
125 | I5 | DIAG | Internal voltage 24V min | FLOAT | R | 0...50
125 | I6 | DIAG | Internal voltage 24V deviation | FLOAT | R | 0...50
138 | I1 | MBIO | Input value | FLOAT | R | -101...2000
138 | I2 | MBIO | Input value | FLOAT | R | -101...2000
138 | I3 | MBIO | Input value | FLOAT | R | -101...2000
138 | I4 | MBIO | Input value | FLOAT | R | -101...2000
138 | I5 | MBIO | Input value | FLOAT | R | -101...2000
138 | I6 | MBIO | Input value | FLOAT | R | -101...2000
138 | I7 | MBIO | Input value | FLOAT | R | -101...2000
138 | I8 | MBIO | Input value | FLOAT | R | -101...2000
138 | I9 | MBIO | Input value | FLOAT | R | -101...2000
138 | I10 | MBIO | Input value | FLOAT | R | -101...2000
138 | I11 | MBIO | Input value | FLOAT | R | -101...2000
138 | I12 | MBIO | Input value | FLOAT | R | -101...2000
138 | I13 | MBIO | Input value | FLOAT | R | -101...2000
138 | I14 | MBIO | Input value | FLOAT | R | -101...2000
138 | I15 | MBIO | Input value | FLOAT | R | -101...2000
138 | I16 | MBIO | Input value | FLOAT | R | -101...2000
138 | I17 | MBIO | Input value | FLOAT | R | -101...2000
138 | I18 | MBIO | Input value | FLOAT | R | -101...2000
138 | I19 | MBIO | Input value | FLOAT | R | -101...2000
138 | I20 | MBIO | Input value | FLOAT | R | -101...2000
138 | I21 | MBIO | Input value | FLOAT | R | -101...2000
138 | I22 | MBIO | Input value | FLOAT | R | -101...2000
138 | I23 | MBIO | Input value | FLOAT | R | -101...2000
138 | I24 | MBIO | Input value | FLOAT | R | -101...2000
138 | I25 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I26 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I27 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I28 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I29 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I30 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I31 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I32 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I33 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I34 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I35 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I36 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I37 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I38 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I39 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I40 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I41 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I42 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I43 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I44 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I45 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I46 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I47 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | I48 | MBIO | Input status | UINT32 | R | 0=Invalid;1=OK
138 | O1 | MBIO | MBIO ModA Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O2 | MBIO | MBIO ModA Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O3 | MBIO | MBIO ModA Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O4 | MBIO | MBIO ModA Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O5 | MBIO | MBIO ModA Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O6 | MBIO | MBIO ModA Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O7 | MBIO | MBIO ModA Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O8 | MBIO | MBIO ModA Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O9 | MBIO | MBIO ModB Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O10 | MBIO | MBIO ModB Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O11 | MBIO | MBIO ModB Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O12 | MBIO | MBIO ModB Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O13 | MBIO | MBIO ModB Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O14 | MBIO | MBIO ModB Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O15 | MBIO | MBIO ModB Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O16 | MBIO | MBIO ModB Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O17 | MBIO | MBIO ModC Ch1 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O18 | MBIO | MBIO ModC Ch2 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O19 | MBIO | MBIO ModC Ch3 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O20 | MBIO | MBIO ModC Ch4 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O21 | MBIO | MBIO ModC Ch5 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O22 | MBIO | MBIO ModC Ch6 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O23 | MBIO | MBIO ModC Ch7 Invalid | SIGNAL_OUT | RW | 0...4294967295
138 | O24 | MBIO | MBIO ModC Ch8 Invalid | SIGNAL_OUT | RW | 0...4294967295
139 | V1 | LOGIC | Reset Latches | UINT32 | RW | 0=-;1=Reset
8 | O1 | LOGIC1 | Logic out 1-32 | UINT32 | RW | 0...4294967295
139 | O1 | LOGIC | Logical Output 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O2 | LOGIC | Logical Output 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O3 | LOGIC | Logical Output 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O4 | LOGIC | Logical Output 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O5 | LOGIC | Logical Output 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O6 | LOGIC | Logical Output 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O7 | LOGIC | Logical Output 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O8 | LOGIC | Logical Output 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O9 | LOGIC | Logical Output 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O10 | LOGIC | Logical Output 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O11 | LOGIC | Logical Output 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O12 | LOGIC | Logical Output 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O13 | LOGIC | Logical Output 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O14 | LOGIC | Logical Output 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O15 | LOGIC | Logical Output 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O16 | LOGIC | Logical Output 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O17 | LOGIC | Logical Output 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O18 | LOGIC | Logical Output 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O19 | LOGIC | Logical Output 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O20 | LOGIC | Logical Output 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O21 | LOGIC | Logical Output 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O22 | LOGIC | Logical Output 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O23 | LOGIC | Logical Output 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O24 | LOGIC | Logical Output 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O25 | LOGIC | Logical Output 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O26 | LOGIC | Logical Output 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O27 | LOGIC | Logical Output 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O28 | LOGIC | Logical Output 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O29 | LOGIC | Logical Output 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O30 | LOGIC | Logical Output 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O31 | LOGIC | Logical Output 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O32 | LOGIC | Logical Output 32 | SIGNAL_OUT | RW | 0...4294967295
139 | O33 | LOGIC | Logical Input 1 | SIGNAL_OUT | RW | 0...4294967295
139 | O34 | LOGIC | Logical Input 2 | SIGNAL_OUT | RW | 0...4294967295
139 | O35 | LOGIC | Logical Input 3 | SIGNAL_OUT | RW | 0...4294967295
139 | O36 | LOGIC | Logical Input 4 | SIGNAL_OUT | RW | 0...4294967295
139 | O37 | LOGIC | Logical Input 5 | SIGNAL_OUT | RW | 0...4294967295
139 | O38 | LOGIC | Logical Input 6 | SIGNAL_OUT | RW | 0...4294967295
139 | O39 | LOGIC | Logical Input 7 | SIGNAL_OUT | RW | 0...4294967295
139 | O40 | LOGIC | Logical Input 8 | SIGNAL_OUT | RW | 0...4294967295
139 | O41 | LOGIC | Logical Input 9 | SIGNAL_OUT | RW | 0...4294967295
139 | O42 | LOGIC | Logical Input 10 | SIGNAL_OUT | RW | 0...4294967295
139 | O43 | LOGIC | Logical Input 11 | SIGNAL_OUT | RW | 0...4294967295
139 | O44 | LOGIC | Logical Input 12 | SIGNAL_OUT | RW | 0...4294967295
139 | O45 | LOGIC | Logical Input 13 | SIGNAL_OUT | RW | 0...4294967295
139 | O46 | LOGIC | Logical Input 14 | SIGNAL_OUT | RW | 0...4294967295
139 | O47 | LOGIC | Logical Input 15 | SIGNAL_OUT | RW | 0...4294967295
139 | O48 | LOGIC | Logical Input 16 | SIGNAL_OUT | RW | 0...4294967295
139 | O49 | LOGIC | Logical Input 17 | SIGNAL_OUT | RW | 0...4294967295
139 | O50 | LOGIC | Logical Input 18 | SIGNAL_OUT | RW | 0...4294967295
139 | O51 | LOGIC | Logical Input 19 | SIGNAL_OUT | RW | 0...4294967295
139 | O52 | LOGIC | Logical Input 20 | SIGNAL_OUT | RW | 0...4294967295
139 | O53 | LOGIC | Logical Input 21 | SIGNAL_OUT | RW | 0...4294967295
139 | O54 | LOGIC | Logical Input 22 | SIGNAL_OUT | RW | 0...4294967295
139 | O55 | LOGIC | Logical Input 23 | SIGNAL_OUT | RW | 0...4294967295
139 | O56 | LOGIC | Logical Input 24 | SIGNAL_OUT | RW | 0...4294967295
139 | O57 | LOGIC | Logical Input 25 | SIGNAL_OUT | RW | 0...4294967295
139 | O58 | LOGIC | Logical Input 26 | SIGNAL_OUT | RW | 0...4294967295
139 | O59 | LOGIC | Logical Input 27 | SIGNAL_OUT | RW | 0...4294967295
139 | O60 | LOGIC | Logical Input 28 | SIGNAL_OUT | RW | 0...4294967295
139 | O61 | LOGIC | Logical Input 29 | SIGNAL_OUT | RW | 0...4294967295
139 | O62 | LOGIC | Logical Input 30 | SIGNAL_OUT | RW | 0...4294967295
139 | O63 | LOGIC | Logical Input 31 | SIGNAL_OUT | RW | 0...4294967295
139 | O64 | LOGIC | Logical Input 32 | SIGNAL_OUT | RW | 0...4294967295
8 | S1 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
8 | S2 | LOGIC1 | LO EventMask | UINT32 | RW | 0...4294967295
9 | S1 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
9 | S2 | LOGIC2 | LI EventMask | UINT32 | RW | 0...4294967295
140 | O1 | TIMER | Timer1 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O2 | TIMER | Timer2 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O3 | TIMER | Timer3 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O4 | TIMER | Timer4 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O5 | TIMER | Timer5 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O6 | TIMER | Timer6 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O7 | TIMER | Timer7 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O8 | TIMER | Timer8 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O9 | TIMER | Timer9 Output | SIGNAL_OUT | RW | 0...4294967295
140 | O10 | TIMER | Timer10 Output | SIGNAL_OUT | RW | 0...4294967295
2 | I1 | IRF | Internal Relay Fault status | UINT32 | R | 0b=Storage error;1b=Logic file missing;2b=Aquisition unit error;3b=Measurement config error;4b=Relay hardware setup error;5b=System overload error;6b=Not configured yet;7b=Firmware upgrade done;8b=Slot supervision error;9b=Software inconsistency error;10b=Safe setting mode active;
2 | S1 | IRF | Clear Fault status | UINT32 | W | 0=-;1=Clear
2 | I2 | IRF | Option card health status | UINT32 | R | 0b=Baseboard fault;1b=Card slot A fault;2b=Card slot B fault;3b=Card slot C fault;4b=Card slot D fault;5b=Card slot E fault;6b=Card slot F fault;
20 | S1 | NOC1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
20 | V1 | NOC1 | I> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
20 | V2 | NOC1 | I> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
20 | I1 | NOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
20 | I2 | NOC1 | I> starts | UINT32 | R | 0...4294967295
20 | I3 | NOC1 | I> trips | UINT32 | R | 0...4294967295
20 | I4 | NOC1 | I> blocks | UINT32 | R | 0...4294967295
20 | S2 | NOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
20 | S3 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S4 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S5 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S6 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S7 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S8 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S9 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S10 | NOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...50
20 | S11 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S12 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S13 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S14 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S15 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S16 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S17 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S18 | NOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
20 | S19 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S20 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S21 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S22 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S23 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S24 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S25 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S26 | NOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
20 | S27 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S28 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S29 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S30 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S31 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S32 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S33 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | S34 | NOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
20 | O1 | NOC1 | I> START (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O2 | NOC1 | I> START(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O3 | NOC1 | I> START(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O4 | NOC1 | I> START(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O5 | NOC1 | I> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
20 | O6 | NOC1 | I> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
20 | O7 | NOC1 | I> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
20 | O8 | NOC1 | I> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
20 | O9 | NOC1 | I> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
20 | V3 | NOC1 | Newest Register | UINT32 | R | 0...12
20 | V4 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V5 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V6 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V7 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V8 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V9 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V10 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V11 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V12 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V13 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V14 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V15 | NOC1 | Phase A fault current | FLOAT | R | 0...250
20 | V16 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V17 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V18 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V19 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V20 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V21 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V22 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V23 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V24 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V25 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V26 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V27 | NOC1 | Phase B fault current | FLOAT | R | 0...250
20 | V28 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V29 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V30 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V31 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V32 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V33 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V34 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V35 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V36 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V37 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V38 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | V39 | NOC1 | Phase C fault current | FLOAT | R | 0...250
20 | S35 | NOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
21 | S1 | NOC2 | I>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
21 | S2 | NOC2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
21 | V1 | NOC2 | I>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
21 | V2 | NOC2 | I>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
21 | I1 | NOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
21 | I2 | NOC2 | I>> starts | UINT32 | R | 0...4294967295
21 | I3 | NOC2 | I>> trips | UINT32 | R | 0...4294967295
21 | I4 | NOC2 | I>> blocks | UINT32 | R | 0...4294967295
21 | S3 | NOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
21 | S4 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S5 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S6 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S7 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S8 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S9 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S10 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S11 | NOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...50
21 | S12 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S13 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S14 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S15 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S16 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S17 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S18 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S19 | NOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
21 | S20 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S21 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S22 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S23 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S24 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S25 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S26 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S27 | NOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
21 | S28 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S29 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S30 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S31 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S32 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S33 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S34 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | S35 | NOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
21 | O1 | NOC2 | I>> START (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O2 | NOC2 | I>> START(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O3 | NOC2 | I>> START(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O4 | NOC2 | I>> START(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O5 | NOC2 | I>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
21 | O6 | NOC2 | I>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
21 | O7 | NOC2 | I>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
21 | O8 | NOC2 | I>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
21 | O9 | NOC2 | I>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
21 | V3 | NOC2 | Newest Register | UINT32 | R | 0...12
21 | V4 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V5 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V6 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V7 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V8 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V9 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V10 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V11 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V12 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V13 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V14 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V15 | NOC2 | Phase A fault current | FLOAT | R | 0...250
21 | V16 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V17 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V18 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V19 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V20 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V21 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V22 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V23 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V24 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V25 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V26 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V27 | NOC2 | Phase B fault current | FLOAT | R | 0...250
21 | V28 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V29 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V30 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V31 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V32 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V33 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V34 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V35 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V36 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V37 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V38 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | V39 | NOC2 | Phase C fault current | FLOAT | R | 0...250
21 | S36 | NOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
22 | S1 | NOC3 | I>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
22 | S2 | NOC3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
22 | V1 | NOC3 | I>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
22 | V2 | NOC3 | I>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
22 | I1 | NOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
22 | I2 | NOC3 | I>>> starts | UINT32 | R | 0...4294967295
22 | I3 | NOC3 | I>>> trips | UINT32 | R | 0...4294967295
22 | I4 | NOC3 | I>>> blocks | UINT32 | R | 0...4294967295
22 | S3 | NOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
22 | S4 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S5 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S6 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S7 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S8 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S9 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S10 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S11 | NOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...50
22 | S12 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S13 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S14 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S15 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S16 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S17 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S18 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S19 | NOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
22 | S20 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S21 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S22 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S23 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S24 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S25 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S26 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S27 | NOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
22 | S28 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S29 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S30 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S31 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S32 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S33 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S34 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | S35 | NOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
22 | O1 | NOC3 | I>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O2 | NOC3 | I>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O3 | NOC3 | I>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O4 | NOC3 | I>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O5 | NOC3 | I>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
22 | O6 | NOC3 | I>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
22 | O7 | NOC3 | I>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
22 | O8 | NOC3 | I>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
22 | O9 | NOC3 | I>>>BLOCKED | SIGNAL_OUT | RW | 0...4294967295
22 | V3 | NOC3 | Newest Register | UINT32 | R | 0...12
22 | V4 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V5 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V6 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V7 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V8 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V9 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V10 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V11 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V12 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V13 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V14 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V15 | NOC3 | Phase A fault current | FLOAT | R | 0...250
22 | V16 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V17 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V18 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V19 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V20 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V21 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V22 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V23 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V24 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V25 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V26 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V27 | NOC3 | Phase B fault current | FLOAT | R | 0...250
22 | V28 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V29 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V30 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V31 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V32 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V33 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V34 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V35 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V36 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V37 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V38 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | V39 | NOC3 | Phase C fault current | FLOAT | R | 0...250
22 | S36 | NOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
23 | S1 | NOC4 | I>>>> [50/51] mode | UINT32 | RW | 0=Disabled;1=Activated
23 | S2 | NOC4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
23 | V1 | NOC4 | I>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
23 | V2 | NOC4 | I>>>> Phases condition | UINT32 | R | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
23 | I1 | NOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
23 | I2 | NOC4 | I>>>> starts | UINT32 | R | 0...4294967295
23 | I3 | NOC4 | I>>>> trips | UINT32 | R | 0...4294967295
23 | I4 | NOC4 | I>>>> blocks | UINT32 | R | 0...4294967295
23 | S3 | NOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
23 | S4 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S5 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S6 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S7 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S8 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S9 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S10 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S11 | NOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...50
23 | S12 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S13 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S14 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S15 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S16 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S17 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S18 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S19 | NOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
23 | S20 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S21 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S22 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S23 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S24 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S25 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S26 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S27 | NOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
23 | S28 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S29 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S30 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S31 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S32 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S33 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S34 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | S35 | NOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
23 | O1 | NOC4 | I>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O2 | NOC4 | I>>>> START(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O3 | NOC4 | I>>>> START(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O4 | NOC4 | I>>>> START(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O5 | NOC4 | I>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
23 | O6 | NOC4 | I>>>> TRIP(A) | SIGNAL_OUT | RW | 0...4294967295
23 | O7 | NOC4 | I>>>> TRIP(B) | SIGNAL_OUT | RW | 0...4294967295
23 | O8 | NOC4 | I>>>> TRIP(C) | SIGNAL_OUT | RW | 0...4294967295
23 | O9 | NOC4 | I>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
23 | V3 | NOC4 | Newest Register | UINT32 | R | 0...12
23 | V4 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V5 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V6 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V7 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V8 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V9 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V10 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V11 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V12 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V13 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V14 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V15 | NOC4 | Phase A fault current | FLOAT | R | 0...250
23 | V16 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V17 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V18 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V19 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V20 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V21 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V22 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V23 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V24 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V25 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V26 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V27 | NOC4 | Phase B fault current | FLOAT | R | 0...250
23 | V28 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V29 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V30 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V31 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V32 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V33 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V34 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V35 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V36 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V37 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V38 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | V39 | NOC4 | Phase C fault current | FLOAT | R | 0...250
23 | S36 | NOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
205 | V1 | ROC1 | Idrw> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
205 | I1 | ROC1 | Idrw> Imeas/Iset at the moment | FLOAT | R | -1250...1250
205 | I2 | ROC1 | Idrw> I/U Angle atm. | FLOAT | R | -360...360
205 | I3 | ROC1 | Idrw> I measured p.u. | FLOAT | R | 0...1250
205 | I4 | ROC1 | Idrw> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
205 | I5 | ROC1 | Idrw> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
205 | I6 | ROC1 | Idrw> U measured p.u. | FLOAT | R | 0...1250
205 | I7 | ROC1 | Idrw> starts | UINT32 | R | 0...4294967295
205 | I8 | ROC1 | Idrw> trips | UINT32 | R | 0...4294967295
205 | I9 | ROC1 | Idrw> blocks | UINT32 | R | 0...4294967295
205 | S1 | ROC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
205 | S2 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S3 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S4 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S5 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S6 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S7 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S8 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S9 | ROC1 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
205 | S10 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S11 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S12 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S13 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S14 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S15 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S16 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S17 | ROC1 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
205 | S18 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S19 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S20 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S21 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S22 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S23 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S24 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S25 | ROC1 | Directional angle center at | FLOAT | RW | 0...360
205 | S26 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S27 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S28 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S29 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S30 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S31 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S32 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S33 | ROC1 | Operating sector +/- center | FLOAT | RW | 0...179
205 | S34 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S35 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S36 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S37 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S38 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S39 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S40 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S41 | ROC1 | Pick-up setting Iset> | FLOAT | RW | -50...50
205 | S42 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S43 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S44 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S45 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S46 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S47 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S48 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S49 | ROC1 | Pick-up setting Uset> | FLOAT | RW | 0...100
205 | S50 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S51 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S52 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S53 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S54 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S55 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S56 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S57 | ROC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
205 | S58 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S59 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S60 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S61 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S62 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S63 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S64 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | S65 | ROC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
205 | O1 | ROC1 | Idrw> START | SIGNAL_OUT | RW | 0...4294967295
205 | O2 | ROC1 | Idrw> TRIP | SIGNAL_OUT | RW | 0...4294967295
205 | O3 | ROC1 | Idrw> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
205 | V2 | ROC1 | Newest Register | UINT32 | R | 0...12
205 | V3 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V4 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V5 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V6 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V7 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V8 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V9 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V10 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V11 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V12 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V13 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V14 | ROC1 | Fault Imeas/Iset | FLOAT | R | 0...250
205 | V15 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V16 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V17 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V18 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V19 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V20 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V21 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V22 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V23 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V24 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V25 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | V26 | ROC1 | Prefault Imeas/Iset | FLOAT | R | 0...250
205 | S66 | ROC1 | EventMaskLo | UINT32 | RW | 0...4294967295
206 | V1 | ROC2 | Idrw>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
206 | I1 | ROC2 | Idrw>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
206 | I2 | ROC2 | Idrw>> I/U Angle atm. | FLOAT | R | -360...360
206 | I3 | ROC2 | Idrw>> I measured p.u. | FLOAT | R | 0...1250
206 | I4 | ROC2 | Idrw>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
206 | I5 | ROC2 | Idrw>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
206 | I6 | ROC2 | Idrw>> U measured p.u. | FLOAT | R | 0...1250
206 | I7 | ROC2 | Idrw>> starts | UINT32 | R | 0...4294967295
206 | I8 | ROC2 | Idrw>> trips | UINT32 | R | 0...4294967295
206 | I9 | ROC2 | Idrw>> blocks | UINT32 | R | 0...4294967295
206 | S1 | ROC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
206 | S2 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S3 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S4 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S5 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S6 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S7 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S8 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S9 | ROC2 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
206 | S10 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S11 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S12 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S13 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S14 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S15 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S16 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S17 | ROC2 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
206 | S18 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S19 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S20 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S21 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S22 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S23 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S24 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S25 | ROC2 | Directional angle center at | FLOAT | RW | 0...360
206 | S26 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S27 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S28 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S29 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S30 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S31 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S32 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S33 | ROC2 | Operating sector +/- center | FLOAT | RW | 0...179
206 | S34 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S35 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S36 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S37 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S38 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S39 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S40 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S41 | ROC2 | Pick-up setting Iset>> | FLOAT | RW | -50...50
206 | S42 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S43 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S44 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S45 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S46 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S47 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S48 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S49 | ROC2 | Pick-up setting Uset>> | FLOAT | RW | 0...100
206 | S50 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S51 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S52 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S53 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S54 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S55 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S56 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S57 | ROC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
206 | S58 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S59 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S60 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S61 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S62 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S63 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S64 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | S65 | ROC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
206 | O1 | ROC2 | Idrw>> START | SIGNAL_OUT | RW | 0...4294967295
206 | O2 | ROC2 | Idrw>> TRIP | SIGNAL_OUT | RW | 0...4294967295
206 | O3 | ROC2 | Idrw>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
206 | V2 | ROC2 | Newest Register | UINT32 | R | 0...12
206 | V3 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V4 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V5 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V6 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V7 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V8 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V9 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V10 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V11 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V12 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V13 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V14 | ROC2 | Fault Imeas/Iset | FLOAT | R | 0...250
206 | V15 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V16 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V17 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V18 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V19 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V20 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V21 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V22 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V23 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V24 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V25 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | V26 | ROC2 | Prefault Imeas/Iset | FLOAT | R | 0...250
206 | S66 | ROC2 | EventMaskLo | UINT32 | RW | 0...4294967295
207 | V1 | ROC3 | Idrw>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
207 | I1 | ROC3 | Idrw>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
207 | I2 | ROC3 | Idrw>>> I/U Angle atm. | FLOAT | R | -360...360
207 | I3 | ROC3 | Idrw>>> I measured p.u. | FLOAT | R | 0...1250
207 | I4 | ROC3 | Idrw>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
207 | I5 | ROC3 | Idrw>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
207 | I6 | ROC3 | Idrw>>> U measured p.u. | FLOAT | R | 0...1250
207 | I7 | ROC3 | Idrw>>> starts | UINT32 | R | 0...4294967295
207 | I8 | ROC3 | Idrw>>> trips | UINT32 | R | 0...4294967295
207 | I9 | ROC3 | Idrw>>> blocks | UINT32 | R | 0...4294967295
207 | S1 | ROC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
207 | S2 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S3 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S4 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S5 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S6 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S7 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S8 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S9 | ROC3 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
207 | S10 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S11 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S12 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S13 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S14 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S15 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S16 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S17 | ROC3 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
207 | S18 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S19 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S20 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S21 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S22 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S23 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S24 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S25 | ROC3 | Directional angle center at | FLOAT | RW | 0...360
207 | S26 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S27 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S28 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S29 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S30 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S31 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S32 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S33 | ROC3 | Operating sector +/- center | FLOAT | RW | 0...179
207 | S34 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S35 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S36 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S37 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S38 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S39 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S40 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S41 | ROC3 | Pick-up setting Iset>>> | FLOAT | RW | -50...50
207 | S42 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S43 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S44 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S45 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S46 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S47 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S48 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S49 | ROC3 | Pick-up setting Uset>>> | FLOAT | RW | 0...100
207 | S50 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S51 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S52 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S53 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S54 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S55 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S56 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S57 | ROC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
207 | S58 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S59 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S60 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S61 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S62 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S63 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S64 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | S65 | ROC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
207 | O1 | ROC3 | Idrw>>> START | SIGNAL_OUT | RW | 0...4294967295
207 | O2 | ROC3 | Idrw>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
207 | O3 | ROC3 | Idrw>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
207 | V2 | ROC3 | Newest Register | UINT32 | R | 0...12
207 | V3 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V4 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V5 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V6 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V7 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V8 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V9 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V10 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V11 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V12 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V13 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V14 | ROC3 | Fault Imeas/Iset | FLOAT | R | 0...250
207 | V15 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V16 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V17 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V18 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V19 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V20 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V21 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V22 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V23 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V24 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V25 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | V26 | ROC3 | Prefault Imeas/Iset | FLOAT | R | 0...250
207 | S66 | ROC3 | EventMaskLo | UINT32 | RW | 0...4294967295
208 | V1 | ROC4 | Idrw>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
208 | I1 | ROC4 | Idrw>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
208 | I2 | ROC4 | Idrw>>>> I/U Angle atm. | FLOAT | R | -360...360
208 | I3 | ROC4 | Idrw>>>> I measured p.u. | FLOAT | R | 0...1250
208 | I4 | ROC4 | Idrw>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
208 | I5 | ROC4 | Idrw>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
208 | I6 | ROC4 | Idrw>>>> U measured p.u. | FLOAT | R | 0...1250
208 | I7 | ROC4 | Idrw>>>> starts | UINT32 | R | 0...4294967295
208 | I8 | ROC4 | Idrw>>>> trips | UINT32 | R | 0...4294967295
208 | I9 | ROC4 | Idrw>>>> blocks | UINT32 | R | 0...4294967295
208 | S1 | ROC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
208 | S2 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S3 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S4 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S5 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S6 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S7 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S8 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S9 | ROC4 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
208 | S10 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S11 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S12 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S13 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S14 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S15 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S16 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S17 | ROC4 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
208 | S18 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S19 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S20 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S21 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S22 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S23 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S24 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S25 | ROC4 | Directional angle center at | FLOAT | RW | 0...360
208 | S26 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S27 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S28 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S29 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S30 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S31 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S32 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S33 | ROC4 | Operating sector +/- center | FLOAT | RW | 0...179
208 | S34 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S35 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S36 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S37 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S38 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S39 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S40 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S41 | ROC4 | Pick-up setting Iset>>>> | FLOAT | RW | -50...50
208 | S42 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S43 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S44 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S45 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S46 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S47 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S48 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S49 | ROC4 | Pick-up setting Uset>>>> | FLOAT | RW | 0...100
208 | S50 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S51 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S52 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S53 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S54 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S55 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S56 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S57 | ROC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
208 | S58 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S59 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S60 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S61 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S62 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S63 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S64 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | S65 | ROC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
208 | O1 | ROC4 | Idrw>>>> START | SIGNAL_OUT | RW | 0...4294967295
208 | O2 | ROC4 | Idrw>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
208 | O3 | ROC4 | Idrw>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
208 | V2 | ROC4 | Newest Register | UINT32 | R | 0...12
208 | V3 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V4 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V5 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V6 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V7 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V8 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V9 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V10 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V11 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V12 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V13 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V14 | ROC4 | Fault Imeas/Iset | FLOAT | R | 0...250
208 | V15 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V16 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V17 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V18 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V19 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V20 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V21 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V22 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V23 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V24 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V25 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | V26 | ROC4 | Prefault Imeas/Iset | FLOAT | R | 0...250
208 | S66 | ROC4 | EventMaskLo | UINT32 | RW | 0...4294967295
209 | V1 | ROC5 | Idrw>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
209 | I1 | ROC5 | Idrw>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
209 | I2 | ROC5 | Idrw>>>>> I/U Angle atm. | FLOAT | R | -360...360
209 | I3 | ROC5 | Idrw>>>>> I measured p.u. | FLOAT | R | 0...1250
209 | I4 | ROC5 | Idrw>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
209 | I5 | ROC5 | Idrw>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
209 | I6 | ROC5 | Idrw>>>>> U measured p.u. | FLOAT | R | 0...1250
209 | I7 | ROC5 | Idrw>>>>> starts | UINT32 | R | 0...4294967295
209 | I8 | ROC5 | Idrw>>>>> trips | UINT32 | R | 0...4294967295
209 | I9 | ROC5 | Idrw>>>>> blocks | UINT32 | R | 0...4294967295
209 | S1 | ROC5 | Clear statistics | UINT32 | W | 0=-;1=Clear
209 | S2 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S3 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S4 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S5 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S6 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S7 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S8 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S9 | ROC5 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
209 | S10 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S11 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S12 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S13 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S14 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S15 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S16 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S17 | ROC5 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
209 | S18 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S19 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S20 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S21 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S22 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S23 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S24 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S25 | ROC5 | Directional angle center at | FLOAT | RW | 0...360
209 | S26 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S27 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S28 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S29 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S30 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S31 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S32 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S33 | ROC5 | Operating sector +/- center | FLOAT | RW | 0...179
209 | S34 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S35 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S36 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S37 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S38 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S39 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S40 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S41 | ROC5 | Pick-up setting Iset>>>>> | FLOAT | RW | -50...50
209 | S42 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S43 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S44 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S45 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S46 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S47 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S48 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S49 | ROC5 | Pick-up setting Uset>>>>> | FLOAT | RW | 0...100
209 | S50 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S51 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S52 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S53 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S54 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S55 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S56 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S57 | ROC5 | Delay type | UINT32 | RW | 0=DT;1=IDMT
209 | S58 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S59 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S60 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S61 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S62 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S63 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S64 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | S65 | ROC5 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
209 | O1 | ROC5 | Idrw>>>>> START | SIGNAL_OUT | RW | 0...4294967295
209 | O2 | ROC5 | Idrw>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
209 | O3 | ROC5 | Idrw>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
209 | V2 | ROC5 | Newest Register | UINT32 | R | 0...12
209 | V3 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V4 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V5 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V6 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V7 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V8 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V9 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V10 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V11 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V12 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V13 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V14 | ROC5 | Fault Imeas/Iset | FLOAT | R | 0...250
209 | V15 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V16 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V17 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V18 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V19 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V20 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V21 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V22 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V23 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V24 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V25 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | V26 | ROC5 | Prefault Imeas/Iset | FLOAT | R | 0...250
209 | S66 | ROC5 | EventMaskLo | UINT32 | RW | 0...4294967295
210 | V1 | ROC6 | Idrw>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
210 | I1 | ROC6 | Idrw>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
210 | I2 | ROC6 | Idrw>>>>>> I/U Angle atm. | FLOAT | R | -360...360
210 | I3 | ROC6 | Idrw>>>>>> I measured p.u. | FLOAT | R | 0...1250
210 | I4 | ROC6 | Idrw>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
210 | I5 | ROC6 | Idrw>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
210 | I6 | ROC6 | Idrw>>>>>> U measured p.u. | FLOAT | R | 0...1250
210 | I7 | ROC6 | Idrw>>>>>> starts | UINT32 | R | 0...4294967295
210 | I8 | ROC6 | Idrw>>>>>> trips | UINT32 | R | 0...4294967295
210 | I9 | ROC6 | Idrw>>>>>> blocks | UINT32 | R | 0...4294967295
210 | S1 | ROC6 | Clear statistics | UINT32 | W | 0=-;1=Clear
210 | S2 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S3 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S4 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S5 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S6 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S7 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S8 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S9 | ROC6 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
210 | S10 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S11 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S12 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S13 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S14 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S15 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S16 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S17 | ROC6 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
210 | S18 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S19 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S20 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S21 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S22 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S23 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S24 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S25 | ROC6 | Directional angle center at | FLOAT | RW | 0...360
210 | S26 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S27 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S28 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S29 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S30 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S31 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S32 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S33 | ROC6 | Operating sector +/- center | FLOAT | RW | 0...179
210 | S34 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S35 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S36 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S37 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S38 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S39 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S40 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S41 | ROC6 | Pick-up setting Iset>>>>>> | FLOAT | RW | -50...50
210 | S42 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S43 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S44 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S45 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S46 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S47 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S48 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S49 | ROC6 | Pick-up setting Uset>>>>>> | FLOAT | RW | 0...100
210 | S50 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S51 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S52 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S53 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S54 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S55 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S56 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S57 | ROC6 | Delay type | UINT32 | RW | 0=DT;1=IDMT
210 | S58 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S59 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S60 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S61 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S62 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S63 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S64 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | S65 | ROC6 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
210 | O1 | ROC6 | Idrw>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
210 | O2 | ROC6 | Idrw>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
210 | O3 | ROC6 | Idrw>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
210 | V2 | ROC6 | Newest Register | UINT32 | R | 0...12
210 | V3 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V4 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V5 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V6 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V7 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V8 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V9 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V10 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V11 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V12 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V13 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V14 | ROC6 | Fault Imeas/Iset | FLOAT | R | 0...250
210 | V15 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V16 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V17 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V18 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V19 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V20 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V21 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V22 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V23 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V24 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V25 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | V26 | ROC6 | Prefault Imeas/Iset | FLOAT | R | 0...250
210 | S66 | ROC6 | EventMaskLo | UINT32 | RW | 0...4294967295
211 | V1 | ROC7 | Idrw>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
211 | I1 | ROC7 | Idrw>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
211 | I2 | ROC7 | Idrw>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
211 | I3 | ROC7 | Idrw>>>>>>> I measured p.u. | FLOAT | R | 0...1250
211 | I4 | ROC7 | Idrw>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
211 | I5 | ROC7 | Idrw>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
211 | I6 | ROC7 | Idrw>>>>>>> U measured p.u. | FLOAT | R | 0...1250
211 | I7 | ROC7 | Idrw>>>>>>> starts | UINT32 | R | 0...4294967295
211 | I8 | ROC7 | Idrw>>>>>>> trips | UINT32 | R | 0...4294967295
211 | I9 | ROC7 | Idrw>>>>>>> blocks | UINT32 | R | 0...4294967295
211 | S1 | ROC7 | Clear statistics | UINT32 | W | 0=-;1=Clear
211 | S2 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S3 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S4 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S5 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S6 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S7 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S8 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S9 | ROC7 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
211 | S10 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S11 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S12 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S13 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S14 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S15 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S16 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S17 | ROC7 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
211 | S18 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S19 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S20 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S21 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S22 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S23 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S24 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S25 | ROC7 | Directional angle center at | FLOAT | RW | 0...360
211 | S26 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S27 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S28 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S29 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S30 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S31 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S32 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S33 | ROC7 | Operating sector +/- center | FLOAT | RW | 0...179
211 | S34 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S35 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S36 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S37 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S38 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S39 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S40 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S41 | ROC7 | Pick-up setting Iset>>>>>>> | FLOAT | RW | -50...50
211 | S42 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S43 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S44 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S45 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S46 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S47 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S48 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S49 | ROC7 | Pick-up setting Uset>>>>>>> | FLOAT | RW | 0...100
211 | S50 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S51 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S52 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S53 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S54 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S55 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S56 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S57 | ROC7 | Delay type | UINT32 | RW | 0=DT;1=IDMT
211 | S58 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S59 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S60 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S61 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S62 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S63 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S64 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | S65 | ROC7 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
211 | O1 | ROC7 | Idrw>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
211 | O2 | ROC7 | Idrw>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
211 | O3 | ROC7 | Idrw>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
211 | V2 | ROC7 | Newest Register | UINT32 | R | 0...12
211 | V3 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V4 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V5 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V6 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V7 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V8 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V9 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V10 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V11 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V12 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V13 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V14 | ROC7 | Fault Imeas/Iset | FLOAT | R | 0...250
211 | V15 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V16 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V17 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V18 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V19 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V20 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V21 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V22 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V23 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V24 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V25 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | V26 | ROC7 | Prefault Imeas/Iset | FLOAT | R | 0...250
211 | S66 | ROC7 | EventMaskLo | UINT32 | RW | 0...4294967295
212 | V1 | ROC8 | Idrw>>>>>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
212 | I1 | ROC8 | Idrw>>>>>>>> Imeas/Iset at the moment | FLOAT | R | -1250...1250
212 | I2 | ROC8 | Idrw>>>>>>>> I/U Angle atm. | FLOAT | R | -360...360
212 | I3 | ROC8 | Idrw>>>>>>>> I measured p.u. | FLOAT | R | 0...1250
212 | I4 | ROC8 | Idrw>>>>>>>> I measured p.u. (Resistive) | FLOAT | R | -1250...1250
212 | I5 | ROC8 | Idrw>>>>>>>> I measured p.u. (Reactive) | FLOAT | R | -1250...1250
212 | I6 | ROC8 | Idrw>>>>>>>> U measured p.u. | FLOAT | R | 0...1250
212 | I7 | ROC8 | Idrw>>>>>>>> starts | UINT32 | R | 0...4294967295
212 | I8 | ROC8 | Idrw>>>>>>>> trips | UINT32 | R | 0...4294967295
212 | I9 | ROC8 | Idrw>>>>>>>> blocks | UINT32 | R | 0...4294967295
212 | S1 | ROC8 | Clear statistics | UINT32 | W | 0=-;1=Clear
212 | S2 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S3 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S4 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S5 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S6 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S7 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S8 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S9 | ROC8 | Operating mode | UINT32 | RW | 0=Non directional;1=Directional Sector;2=Directional IxCos(U/I);3=Directional IxSin(U/I)
212 | S10 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S11 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S12 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S13 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S14 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S15 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S16 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S17 | ROC8 | Directional voltage reference from | UINT32 | RW | 0=U1;1=U2;2=U3;3=U4;4=Sum(U1+U2)
212 | S18 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S19 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S20 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S21 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S22 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S23 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S24 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S25 | ROC8 | Directional angle center at | FLOAT | RW | 0...360
212 | S26 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S27 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S28 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S29 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S30 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S31 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S32 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S33 | ROC8 | Operating sector +/- center | FLOAT | RW | 0...179
212 | S34 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S35 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S36 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S37 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S38 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S39 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S40 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S41 | ROC8 | Pick-up setting Iset>>>>>>>> | FLOAT | RW | -50...50
212 | S42 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S43 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S44 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S45 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S46 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S47 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S48 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S49 | ROC8 | Pick-up setting Uset>>>>>>>> | FLOAT | RW | 0...100
212 | S50 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S51 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S52 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S53 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S54 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S55 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S56 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S57 | ROC8 | Delay type | UINT32 | RW | 0=DT;1=IDMT
212 | S58 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S59 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S60 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S61 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S62 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S63 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S64 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | S65 | ROC8 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
212 | O1 | ROC8 | Idrw>>>>>>>> START | SIGNAL_OUT | RW | 0...4294967295
212 | O2 | ROC8 | Idrw>>>>>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
212 | O3 | ROC8 | Idrw>>>>>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
212 | V2 | ROC8 | Newest Register | UINT32 | R | 0...12
212 | V3 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V4 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V5 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V6 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V7 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V8 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V9 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V10 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V11 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V12 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V13 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V14 | ROC8 | Fault Imeas/Iset | FLOAT | R | 0...250
212 | V15 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V16 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V17 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V18 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V19 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V20 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V21 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V22 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V23 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V24 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V25 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | V26 | ROC8 | Prefault Imeas/Iset | FLOAT | R | 0...250
212 | S66 | ROC8 | EventMaskLo | UINT32 | RW | 0...4294967295
213 | V1 | ROV1 | Urw>/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
213 | I1 | ROV1 | Urw>/< Umeas/Uset at the moment | FLOAT | R | 0...1250
213 | I2 | ROV1 | Urw>/< U measured p.u. | FLOAT | R | 0...1250
213 | I3 | ROV1 | Urw>/< starts | UINT32 | R | 0...4294967295
213 | I4 | ROV1 | Urw>/< trips | UINT32 | R | 0...4294967295
213 | I5 | ROV1 | Urw>/< blocks | UINT32 | R | 0...4294967295
213 | S1 | ROV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
213 | S2 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S3 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S4 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S5 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S6 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S7 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S8 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S9 | ROV1 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
213 | S10 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S11 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S12 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S13 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S14 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S15 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S16 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S17 | ROV1 | Pick-up setting Uset>/< | FLOAT | RW | 0.1...150
213 | S18 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S19 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S20 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S21 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S22 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S23 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S24 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S25 | ROV1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
213 | S26 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S27 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S28 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S29 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S30 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S31 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S32 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S33 | ROV1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
213 | S34 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S35 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S36 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S37 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S38 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S39 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S40 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S41 | ROV1 | Block setting Uset< | FLOAT | RW | 0...80
213 | S42 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S43 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S44 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S45 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S46 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S47 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S48 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | S49 | ROV1 | Trip pulse length | FLOAT | RW | 0...1800
213 | O1 | ROV1 | Urw>/< START | SIGNAL_OUT | RW | 0...4294967295
213 | O2 | ROV1 | Urw>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
213 | O3 | ROV1 | Urw>/< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
213 | O4 | ROV1 | Urw>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
213 | V2 | ROV1 | Newest Register | UINT32 | R | 0...12
213 | V3 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V4 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V5 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V6 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V7 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V8 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V9 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V10 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V11 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V12 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V13 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V14 | ROV1 | Fault Umeas/Uset | FLOAT | R | 0...250
213 | V15 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V16 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V17 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V18 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V19 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V20 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V21 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V22 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V23 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V24 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V25 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | V26 | ROV1 | Prefault Umeas/Uset | FLOAT | R | 0...250
213 | S50 | ROV1 | EventMaskLo | UINT32 | RW | 0...4294967295
214 | V1 | ROV2 | Urw>>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
214 | I1 | ROV2 | Urw>>/<< Umeas/Uset at the moment | FLOAT | R | 0...1250
214 | I2 | ROV2 | Urw>>/<< U measured p.u. | FLOAT | R | 0...1250
214 | I3 | ROV2 | Urw>>/<< starts | UINT32 | R | 0...4294967295
214 | I4 | ROV2 | Urw>>/<< trips | UINT32 | R | 0...4294967295
214 | I5 | ROV2 | Urw>>/<< blocks | UINT32 | R | 0...4294967295
214 | S1 | ROV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
214 | S2 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S3 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S4 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S5 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S6 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S7 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S8 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S9 | ROV2 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
214 | S10 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S11 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S12 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S13 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S14 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S15 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S16 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S17 | ROV2 | Pick-up setting Uset>>/<< | FLOAT | RW | 0.1...150
214 | S18 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S19 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S20 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S21 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S22 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S23 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S24 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S25 | ROV2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
214 | S26 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S27 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S28 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S29 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S30 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S31 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S32 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S33 | ROV2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
214 | S34 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S35 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S36 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S37 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S38 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S39 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S40 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S41 | ROV2 | Block setting Uset<< | FLOAT | RW | 0...80
214 | S42 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S43 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S44 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S45 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S46 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S47 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S48 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | S49 | ROV2 | Trip pulse length | FLOAT | RW | 0...1800
214 | O1 | ROV2 | Urw>>/<< START | SIGNAL_OUT | RW | 0...4294967295
214 | O2 | ROV2 | Urw>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
214 | O3 | ROV2 | Urw>>/<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
214 | O4 | ROV2 | Urw>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
214 | V2 | ROV2 | Newest Register | UINT32 | R | 0...12
214 | V3 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V4 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V5 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V6 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V7 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V8 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V9 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V10 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V11 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V12 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V13 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V14 | ROV2 | Fault Umeas/Uset | FLOAT | R | 0...250
214 | V15 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V16 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V17 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V18 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V19 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V20 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V21 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V22 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V23 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V24 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V25 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | V26 | ROV2 | Prefault Umeas/Uset | FLOAT | R | 0...250
214 | S50 | ROV2 | EventMaskLo | UINT32 | RW | 0...4294967295
215 | V1 | ROV3 | Urw>>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
215 | I1 | ROV3 | Urw>>>/<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
215 | I2 | ROV3 | Urw>>>/<<< U measured p.u. | FLOAT | R | 0...1250
215 | I3 | ROV3 | Urw>>>/<<< starts | UINT32 | R | 0...4294967295
215 | I4 | ROV3 | Urw>>>/<<< trips | UINT32 | R | 0...4294967295
215 | I5 | ROV3 | Urw>>>/<<< blocks | UINT32 | R | 0...4294967295
215 | S1 | ROV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
215 | S2 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S3 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S4 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S5 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S6 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S7 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S8 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S9 | ROV3 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
215 | S10 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S11 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S12 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S13 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S14 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S15 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S16 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S17 | ROV3 | Pick-up setting Uset>>>/<<< | FLOAT | RW | 0.1...150
215 | S18 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S19 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S20 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S21 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S22 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S23 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S24 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S25 | ROV3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
215 | S26 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S27 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S28 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S29 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S30 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S31 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S32 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S33 | ROV3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
215 | S34 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S35 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S36 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S37 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S38 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S39 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S40 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S41 | ROV3 | Block setting Uset<<< | FLOAT | RW | 0...80
215 | S42 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S43 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S44 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S45 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S46 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S47 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S48 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | S49 | ROV3 | Trip pulse length | FLOAT | RW | 0...1800
215 | O1 | ROV3 | Urw>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
215 | O2 | ROV3 | Urw>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
215 | O3 | ROV3 | Urw>>>/<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
215 | O4 | ROV3 | Urw>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
215 | V2 | ROV3 | Newest Register | UINT32 | R | 0...12
215 | V3 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V4 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V5 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V6 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V7 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V8 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V9 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V10 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V11 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V12 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V13 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V14 | ROV3 | Fault Umeas/Uset | FLOAT | R | 0...250
215 | V15 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V16 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V17 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V18 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V19 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V20 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V21 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V22 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V23 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V24 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V25 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | V26 | ROV3 | Prefault Umeas/Uset | FLOAT | R | 0...250
215 | S50 | ROV3 | EventMaskLo | UINT32 | RW | 0...4294967295
216 | V1 | ROV4 | Urw>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
216 | I1 | ROV4 | Urw>>>>/<<<< Umeas/Uset at the moment | FLOAT | R | 0...1250
216 | I2 | ROV4 | Urw>>>>/<<<< U measured p.u. | FLOAT | R | 0...1250
216 | I3 | ROV4 | Urw>>>>/<<<< starts | UINT32 | R | 0...4294967295
216 | I4 | ROV4 | Urw>>>>/<<<< trips | UINT32 | R | 0...4294967295
216 | I5 | ROV4 | Urw>>>>/<<<< blocks | UINT32 | R | 0...4294967295
216 | S1 | ROV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
216 | S2 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S3 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S4 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S5 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S6 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S7 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S8 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S9 | ROV4 | Operating mode | UINT32 | RW | 0=Over >;1=Under <
216 | S10 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S11 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S12 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S13 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S14 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S15 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S16 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S17 | ROV4 | Pick-up setting Uset>>>>/<<<< | FLOAT | RW | 0.1...150
216 | S18 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S19 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S20 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S21 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S22 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S23 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S24 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S25 | ROV4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
216 | S26 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S27 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S28 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S29 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S30 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S31 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S32 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S33 | ROV4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
216 | S34 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S35 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S36 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S37 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S38 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S39 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S40 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S41 | ROV4 | Block setting Uset< | FLOAT | RW | 0...80
216 | S42 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S43 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S44 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S45 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S46 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S47 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S48 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | S49 | ROV4 | Trip pulse length | FLOAT | RW | 0...1800
216 | O1 | ROV4 | Urw>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
216 | O2 | ROV4 | Urw>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
216 | O3 | ROV4 | Urw>>>>/<<<< TRIP PULSE | SIGNAL_OUT | RW | 0...4294967295
216 | O4 | ROV4 | Urw>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
216 | V2 | ROV4 | Newest Register | UINT32 | R | 0...12
216 | V3 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V4 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V5 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V6 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V7 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V8 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V9 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V10 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V11 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V12 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V13 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V14 | ROV4 | Fault Umeas/Uset | FLOAT | R | 0...250
216 | V15 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V16 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V17 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V18 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V19 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V20 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V21 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V22 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V23 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V24 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V25 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | V26 | ROV4 | Prefault Umeas/Uset | FLOAT | R | 0...250
216 | S50 | ROV4 | EventMaskLo | UINT32 | RW | 0...4294967295
224 | I1 | CNU1 | Measured unbalance current | FLOAT | R | 0...50.00
224 | I2 | CNU1 | Unbalance current angle | FLOAT | R | -360.00...360.00
224 | S1 | CNU1 | Natural unbalance compensation | UINT32 | RW | 0=Not used;1=In use
224 | S2 | CNU1 | Compensate natural unbal. | UINT32 | RW | 0=-;1=Comp
224 | I3 | CNU1 | Natural unbalance | FLOAT | R | -50.00...50.00
224 | I4 | CNU1 | Natural unbalance ang | FLOAT | R | -360.00...360.00
224 | I5 | CNU1 | Compensated magnitude | FLOAT | R | -50.00...50.00
224 | I6 | CNU1 | Compensated angle | FLOAT | R | -360.00...360.00
217 | V1 | UCP1 | IUC> condition | UINT32 | R | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
217 | I1 | UCP1 | Unbalance current atm. | FLOAT | R | 0...1250
217 | I2 | UCP1 | Imeas/Iset (ALARM) atm. | FLOAT | R | 0...1250
217 | I3 | UCP1 | Imeas/Iset (TRIP) atm. | FLOAT | R | 0...1250
217 | I4 | UCP1 | IUC> Alarm Starts | UINT32 | R | 0...4294967295
217 | I5 | UCP1 | IUC> Alarms | UINT32 | R | 0...4294967295
217 | I6 | UCP1 | IUC> Starts | UINT32 | R | 0...4294967295
217 | I7 | UCP1 | IUC> Trips | UINT32 | R | 0...4294967295
217 | I8 | UCP1 | IUC> Blocks | UINT32 | R | 0...4294967295
217 | S1 | UCP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
217 | S2 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S3 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S4 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S5 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S6 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S7 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S8 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S9 | UCP1 | Pick-up setting Iset Alarm | FLOAT | RW | 0.1...50
217 | S10 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S11 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S12 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S13 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S14 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S15 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S16 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S17 | UCP1 | Definite time delay Alarm | FLOAT | RW | 0...1800
217 | S18 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S19 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S20 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S21 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S22 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S23 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S24 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S25 | UCP1 | Pick-up setting Iset Trip | FLOAT | RW | 0.1...50
217 | S26 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S27 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S28 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S29 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S30 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S31 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S32 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S33 | UCP1 | Definite time delay Trip | FLOAT | RW | 0...1800
217 | S34 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S35 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S36 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S37 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S38 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S39 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S40 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | S41 | UCP1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
217 | O1 | UCP1 | IUC> ALARM START | SIGNAL_OUT | RW | 0...4294967295
217 | O2 | UCP1 | IUC> ALARM | SIGNAL_OUT | RW | 0...4294967295
217 | O3 | UCP1 | IUC> START | SIGNAL_OUT | RW | 0...4294967295
217 | O4 | UCP1 | IUC> TRIP | SIGNAL_OUT | RW | 0...4294967295
217 | O5 | UCP1 | IUC> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
217 | V2 | UCP1 | Newest Register | UINT32 | R | 0...12
217 | V3 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V4 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V5 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V6 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V7 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V8 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V9 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V10 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V11 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V12 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V13 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | V14 | UCP1 | Unbalance fault current | FLOAT | R | 0...250
217 | S42 | UCP1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S1 | DOC1 | Idir> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
75 | V1 | DOC1 | Idir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
75 | I1 | DOC1 | Operating angle now | FLOAT | R | -360...360
75 | I2 | DOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
75 | I3 | DOC1 | Idir> starts | UINT32 | R | 0...4294967295
75 | I4 | DOC1 | Idir> trips | UINT32 | R | 0...4294967295
75 | I5 | DOC1 | Idir> blocks | UINT32 | R | 0...4294967295
75 | S2 | DOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
75 | S3 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S4 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S5 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S6 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S7 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S8 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S9 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S10 | DOC1 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
75 | S11 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S12 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S13 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S14 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S15 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S16 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S17 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S18 | DOC1 | Operating sector size (+/-) | FLOAT | RW | 1...170
75 | S19 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S20 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S21 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S22 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S23 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S24 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S25 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S26 | DOC1 | Operating sector center | FLOAT | RW | -180...180
75 | S27 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S28 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S29 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S30 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S31 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S32 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S33 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S34 | DOC1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
75 | S35 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S36 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S37 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S38 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S39 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S40 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S41 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S42 | DOC1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
75 | S43 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S44 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S45 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S46 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S47 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S48 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S49 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S50 | DOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
75 | S51 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S52 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S53 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S54 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S55 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S56 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S57 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | S58 | DOC1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
75 | O1 | DOC1 | Idir> START | SIGNAL_OUT | RW | 0...4294967295
75 | O2 | DOC1 | Idir> TRIP | SIGNAL_OUT | RW | 0...4294967295
75 | O3 | DOC1 | Idir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
75 | S59 | DOC1 | Clear registers | UINT32 | W | 0=-;1=Clear
75 | I6 | DOC1 | Newest Register | UINT32 | R | 0...12
75 | I7 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I8 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I9 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I10 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I11 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I12 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I13 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I14 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I15 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I16 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I17 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I18 | DOC1 | Phase A fault current | FLOAT | R | 0...250
75 | I19 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I20 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I21 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I22 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I23 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I24 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I25 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I26 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I27 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I28 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I29 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I30 | DOC1 | Phase B fault current | FLOAT | R | 0...250
75 | I31 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I32 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I33 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I34 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I35 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I36 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I37 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I38 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I39 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I40 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I41 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I42 | DOC1 | Phase C fault current | FLOAT | R | 0...250
75 | I43 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I44 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I45 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I46 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I47 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I48 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I49 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I50 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I51 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I52 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I53 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | I54 | DOC1 | Operating angle | FLOAT | R | -360.00...360.00
75 | S60 | DOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
75 | S61 | DOC1 | EventMaskHi | UINT32 | RW | 0...4294967295
76 | S1 | DOC2 | Idir>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
76 | V1 | DOC2 | Idir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
76 | I1 | DOC2 | Operating angle now | FLOAT | R | -360.00...360.00
76 | I2 | DOC2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
76 | I3 | DOC2 | Idir>> starts | UINT32 | R | 0...4294967295
76 | I4 | DOC2 | Idir>> trips | UINT32 | R | 0...4294967295
76 | I5 | DOC2 | Idir>> blocks | UINT32 | R | 0...4294967295
76 | S2 | DOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
76 | S3 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S4 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S5 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S6 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S7 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S8 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S9 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S10 | DOC2 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
76 | S11 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S12 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S13 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S14 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S15 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S16 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S17 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S18 | DOC2 | Operating sector size (+/-) | FLOAT | RW | 1...170
76 | S19 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S20 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S21 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S22 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S23 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S24 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S25 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S26 | DOC2 | Operating sector center | FLOAT | RW | -180...180
76 | S27 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S28 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S29 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S30 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S31 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S32 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S33 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S34 | DOC2 | Pick-up setting Iset | FLOAT | RW | 0.1...40
76 | S35 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S36 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S37 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S38 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S39 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S40 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S41 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S42 | DOC2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
76 | S43 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S44 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S45 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S46 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S47 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S48 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S49 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S50 | DOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
76 | S51 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S52 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S53 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S54 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S55 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S56 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S57 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | S58 | DOC2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
76 | O1 | DOC2 | Idir>> START | SIGNAL_OUT | RW | 0...4294967295
76 | O2 | DOC2 | Idir>> TRIP | SIGNAL_OUT | RW | 0...4294967295
76 | O3 | DOC2 | Idir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
76 | S59 | DOC2 | Clear registers | UINT32 | W | 0=-;1=Clear
76 | I6 | DOC2 | Newest Register | UINT32 | R | 0...12
76 | I7 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I8 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I9 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I10 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I11 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I12 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I13 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I14 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I15 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I16 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I17 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I18 | DOC2 | Phase A fault current | FLOAT | R | 0...250
76 | I19 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I20 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I21 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I22 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I23 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I24 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I25 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I26 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I27 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I28 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I29 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I30 | DOC2 | Phase B fault current | FLOAT | R | 0...250
76 | I31 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I32 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I33 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I34 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I35 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I36 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I37 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I38 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I39 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I40 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I41 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I42 | DOC2 | Phase C fault current | FLOAT | R | 0...250
76 | I43 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I44 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I45 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I46 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I47 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I48 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I49 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I50 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I51 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I52 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I53 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | I54 | DOC2 | Operating angle | FLOAT | R | -360.00...360.00
76 | S60 | DOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
76 | S61 | DOC2 | EventMaskHi | UINT32 | RW | 0...4294967295
77 | S1 | DOC3 | Idir>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
77 | V1 | DOC3 | Idir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
77 | I1 | DOC3 | Operating angle now | FLOAT | R | -360...360
77 | I2 | DOC3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
77 | I3 | DOC3 | Idir>>> starts | UINT32 | R | 0...4294967295
77 | I4 | DOC3 | Idir>>> trips | UINT32 | R | 0...4294967295
77 | I5 | DOC3 | Idir>>> blocks | UINT32 | R | 0...4294967295
77 | S2 | DOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
77 | S3 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S4 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S5 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S6 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S7 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S8 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S9 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S10 | DOC3 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
77 | S11 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S12 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S13 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S14 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S15 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S16 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S17 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S18 | DOC3 | Operating sector size (+/-) | FLOAT | RW | 1...170
77 | S19 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S20 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S21 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S22 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S23 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S24 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S25 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S26 | DOC3 | Operating sector center | FLOAT | RW | -180...180
77 | S27 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S28 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S29 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S30 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S31 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S32 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S33 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S34 | DOC3 | Pick-up setting Iset | FLOAT | RW | 0.1...40
77 | S35 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S36 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S37 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S38 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S39 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S40 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S41 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S42 | DOC3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
77 | S43 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S44 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S45 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S46 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S47 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S48 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S49 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S50 | DOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
77 | S51 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S52 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S53 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S54 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S55 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S56 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S57 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | S58 | DOC3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
77 | O1 | DOC3 | Idir>>> START | SIGNAL_OUT | RW | 0...4294967295
77 | O2 | DOC3 | Idir>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
77 | O3 | DOC3 | Idir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
77 | S59 | DOC3 | Clear registers | UINT32 | W | 0=-;1=Clear
77 | I6 | DOC3 | Newest Register | UINT32 | R | 0...12
77 | I7 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I8 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I9 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I10 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I11 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I12 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I13 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I14 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I15 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I16 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I17 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I18 | DOC3 | Phase A fault current | FLOAT | R | 0...250
77 | I19 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I20 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I21 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I22 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I23 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I24 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I25 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I26 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I27 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I28 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I29 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I30 | DOC3 | Phase B fault current | FLOAT | R | 0...250
77 | I31 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I32 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I33 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I34 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I35 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I36 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I37 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I38 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I39 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I40 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I41 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I42 | DOC3 | Phase C fault current | FLOAT | R | 0...250
77 | I43 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I44 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I45 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I46 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I47 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I48 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I49 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I50 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I51 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I52 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I53 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | I54 | DOC3 | Operating angle | FLOAT | R | -360.00...360.00
77 | S60 | DOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
77 | S61 | DOC3 | EventMaskHi | UINT32 | RW | 0...4294967295
78 | S1 | DOC4 | Idir>>>> [67] mode | UINT32 | RW | 0=Disabled;1=Activated
78 | V1 | DOC4 | Idir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
78 | I1 | DOC4 | Operating angle now | FLOAT | R | -360.00...360.00
78 | I2 | DOC4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
78 | I3 | DOC4 | Idir>>>> starts | UINT32 | R | 0...4294967295
78 | I4 | DOC4 | Idir>>>> trips | UINT32 | R | 0...4294967295
78 | I5 | DOC4 | Idir>>>> blocks | UINT32 | R | 0...4294967295
78 | S2 | DOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
78 | S3 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S4 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S5 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S6 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S7 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S8 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S9 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S10 | DOC4 | Characteristic direction | UINT32 | RW | 0=Directional;1=NonDir
78 | S11 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S12 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S13 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S14 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S15 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S16 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S17 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S18 | DOC4 | Operating sector size (+/-) | FLOAT | RW | 1...170
78 | S19 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S20 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S21 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S22 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S23 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S24 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S25 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S26 | DOC4 | Operating sector center | FLOAT | RW | -180...180
78 | S27 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S28 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S29 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S30 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S31 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S32 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S33 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S34 | DOC4 | Pick-up setting Iset | FLOAT | RW | 0.1...40
78 | S35 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S36 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S37 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S38 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S39 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S40 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S41 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S42 | DOC4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
78 | S43 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S44 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S45 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S46 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S47 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S48 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S49 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S50 | DOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
78 | S51 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S52 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S53 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S54 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S55 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S56 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S57 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | S58 | DOC4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
78 | O1 | DOC4 | Idir>>>> START | SIGNAL_OUT | RW | 0...4294967295
78 | O2 | DOC4 | Idir>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
78 | O3 | DOC4 | Idir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
78 | S59 | DOC4 | Clear registers | UINT32 | W | 0=-;1=Clear
78 | I6 | DOC4 | Newest Register | UINT32 | R | 0...12
78 | I7 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I8 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I9 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I10 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I11 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I12 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I13 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I14 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I15 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I16 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I17 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I18 | DOC4 | Phase A fault current | FLOAT | R | 0...250
78 | I19 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I20 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I21 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I22 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I23 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I24 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I25 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I26 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I27 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I28 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I29 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I30 | DOC4 | Phase B fault current | FLOAT | R | 0...250
78 | I31 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I32 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I33 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I34 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I35 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I36 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I37 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I38 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I39 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I40 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I41 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I42 | DOC4 | Phase C fault current | FLOAT | R | 0...250
78 | I43 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I44 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I45 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I46 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I47 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I48 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I49 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I50 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I51 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I52 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I53 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | I54 | DOC4 | Operating angle | FLOAT | R | -360.00...360.00
78 | S60 | DOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
78 | S61 | DOC4 | EventMaskHi | UINT32 | RW | 0...4294967295
26 | S1 | NEF1 | I0> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
26 | S2 | NEF1 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
26 | V1 | NEF1 | I0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
26 | I1 | NEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
26 | I2 | NEF1 | I0> starts | UINT32 | R | 0...4294967295
26 | I3 | NEF1 | I0> trips | UINT32 | R | 0...4294967295
26 | I4 | NEF1 | I0> blocks | UINT32 | R | 0...4294967295
26 | S3 | NEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
26 | S4 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S5 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S6 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S7 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S8 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S9 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S10 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S11 | NEF1 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
26 | S12 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S13 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S14 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S15 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S16 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S17 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S18 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S19 | NEF1 | Delay type | UINT32 | RW | 0=DT;1=IDMT
26 | S20 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S21 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S22 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S23 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S24 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S25 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S26 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S27 | NEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
26 | S28 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S29 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S30 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S31 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S32 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S33 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S34 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | S35 | NEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
26 | O1 | NEF1 | I0> START | SIGNAL_OUT | RW | 0...4294967295
26 | O2 | NEF1 | I0> TRIP | SIGNAL_OUT | RW | 0...4294967295
26 | O3 | NEF1 | I0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
26 | I5 | NEF1 | Newest Register | UINT32 | R | 0...12
26 | I6 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I7 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I8 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I9 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I10 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I11 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I12 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I13 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I14 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I15 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I16 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | I17 | NEF1 | I0 Fault current | FLOAT | R | 0...250
26 | S36 | NEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
27 | S1 | NEF2 | I0>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
27 | S2 | NEF2 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
27 | V1 | NEF2 | I0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
27 | I1 | NEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
27 | I2 | NEF2 | I0>> starts | UINT32 | R | 0...4294967295
27 | I3 | NEF2 | I0>> trips | UINT32 | R | 0...4294967295
27 | I4 | NEF2 | I0>> blocks | UINT32 | R | 0...4294967295
27 | S3 | NEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
27 | S4 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S5 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S6 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S7 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S8 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S9 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S10 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S11 | NEF2 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
27 | S12 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S13 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S14 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S15 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S16 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S17 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S18 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S19 | NEF2 | Delay type | UINT32 | RW | 0=DT;1=IDMT
27 | S20 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S21 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S22 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S23 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S24 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S25 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S26 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S27 | NEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
27 | S28 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S29 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S30 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S31 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S32 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S33 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S34 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | S35 | NEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
27 | O1 | NEF2 | I0>> START | SIGNAL_OUT | RW | 0...4294967295
27 | O2 | NEF2 | I0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
27 | O3 | NEF2 | I0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
27 | I5 | NEF2 | Newest Register | UINT32 | R | 0...12
27 | I6 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I7 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I8 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I9 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I10 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I11 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I12 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I13 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I14 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I15 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I16 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | I17 | NEF2 | I0 Fault current | FLOAT | R | 0...250
27 | S36 | NEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
28 | S1 | NEF3 | I0>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
28 | S2 | NEF3 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
28 | V1 | NEF3 | I0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
28 | I1 | NEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
28 | I2 | NEF3 | I0>>> starts | UINT32 | R | 0...4294967295
28 | I3 | NEF3 | I0>>> trips | UINT32 | R | 0...4294967295
28 | I4 | NEF3 | I0>>> blocks | UINT32 | R | 0...4294967295
28 | S3 | NEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
28 | S4 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S5 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S6 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S7 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S8 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S9 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S10 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S11 | NEF3 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
28 | S12 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S13 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S14 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S15 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S16 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S17 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S18 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S19 | NEF3 | Delay type | UINT32 | RW | 0=DT;1=IDMT
28 | S20 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S21 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S22 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S23 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S24 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S25 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S26 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S27 | NEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
28 | S28 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S29 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S30 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S31 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S32 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S33 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S34 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | S35 | NEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
28 | O1 | NEF3 | I0>>> START | SIGNAL_OUT | RW | 0...4294967295
28 | O2 | NEF3 | I0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
28 | O3 | NEF3 | I0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
28 | I5 | NEF3 | Newest Register | UINT32 | R | 0...12
28 | I6 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I7 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I8 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I9 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I10 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I11 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I12 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I13 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I14 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I15 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I16 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | I17 | NEF3 | I0 Fault current | FLOAT | R | 0...250
28 | S36 | NEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
29 | S1 | NEF4 | I0>>>> [50N/51N] mode | UINT32 | RW | 0=Disabled;1=Activated
29 | S2 | NEF4 | I> Setting control from comm bus | UINT32 | RW | 0=Disabled;1=Allowed
29 | V1 | NEF4 | I0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
29 | I1 | NEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
29 | I2 | NEF4 | I0>>>> starts | UINT32 | R | 0...4294967295
29 | I3 | NEF4 | I0>>>> trips | UINT32 | R | 0...4294967295
29 | I4 | NEF4 | I0>>>> blocks | UINT32 | R | 0...4294967295
29 | S3 | NEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
29 | S4 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S5 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S6 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S7 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S8 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S9 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S10 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S11 | NEF4 | Pick-up setting I0set | FLOAT | RW | 0.0001...40
29 | S12 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S13 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S14 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S15 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S16 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S17 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S18 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S19 | NEF4 | Delay type | UINT32 | RW | 0=DT;1=IDMT
29 | S20 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S21 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S22 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S23 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S24 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S25 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S26 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S27 | NEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
29 | S28 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S29 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S30 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S31 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S32 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S33 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S34 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | S35 | NEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
29 | O1 | NEF4 | I0>>>> START | SIGNAL_OUT | RW | 0...4294967295
29 | O2 | NEF4 | I0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
29 | O3 | NEF4 | I0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
29 | I5 | NEF4 | Newest Register | UINT32 | R | 0...12
29 | I6 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I7 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I8 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I9 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I10 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I11 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I12 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I13 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I14 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I15 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I16 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | I17 | NEF4 | I0 Fault current | FLOAT | R | 0...250
29 | S36 | NEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | S1 | DEF1 | I0dir> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
81 | V1 | DEF1 | I0dir> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
81 | I1 | DEF1 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
81 | I2 | DEF1 | I0 Magnitude | FLOAT | R | 0...250
81 | I3 | DEF1 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
81 | I4 | DEF1 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
81 | I5 | DEF1 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
81 | I6 | DEF1 | DEF(1) Measured residual current change | FLOAT | R | 0...250
81 | I7 | DEF1 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
81 | I8 | DEF1 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
81 | I9 | DEF1 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
81 | I10 | DEF1 | I0 meas / I0 set now | FLOAT | R | -250...250
81 | I11 | DEF1 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
81 | I12 | DEF1 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
81 | I13 | DEF1 | U0 meas now | FLOAT | R | 0...500
81 | I14 | DEF1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
81 | I15 | DEF1 | I0dir> starts | UINT32 | R | 0...4294967295
81 | I16 | DEF1 | I0dir> trips | UINT32 | R | 0...4294967295
81 | I17 | DEF1 | I0dir> blocks | UINT32 | R | 0...4294967295
81 | S2 | DEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
81 | S3 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S4 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S5 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S6 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S7 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S8 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S9 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S10 | DEF1 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
81 | S11 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S12 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S13 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S14 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S15 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S16 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S17 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S18 | DEF1 | Pick-up setting I0set> | FLOAT | RW | 0.005...40
81 | S19 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S20 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S21 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S22 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S23 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S24 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S25 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S26 | DEF1 | Pick-up setting U0set> | FLOAT | RW | 1...75
81 | S27 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S28 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S29 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S30 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S31 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S32 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S33 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S34 | DEF1 | Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
81 | S35 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S36 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S37 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S38 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S39 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S40 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S41 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S42 | DEF1 | Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
81 | S43 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S44 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S45 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S46 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S47 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S48 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S49 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S50 | DEF1 | Unearthed / Compensated border angle (0 = not in use) | FLOAT | RW | -45...90
81 | S51 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S52 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S53 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S54 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S55 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S56 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S57 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S58 | DEF1 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
81 | S59 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S60 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S61 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S62 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S63 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S64 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S65 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S66 | DEF1 | Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
81 | S67 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S68 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S69 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S70 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S71 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S72 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S73 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S74 | DEF1 | Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
81 | S75 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S76 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S77 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S78 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S79 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S80 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S81 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S82 | DEF1 | Trip area size (+/-) | FLOAT | RW | 5...135
81 | S83 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S84 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S85 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S86 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S87 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S88 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S89 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S90 | DEF1 | Trip area center | FLOAT | RW | -360...360
81 | S91 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S92 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S93 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S94 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S95 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S96 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S97 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S98 | DEF1 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
81 | S99 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S100 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S101 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S102 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S103 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S104 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S105 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S106 | DEF1 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
81 | S107 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S108 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S109 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S110 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S111 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S112 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S113 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S114 | DEF1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
81 | S115 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S116 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S117 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S118 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S119 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S120 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S121 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | S122 | DEF1 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
81 | O1 | DEF1 | I0dir> START (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O2 | DEF1 | I0dir> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
81 | O3 | DEF1 | I0dir> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O4 | DEF1 | I0dir> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
81 | O5 | DEF1 | I0dir> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O6 | DEF1 | I0dir> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
81 | O7 | DEF1 | I0dir> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
81 | I18 | DEF1 | Newest Register | UINT32 | R | 0...12
81 | I19 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I20 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I21 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I22 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I23 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I24 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I25 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I26 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I27 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I28 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I29 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I30 | DEF1 | I0 Fault current | FLOAT | R | 0...250
81 | I31 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I32 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I33 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I34 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I35 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I36 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I37 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I38 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I39 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I40 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I41 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I42 | DEF1 | Fault Capacit I0 | FLOAT | R | -250...250
81 | I43 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I44 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I45 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I46 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I47 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I48 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I49 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I50 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I51 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I52 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I53 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I54 | DEF1 | Fault Resist I0 | FLOAT | R | -250...250
81 | I55 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I56 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I57 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I58 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I59 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I60 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I61 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I62 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I63 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I64 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I65 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I66 | DEF1 | Fault U0(%) | FLOAT | R | 0...500
81 | I67 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I68 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I69 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I70 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I71 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I72 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I73 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I74 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I75 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I76 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I77 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I78 | DEF1 | I0(U0) Fault angle | FLOAT | R | -360...360
81 | I79 | DEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
81 | I80 | DEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
82 | S1 | DEF2 | I0dir>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
82 | V1 | DEF2 | I0dir>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
82 | I1 | DEF2 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
82 | I2 | DEF2 | I0 Magnitude | FLOAT | R | 0...250
82 | I3 | DEF2 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
82 | I4 | DEF2 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
82 | I5 | DEF2 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
82 | I6 | DEF2 | DEF(1) Measured residual current change | FLOAT | R | 0...250
82 | I7 | DEF2 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
82 | I8 | DEF2 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
82 | I9 | DEF2 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
82 | I10 | DEF2 | I0 meas / I0 set now | FLOAT | R | -250...250
82 | I11 | DEF2 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
82 | I12 | DEF2 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
82 | I13 | DEF2 | U0 meas now | FLOAT | R | 0...500
82 | I14 | DEF2 | Imeas/Iset at the moment | FLOAT | R | 0...1250
82 | I15 | DEF2 | I0dir>> starts | UINT32 | R | 0...4294967295
82 | I16 | DEF2 | I0dir>> trips | UINT32 | R | 0...4294967295
82 | I17 | DEF2 | I0dir>> blocks | UINT32 | R | 0...4294967295
82 | S2 | DEF2 | Clear statistics | UINT32 | W | 0=-;1=Clear
82 | S3 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S4 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S5 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S6 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S7 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S8 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S9 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S10 | DEF2 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
82 | S11 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S12 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S13 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S14 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S15 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S16 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S17 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S18 | DEF2 | Pick-up setting I0set>> | FLOAT | RW | 0.005...40
82 | S19 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S20 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S21 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S22 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S23 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S24 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S25 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S26 | DEF2 | Pick-up setting U0set>> | FLOAT | RW | 1...75
82 | S27 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S28 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S29 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S30 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S31 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S32 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S33 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S34 | DEF2 | Comp. Pick-up setting I0set (I0Cosfi)>> | FLOAT | RW | 0.005...40
82 | S35 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S36 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S37 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S38 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S39 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S40 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S41 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S42 | DEF2 | Comp. Pick-up setting U0set(I0Cosfi)>> | FLOAT | RW | 1...75
82 | S43 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S44 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S45 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S46 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S47 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S48 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S49 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S50 | DEF2 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
82 | S51 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S52 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S53 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S54 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S55 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S56 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S57 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S58 | DEF2 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
82 | S59 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S60 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S61 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S62 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S63 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S64 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S65 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S66 | DEF2 | Unearth. Pick-up setting I0set (I0Sinfi)>> | FLOAT | RW | 0.005...40
82 | S67 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S68 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S69 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S70 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S71 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S72 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S73 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S74 | DEF2 | Unearth. Pick-up setting U0set(I0Sinfi)>> | FLOAT | RW | 1...75
82 | S75 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S76 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S77 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S78 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S79 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S80 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S81 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S82 | DEF2 | Trip area size (+/-) | FLOAT | RW | 5...135
82 | S83 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S84 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S85 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S86 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S87 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S88 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S89 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S90 | DEF2 | Trip area center | FLOAT | RW | -360...360
82 | S91 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S92 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S93 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S94 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S95 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S96 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S97 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S98 | DEF2 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
82 | S99 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S100 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S101 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S102 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S103 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S104 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S105 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S106 | DEF2 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
82 | S107 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S108 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S109 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S110 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S111 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S112 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S113 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S114 | DEF2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
82 | S115 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S116 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S117 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S118 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S119 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S120 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S121 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | S122 | DEF2 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
82 | O1 | DEF2 | I0dir>> START (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O2 | DEF2 | I0dir>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
82 | O3 | DEF2 | I0dir>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O4 | DEF2 | I0dir>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
82 | O5 | DEF2 | I0dir>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O6 | DEF2 | I0dir>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
82 | O7 | DEF2 | I0dir>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
82 | I18 | DEF2 | Newest Register | UINT32 | R | 0...12
82 | I19 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I20 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I21 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I22 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I23 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I24 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I25 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I26 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I27 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I28 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I29 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I30 | DEF2 | I0 Fault current | FLOAT | R | 0...250
82 | I31 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I32 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I33 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I34 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I35 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I36 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I37 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I38 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I39 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I40 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I41 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I42 | DEF2 | Fault Capacit I0 | FLOAT | R | -250...250
82 | I43 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I44 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I45 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I46 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I47 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I48 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I49 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I50 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I51 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I52 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I53 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I54 | DEF2 | Fault Resist I0 | FLOAT | R | -250...250
82 | I55 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I56 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I57 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I58 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I59 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I60 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I61 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I62 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I63 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I64 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I65 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I66 | DEF2 | Fault U0(%) | FLOAT | R | 0...500
82 | I67 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I68 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I69 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I70 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I71 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I72 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I73 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I74 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I75 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I76 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I77 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I78 | DEF2 | I0(U0) Fault angle | FLOAT | R | -360...360
82 | I79 | DEF2 | EventMaskLo | UINT32 | RW | 0...4294967295
82 | I80 | DEF2 | EventMaskHi | UINT32 | RW | 0...4294967295
83 | S1 | DEF3 | I0dir>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
83 | V1 | DEF3 | I0dir>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
83 | I1 | DEF3 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
83 | I2 | DEF3 | I0 Magnitude | FLOAT | R | 0...250
83 | I3 | DEF3 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
83 | I4 | DEF3 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
83 | I5 | DEF3 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
83 | I6 | DEF3 | DEF(1) Measured residual current change | FLOAT | R | 0...250
83 | I7 | DEF3 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
83 | I8 | DEF3 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
83 | I9 | DEF3 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
83 | I10 | DEF3 | I0 meas / I0 set now | FLOAT | R | -250...250
83 | I11 | DEF3 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
83 | I12 | DEF3 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
83 | I13 | DEF3 | U0 meas now | FLOAT | R | 0...500
83 | I14 | DEF3 | Imeas/Iset at the moment | FLOAT | R | 0...1250
83 | I15 | DEF3 | I0dir>>> starts | UINT32 | R | 0...4294967295
83 | I16 | DEF3 | I0dir>>> trips | UINT32 | R | 0...4294967295
83 | I17 | DEF3 | I0dir>>> blocks | UINT32 | R | 0...4294967295
83 | S2 | DEF3 | Clear statistics | UINT32 | W | 0=-;1=Clear
83 | S3 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S4 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S5 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S6 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S7 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S8 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S9 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S10 | DEF3 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
83 | S11 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S12 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S13 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S14 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S15 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S16 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S17 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S18 | DEF3 | Pick-up setting I0set>>> | FLOAT | RW | 0.005...40
83 | S19 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S20 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S21 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S22 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S23 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S24 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S25 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S26 | DEF3 | Pick-up setting U0set>>> | FLOAT | RW | 1...75
83 | S27 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S28 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S29 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S30 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S31 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S32 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S33 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S34 | DEF3 | Comp. Pick-up setting I0set (I0Cosfi)>>> | FLOAT | RW | 0.005...40
83 | S35 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S36 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S37 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S38 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S39 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S40 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S41 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S42 | DEF3 | Comp. Pick-up setting U0set(I0Cosfi)>>> | FLOAT | RW | 1...75
83 | S43 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S44 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S45 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S46 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S47 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S48 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S49 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S50 | DEF3 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
83 | S51 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S52 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S53 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S54 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S55 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S56 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S57 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S58 | DEF3 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
83 | S59 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S60 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S61 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S62 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S63 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S64 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S65 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S66 | DEF3 | Unearth. Pick-up setting I0set (I0Sinfi)>>> | FLOAT | RW | 0.005...40
83 | S67 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S68 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S69 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S70 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S71 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S72 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S73 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S74 | DEF3 | Unearth. Pick-up setting U0set(I0Sinfi)>>> | FLOAT | RW | 1...75
83 | S75 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S76 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S77 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S78 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S79 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S80 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S81 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S82 | DEF3 | Trip area size (+/-) | FLOAT | RW | 5...135
83 | S83 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S84 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S85 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S86 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S87 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S88 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S89 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S90 | DEF3 | Trip area center | FLOAT | RW | -360...360
83 | S91 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S92 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S93 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S94 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S95 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S96 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S97 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S98 | DEF3 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
83 | S99 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S100 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S101 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S102 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S103 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S104 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S105 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S106 | DEF3 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
83 | S107 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S108 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S109 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S110 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S111 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S112 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S113 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S114 | DEF3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
83 | S115 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S116 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S117 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S118 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S119 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S120 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S121 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | S122 | DEF3 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
83 | O1 | DEF3 | I0dir>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O2 | DEF3 | I0dir>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
83 | O3 | DEF3 | I0dir>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O4 | DEF3 | I0dir>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
83 | O5 | DEF3 | I0dir>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O6 | DEF3 | I0dir>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
83 | O7 | DEF3 | I0dir>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
83 | I18 | DEF3 | Newest Register | UINT32 | R | 0...12
83 | I19 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I20 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I21 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I22 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I23 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I24 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I25 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I26 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I27 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I28 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I29 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I30 | DEF3 | I0 Fault current | FLOAT | R | 0...250
83 | I31 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I32 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I33 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I34 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I35 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I36 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I37 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I38 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I39 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I40 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I41 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I42 | DEF3 | Fault Capacit I0 | FLOAT | R | -250...250
83 | I43 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I44 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I45 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I46 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I47 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I48 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I49 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I50 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I51 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I52 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I53 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I54 | DEF3 | Fault Resist I0 | FLOAT | R | -250...250
83 | I55 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I56 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I57 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I58 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I59 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I60 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I61 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I62 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I63 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I64 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I65 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I66 | DEF3 | Fault U0(%) | FLOAT | R | 0...500
83 | I67 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I68 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I69 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I70 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I71 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I72 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I73 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I74 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I75 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I76 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I77 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I78 | DEF3 | I0(U0) Fault angle | FLOAT | R | -360...360
83 | I79 | DEF3 | EventMaskLo | UINT32 | RW | 0...4294967295
83 | I80 | DEF3 | EventMaskHi | UINT32 | RW | 0...4294967295
84 | S1 | DEF4 | I0dir>>>> [67N/32N] mode | UINT32 | RW | 0=Disabled;1=Activated
84 | V1 | DEF4 | I0dir>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
84 | I1 | DEF4 | Detected U0I0 angle (fi) | FLOAT | R | -360...360
84 | I2 | DEF4 | I0 Magnitude | FLOAT | R | 0...250
84 | I3 | DEF4 | I0 Wattmetric I0xCos(fi) | FLOAT | R | -250...250
84 | I4 | DEF4 | I0 Varmetric I0xSin(fi) | FLOAT | R | -250...250
84 | I5 | DEF4 | DEF(1) Measured unbalance change | FLOAT | R | 0...250
84 | I6 | DEF4 | DEF(1) Measured residual current change | FLOAT | R | 0...250
84 | I7 | DEF4 | DEF(1) Measured admittance mag change | FLOAT | R | 0...250
84 | I8 | DEF4 | DEF(1) Measured admittance angle change | FLOAT | R | 0...250
84 | I9 | DEF4 | I0 Direction now | UINT32 | R | 0=Reverse;1=Forward;2=Undefined;
84 | I10 | DEF4 | I0 meas / I0 set now | FLOAT | R | -250...250
84 | I11 | DEF4 | I0 meas / I0 set now (Compensated) | FLOAT | R | -250...250
84 | I12 | DEF4 | I0 meas / I0 set now (Unearthed) | FLOAT | R | -250...250
84 | I13 | DEF4 | U0 meas now | FLOAT | R | 0...500
84 | I14 | DEF4 | Imeas/Iset at the moment | FLOAT | R | 0...1250
84 | I15 | DEF4 | I0dir>>>> starts | UINT32 | R | 0...4294967295
84 | I16 | DEF4 | I0dir>>>> trips | UINT32 | R | 0...4294967295
84 | I17 | DEF4 | I0dir>>>> blocks | UINT32 | R | 0...4294967295
84 | S2 | DEF4 | Clear statistics | UINT32 | W | 0=-;1=Clear
84 | S3 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S4 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S5 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S6 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S7 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S8 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S9 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S10 | DEF4 | Grounding type | UINT32 | RW | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
84 | S11 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S12 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S13 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S14 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S15 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S16 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S17 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S18 | DEF4 | Pick-up setting I0set>>>> | FLOAT | RW | 0.005...40
84 | S19 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S20 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S21 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S22 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S23 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S24 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S25 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S26 | DEF4 | Pick-up setting U0set>>>> | FLOAT | RW | 1...75
84 | S27 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S28 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S29 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S30 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S31 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S32 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S33 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S34 | DEF4 | Comp. Pick-up setting I0set (I0Cosfi)>>>> | FLOAT | RW | 0.005...40
84 | S35 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S36 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S37 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S38 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S39 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S40 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S41 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S42 | DEF4 | Comp. Pick-up setting U0set(I0Cosfi)>>>> | FLOAT | RW | 1...75
84 | S43 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S44 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S45 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S46 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S47 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S48 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S49 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S50 | DEF4 | Unearthed / Compensated border angle | FLOAT | RW | -45...90
84 | S51 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S52 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S53 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S54 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S55 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S56 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S57 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S58 | DEF4 | Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
84 | S59 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S60 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S61 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S62 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S63 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S64 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S65 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S66 | DEF4 | Unearth. Pick-up setting I0set (I0Sinfi)>>>> | FLOAT | RW | 0.005...40
84 | S67 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S68 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S69 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S70 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S71 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S72 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S73 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S74 | DEF4 | Unearth. Pick-up setting U0set(I0Sinfi)>>>> | FLOAT | RW | 1...75
84 | S75 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S76 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S77 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S78 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S79 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S80 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S81 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S82 | DEF4 | Trip area size (+/-) | FLOAT | RW | 5...135
84 | S83 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S84 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S85 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S86 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S87 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S88 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S89 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S90 | DEF4 | Trip area center | FLOAT | RW | -360...360
84 | S91 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S92 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S93 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S94 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S95 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S96 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S97 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S98 | DEF4 | Definite operating time delay(Compensated) | FLOAT | RW | 0...1800
84 | S99 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S100 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S101 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S102 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S103 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S104 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S105 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S106 | DEF4 | Definite operating time delay(Unearthed) | FLOAT | RW | 0...1800
84 | S107 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S108 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S109 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S110 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S111 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S112 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S113 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S114 | DEF4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
84 | S115 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S116 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S117 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S118 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S119 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S120 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S121 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | S122 | DEF4 | 2.nd Harmonic Block Limit (Iharm / Ifund) | FLOAT | RW | 0.1...50
84 | O1 | DEF4 | I0dir>>>> START (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O2 | DEF4 | I0dir>>>> TRIP (General) | SIGNAL_OUT | RW | 0...4294967295
84 | O3 | DEF4 | I0dir>>>> START (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O4 | DEF4 | I0dir>>>> TRIP (Unearthed) | SIGNAL_OUT | RW | 0...4294967295
84 | O5 | DEF4 | I0dir>>>> START (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O6 | DEF4 | I0dir>>>> TRIP (Compensated) | SIGNAL_OUT | RW | 0...4294967295
84 | O7 | DEF4 | I0dir>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
84 | I18 | DEF4 | Newest Register | UINT32 | R | 0...12
84 | I19 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I20 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I21 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I22 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I23 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I24 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I25 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I26 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I27 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I28 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I29 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I30 | DEF4 | I0 Fault current | FLOAT | R | 0...250
84 | I31 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I32 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I33 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I34 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I35 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I36 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I37 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I38 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I39 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I40 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I41 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I42 | DEF4 | Fault Capacit I0 | FLOAT | R | -250...250
84 | I43 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I44 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I45 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I46 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I47 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I48 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I49 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I50 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I51 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I52 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I53 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I54 | DEF4 | Fault Resist I0 | FLOAT | R | -250...250
84 | I55 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I56 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I57 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I58 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I59 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I60 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I61 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I62 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I63 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I64 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I65 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I66 | DEF4 | Fault U0(%) | FLOAT | R | 0...500
84 | I67 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I68 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I69 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I70 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I71 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I72 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I73 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I74 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I75 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I76 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I77 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I78 | DEF4 | I0(U0) Fault angle | FLOAT | R | -360...360
84 | I79 | DEF4 | EventMaskLo | UINT32 | RW | 0...4294967295
84 | I80 | DEF4 | EventMaskHi | UINT32 | RW | 0...4294967295
114 | S1 | IEF1 | I0Int> [67NT] mode | UINT32 | RW | 0=Disabled;1=Activated
114 | V1 | IEF1 | I0Int> condition | UINT32 | R | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
114 | I1 | IEF1 | Spikes needed for trip > | UINT32 | R | 0...4294967295
114 | I2 | IEF1 | I0Int> starts FWD | UINT32 | R | 0...4294967295
114 | I3 | IEF1 | I0Int> starts REV | UINT32 | R | 0...4294967295
114 | I4 | IEF1 | I0Int> trips | UINT32 | R | 0...4294967295
114 | I5 | IEF1 | I0Int> blocks | UINT32 | R | 0...4294967295
114 | S2 | IEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
114 | S3 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S4 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S5 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S6 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S7 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S8 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S9 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S10 | IEF1 | U0 Detect spike > | FLOAT | RW | 1...100
114 | S11 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S12 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S13 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S14 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S15 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S16 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S17 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S18 | IEF1 | I0 Detect spike > | FLOAT | RW | 0.05...40
114 | S19 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S20 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S21 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S22 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S23 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S24 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S25 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S26 | IEF1 | FWD reset time | FLOAT | RW | 0...1800
114 | S27 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S28 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S29 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S30 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S31 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S32 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S33 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S34 | IEF1 | REV reset time | FLOAT | RW | 0...1800
114 | S35 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S36 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S37 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S38 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S39 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S40 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S41 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S42 | IEF1 | Definite operating time delay | FLOAT | RW | 0...1800
114 | S43 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S44 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S45 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S46 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S47 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S48 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S49 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | S50 | IEF1 | Spikes to trip > | UINT32 | RW | 1...50
114 | O1 | IEF1 | I0Int> IEF DETECTED | SIGNAL_OUT | RW | 0...4294967295
114 | O2 | IEF1 | I0Int> STARTFWD | SIGNAL_OUT | RW | 0...4294967295
114 | O3 | IEF1 | I0Int> STARTREV | SIGNAL_OUT | RW | 0...4294967295
114 | O4 | IEF1 | I0Int> TRIP | SIGNAL_OUT | RW | 0...4294967295
114 | O5 | IEF1 | I0Int> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
114 | I6 | IEF1 | Newest Register | UINT32 | R | 0...12
114 | I7 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I8 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I9 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I10 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I11 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I12 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I13 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I14 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I15 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I16 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I17 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I18 | IEF1 | Started fwd | UINT32 | R | 0=No;1=Yes
114 | I19 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I20 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I21 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I22 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I23 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I24 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I25 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I26 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I27 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I28 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I29 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I30 | IEF1 | Spikes fwd | UINT32 | R | 0...2
114 | I31 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I32 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I33 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I34 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I35 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I36 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I37 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I38 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I39 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I40 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I41 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I42 | IEF1 | Started rev | UINT32 | R | 0=No;1=Yes
114 | I43 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I44 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I45 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I46 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I47 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I48 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I49 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I50 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I51 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I52 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I53 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I54 | IEF1 | Spikes rev | UINT32 | R | 0...2
114 | I55 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I56 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I57 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I58 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I59 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I60 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I61 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I62 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I63 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I64 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I65 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | I66 | IEF1 | Spikesto trip | UINT32 | R | 0...2
114 | S51 | IEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
114 | S52 | IEF1 | EventMaskHi | UINT32 | RW | 0...4294967295
32 | S1 | CUB1 | I2> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
32 | V1 | CUB1 | I2> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
32 | I1 | CUB1 | I2> starts | UINT32 | R | 0...4294967295
32 | I2 | CUB1 | I2> trips | UINT32 | R | 0...4294967295
32 | I3 | CUB1 | I2> blocks | UINT32 | R | 0...4294967295
32 | S2 | CUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
32 | I4 | CUB1 | I2> I2I1 relation | FLOAT | R | 0...100000
32 | I5 | CUB1 | I2 meas/I2 set | FLOAT | R | 0...100000
32 | S3 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S4 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S5 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S6 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S7 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S8 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S9 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S10 | CUB1 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
32 | S11 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S12 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S13 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S14 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S15 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S16 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S17 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S18 | CUB1 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
32 | S19 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S20 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S21 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S22 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S23 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S24 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S25 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S26 | CUB1 | Minimum phase current | FLOAT | RW | 0.01...2
32 | S27 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S28 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S29 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S30 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S31 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S32 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S33 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | S34 | CUB1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
32 | O1 | CUB1 | I2> START | SIGNAL_OUT | RW | 0...4294967295
32 | O2 | CUB1 | I2> TRIP | SIGNAL_OUT | RW | 0...4294967295
32 | O3 | CUB1 | I2> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
32 | I6 | CUB1 | Newest Register | UINT32 | R | 0...12
32 | I7 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I8 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I9 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I10 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I11 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I12 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I13 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I14 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I15 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I16 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I17 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I18 | CUB1 | I2 Fault current | FLOAT | R | 0...250
32 | I19 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I20 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I21 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I22 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I23 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I24 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I25 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I26 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I27 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I28 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I29 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | I30 | CUB1 | I2/I1 Fault current | FLOAT | R | 0...250
32 | S35 | CUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
33 | S1 | CUB2 | I2>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
33 | V1 | CUB2 | I2>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
33 | I1 | CUB2 | I2>> starts | UINT32 | R | 0...4294967295
33 | I2 | CUB2 | I2>> trips | UINT32 | R | 0...4294967295
33 | I3 | CUB2 | I2>> blocks | UINT32 | R | 0...4294967295
33 | S2 | CUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
33 | I4 | CUB2 | I2>> I2I1 relation | FLOAT | R | 0...100000
33 | I5 | CUB2 | I2 meas/I2 set | FLOAT | R | 0...100000
33 | S3 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S4 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S5 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S6 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S7 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S8 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S9 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S10 | CUB2 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
33 | S11 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S12 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S13 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S14 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S15 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S16 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S17 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S18 | CUB2 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
33 | S19 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S20 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S21 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S22 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S23 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S24 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S25 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S26 | CUB2 | Minimum phase current | FLOAT | RW | 0.01...2
33 | S27 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S28 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S29 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S30 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S31 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S32 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S33 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | S34 | CUB2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
33 | O1 | CUB2 | I2>> START | SIGNAL_OUT | RW | 0...4294967295
33 | O2 | CUB2 | I2>> TRIP | SIGNAL_OUT | RW | 0...4294967295
33 | O3 | CUB2 | I2>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
33 | I6 | CUB2 | Newest Register | UINT32 | R | 0...12
33 | I7 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I8 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I9 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I10 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I11 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I12 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I13 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I14 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I15 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I16 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I17 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I18 | CUB2 | I2 Fault current | FLOAT | R | 0...250
33 | I19 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I20 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I21 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I22 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I23 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I24 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I25 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I26 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I27 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I28 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I29 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | I30 | CUB2 | I2/I1 Fault current | FLOAT | R | 0...250
33 | S35 | CUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
34 | S1 | CUB3 | I2>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
34 | V1 | CUB3 | I2>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
34 | I1 | CUB3 | I2>>> starts | UINT32 | R | 0...4294967295
34 | I2 | CUB3 | I2>>> trips | UINT32 | R | 0...4294967295
34 | I3 | CUB3 | I2>>> blocks | UINT32 | R | 0...4294967295
34 | S2 | CUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
34 | I4 | CUB3 | I2>>> I2I1 relation | FLOAT | R | 0...100000
34 | I5 | CUB3 | I2 meas/I2 set | FLOAT | R | 0...100000
34 | S3 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S4 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S5 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S6 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S7 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S8 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S9 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S10 | CUB3 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
34 | S11 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S12 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S13 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S14 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S15 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S16 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S17 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S18 | CUB3 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
34 | S19 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S20 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S21 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S22 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S23 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S24 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S25 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S26 | CUB3 | Minimum phase current | FLOAT | RW | 0.01...2
34 | S27 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S28 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S29 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S30 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S31 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S32 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S33 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | S34 | CUB3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
34 | O1 | CUB3 | I2>>> START | SIGNAL_OUT | RW | 0...4294967295
34 | O2 | CUB3 | I2>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
34 | O3 | CUB3 | I2>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
34 | I6 | CUB3 | Newest Register | UINT32 | R | 0...12
34 | I7 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I8 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I9 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I10 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I11 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I12 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I13 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I14 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I15 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I16 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I17 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I18 | CUB3 | I2 Fault current | FLOAT | R | 0...250
34 | I19 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I20 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I21 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I22 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I23 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I24 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I25 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I26 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I27 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I28 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I29 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | I30 | CUB3 | I2/I1 Fault current | FLOAT | R | 0...250
34 | S35 | CUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
35 | S1 | CUB4 | I2>>>> [46] mode | UINT32 | RW | 0=Disabled;1=Activated
35 | V1 | CUB4 | I2>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
35 | I1 | CUB4 | I2>>>> starts | UINT32 | R | 0...4294967295
35 | I2 | CUB4 | I2>>>> trips | UINT32 | R | 0...4294967295
35 | I3 | CUB4 | I2>>>> blocks | UINT32 | R | 0...4294967295
35 | S2 | CUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
35 | I4 | CUB4 | I2>>>> I2I1 relation | FLOAT | R | 0...100000
35 | I5 | CUB4 | I2 meas/I2 set | FLOAT | R | 0...100000
35 | S3 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S4 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S5 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S6 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S7 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S8 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S9 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S10 | CUB4 | Pick-up setting I2set pu | FLOAT | RW | 0.01...40
35 | S11 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S12 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S13 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S14 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S15 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S16 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S17 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S18 | CUB4 | Pick-up setting I2/I1 | FLOAT | RW | 1...200
35 | S19 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S20 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S21 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S22 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S23 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S24 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S25 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S26 | CUB4 | Minimum phase current | FLOAT | RW | 0.01...2
35 | S27 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S28 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S29 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S30 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S31 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S32 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S33 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | S34 | CUB4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
35 | O1 | CUB4 | I2>>>> START | SIGNAL_OUT | RW | 0...4294967295
35 | O2 | CUB4 | I2>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
35 | O3 | CUB4 | I2>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
35 | I6 | CUB4 | Newest Register | UINT32 | R | 0...12
35 | I7 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I8 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I9 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I10 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I11 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I12 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I13 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I14 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I15 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I16 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I17 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I18 | CUB4 | I2 Fault current | FLOAT | R | 0...250
35 | I19 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I20 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I21 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I22 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I23 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I24 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I25 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I26 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I27 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I28 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I29 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | I30 | CUB4 | I2/I1 Fault current | FLOAT | R | 0...250
35 | S35 | CUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
37 | S1 | HOC1 | Ih> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
37 | V1 | HOC1 | Ih> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
37 | I1 | HOC1 | Ih> starts | UINT32 | R | 0...4294967295
37 | I2 | HOC1 | Ih> trips | UINT32 | R | 0...4294967295
37 | I3 | HOC1 | Ih> blocks | UINT32 | R | 0...4294967295
37 | S2 | HOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
37 | I4 | HOC1 | Ih meas/ Ih set | FLOAT | R | 0...100000
37 | S3 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S4 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S5 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S6 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S7 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S8 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S9 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S10 | HOC1 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
37 | S11 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S12 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S13 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S14 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S15 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S16 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S17 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S18 | HOC1 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
37 | S19 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S20 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S21 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S22 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S23 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S24 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S25 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S26 | HOC1 | Minimum phase current | FLOAT | RW | 0.01...40
37 | S27 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S28 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S29 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S30 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S31 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S32 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S33 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | S34 | HOC1 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
37 | O1 | HOC1 | Ih> START | SIGNAL_OUT | RW | 0...4294967295
37 | O2 | HOC1 | Ih> TRIP | SIGNAL_OUT | RW | 0...4294967295
37 | O3 | HOC1 | Ih> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
37 | I5 | HOC1 | Newest Register | UINT32 | R | 0...12
37 | I6 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I7 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I8 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I9 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I10 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I11 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I12 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I13 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I14 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I15 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I16 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I17 | HOC1 | L1h Fault current | FLOAT | R | 0...250
37 | I18 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I19 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I20 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I21 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I22 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I23 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I24 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I25 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I26 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I27 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I28 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I29 | HOC1 | L2h Fault current | FLOAT | R | 0...250
37 | I30 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I31 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I32 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I33 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I34 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I35 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I36 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I37 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I38 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I39 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I40 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I41 | HOC1 | L3h Fault current | FLOAT | R | 0...250
37 | I42 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I43 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I44 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I45 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I46 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I47 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I48 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I49 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I50 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I51 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I52 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I53 | HOC1 | I01h Fault current | FLOAT | R | 0...250
37 | I54 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I55 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I56 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I57 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I58 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I59 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I60 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I61 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I62 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I63 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I64 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | I65 | HOC1 | I02h Fault current | FLOAT | R | 0...250
37 | S35 | HOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
38 | S1 | HOC2 | Ih>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
38 | V1 | HOC2 | Ih>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
38 | I1 | HOC2 | Ih>> starts | UINT32 | R | 0...4294967295
38 | I2 | HOC2 | Ih>> trips | UINT32 | R | 0...4294967295
38 | I3 | HOC2 | Ih>> blocks | UINT32 | R | 0...4294967295
38 | S2 | HOC2 | Clear statistics | UINT32 | W | 0=-;1=Clear
38 | I4 | HOC2 | Ih meas/ Ih set | FLOAT | R | 0...100000
38 | S3 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S4 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S5 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S6 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S7 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S8 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S9 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S10 | HOC2 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
38 | S11 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S12 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S13 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S14 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S15 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S16 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S17 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S18 | HOC2 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
38 | S19 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S20 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S21 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S22 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S23 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S24 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S25 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S26 | HOC2 | Minimum phase current | FLOAT | RW | 0.01...40
38 | S27 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S28 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S29 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S30 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S31 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S32 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S33 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | S34 | HOC2 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
38 | O1 | HOC2 | Ih>> START | SIGNAL_OUT | RW | 0...4294967295
38 | O2 | HOC2 | Ih>> TRIP | SIGNAL_OUT | RW | 0...4294967295
38 | O3 | HOC2 | Ih>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
38 | I5 | HOC2 | Newest Register | UINT32 | R | 0...12
38 | I6 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I7 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I8 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I9 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I10 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I11 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I12 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I13 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I14 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I15 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I16 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I17 | HOC2 | L1h Fault current | FLOAT | R | 0...250
38 | I18 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I19 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I20 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I21 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I22 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I23 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I24 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I25 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I26 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I27 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I28 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I29 | HOC2 | L2h Fault current | FLOAT | R | 0...250
38 | I30 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I31 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I32 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I33 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I34 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I35 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I36 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I37 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I38 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I39 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I40 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I41 | HOC2 | L3h Fault current | FLOAT | R | 0...250
38 | I42 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I43 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I44 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I45 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I46 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I47 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I48 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I49 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I50 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I51 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I52 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I53 | HOC2 | I01h Fault current | FLOAT | R | 0...250
38 | I54 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I55 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I56 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I57 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I58 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I59 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I60 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I61 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I62 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I63 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I64 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | I65 | HOC2 | I02h Fault current | FLOAT | R | 0...250
38 | S35 | HOC2 | EventMaskLo | UINT32 | RW | 0...4294967295
39 | S1 | HOC3 | Ih>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
39 | V1 | HOC3 | Ih>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
39 | I1 | HOC3 | Ih>>> starts | UINT32 | R | 0...4294967295
39 | I2 | HOC3 | Ih>>> trips | UINT32 | R | 0...4294967295
39 | I3 | HOC3 | Ih>>> blocks | UINT32 | R | 0...4294967295
39 | S2 | HOC3 | Clear statistics | UINT32 | W | 0=-;1=Clear
39 | I4 | HOC3 | Ih meas/ Ih set | FLOAT | R | 0...100000
39 | S3 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S4 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S5 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S6 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S7 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S8 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S9 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S10 | HOC3 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
39 | S11 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S12 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S13 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S14 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S15 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S16 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S17 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S18 | HOC3 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
39 | S19 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S20 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S21 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S22 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S23 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S24 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S25 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S26 | HOC3 | Minimum phase current | FLOAT | RW | 0.01...40
39 | S27 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S28 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S29 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S30 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S31 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S32 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S33 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | S34 | HOC3 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
39 | O1 | HOC3 | Ih>>> START | SIGNAL_OUT | RW | 0...4294967295
39 | O2 | HOC3 | Ih>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
39 | O3 | HOC3 | Ih>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
39 | I5 | HOC3 | Newest Register | UINT32 | R | 0...12
39 | I6 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I7 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I8 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I9 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I10 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I11 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I12 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I13 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I14 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I15 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I16 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I17 | HOC3 | L1h Fault current | FLOAT | R | 0...250
39 | I18 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I19 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I20 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I21 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I22 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I23 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I24 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I25 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I26 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I27 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I28 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I29 | HOC3 | L2h Fault current | FLOAT | R | 0...250
39 | I30 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I31 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I32 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I33 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I34 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I35 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I36 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I37 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I38 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I39 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I40 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I41 | HOC3 | L3h Fault current | FLOAT | R | 0...250
39 | I42 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I43 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I44 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I45 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I46 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I47 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I48 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I49 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I50 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I51 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I52 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I53 | HOC3 | I01h Fault current | FLOAT | R | 0...250
39 | I54 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I55 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I56 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I57 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I58 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I59 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I60 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I61 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I62 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I63 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I64 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | I65 | HOC3 | I02h Fault current | FLOAT | R | 0...250
39 | S35 | HOC3 | EventMaskLo | UINT32 | RW | 0...4294967295
40 | S1 | HOC4 | Ih>>>> [50H/51H/68H] mode | UINT32 | RW | 0=Disabled;1=Activated
40 | V1 | HOC4 | Ih>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
40 | I1 | HOC4 | Ih>>>> starts | UINT32 | R | 0...4294967295
40 | I2 | HOC4 | Ih>>>> trips | UINT32 | R | 0...4294967295
40 | I3 | HOC4 | Ih>>>> blocks | UINT32 | R | 0...4294967295
40 | S2 | HOC4 | Clear statistics | UINT32 | W | 0=-;1=Clear
40 | I4 | HOC4 | Ih meas/ Ih set | FLOAT | R | 0...100000
40 | S3 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S4 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S5 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S6 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S7 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S8 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S9 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S10 | HOC4 | Pick-up setting Ihset pu | FLOAT | RW | 0.05...2
40 | S11 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S12 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S13 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S14 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S15 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S16 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S17 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S18 | HOC4 | Pick-up setting Ih/IL | FLOAT | RW | 5...200
40 | S19 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S20 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S21 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S22 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S23 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S24 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S25 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S26 | HOC4 | Minimum phase current | FLOAT | RW | 0.01...40
40 | S27 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S28 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S29 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S30 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S31 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S32 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S33 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | S34 | HOC4 | Definite (minimum) operating time delay | FLOAT | RW | 0...1800
40 | O1 | HOC4 | Ih>>>> START | SIGNAL_OUT | RW | 0...4294967295
40 | O2 | HOC4 | Ih>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
40 | O3 | HOC4 | Ih>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
40 | I5 | HOC4 | Newest Register | UINT32 | R | 0...12
40 | I6 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I7 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I8 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I9 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I10 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I11 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I12 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I13 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I14 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I15 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I16 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I17 | HOC4 | L1h Fault current | FLOAT | R | 0...250
40 | I18 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I19 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I20 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I21 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I22 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I23 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I24 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I25 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I26 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I27 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I28 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I29 | HOC4 | L2h Fault current | FLOAT | R | 0...250
40 | I30 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I31 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I32 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I33 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I34 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I35 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I36 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I37 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I38 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I39 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I40 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I41 | HOC4 | L3h Fault current | FLOAT | R | 0...250
40 | I42 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I43 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I44 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I45 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I46 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I47 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I48 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I49 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I50 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I51 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I52 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I53 | HOC4 | I01h Fault current | FLOAT | R | 0...250
40 | I54 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I55 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I56 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I57 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I58 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I59 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I60 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I61 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I62 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I63 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I64 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | I65 | HOC4 | I02h Fault current | FLOAT | R | 0...250
40 | S35 | HOC4 | EventMaskLo | UINT32 | RW | 0...4294967295
42 | S1 | CLP1 | CLP mode | UINT32 | RW | 0=Disabled;1=Activated
42 | V1 | CLP1 | CLP condition | UINT32 | R | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
42 | I1 | CLP1 | CLP starts | UINT32 | R | 0...4294967295
42 | I2 | CLP1 | CLP blocks | UINT32 | R | 0...4294967295
42 | S2 | CLP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
42 | S3 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S4 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S5 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S6 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S7 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S8 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S9 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S10 | CLP1 | I Low | FLOAT | RW | 0.01...40
42 | S11 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S12 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S13 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S14 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S15 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S16 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S17 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S18 | CLP1 | I High | FLOAT | RW | 0.01...40
42 | S19 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S20 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S21 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S22 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S23 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S24 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S25 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S26 | CLP1 | I Over | FLOAT | RW | 0.01...40
42 | S27 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S28 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S29 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S30 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S31 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S32 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S33 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S34 | CLP1 | CLPU tset | FLOAT | RW | 0...1800
42 | S35 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S36 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S37 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S38 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S39 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S40 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S41 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S42 | CLP1 | CLPU tmax | FLOAT | RW | 0...1800
42 | S43 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S44 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S45 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S46 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S47 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S48 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S49 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | S50 | CLP1 | CLPU tmin | FLOAT | RW | 0.02...1800
42 | O1 | CLP1 | CLPU ACT | SIGNAL_OUT | RW | 0...4294967295
42 | O2 | CLP1 | CLPU BLOCKED | SIGNAL_OUT | RW | 0...4294967295
42 | I3 | CLP1 | Newest Register | UINT32 | R | 0...12
42 | I4 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I5 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I6 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I7 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I8 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I9 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I10 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I11 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I12 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I13 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I14 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I15 | CLP1 | L1 Current | FLOAT | R | 0...250
42 | I16 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I17 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I18 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I19 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I20 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I21 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I22 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I23 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I24 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I25 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I26 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I27 | CLP1 | L2 Current | FLOAT | R | 0...250
42 | I28 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I29 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I30 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I31 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I32 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I33 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I34 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I35 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I36 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I37 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I38 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | I39 | CLP1 | L3 Current | FLOAT | R | 0...250
42 | S51 | CLP1 | EventMaskLo | UINT32 | RW | 0...4294967295
44 | S1 | CBF1 | CBFP [50BF] mode | UINT32 | RW | 0=Disabled;1=Activated
44 | V1 | CBF1 | CBFP condition | UINT32 | R | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
44 | I1 | CBF1 | Retrips | UINT32 | R | 0...4294967295
44 | I2 | CBF1 | CBFPs | UINT32 | R | 0...4294967295
44 | I3 | CBF1 | CBFP starts | UINT32 | R | 0...4294967295
44 | I4 | CBF1 | CBFP blocks | UINT32 | R | 0...4294967295
44 | S2 | CBF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
44 | S3 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S4 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S5 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S6 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S7 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S8 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S9 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S10 | CBF1 | Operating mode selection | UINT32 | RW | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
44 | S11 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S12 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S13 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S14 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S15 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S16 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S17 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S18 | CBF1 | Iset | FLOAT | RW | 0.01...40
44 | S19 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S20 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S21 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S22 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S23 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S24 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S25 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S26 | CBF1 | I0 input selection | UINT32 | RW | 0=Not in use;1=I01;2=I02;3=I0Calc
44 | S27 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S28 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S29 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S30 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S31 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S32 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S33 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S34 | CBF1 | I0set | FLOAT | RW | 0.005...40
44 | S35 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S36 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S37 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S38 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S39 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S40 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S41 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S42 | CBF1 | Enable retrip | UINT32 | RW | 0=No;1=yes
44 | S43 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S44 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S45 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S46 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S47 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S48 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S49 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S50 | CBF1 | Retrip time delay | FLOAT | RW | 0.05...1800
44 | S51 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S52 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S53 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S54 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S55 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S56 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S57 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | S58 | CBF1 | CBFP time delay | FLOAT | RW | 0.05...1800
44 | O1 | CBF1 | CBFP START | SIGNAL_OUT | RW | 0...4294967295
44 | O2 | CBF1 | CBFP RETRIP | SIGNAL_OUT | RW | 0...4294967295
44 | O3 | CBF1 | CBFP ACT | SIGNAL_OUT | RW | 0...4294967295
44 | O4 | CBF1 | CBFP BLOCKED | SIGNAL_OUT | RW | 0...4294967295
44 | I5 | CBF1 | Newest Register | UINT32 | R | 0...12
44 | I6 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I7 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I8 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I9 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I10 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I11 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I12 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I13 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I14 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I15 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I16 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I17 | CBF1 | Max Phase curr | FLOAT | R | 0...250
44 | I18 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I19 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I20 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I21 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I22 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I23 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I24 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I25 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I26 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I27 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I28 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I29 | CBF1 | Residual curr | FLOAT | R | 0...250
44 | I30 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I31 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I32 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I33 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I34 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I35 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I36 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I37 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I38 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I39 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I40 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I41 | CBF1 | Time to RETR | FLOAT | R | 0...1800
44 | I42 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I43 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I44 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I45 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I46 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I47 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I48 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I49 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I50 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I51 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I52 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | I53 | CBF1 | Time to CBFP | FLOAT | R | 0...1800
44 | S59 | CBF1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S1 | MST1 | MST mode | UINT32 | R | 0=Disabled; 1=Activated
62 | V1 | MST1 | Motor is now | UINT32 | R | 0=Stopped;1=Starting;2=Running;3=Stalled
62 | I1 | MST1 | Times motor started | UINT32 | R | 0...4294967295
62 | I2 | MST1 | Times motor starts succeed | UINT32 | R | 0...4294967295
62 | I3 | MST1 | Times motor stopped | UINT32 | R | 0...4294967295
62 | S2 | MST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
62 | I4 | MST1 | Run after last start | UINT32 | R | 0...4294967295
62 | I5 | MST1 | Total motor run time | UINT32 | R | 0...4294967295
62 | I6 | MST1 | Last start duration | UINT32 | R | 0...4294967295
62 | I7 | MST1 | Total starting time | UINT32 | R | 0...4294967295
62 | I8 | MST1 | Last stopped duration | UINT32 | R | 0...4294967295
62 | I9 | MST1 | Total stopped time | UINT32 | R | 0...4294967295
62 | S3 | MST1 | Clear total times | UINT32 | W | 0=-;1=Clear
62 | S4 | MST1 | Per unitize relay currents to Motor In | UINT32 | RW | 0=No, use CT nominal as pu.;1=Yes, scale all to Imot
62 | S5 | MST1 | Motor nominal current | FLOAT | RW | 0.1...10000
62 | S6 | MST1 | Nominal Starting current | FLOAT | RW | 0.1...40
62 | S7 | MST1 | Start detect current | FLOAT | RW | 0.1...40
62 | S8 | MST1 | Min locked rotor current | FLOAT | RW | 0.1...40
62 | S9 | MST1 | Max locked rotor current | FLOAT | RW | 0.1...40
62 | S10 | MST1 | Maximum overload current | FLOAT | RW | 0.1...40
62 | S11 | MST1 | No Load current | FLOAT | RW | 0.1...40
62 | S12 | MST1 | Motor service factor | FLOAT | RW | 0.01...5
62 | S13 | MST1 | Hot condition theta limit | FLOAT | RW | 0...100
62 | S14 | MST1 | Safe stall time cold | FLOAT | RW | 0.1...600
62 | S15 | MST1 | Safe stall time hot | FLOAT | RW | 0.1...600
62 | S16 | MST1 | Allowed Starts when cold | UINT32 | RW | 1...100
62 | S17 | MST1 | Allowed Starts when hot | UINT32 | RW | 1...100
62 | S18 | MST1 | Given Hot/Cold starts in time of: | FLOAT | RW | 0.01...1800
62 | S19 | MST1 | Min time betw. starts | FLOAT | RW | 0...3600
62 | S20 | MST1 | Overall differential protection | UINT32 | RW | 0=Machine diff. (Yy);1=Diff.with trafo(Xx)
62 | O1 | MST1 | Motor stopped | SIGNAL_OUT | RW | 0...4294967295
62 | O2 | MST1 | Motor starting | SIGNAL_OUT | RW | 0...4294967295
62 | O3 | MST1 | Motor running | SIGNAL_OUT | RW | 0...4294967295
62 | O4 | MST1 | Motor stalled | SIGNAL_OUT | RW | 0...4294967295
62 | O5 | MST1 | Missing phase | SIGNAL_OUT | RW | 0...4294967295
62 | O6 | MST1 | Load Normal | SIGNAL_OUT | RW | 0...4294967295
62 | O7 | MST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
62 | O8 | MST1 | High overcurrent | SIGNAL_OUT | RW | 0...4294967295
62 | I10 | MST1 | Newest Register | UINT32 | R | 0...12
62 | I11 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I12 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I13 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I14 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I15 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I16 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I17 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I18 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I19 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I20 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I21 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I22 | MST1 | L1 Current | FLOAT | R | 0...250
62 | I23 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I24 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I25 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I26 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I27 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I28 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I29 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I30 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I31 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I32 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I33 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I34 | MST1 | L2 Current | FLOAT | R | 0...250
62 | I35 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I36 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I37 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I38 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I39 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I40 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I41 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I42 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I43 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I44 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I45 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I46 | MST1 | L3 Current | FLOAT | R | 0...250
62 | I47 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I48 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I49 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I50 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I51 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I52 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I53 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I54 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I55 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I56 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I57 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I58 | MST1 | Therm delta | FLOAT | R | 0...250
62 | I59 | MST1 | Motor load | FLOAT | R | 0...250
62 | I60 | MST1 | Motor load | FLOAT | R | 0...250
62 | I61 | MST1 | Motor load | FLOAT | R | 0...250
62 | I62 | MST1 | Motor load | FLOAT | R | 0...250
62 | I63 | MST1 | Motor load | FLOAT | R | 0...250
62 | I64 | MST1 | Motor load | FLOAT | R | 0...250
62 | I65 | MST1 | Motor load | FLOAT | R | 0...250
62 | I66 | MST1 | Motor load | FLOAT | R | 0...250
62 | I67 | MST1 | Motor load | FLOAT | R | 0...250
62 | I68 | MST1 | Motor load | FLOAT | R | 0...250
62 | I69 | MST1 | Motor load | FLOAT | R | 0...250
62 | I70 | MST1 | Motor load | FLOAT | R | 0...250
62 | S21 | MST1 | EventMaskLo | UINT32 | RW | 0...4294967295
62 | S22 | MST1 | EventMaskHi | UINT32 | RW | 0...4294967295
72 | V1 | TRF1 | Transformer is now | UINT32 | R | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
72 | I1 | TRF1 | Times Overloaded | UINT32 | R | 0...4294967295
72 | I2 | TRF1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
72 | S1 | TRF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
72 | I3 | TRF1 | Normal loading | UINT32 | R | 0...4294967295
72 | I4 | TRF1 | Overloading cumulative | UINT32 | R | 0...4294967295
72 | I5 | TRF1 | Last overload duration | UINT32 | R | 0...4294967295
72 | I6 | TRF1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
72 | I7 | TRF1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
72 | S2 | TRF1 | Clear total times | UINT32 | W | 0=-;1=Clear
72 | S3 | TRF1 | Transformer nominal MVA | FLOAT | RW | 0.1...500
72 | S4 | TRF1 | HV side nominal voltage | FLOAT | RW | 0.1...500
72 | S5 | TRF1 | LV side nominal voltage | FLOAT | RW | 0.1...500
72 | S6 | TRF1 | Transformer Zk % | FLOAT | RW | 0.01...25
72 | S7 | TRF1 | Transformer nom freq. | FLOAT | RW | 10...75
72 | V2 | TRF1 | Bias selection | UINT32 | R | 0=Selection Ok;1=Selection different
72 | V3 | TRF1 | Pick-up setting | UINT32 | R | 0=not checked;1=Setting seems ok;2=Sensitive ok;3=Too sensitive;4=False trip likely;5=Coarse ok;6=Insensitive;7=Dangerously high
72 | V4 | TRF1 | Turnpoint1 setting | UINT32 | R | 0=not checked;1=Ok;2=Seems average;3=Is sensitive;4=Ok;5=Is conservative;6=Is sensitive;7=Ok;8=Is average;9=Is conservative;10=Ok;11=Too conservative;12=Too sensitive
72 | V5 | TRF1 | Slope1 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V6 | TRF1 | Turnpoint2 setting | UINT32 | R | 0=not checked;1=Ok;2=Too high, check;3=Too low, check;
72 | V7 | TRF1 | Slope2 setting | UINT32 | R | 0=not checked;1=Ok;2=Wrong;
72 | O1 | TRF1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
72 | O2 | TRF1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O3 | TRF1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
72 | O4 | TRF1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
72 | O5 | TRF1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | O6 | TRF1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
72 | I8 | TRF1 | Newest Register | UINT32 | R | 0...12
72 | I9 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I10 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I11 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I12 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I13 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I14 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I15 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I16 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I17 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I18 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I19 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I20 | TRF1 | HV L1 Current | FLOAT | R | 0...250
72 | I21 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I22 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I23 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I24 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I25 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I26 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I27 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I28 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I29 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I30 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I31 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I32 | TRF1 | HV L2 Current | FLOAT | R | 0...250
72 | I33 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I34 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I35 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I36 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I37 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I38 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I39 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I40 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I41 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I42 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I43 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I44 | TRF1 | HV L3 Current | FLOAT | R | 0...250
72 | I45 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I46 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I47 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I48 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I49 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I50 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I51 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I52 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I53 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I54 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I55 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I56 | TRF1 | LV L1 Current | FLOAT | R | 0...250
72 | I57 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I58 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I59 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I60 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I61 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I62 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I63 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I64 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I65 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I66 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I67 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I68 | TRF1 | LV L2 Current | FLOAT | R | 0...250
72 | I69 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I70 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I71 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I72 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I73 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I74 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I75 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I76 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I77 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I78 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I79 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | I80 | TRF1 | LV L3 Current | FLOAT | R | 0...250
72 | S8 | TRF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S1 | DIF1 | Idx> [87T/87N] mode | UINT32 | RW | 0=Disabled;1=Activated
71 | V1 | DIF1 | Idx> condition | UINT32 | R | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On
71 | V2 | DIF1 | REFHV> condition | UINT32 | R | 0b=HV REF Blocked;1b=HV REF Trip
71 | V3 | DIF1 | REFLV> condition | UINT32 | R | 0b=LV REF Blocked;1b=LV REF Trip
71 | I1 | DIF1 | Idb> trips | UINT32 | R | 0...4294967295
71 | I2 | DIF1 | Idb> f2h blocks | UINT32 | R | 0...4294967295
71 | I3 | DIF1 | Idb> f5h blocks | UINT32 | R | 0...4294967295
71 | I4 | DIF1 | Idb> Ext blocks | UINT32 | R | 0...4294967295
71 | I5 | DIF1 | Idi> trips | UINT32 | R | 0...4294967295
71 | I6 | DIF1 | Idi> Ext blocks | UINT32 | R | 0...4294967295
71 | I7 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I8 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | I9 | DIF1 | HV I0d> blocks | UINT32 | R | 0...4294967295
71 | I10 | DIF1 | HV I0d>TRIPS | UINT32 | R | 0...4294967295
71 | S2 | DIF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
71 | I11 | DIF1 | L1 Bias current | FLOAT | R | 0...50
71 | I12 | DIF1 | L1 Diff current | FLOAT | R | 0...4000
71 | I13 | DIF1 | L1 Char current | FLOAT | R | 0...4000
71 | I14 | DIF1 | L2 Bias current | FLOAT | R | 0...50
71 | I15 | DIF1 | L2 Diff current | FLOAT | R | 0...4000
71 | I16 | DIF1 | L2 Char current | FLOAT | R | 0...4000
71 | I17 | DIF1 | L3 Bias current | FLOAT | R | 0...50
71 | I18 | DIF1 | L3 Diff current | FLOAT | R | 0...4000
71 | I19 | DIF1 | L3 Char current | FLOAT | R | 0...4000
71 | I20 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...50
71 | I21 | DIF1 | HV I0d> Diff current | FLOAT | R | 0...4000
71 | I22 | DIF1 | HV I0d> Char current | FLOAT | R | 0...4000
71 | I23 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...50
71 | I24 | DIF1 | LV I0d> Diff current | FLOAT | R | 0...4000
71 | I25 | DIF1 | LV I0d> Char current | FLOAT | R | 0...4000
71 | S3 | DIF1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
71 | V4 | DIF1 | L1 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V5 | DIF1 | L2 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | V6 | DIF1 | L3 Condition | UINT32 | R | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
71 | I26 | DIF1 | L1 Mag. diff. | FLOAT | R | 0...50
71 | I27 | DIF1 | L1 Ang. diff. | FLOAT | R | -360...360
71 | I28 | DIF1 | L2 Mag. diff. | FLOAT | R | 0...50
71 | I29 | DIF1 | L2 Ang. diff. | FLOAT | R | -360...360
71 | I30 | DIF1 | L3 Mag. diff. | FLOAT | R | 0...50
71 | I31 | DIF1 | L3 Ang. diff. | FLOAT | R | -360...360
71 | S4 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S5 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S6 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S7 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S8 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S9 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S10 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S11 | DIF1 | Differential calculation mode | UINT32 | RW | 0=subtract;1=Add
71 | S12 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S13 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S14 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S15 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S16 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S17 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S18 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S19 | DIF1 | Bias calculation mode | UINT32 | RW | 0=Average;1=Maximum
71 | S20 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S21 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S22 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S23 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S24 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S25 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S26 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S27 | DIF1 | Idb> Pickup | FLOAT | RW | 0.01...100
71 | S28 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S29 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S30 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S31 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S32 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S33 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S34 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S35 | DIF1 | Idb> Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S36 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S37 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S38 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S39 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S40 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S41 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S42 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S43 | DIF1 | Idb> Slope 1 | FLOAT | RW | 0.01...250
71 | S44 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S45 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S46 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S47 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S48 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S49 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S50 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S51 | DIF1 | Idb> Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S52 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S53 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S54 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S55 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S56 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S57 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S58 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S59 | DIF1 | Idb> Slope 2 | FLOAT | RW | 0.01...250
71 | S60 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S61 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S62 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S63 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S64 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S65 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S66 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S67 | DIF1 | Enable harmonic blocking | UINT32 | RW | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
71 | S68 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S69 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S70 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S71 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S72 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S73 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S74 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S75 | DIF1 | 2nd harm block Pickup | FLOAT | RW | 0.01...50
71 | S76 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S77 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S78 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S79 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S80 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S81 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S82 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S83 | DIF1 | 5th harm block Pickup | FLOAT | RW | 0.01...50
71 | S84 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S85 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S86 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S87 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S88 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S89 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S90 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S91 | DIF1 | Enable Idi> stage (nonbias) | UINT32 | RW | 0=Disabled;1=Enabled
71 | S92 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S93 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S94 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S95 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S96 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S97 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S98 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S99 | DIF1 | Idi> No bias Pickup | FLOAT | RW | 200...1500
71 | S100 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S101 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S102 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S103 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S104 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S105 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S106 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S107 | DIF1 | HV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S108 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S109 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S110 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S111 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S112 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S113 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S114 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S115 | DIF1 | HV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S116 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S117 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S118 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S119 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S120 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S121 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S122 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S123 | DIF1 | HV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S124 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S125 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S126 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S127 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S128 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S129 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S130 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S131 | DIF1 | HV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S132 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S133 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S134 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S135 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S136 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S137 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S138 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S139 | DIF1 | HV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S140 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S141 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S142 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S143 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S144 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S145 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S146 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S147 | DIF1 | HV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S148 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S149 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S150 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S151 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S152 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S153 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S154 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S155 | DIF1 | HV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S156 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S157 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S158 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S159 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S160 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S161 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S162 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S163 | DIF1 | LV REF diff calc. mode | UINT32 | RW | 0=Add;1=subtract
71 | S164 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S165 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S166 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S167 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S168 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S169 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S170 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S171 | DIF1 | LV REF Bias calc. mode | UINT32 | RW | 0=Average;1=Maximum
71 | S172 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S173 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S174 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S175 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S176 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S177 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S178 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S179 | DIF1 | LV I0d> Pickup | FLOAT | RW | 0.01...100
71 | S180 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S181 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S182 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S183 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S184 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S185 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S186 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S187 | DIF1 | LV I0d>Turnpoint 1 | FLOAT | RW | 0.01...50
71 | S188 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S189 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S190 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S191 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S192 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S193 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S194 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S195 | DIF1 | LV I0d>Slope 1 | FLOAT | RW | 0.01...250
71 | S196 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S197 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S198 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S199 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S200 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S201 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S202 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S203 | DIF1 | LV I0d>Turnpoint 2 | FLOAT | RW | 0.01...50
71 | S204 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S205 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S206 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S207 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S208 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S209 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S210 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | S211 | DIF1 | LV I0d>Slope 2 | FLOAT | RW | 0.01...250
71 | O1 | DIF1 | Idb> BIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O2 | DIF1 | Idb> BIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O3 | DIF1 | Idi> NOBIAS TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O4 | DIF1 | Idi> NOBIAS BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O5 | DIF1 | Id> 2nd harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O6 | DIF1 | Id> 5th harm. block on | SIGNAL_OUT | RW | 0...4294967295
71 | O7 | DIF1 | HV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O8 | DIF1 | HV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | O9 | DIF1 | LV I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
71 | O10 | DIF1 | LV I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
71 | I32 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I33 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I34 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I35 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I36 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I37 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I38 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I39 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I40 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I41 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I42 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I43 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I44 | DIF1 | L1 Bias current | FLOAT | R | 0...250
71 | I45 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I46 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I47 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I48 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I49 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I50 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I51 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I52 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I53 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I54 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I55 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I56 | DIF1 | L1 Differential current | FLOAT | R | 0...250
71 | I57 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I58 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I59 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I60 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I61 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I62 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I63 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I64 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I65 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I66 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I67 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I68 | DIF1 | L1 Characteristics current | FLOAT | R | 0...250
71 | I69 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I70 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I71 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I72 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I73 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I74 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I75 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I76 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I77 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I78 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I79 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I80 | DIF1 | L2 Bias current | FLOAT | R | 0...250
71 | I81 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I82 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I83 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I84 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I85 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I86 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I87 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I88 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I89 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I90 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I91 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I92 | DIF1 | L2 Differential current | FLOAT | R | 0...250
71 | I93 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I94 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I95 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I96 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I97 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I98 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I99 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I100 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I101 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I102 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I103 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I104 | DIF1 | L2 Characteristics current | FLOAT | R | 0...250
71 | I105 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I106 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I107 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I108 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I109 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I110 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I111 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I112 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I113 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I114 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I115 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I116 | DIF1 | L3 Bias current | FLOAT | R | 0...250
71 | I117 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I118 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I119 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I120 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I121 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I122 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I123 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I124 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I125 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I126 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I127 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I128 | DIF1 | L3 Differential current | FLOAT | R | 0...250
71 | I129 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I130 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I131 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I132 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I133 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I134 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I135 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I136 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I137 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I138 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I139 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | I140 | DIF1 | L3 Characteristics current | FLOAT | R | 0...250
71 | V7 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V8 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V9 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V10 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V11 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V12 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V13 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V14 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V15 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V16 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V17 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | V18 | DIF1 | Fault type | UINT32 | R | 0=-;1=L1;2=L2;3=L3;4=L1-L2;5=L2-L3;6=L1-L3;7=L1-L2-L3
71 | I141 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I142 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I143 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I144 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I145 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I146 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I147 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I148 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I149 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I150 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I151 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I152 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I153 | DIF1 | HV I0d> Bias current | FLOAT | R | 0...250
71 | I154 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I155 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I156 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I157 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I158 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I159 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I160 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I161 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I162 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I163 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I164 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I165 | DIF1 | HV I0d> Differential current | FLOAT | R | 0...250
71 | I166 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I167 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I168 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I169 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I170 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I171 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I172 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I173 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I174 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I175 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I176 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I177 | DIF1 | HV I0d> Characteristics current | FLOAT | R | 0...250
71 | I178 | DIF1 | Newest Register | UINT32 | R | 0...12
71 | I179 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I180 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I181 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I182 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I183 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I184 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I185 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I186 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I187 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I188 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I189 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I190 | DIF1 | LV I0d> Bias current | FLOAT | R | 0...250
71 | I191 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I192 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I193 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I194 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I195 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I196 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I197 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I198 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I199 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I200 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I201 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I202 | DIF1 | LV I0d> Differential current | FLOAT | R | 0...250
71 | I203 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I204 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I205 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I206 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I207 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I208 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I209 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I210 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I211 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I212 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I213 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | I214 | DIF1 | LV I0d> Characteristics current | FLOAT | R | 0...250
71 | S212 | DIF1 | EventMaskLo | UINT32 | RW | 0...4294967295
71 | S213 | DIF1 | EventMaskHi | UINT32 | RW | 0...4294967295
66 | S1 | REF1 | I0d> [87N] mode | UINT32 | RW | 0=Disabled;1=Activated
66 | V1 | REF1 | I0d> condition | UINT32 | R | 0=Normal;1=Trip;2=Blocked
66 | S2 | REF1 | Select | UINT32 | RW | 0=Primary A;1=Secondary A;2=Per Unit
66 | S3 | REF1 | Select | UINT32 | RW | 0=REF Curr
66 | I1 | REF1 | I0d> Bias current | FLOAT | R | 0...50
66 | I2 | REF1 | I0d> Diff current | FLOAT | R | 0...50
66 | I3 | REF1 | I0d> Char current | FLOAT | R | 0...50
66 | I4 | REF1 | Calculated I0 (I0Calc) | FLOAT | R | 0...50
66 | I5 | REF1 | Measured I0 (3I0) | FLOAT | R | 0...50
66 | S4 | REF1 | REF or Cable end Diff | UINT32 | RW | 0=REF;1=CED
66 | S5 | REF1 | Comp. natural unbal. | UINT32 | RW | 0=-;1=Comp
66 | I6 | REF1 | Natural unbalance | FLOAT | R | 0...50
66 | I7 | REF1 | Natural unbalance ang | FLOAT | R | -360...360
66 | I8 | REF1 | Current for CED | FLOAT | R | 0...50
66 | I9 | REF1 | Angle for CED | FLOAT | R | -360...360
66 | S6 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S7 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S8 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S9 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S10 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S11 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S12 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S13 | REF1 | I0 input | UINT32 | RW | 0=I01;1=I02
66 | S14 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S15 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S16 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S17 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S18 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S19 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S20 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S21 | REF1 | I0 direction | UINT32 | RW | 0=Add;1=subtract
66 | S22 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S23 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S24 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S25 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S26 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S27 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S28 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S29 | REF1 | Bias current calc | UINT32 | RW | 0=(3I0+I0calc)/2;1=max(3I0,I0calc)
66 | S30 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S31 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S32 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S33 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S34 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S35 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S36 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S37 | REF1 | I0d> Pickup | FLOAT | RW | 0.01...50
66 | S38 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S39 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S40 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S41 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S42 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S43 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S44 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S45 | REF1 | Turnpoint 1 | FLOAT | RW | 0.01...50
66 | S46 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S47 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S48 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S49 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S50 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S51 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S52 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S53 | REF1 | Slope 1 | FLOAT | RW | 0.01...150
66 | S54 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S55 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S56 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S57 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S58 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S59 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S60 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S61 | REF1 | Turnpoint 2 | FLOAT | RW | 0.01...50
66 | S62 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S63 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S64 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S65 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S66 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S67 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S68 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S69 | REF1 | Slope 2 | FLOAT | RW | 0.01...250
66 | S70 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S71 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S72 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S73 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S74 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S75 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S76 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | S77 | REF1 | REF Trip delay | FLOAT | RW | 0...3600
66 | O1 | REF1 | I0d> TRIP | SIGNAL_OUT | RW | 0...4294967295
66 | O2 | REF1 | I0d> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
66 | I10 | REF1 | Newest Register | UINT32 | R | 0...12
66 | I11 | REF1 | Bias current | FLOAT | R | 0...250
66 | I12 | REF1 | Bias current | FLOAT | R | 0...250
66 | I13 | REF1 | Bias current | FLOAT | R | 0...250
66 | I14 | REF1 | Bias current | FLOAT | R | 0...250
66 | I15 | REF1 | Bias current | FLOAT | R | 0...250
66 | I16 | REF1 | Bias current | FLOAT | R | 0...250
66 | I17 | REF1 | Bias current | FLOAT | R | 0...250
66 | I18 | REF1 | Bias current | FLOAT | R | 0...250
66 | I19 | REF1 | Bias current | FLOAT | R | 0...250
66 | I20 | REF1 | Bias current | FLOAT | R | 0...250
66 | I21 | REF1 | Bias current | FLOAT | R | 0...250
66 | I22 | REF1 | Bias current | FLOAT | R | 0...250
66 | I23 | REF1 | Differential current | FLOAT | R | 0...250
66 | I24 | REF1 | Differential current | FLOAT | R | 0...250
66 | I25 | REF1 | Differential current | FLOAT | R | 0...250
66 | I26 | REF1 | Differential current | FLOAT | R | 0...250
66 | I27 | REF1 | Differential current | FLOAT | R | 0...250
66 | I28 | REF1 | Differential current | FLOAT | R | 0...250
66 | I29 | REF1 | Differential current | FLOAT | R | 0...250
66 | I30 | REF1 | Differential current | FLOAT | R | 0...250
66 | I31 | REF1 | Differential current | FLOAT | R | 0...250
66 | I32 | REF1 | Differential current | FLOAT | R | 0...250
66 | I33 | REF1 | Differential current | FLOAT | R | 0...250
66 | I34 | REF1 | Differential current | FLOAT | R | 0...250
66 | I35 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I36 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I37 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I38 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I39 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I40 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I41 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I42 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I43 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I44 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I45 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | I46 | REF1 | Characteristics current | FLOAT | R | 0...250
66 | S78 | REF1 | EventMaskLo | UINT32 | RW | 0...4294967295
66 | S79 | REF1 | EventMaskHi | UINT32 | RW | 0...4294967295
73 | S1 | TOLT1 | TT> [49T] mode | UINT32 | RW | 0=Disabled;1=Activated
73 | V1 | TOLT1 | TT> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
73 | V2 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
73 | V3 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
73 | V4 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
73 | V5 | TOLT1 | TT> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
73 | V6 | TOLT1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
73 | I1 | TOLT1 | IN thermal cap current | FLOAT | RW | 0...40
73 | I2 | TOLT1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
73 | S2 | TOLT1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
73 | S3 | TOLT1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
73 | I3 | TOLT1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
73 | I4 | TOLT1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
73 | S4 | TOLT1 | tau1 (t const heating) | FLOAT | RW | 0...500
73 | S5 | TOLT1 | tau2 (t const cooling) | FLOAT | RW | 0...500
73 | S6 | TOLT1 | kSF (service factor) | FLOAT | RW | 0.01...5
73 | S7 | TOLT1 | Cold Reset default theta | FLOAT | RW | 0...150
73 | V7 | TOLT1 | TT> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
73 | I5 | TOLT1 | TT> Time to 100% Theta | UINT32 | R | 0...4294967295
73 | I6 | TOLT1 | TT> Reference T curr. | FLOAT | R | 0...50
73 | I7 | TOLT1 | TT> Active meas curr. | FLOAT | R | 0...50
73 | I8 | TOLT1 | TT> T est.with act. curr. | FLOAT | R | 0...500
73 | I9 | TOLT1 | TT> T at the moment | FLOAT | R | 0...500
73 | I10 | TOLT1 | TT> Max.Temp.Rise All. | FLOAT | R | 0...250
73 | I11 | TOLT1 | TT> Temp.Rise atm. | FLOAT | R | 0...250
73 | I12 | TOLT1 | TT> Hot Spot estimate | FLOAT | R | 0...250
73 | I13 | TOLT1 | TT> Hot Spot Max. All | FLOAT | R | 0...250
73 | I14 | TOLT1 | TT> Used k for amb. temp | FLOAT | R | 0...3
73 | I15 | TOLT1 | TT> Trip delay remaining | UINT32 | R | 0...4294967295
73 | I16 | TOLT1 | TT> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
73 | I17 | TOLT1 | TT> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
73 | I18 | TOLT1 | TT> Inhibit time to rel. | UINT32 | R | 0...4294967295
73 | I19 | TOLT1 | TT> Trip time to rel. | UINT32 | R | 0...4294967295
73 | I20 | TOLT1 | TT> Thermal cap used | FLOAT | R | 0...500
73 | I21 | TOLT1 | Alarm1 inits | UINT32 | R | 0...4294967295
73 | I22 | TOLT1 | Alarm2 inits | UINT32 | R | 0...4294967295
73 | I23 | TOLT1 | Restart Inhibits | UINT32 | R | 0...4294967295
73 | I24 | TOLT1 | Trips | UINT32 | R | 0...4294967295
73 | I25 | TOLT1 | Trips Blocked | UINT32 | R | 0...4294967295
73 | S8 | TOLT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
73 | S9 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S10 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S11 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S12 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S13 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S14 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S15 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S16 | TOLT1 | Enable TT> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S17 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S18 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S19 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S20 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S21 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S22 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S23 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S24 | TOLT1 | TT> Alarm1 level | FLOAT | RW | 0...150
73 | S25 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S26 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S27 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S28 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S29 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S30 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S31 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S32 | TOLT1 | Enable TT> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
73 | S33 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S34 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S35 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S36 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S37 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S38 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S39 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S40 | TOLT1 | TT> Alarm2 level | FLOAT | RW | 0...150
73 | S41 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S42 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S43 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S44 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S45 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S46 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S47 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S48 | TOLT1 | Enable TT> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
73 | S49 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S50 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S51 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S52 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S53 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S54 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S55 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S56 | TOLT1 | TT> Inhibit level | FLOAT | RW | 0...150
73 | S57 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S58 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S59 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S60 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S61 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S62 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S63 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S64 | TOLT1 | TT> Trip level | FLOAT | RW | 0...150
73 | S65 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S66 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S67 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S68 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S69 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S70 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S71 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | S72 | TOLT1 | TT> Trip delay | FLOAT | RW | 0...3600
73 | O1 | TOLT1 | TT> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
73 | O2 | TOLT1 | TT> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
73 | O3 | TOLT1 | TT> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
73 | O4 | TOLT1 | TT> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
73 | O5 | TOLT1 | TT> Trip | SIGNAL_OUT | RW | 0...4294967295
73 | I26 | TOLT1 | Newest Register | UINT32 | R | 0...12
73 | I27 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I28 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I29 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I30 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I31 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I32 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I33 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I34 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I35 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I36 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I37 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I38 | TOLT1 | Reference T current | FLOAT | R | 0...50
73 | I39 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I40 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I41 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I42 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I43 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I44 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I45 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I46 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I47 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I48 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I49 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I50 | TOLT1 | Active meas current | FLOAT | R | 0...250
73 | I51 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I52 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I53 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I54 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I55 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I56 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I57 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I58 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I59 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I60 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I61 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | I62 | TOLT1 | T at the moment | FLOAT | R | 0...600000
73 | S73 | TOLT1 | EventMaskLo | UINT32 | RW | 0...4294967295
73 | S74 | TOLT1 | EventMaskHi | UINT32 | RW | 0...4294967295
67 | S1 | TOLF1 | TF> [49F] mode | UINT32 | RW | 0=Disabled;1=Activated
67 | V1 | TOLF1 | TF> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
67 | V2 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
67 | V3 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
67 | V4 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
67 | V5 | TOLF1 | TF> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
67 | V6 | TOLF1 | Thermal status | UINT32 | R | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
67 | I1 | TOLF1 | IN thermal cap current | FLOAT | RW | 0...40
67 | I2 | TOLF1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
67 | I3 | TOLF1 | Ambient Temp Sel | UINT32 | RW | 0=Manual Set;1=RTD Meas
67 | I4 | TOLF1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
67 | I5 | TOLF1 | RTD Amb.Temp.Read | FLOAT | R | -101...2000
67 | I6 | TOLF1 | RTD Sensor | UINT32 | R | 0=Invalid;1=OK
67 | S2 | TOLF1 | tau (t const) | FLOAT | RW | 0...500
67 | S3 | TOLF1 | Nominal current | FLOAT | RW | 1...9999999
67 | S4 | TOLF1 | kSF (service factor) | FLOAT | RW | 0.01...5
67 | I7 | TOLF1 | TF> Time to 100% Theta | UINT32 | R | 0...4294967295
67 | I8 | TOLF1 | TF> Reference T curr. | FLOAT | R | 0...50
67 | I9 | TOLF1 | TF> Active meas curr. | FLOAT | R | 0...50
67 | I10 | TOLF1 | TF> T est.with act. curr. | FLOAT | R | 0...500
67 | I11 | TOLF1 | TF> T at the moment | FLOAT | R | 0...500
67 | I12 | TOLF1 | TF> Max.Temp.Rise All. | FLOAT | R | 0...250
67 | I13 | TOLF1 | TF> Temp.Rise atm. | FLOAT | R | 0...250
67 | I14 | TOLF1 | TF> Hot Spot estimate | FLOAT | R | 0...250
67 | I15 | TOLF1 | TF> Hot Spot Max. All | FLOAT | R | 0...250
67 | I16 | TOLF1 | TF> Used k for amb. temp | FLOAT | R | 0...3
67 | I17 | TOLF1 | TF> Trip delay remaining | UINT32 | R | 0...4294967295
67 | I18 | TOLF1 | TF> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
67 | I19 | TOLF1 | TF> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
67 | I20 | TOLF1 | TF> Inhibit time to rel. | UINT32 | R | 0...4294967295
67 | I21 | TOLF1 | TF> Trip time to rel. | UINT32 | R | 0...4294967295
67 | I22 | TOLF1 | TF> Thermal cap used | FLOAT | R | 0...500
67 | I23 | TOLF1 | Alarm1 inits | UINT32 | R | 0...4294967295
67 | I24 | TOLF1 | Alarm2 inits | UINT32 | R | 0...4294967295
67 | I25 | TOLF1 | Restart Inhibits | UINT32 | R | 0...4294967295
67 | I26 | TOLF1 | Trips | UINT32 | R | 0...4294967295
67 | I27 | TOLF1 | Trips Blocked | UINT32 | R | 0...4294967295
67 | S5 | TOLF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
67 | S6 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S7 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S8 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S9 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S10 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S11 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S12 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S13 | TOLF1 | Enable TF> Alarm1 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S14 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S15 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S16 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S17 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S18 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S19 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S20 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S21 | TOLF1 | TF> Alarm1 level | FLOAT | RW | 0...150
67 | S22 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S23 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S24 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S25 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S26 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S27 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S28 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S29 | TOLF1 | Enable TF> Alarm2 | UINT32 | RW | 0=Disabled;1=Enabled
67 | S30 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S31 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S32 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S33 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S34 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S35 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S36 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S37 | TOLF1 | TF> Alarm2 level | FLOAT | RW | 0...150
67 | S38 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S39 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S40 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S41 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S42 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S43 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S44 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S45 | TOLF1 | Enable TF> Rest Inhibit | UINT32 | RW | 0=Disabled;1=Enabled
67 | S46 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S47 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S48 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S49 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S50 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S51 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S52 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S53 | TOLF1 | TF> Inhibit level | FLOAT | RW | 0...150
67 | S54 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S55 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S56 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S57 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S58 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S59 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S60 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S61 | TOLF1 | TF> Trip level | FLOAT | RW | 0...150
67 | S62 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S63 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S64 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S65 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S66 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S67 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S68 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | S69 | TOLF1 | TF> Trip delay | FLOAT | RW | 0...3600
67 | O1 | TOLF1 | TF> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
67 | O2 | TOLF1 | TF> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
67 | O3 | TOLF1 | TF> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
67 | O4 | TOLF1 | TF> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
67 | O5 | TOLF1 | TF> Trip | SIGNAL_OUT | RW | 0...4294967295
67 | I28 | TOLF1 | Newest Register | UINT32 | R | 0...12
67 | I29 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I30 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I31 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I32 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I33 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I34 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I35 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I36 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I37 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I38 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I39 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I40 | TOLF1 | Reference T current | FLOAT | R | 0...50
67 | I41 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I42 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I43 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I44 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I45 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I46 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I47 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I48 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I49 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I50 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I51 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I52 | TOLF1 | Active meas current | FLOAT | R | 0...250
67 | I53 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I54 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I55 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I56 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I57 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I58 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I59 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I60 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I61 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I62 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I63 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I64 | TOLF1 | T at the moment | FLOAT | R | 0...600000
67 | I65 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I66 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I67 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I68 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I69 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I70 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I71 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I72 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I73 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I74 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I75 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | I76 | TOLF1 | Hot Spot estimate | FLOAT | R | 0...500
67 | S70 | TOLF1 | EventMaskLo | UINT32 | RW | 0...4294967295
67 | S71 | TOLF1 | EventMaskHi | UINT32 | RW | 0...4294967295
68 | S1 | TOLM1 | TM> [49M] mode | UINT32 | RW | 0=Disabled; 1=Activated
68 | V1 | TOLM1 | TM> condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
68 | V2 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=SF setting ok;1=Service factor set fault. Override to 1.0
68 | V3 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
68 | V4 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
68 | V5 | TOLM1 | TM> Setting alarm | UINT32 | R | 0=Ambient setting ok;1=Inconsistent setting of ambient k
68 | V6 | TOLM1 | Motor status | UINT32 | R | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
68 | S2 | TOLM1 | Pick-up current (x In) | FLOAT | RW | 0...40
68 | S3 | TOLM1 | NPS Biasing in use | UINT32 | RW | 0=No NPS biasing;1=NPS Biasing in use
68 | S4 | TOLM1 | NPS Bias factor | FLOAT | RW | 0.1...10
68 | S5 | TOLM1 | Time constants | UINT32 | RW | 0=Single;1=Multiple
68 | S6 | TOLM1 | Long Heat T const (cold) | FLOAT | RW | 0...500
68 | S7 | TOLM1 | Long Heat T const (hot) | FLOAT | RW | 0...500
68 | S8 | TOLM1 | Long Cool T const Run | FLOAT | RW | 0...3000
68 | S9 | TOLM1 | Long Cool T const Stop | FLOAT | RW | 0...3000
68 | S10 | TOLM1 | Short Heat T const (cold) | FLOAT | RW | 0...500
68 | S11 | TOLM1 | Short Heat T const (hot) | FLOAT | RW | 0...500
68 | S12 | TOLM1 | Short Cool T const | FLOAT | RW | 0...3000
68 | S13 | TOLM1 | Wf factor for L/S T const | FLOAT | RW | 0...1
68 | S14 | TOLM1 | T const dyn. balancing | UINT32 | RW | 0=Fixed;1=Dynamic
68 | S15 | TOLM1 | Short Cool T used when stop | FLOAT | RW | 0...3000
68 | S16 | TOLM1 | Cold Reset Theta Default | FLOAT | RW | 0...150
68 | I1 | TOLM1 | Wf in use | FLOAT | R | 0...1
68 | I2 | TOLM1 | Long heat TC in use | FLOAT | R | 0...500
68 | I3 | TOLM1 | Short heat TC in use | FLOAT | R | 0...500
68 | I4 | TOLM1 | Long cool TC in use | FLOAT | R | 0...500
68 | I5 | TOLM1 | Short cool TC in use | FLOAT | R | 0...500
68 | I6 | TOLM1 | Cold stall time | FLOAT | R | 0...500
68 | I7 | TOLM1 | Hot stall time | FLOAT | R | 0...500
68 | S17 | TOLM1 | Dev.Temp (tmax) | UINT32 | RW | 0=A;1=B;2=F;3=H;4=Manual set
68 | S18 | TOLM1 | Obj.Max.temp (tmax=100%) | FLOAT | RW | 0...500
68 | S19 | TOLM1 | Amb. T Selection | UINT32 | RW | 0=Manual set;1=RTD
68 | S20 | TOLM1 | Man.Amb.Temp.Set | FLOAT | RW | -60...500
68 | V7 | TOLM1 | TM> trip expect mode | UINT32 | R | 0=NoTrip expected;1=Trip expected
68 | I8 | TOLM1 | TM> Time to 100% T | UINT32 | R | 0...4294967295
68 | I9 | TOLM1 | TM> Reference T curr. | FLOAT | R | 0...50
68 | I10 | TOLM1 | TM> Active meas curr. | FLOAT | R | 0...50
68 | I11 | TOLM1 | TM> T est.with act. curr. | FLOAT | R | 0...500
68 | I12 | TOLM1 | TM> T at the moment | FLOAT | R | 0...500
68 | I13 | TOLM1 | TM> Max.Temp.Rise All. | FLOAT | R | 0...250
68 | I14 | TOLM1 | TM> Temp.Rise atm. | FLOAT | R | 0...250
68 | I15 | TOLM1 | TM> Hot Spot estimate | FLOAT | R | 0...250
68 | I16 | TOLM1 | TM> Hot Spot Max. All | FLOAT | R | 0...250
68 | I17 | TOLM1 | TM> Used k for amb. temp | FLOAT | R | 0...5
68 | I18 | TOLM1 | TM> Trip delay remaining | UINT32 | R | 0...4294967295
68 | I19 | TOLM1 | TM> Alarm 1 time to rel. | UINT32 | R | 0...4294967295
68 | I20 | TOLM1 | TM> Alarm 2 time to rel. | UINT32 | R | 0...4294967295
68 | I21 | TOLM1 | TM> Inhibit time to rel. | UINT32 | R | 0...4294967295
68 | I22 | TOLM1 | TM> Trip time to rel. | UINT32 | R | 0...4294967295
68 | I23 | TOLM1 | TM> Thermal cap used | FLOAT | R | 0...500
68 | I24 | TOLM1 | Alarm1 inits | UINT32 | R | 0...4294967295
68 | I25 | TOLM1 | Alarm2 inits | UINT32 | R | 0...4294967295
68 | I26 | TOLM1 | Restart Inhibits | UINT32 | R | 0...4294967295
68 | I27 | TOLM1 | Trips | UINT32 | R | 0...4294967295
68 | I28 | TOLM1 | Trips Blocked | UINT32 | R | 0...4294967295
68 | S21 | TOLM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
68 | S22 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S23 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S24 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S25 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S26 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S27 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S28 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S29 | TOLM1 | Enable TM> Alarm1 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S30 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S31 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S32 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S33 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S34 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S35 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S36 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S37 | TOLM1 | TM> Alarm1 level | FLOAT | RW | 0...150
68 | S38 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S39 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S40 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S41 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S42 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S43 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S44 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S45 | TOLM1 | Enable TM> Alarm2 | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S46 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S47 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S48 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S49 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S50 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S51 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S52 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S53 | TOLM1 | TM> Alarm2 level | FLOAT | RW | 0...150
68 | S54 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S55 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S56 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S57 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S58 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S59 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S60 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S61 | TOLM1 | Enable TM> Rest Inhibit | UINT32 | RW | 0=Disabled; 1=Enabled
68 | S62 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S63 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S64 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S65 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S66 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S67 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S68 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S69 | TOLM1 | TM> Inhibit level | FLOAT | RW | 0...150
68 | S70 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S71 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S72 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S73 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S74 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S75 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S76 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S77 | TOLM1 | TM> Trip level | FLOAT | RW | 0...150
68 | S78 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S79 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S80 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S81 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S82 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S83 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S84 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | S85 | TOLM1 | TM> Trip delay | FLOAT | RW | 0...3600
68 | O1 | TOLM1 | TM> Trip Blocked | SIGNAL_OUT | RW | 0...4294967295
68 | O2 | TOLM1 | TM> Alarm1 | SIGNAL_OUT | RW | 0...4294967295
68 | O3 | TOLM1 | TM> Alarm2 | SIGNAL_OUT | RW | 0...4294967295
68 | O4 | TOLM1 | TM> Restart Inh. | SIGNAL_OUT | RW | 0...4294967295
68 | O5 | TOLM1 | TM> Trip | SIGNAL_OUT | RW | 0...4294967295
68 | I29 | TOLM1 | Newest Register | UINT32 | R | 0...12
68 | I30 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I31 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I32 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I33 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I34 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I35 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I36 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I37 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I38 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I39 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I40 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I41 | TOLM1 | Time to reach 100% theta | FLOAT | R | 0...60000
68 | I42 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I43 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I44 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I45 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I46 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I47 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I48 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I49 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I50 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I51 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I52 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I53 | TOLM1 | Reference T current | FLOAT | R | 0...50
68 | I54 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I55 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I56 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I57 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I58 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I59 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I60 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I61 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I62 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I63 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I64 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I65 | TOLM1 | Active meas current | FLOAT | R | 0...250
68 | I66 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I67 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I68 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I69 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I70 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I71 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I72 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I73 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I74 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I75 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I76 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I77 | TOLM1 | T est.with act. curr. | FLOAT | R | 0...600000
68 | I78 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I79 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I80 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I81 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I82 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I83 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I84 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I85 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I86 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I87 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I88 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I89 | TOLM1 | T at the moment | FLOAT | R | 0...600000
68 | I90 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I91 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I92 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I93 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I94 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I95 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I96 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I97 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I98 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I99 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I100 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I101 | TOLM1 | Max.Temp.Rise Allowed | FLOAT | R | 0...500
68 | I102 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I103 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I104 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I105 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I106 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I107 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I108 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I109 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I110 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I111 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I112 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I113 | TOLM1 | Temp.Rise at the moment | FLOAT | R | 0...500
68 | I114 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I115 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I116 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I117 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I118 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I119 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I120 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I121 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I122 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I123 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I124 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I125 | TOLM1 | Hot Spot estimate | FLOAT | R | 0...500
68 | I126 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I127 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I128 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I129 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I130 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I131 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I132 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I133 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I134 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I135 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I136 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | I137 | TOLM1 | Hot Spot Max. Allowed | FLOAT | R | 0...500
68 | S86 | TOLM1 | EventMaskLo | UINT32 | RW | 0...4294967295
68 | S87 | TOLM1 | EventMaskHi | UINT32 | RW | 0...4294967295
57 | S1 | LCR1 | ISt> [48/14/50LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
57 | V1 | LCR1 | ISt> condition | UINT32 | R | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
57 | I1 | LCR1 | ISt> starts | UINT32 | R | 0...4294967295
57 | I2 | LCR1 | ISt> Set cap used in last start | FLOAT | R | 0...500
57 | I3 | LCR1 | ISt> Max cap used in last start | FLOAT | R | 0...500
57 | I4 | LCR1 | ISt> Set time trips | UINT32 | R | 0...4294967295
57 | I5 | LCR1 | ISt> Max cap trips | UINT32 | R | 0...4294967295
57 | I6 | LCR1 | ISt> blocks | UINT32 | R | 0...4294967295
57 | S2 | LCR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
57 | S3 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S4 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S5 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S6 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S7 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S8 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S9 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S10 | LCR1 | Starting time | FLOAT | RW | 0...1800
57 | S11 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S12 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S13 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S14 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S15 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S16 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S17 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S18 | LCR1 | Definite time or I2t | UINT32 | RW | 0=Definite;1=I2T mode
57 | S19 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S20 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S21 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S22 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S23 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S24 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S25 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S26 | LCR1 | Speed Switch in use | UINT32 | RW | 0=No;1=Yes
57 | S27 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S28 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S29 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S30 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S31 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S32 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S33 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S34 | LCR1 | Speed SW wait time | FLOAT | RW | 0...1800
57 | S35 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S36 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S37 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S38 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S39 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S40 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S41 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S42 | LCR1 | Speed SW NO/NC | UINT32 | RW | 0=NO;1=NC
57 | S43 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S44 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S45 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S46 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S47 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S48 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S49 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | S50 | LCR1 | Operate mode | UINT32 | RW | 0=Starts only;1=Starts and stall
57 | O1 | LCR1 | ISt> START | SIGNAL_OUT | RW | 0...4294967295
57 | O2 | LCR1 | ISt> Set time TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O3 | LCR1 | ISt> Machine cap.TRIP | SIGNAL_OUT | RW | 0...4294967295
57 | O4 | LCR1 | ISt> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
57 | I7 | LCR1 | Newest Register | UINT32 | R | 0...12
57 | I8 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I9 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I10 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I11 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I12 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I13 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I14 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I15 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I16 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I17 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I18 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I19 | LCR1 | Start/Stall time | FLOAT | R | 0...1800
57 | I20 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I21 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I22 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I23 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I24 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I25 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I26 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I27 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I28 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I29 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I30 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I31 | LCR1 | Max time used | FLOAT | R | 0...250
57 | I32 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I33 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I34 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I35 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I36 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I37 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I38 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I39 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I40 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I41 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I42 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I43 | LCR1 | Set time used | FLOAT | R | 0...250
57 | I44 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I45 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I46 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I47 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I48 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I49 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I50 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I51 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I52 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I53 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I54 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I55 | LCR1 | Therm.cap.used | FLOAT | R | 0...250
57 | I56 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I57 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I58 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I59 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I60 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I61 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I62 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I63 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I64 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I65 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I66 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I67 | LCR1 | Phase A current | FLOAT | R | 0...250
57 | I68 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I69 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I70 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I71 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I72 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I73 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I74 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I75 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I76 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I77 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I78 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I79 | LCR1 | Phase B current | FLOAT | R | 0...250
57 | I80 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I81 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I82 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I83 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I84 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I85 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I86 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I87 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I88 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I89 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I90 | LCR1 | Phase C current | FLOAT | R | 0...250
57 | I91 | LCR1 | Phase C current | FLOAT | R | 0...250
56 | S1 | FSP1 | N> [66/86] mode | UINT32 | RW | 0=Disabled; 1=Activated
56 | V1 | FSP1 | N> condition | UINT32 | R | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
56 | I1 | FSP1 | N> alarms | UINT32 | R | 0...4294967295
56 | I2 | FSP1 | N> Inhibits | UINT32 | R | 0...4294967295
56 | I3 | FSP1 | N> blocks | UINT32 | R | 0...4294967295
56 | S2 | FSP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
56 | I4 | FSP1 | Start monitoring time left | UINT32 | R | 0...4294967295
56 | I5 | FSP1 | Inhibit time on | UINT32 | R | 0...4294967295
56 | I6 | FSP1 | Alarm time on | UINT32 | R | 0...4294967295
56 | I7 | FSP1 | Time since last start | UINT32 | R | 0...4294967295
56 | I8 | FSP1 | Start count atm. | UINT32 | R | 0...4294967295
56 | I9 | FSP1 | Starts left atm. | UINT32 | R | 0...4294967295
56 | S3 | FSP1 | Give one more start (Warning! Motor may overheat) | UINT32 | W | 0=-;1=Deduct one start
56 | O1 | FSP1 | N> One start remaining (Alarm) | SIGNAL_OUT | RW | 0...4294967295
56 | O2 | FSP1 | N> INHIBIT ON (General) | SIGNAL_OUT | RW | 0...4294967295
56 | O3 | FSP1 | N> INHIBIT ON Mot Running | SIGNAL_OUT | RW | 0...4294967295
56 | O4 | FSP1 | N> INHIBIT ON Mot Stopped | SIGNAL_OUT | RW | 0...4294967295
56 | O5 | FSP1 | N> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
56 | I10 | FSP1 | Newest Register | UINT32 | R | 0...12
56 | S4 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S5 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S6 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S7 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S8 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S9 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S10 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S11 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S12 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S13 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S14 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S15 | FSP1 | Inh.time on | FLOAT | R | 0...1800
56 | S16 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S17 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S18 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S19 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S20 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S21 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S22 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S23 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S24 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S25 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S26 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S27 | FSP1 | Time since last start | FLOAT | R | 0...250
56 | S28 | FSP1 | Start count | FLOAT | R | 0...250
56 | S29 | FSP1 | Start count | FLOAT | R | 0...250
56 | S30 | FSP1 | Start count | FLOAT | R | 0...250
56 | S31 | FSP1 | Start count | FLOAT | R | 0...250
56 | S32 | FSP1 | Start count | FLOAT | R | 0...250
56 | S33 | FSP1 | Start count | FLOAT | R | 0...250
56 | S34 | FSP1 | Start count | FLOAT | R | 0...250
56 | S35 | FSP1 | Start count | FLOAT | R | 0...250
56 | S36 | FSP1 | Start count | FLOAT | R | 0...250
56 | S37 | FSP1 | Start count | FLOAT | R | 0...250
56 | S38 | FSP1 | Start count | FLOAT | R | 0...250
56 | S39 | FSP1 | Start count | FLOAT | R | 0...250
56 | S40 | FSP1 | EventMaskLo | UINT32 | RW | 0...4294967295
60 | S1 | NUC1 | I< [37] mode | UINT32 | RW | 0=Disabled; 1=Activated
60 | V1 | NUC1 | I< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
60 | I1 | NUC1 | I< starts | UINT32 | R | 0...4294967295
60 | I2 | NUC1 | I< trips | UINT32 | R | 0...4294967295
60 | I3 | NUC1 | I< blocks | UINT32 | R | 0...4294967295
60 | S2 | NUC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
60 | S3 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S4 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S5 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S6 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S7 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S8 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S9 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S10 | NUC1 | Pick-up setting Iset < | FLOAT | RW | 0.1...40
60 | S11 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S12 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S13 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S14 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S15 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S16 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S17 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S18 | NUC1 | Definite operating time delay | FLOAT | RW | 0...1800
60 | S19 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S20 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S21 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S22 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S23 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S24 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S25 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | S26 | NUC1 | Release Time delay | FLOAT | RW | 0...150
60 | O1 | NUC1 | I< START | SIGNAL_OUT | RW | 0...4294967295
60 | O2 | NUC1 | I< TRIP | SIGNAL_OUT | RW | 0...4294967295
60 | O3 | NUC1 | I< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
60 | I4 | NUC1 | Newest Register | UINT32 | R | 0...12
60 | I5 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I6 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I7 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I8 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I9 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I10 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I11 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I12 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I13 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I14 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I15 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I16 | NUC1 | Phase A fault current | FLOAT | R | 0...250
60 | I17 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I18 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I19 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I20 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I21 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I22 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I23 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I24 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I25 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I26 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I27 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I28 | NUC1 | Phase B fault current | FLOAT | R | 0...250
60 | I29 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I30 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I31 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I32 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I33 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I34 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I35 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I36 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I37 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I38 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I39 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | I40 | NUC1 | Phase C fault current | FLOAT | R | 0...250
60 | S27 | NUC1 | EventMaskLo | UINT32 | RW | 0...4294967295
59 | S1 | MJP1 | Im> [51LR] mode | UINT32 | RW | 0=Disabled; 1=Activated
59 | V1 | MJP1 | Im> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
59 | I1 | MJP1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
59 | I2 | MJP1 | Im> starts | UINT32 | R | 0...4294967295
59 | I3 | MJP1 | Im> trips | UINT32 | R | 0...4294967295
59 | I4 | MJP1 | Im> blocks | UINT32 | R | 0...4294967295
59 | S2 | MJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
59 | S3 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S4 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S5 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S6 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S7 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S8 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S9 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S10 | MJP1 | Pick-up setting Iset | FLOAT | RW | 0.1...40
59 | S11 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S12 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S13 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S14 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S15 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S16 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S17 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | S18 | MJP1 | Definite operating time delay | FLOAT | RW | 0...1800
59 | O1 | MJP1 | Im> START | SIGNAL_OUT | RW | 0...4294967295
59 | O2 | MJP1 | Im> TRIP | SIGNAL_OUT | RW | 0...4294967295
59 | O3 | MJP1 | Im> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
59 | I5 | MJP1 | Newest Register | UINT32 | R | 0...12
59 | I6 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I7 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I8 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I9 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I10 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I11 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I12 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I13 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I14 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I15 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I16 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I17 | MJP1 | Phase A fault current | FLOAT | R | 0...250
59 | I18 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I19 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I20 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I21 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I22 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I23 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I24 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I25 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I26 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I27 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I28 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I29 | MJP1 | Phase B fault current | FLOAT | R | 0...250
59 | I30 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I31 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I32 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I33 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I34 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I35 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I36 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I37 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I38 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I39 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I40 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | I41 | MJP1 | Phase C fault current | FLOAT | R | 0...250
59 | S19 | MJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
85 | S1 | OV1 | U> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
85 | V1 | OV1 | U> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
85 | I1 | OV1 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
85 | I2 | OV1 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
85 | I3 | OV1 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
85 | I4 | OV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
85 | I5 | OV1 | U> starts | UINT32 | R | 0...4294967295
85 | I6 | OV1 | U> trips | UINT32 | R | 0...4294967295
85 | I7 | OV1 | U> blocks | UINT32 | R | 0...4294967295
85 | S2 | OV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
85 | S3 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S4 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S5 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S6 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S7 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S8 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S9 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S10 | OV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
85 | S11 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S12 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S13 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S14 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S15 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S16 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S17 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S18 | OV1 | Pick-up setting Uset | FLOAT | RW | 50...150
85 | S19 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S20 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S21 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S22 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S23 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S24 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S25 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | S26 | OV1 | Definite operating time delay | FLOAT | RW | 0...1800
85 | O1 | OV1 | U> START | SIGNAL_OUT | RW | 0...4294967295
85 | O2 | OV1 | U> TRIP | SIGNAL_OUT | RW | 0...4294967295
85 | O3 | OV1 | U> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
85 | I8 | OV1 | Newest Register | UINT32 | R | 0...12
85 | I9 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I10 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I11 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I12 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I13 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I14 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I15 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I16 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I17 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I18 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I19 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I20 | OV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
85 | I21 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I22 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I23 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I24 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I25 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I26 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I27 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I28 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I29 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I30 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I31 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I32 | OV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
85 | I33 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I34 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I35 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I36 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I37 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I38 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I39 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I40 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I41 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I42 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I43 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | I44 | OV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
85 | S27 | OV1 | EventMaskLo | UINT32 | RW | 0...4294967295
86 | S1 | OV2 | U>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
86 | V1 | OV2 | U>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
86 | I1 | OV2 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
86 | I2 | OV2 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
86 | I3 | OV2 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
86 | I4 | OV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
86 | I5 | OV2 | U>> starts | UINT32 | R | 0...4294967295
86 | I6 | OV2 | U>> trips | UINT32 | R | 0...4294967295
86 | I7 | OV2 | U>> blocks | UINT32 | R | 0...4294967295
86 | S2 | OV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
86 | S3 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S4 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S5 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S6 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S7 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S8 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S9 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S10 | OV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
86 | S11 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S12 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S13 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S14 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S15 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S16 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S17 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S18 | OV2 | Pick-up setting Uset | FLOAT | RW | 50...150
86 | S19 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S20 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S21 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S22 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S23 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S24 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S25 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | S26 | OV2 | Definite operating time delay | FLOAT | RW | 0...1800
86 | O1 | OV2 | U>> START | SIGNAL_OUT | RW | 0...4294967295
86 | O2 | OV2 | U>> TRIP | SIGNAL_OUT | RW | 0...4294967295
86 | O3 | OV2 | U>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
86 | I8 | OV2 | Newest Register | UINT32 | R | 0...12
86 | I9 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I10 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I11 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I12 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I13 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I14 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I15 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I16 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I17 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I18 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I19 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I20 | OV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
86 | I21 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I22 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I23 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I24 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I25 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I26 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I27 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I28 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I29 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I30 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I31 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I32 | OV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
86 | I33 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I34 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I35 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I36 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I37 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I38 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I39 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I40 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I41 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I42 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I43 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | I44 | OV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
86 | S27 | OV2 | EventMaskLo | UINT32 | RW | 0...4294967295
87 | S1 | OV3 | U>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
87 | V1 | OV3 | U>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
87 | I1 | OV3 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
87 | I2 | OV3 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
87 | I3 | OV3 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
87 | I4 | OV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
87 | I5 | OV3 | U>>> starts | UINT32 | R | 0...4294967295
87 | I6 | OV3 | U>>> trips | UINT32 | R | 0...4294967295
87 | I7 | OV3 | U>>> blocks | UINT32 | R | 0...4294967295
87 | S2 | OV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
87 | S3 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S4 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S5 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S6 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S7 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S8 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S9 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S10 | OV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
87 | S11 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S12 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S13 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S14 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S15 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S16 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S17 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S18 | OV3 | Pick-up setting Uset | FLOAT | RW | 50...150
87 | S19 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S20 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S21 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S22 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S23 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S24 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S25 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | S26 | OV3 | Definite operating time delay | FLOAT | RW | 0...1800
87 | O1 | OV3 | U>>> START | SIGNAL_OUT | RW | 0...4294967295
87 | O2 | OV3 | U>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
87 | O3 | OV3 | U>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
87 | I8 | OV3 | Newest Register | UINT32 | R | 0...12
87 | I9 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I10 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I11 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I12 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I13 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I14 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I15 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I16 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I17 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I18 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I19 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I20 | OV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
87 | I21 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I22 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I23 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I24 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I25 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I26 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I27 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I28 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I29 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I30 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I31 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I32 | OV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
87 | I33 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I34 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I35 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I36 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I37 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I38 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I39 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I40 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I41 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I42 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I43 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | I44 | OV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
87 | S27 | OV3 | EventMaskLo | UINT32 | RW | 0...4294967295
88 | S1 | OV4 | U>>>> [59] mode | UINT32 | RW | 0=Disabled;1=Activated
88 | V1 | OV4 | U>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
88 | I1 | OV4 | Umeas/Uset A(B) at the moment | FLOAT | R | 0...1250
88 | I2 | OV4 | Umeas/Uset B(C) at the moment | FLOAT | R | 0...1250
88 | I3 | OV4 | Umeas/Uset C(A) at the moment | FLOAT | R | 0...1250
88 | I4 | OV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
88 | I5 | OV4 | U>>>> starts | UINT32 | R | 0...4294967295
88 | I6 | OV4 | U>>>> trips | UINT32 | R | 0...4294967295
88 | I7 | OV4 | U>>>> blocks | UINT32 | R | 0...4294967295
88 | S2 | OV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
88 | S3 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S4 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S5 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S6 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S7 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S8 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S9 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S10 | OV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
88 | S11 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S12 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S13 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S14 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S15 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S16 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S17 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S18 | OV4 | Pick-up setting Uset | FLOAT | RW | 50...150
88 | S19 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S20 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S21 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S22 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S23 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S24 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S25 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | S26 | OV4 | Definite operating time delay | FLOAT | RW | 0...1800
88 | O1 | OV4 | U>>>> START | SIGNAL_OUT | RW | 0...4294967295
88 | O2 | OV4 | U>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
88 | O3 | OV4 | U>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
88 | I8 | OV4 | Newest Register | UINT32 | R | 0...12
88 | I9 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I10 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I11 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I12 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I13 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I14 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I15 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I16 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I17 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I18 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I19 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I20 | OV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
88 | I21 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I22 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I23 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I24 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I25 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I26 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I27 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I28 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I29 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I30 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I31 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I32 | OV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
88 | I33 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I34 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I35 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I36 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I37 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I38 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I39 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I40 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I41 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I42 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I43 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | I44 | OV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
88 | S27 | OV4 | EventMaskLo | UINT32 | RW | 0...4294967295
89 | S1 | UV1 | U< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
89 | V1 | UV1 | U< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
89 | I1 | UV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
89 | I2 | UV1 | U< starts | UINT32 | R | 0...4294967295
89 | I3 | UV1 | U< trips | UINT32 | R | 0...4294967295
89 | I4 | UV1 | U< blocks | UINT32 | R | 0...4294967295
89 | S2 | UV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
89 | S3 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S4 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S5 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S6 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S7 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S8 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S9 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S10 | UV1 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
89 | S11 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S12 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S13 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S14 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S15 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S16 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S17 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S18 | UV1 | Pick-up setting Uset< | FLOAT | RW | 0...120
89 | S19 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S20 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S21 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S22 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S23 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S24 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S25 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S26 | UV1 | Block setting Uset< | FLOAT | RW | 0...80
89 | S27 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S28 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S29 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S30 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S31 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S32 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S33 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | S34 | UV1 | Definite operating time delay | FLOAT | RW | 0...1800
89 | O1 | UV1 | U< START | SIGNAL_OUT | RW | 0...4294967295
89 | O2 | UV1 | U< TRIP | SIGNAL_OUT | RW | 0...4294967295
89 | O3 | UV1 | U< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
89 | I5 | UV1 | Newest Register | UINT32 | R | 0...12
89 | I6 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I7 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I8 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I9 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I10 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I11 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I12 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I13 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I14 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I15 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I16 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I17 | UV1 | Voltage A(B) fault volt | FLOAT | R | 0...250
89 | I18 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I19 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I20 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I21 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I22 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I23 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I24 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I25 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I26 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I27 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I28 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I29 | UV1 | Voltage B(C) fault volt | FLOAT | R | 0...250
89 | I30 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I31 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I32 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I33 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I34 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I35 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I36 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I37 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I38 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I39 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I40 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | I41 | UV1 | Voltage C(A) fault volt | FLOAT | R | 0...250
89 | S35 | UV1 | EventMaskLo | UINT32 | RW | 0...4294967295
90 | S1 | UV2 | U<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
90 | V1 | UV2 | U<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
90 | I1 | UV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
90 | I2 | UV2 | U<< starts | UINT32 | R | 0...4294967295
90 | I3 | UV2 | U<< trips | UINT32 | R | 0...4294967295
90 | I4 | UV2 | U<< blocks | UINT32 | R | 0...4294967295
90 | S2 | UV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
90 | S3 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S4 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S5 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S6 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S7 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S8 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S9 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S10 | UV2 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
90 | S11 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S12 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S13 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S14 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S15 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S16 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S17 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S18 | UV2 | Pick-up setting Uset<< | FLOAT | RW | 0...120
90 | S19 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S20 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S21 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S22 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S23 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S24 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S25 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S26 | UV2 | Block setting Uset<< | FLOAT | RW | 0...80
90 | S27 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S28 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S29 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S30 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S31 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S32 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S33 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | S34 | UV2 | Definite operating time delay | FLOAT | RW | 0...1800
90 | O1 | UV2 | U<< START | SIGNAL_OUT | RW | 0...4294967295
90 | O2 | UV2 | U<< TRIP | SIGNAL_OUT | RW | 0...4294967295
90 | O3 | UV2 | U<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
90 | I5 | UV2 | Newest Register | UINT32 | R | 0...12
90 | I6 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I7 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I8 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I9 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I10 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I11 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I12 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I13 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I14 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I15 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I16 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I17 | UV2 | Voltage A(B) fault volt | FLOAT | R | 0...250
90 | I18 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I19 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I20 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I21 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I22 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I23 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I24 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I25 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I26 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I27 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I28 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I29 | UV2 | Voltage B(C) fault volt | FLOAT | R | 0...250
90 | I30 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I31 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I32 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I33 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I34 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I35 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I36 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I37 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I38 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I39 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I40 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | I41 | UV2 | Voltage C(A) fault volt | FLOAT | R | 0...250
90 | S35 | UV2 | EventMaskLo | UINT32 | RW | 0...4294967295
91 | S1 | UV3 | U<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
91 | V1 | UV3 | U<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
91 | I1 | UV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
91 | I2 | UV3 | U<<< starts | UINT32 | R | 0...4294967295
91 | I3 | UV3 | U<<< trips | UINT32 | R | 0...4294967295
91 | I4 | UV3 | U<<< blocks | UINT32 | R | 0...4294967295
91 | S2 | UV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
91 | S3 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S4 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S5 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S6 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S7 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S8 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S9 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S10 | UV3 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
91 | S11 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S12 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S13 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S14 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S15 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S16 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S17 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S18 | UV3 | Pick-up setting Uset<<< | FLOAT | RW | 0...120
91 | S19 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S20 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S21 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S22 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S23 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S24 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S25 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S26 | UV3 | Block setting Uset<<< | FLOAT | RW | 0...80
91 | S27 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S28 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S29 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S30 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S31 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S32 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S33 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | S34 | UV3 | Definite operating time delay | FLOAT | RW | 0...1800
91 | O1 | UV3 | U<<< START | SIGNAL_OUT | RW | 0...4294967295
91 | O2 | UV3 | U<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
91 | O3 | UV3 | U<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
91 | I5 | UV3 | Newest Register | UINT32 | R | 0...12
91 | I6 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I7 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I8 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I9 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I10 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I11 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I12 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I13 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I14 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I15 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I16 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I17 | UV3 | Voltage A(B) fault volt | FLOAT | R | 0...250
91 | I18 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I19 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I20 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I21 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I22 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I23 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I24 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I25 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I26 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I27 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I28 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I29 | UV3 | Voltage B(C) fault volt | FLOAT | R | 0...250
91 | I30 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I31 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I32 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I33 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I34 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I35 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I36 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I37 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I38 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I39 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I40 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | I41 | UV3 | Voltage C(A) fault volt | FLOAT | R | 0...250
91 | S35 | UV3 | EventMaskLo | UINT32 | RW | 0...4294967295
92 | S1 | UV4 | U<<<< [27] mode | UINT32 | RW | 0=Disabled;1=Activated
92 | V1 | UV4 | U<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
92 | I1 | UV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
92 | I2 | UV4 | U<<<< starts | UINT32 | R | 0...4294967295
92 | I3 | UV4 | U<<<< trips | UINT32 | R | 0...4294967295
92 | I4 | UV4 | U<<<< blocks | UINT32 | R | 0...4294967295
92 | S2 | UV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
92 | S3 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S4 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S5 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S6 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S7 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S8 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S9 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S10 | UV4 | Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
92 | S11 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S12 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S13 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S14 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S15 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S16 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S17 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S18 | UV4 | Pick-up setting Uset<<<< | FLOAT | RW | 0...120
92 | S19 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S20 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S21 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S22 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S23 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S24 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S25 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S26 | UV4 | Block setting Uset<<<< | FLOAT | RW | 0...80
92 | S27 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S28 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S29 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S30 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S31 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S32 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S33 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | S34 | UV4 | Definite operating time delay | FLOAT | RW | 0...1800
92 | O1 | UV4 | U<<<< START | SIGNAL_OUT | RW | 0...4294967295
92 | O2 | UV4 | U<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
92 | O3 | UV4 | U<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
92 | I5 | UV4 | Newest Register | UINT32 | R | 0...12
92 | I6 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I7 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I8 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I9 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I10 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I11 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I12 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I13 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I14 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I15 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I16 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I17 | UV4 | Voltage A(B) fault volt | FLOAT | R | 0...250
92 | I18 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I19 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I20 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I21 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I22 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I23 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I24 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I25 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I26 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I27 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I28 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I29 | UV4 | Voltage B(C) fault volt | FLOAT | R | 0...250
92 | I30 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I31 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I32 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I33 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I34 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I35 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I36 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I37 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I38 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I39 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I40 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | I41 | UV4 | Voltage C(A) fault volt | FLOAT | R | 0...250
92 | S35 | UV4 | EventMaskLo | UINT32 | RW | 0...4294967295
93 | S1 | NOV1 | U0> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
93 | V1 | NOV1 | U0> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
93 | I1 | NOV1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
93 | I2 | NOV1 | U0> starts | UINT32 | R | 0...4294967295
93 | I3 | NOV1 | U0> trips | UINT32 | R | 0...4294967295
93 | I4 | NOV1 | U0> blocks | UINT32 | R | 0...4294967295
93 | S2 | NOV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
93 | S3 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S4 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S5 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S6 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S7 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S8 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S9 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S10 | NOV1 | Pick-up setting U0set> | FLOAT | RW | 1...99
93 | S11 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S12 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S13 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S14 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S15 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S16 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S17 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | S18 | NOV1 | Definite operating time delay | FLOAT | RW | 0...1800
93 | O1 | NOV1 | U0> START | SIGNAL_OUT | RW | 0...4294967295
93 | O2 | NOV1 | U0> TRIP | SIGNAL_OUT | RW | 0...4294967295
93 | O3 | NOV1 | U0> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
93 | I5 | NOV1 | Newest Register | UINT32 | R | 0...12
93 | I6 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I7 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I8 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I9 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I10 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I11 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I12 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I13 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I14 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I15 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I16 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I17 | NOV1 | U0 Fault (%) | FLOAT | R | 0...250
93 | I18 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I19 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I20 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I21 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I22 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I23 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I24 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I25 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I26 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I27 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I28 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | I29 | NOV1 | U0 Fault (V) | FLOAT | R | 0...250
93 | S19 | NOV1 | EventMaskLo | UINT32 | RW | 0...4294967295
94 | S1 | NOV2 | U0>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
94 | V1 | NOV2 | U0>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
94 | I1 | NOV2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
94 | I2 | NOV2 | U0>> starts | UINT32 | R | 0...4294967295
94 | I3 | NOV2 | U0>> trips | UINT32 | R | 0...4294967295
94 | I4 | NOV2 | U0>> blocks | UINT32 | R | 0...4294967295
94 | S2 | NOV2 | Clear statistics | UINT32 | W | 0=-;1=Clear
94 | S3 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S4 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S5 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S6 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S7 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S8 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S9 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S10 | NOV2 | Pick-up setting U0set> | FLOAT | RW | 1...99
94 | S11 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S12 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S13 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S14 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S15 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S16 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S17 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | S18 | NOV2 | Definite operating time delay | FLOAT | RW | 0...1800
94 | O1 | NOV2 | U0>> START | SIGNAL_OUT | RW | 0...4294967295
94 | O2 | NOV2 | U0>> TRIP | SIGNAL_OUT | RW | 0...4294967295
94 | O3 | NOV2 | U0>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
94 | I5 | NOV2 | Newest Register | UINT32 | R | 0...12
94 | I6 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I7 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I8 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I9 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I10 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I11 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I12 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I13 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I14 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I15 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I16 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I17 | NOV2 | U0 Fault (%) | FLOAT | R | 0...250
94 | I18 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I19 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I20 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I21 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I22 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I23 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I24 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I25 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I26 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I27 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I28 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | I29 | NOV2 | U0 Fault (V) | FLOAT | R | 0...250
94 | S19 | NOV2 | EventMaskLo | UINT32 | RW | 0...4294967295
95 | S1 | NOV3 | U0>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
95 | V1 | NOV3 | U0>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
95 | I1 | NOV3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
95 | I2 | NOV3 | U0>>> starts | UINT32 | R | 0...4294967295
95 | I3 | NOV3 | U0>>> trips | UINT32 | R | 0...4294967295
95 | I4 | NOV3 | U0>>> blocks | UINT32 | R | 0...4294967295
95 | S2 | NOV3 | Clear statistics | UINT32 | W | 0=-;1=Clear
95 | S3 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S4 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S5 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S6 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S7 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S8 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S9 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S10 | NOV3 | Pick-up setting U0set> | FLOAT | RW | 1...99
95 | S11 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S12 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S13 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S14 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S15 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S16 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S17 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | S18 | NOV3 | Definite operating time delay | FLOAT | RW | 0...1800
95 | O1 | NOV3 | U0>>> START | SIGNAL_OUT | RW | 0...4294967295
95 | O2 | NOV3 | U0>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
95 | O3 | NOV3 | U0>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
95 | I5 | NOV3 | Newest Register | UINT32 | R | 0...12
95 | I6 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I7 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I8 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I9 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I10 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I11 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I12 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I13 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I14 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I15 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I16 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I17 | NOV3 | U0 Fault (%) | FLOAT | R | 0...250
95 | I18 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I19 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I20 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I21 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I22 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I23 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I24 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I25 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I26 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I27 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I28 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | I29 | NOV3 | U0 Fault (V) | FLOAT | R | 0...250
95 | S19 | NOV3 | EventMaskLo | UINT32 | RW | 0...4294967295
96 | S1 | NOV4 | U0>>>> [59N] mode | UINT32 | RW | 0=Disabled;1=Activated
96 | V1 | NOV4 | U0>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
96 | I1 | NOV4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
96 | I2 | NOV4 | U0>>>> starts | UINT32 | R | 0...4294967295
96 | I3 | NOV4 | U0>>>> trips | UINT32 | R | 0...4294967295
96 | I4 | NOV4 | U0>>>> blocks | UINT32 | R | 0...4294967295
96 | S2 | NOV4 | Clear statistics | UINT32 | W | 0=-;1=Clear
96 | S3 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S4 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S5 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S6 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S7 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S8 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S9 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S10 | NOV4 | Pick-up setting U0set> | FLOAT | RW | 1...99
96 | S11 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S12 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S13 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S14 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S15 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S16 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S17 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | S18 | NOV4 | Definite operating time delay | FLOAT | RW | 0...1800
96 | O1 | NOV4 | U0>>>> START | SIGNAL_OUT | RW | 0...4294967295
96 | O2 | NOV4 | U0>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
96 | O3 | NOV4 | U0>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
96 | I5 | NOV4 | Newest Register | UINT32 | R | 0...12
96 | I6 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I7 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I8 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I9 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I10 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I11 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I12 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I13 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I14 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I15 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I16 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I17 | NOV4 | U0 Fault (%) | FLOAT | R | 0...250
96 | I18 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I19 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I20 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I21 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I22 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I23 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I24 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I25 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I26 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I27 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I28 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | I29 | NOV4 | U0 Fault (V) | FLOAT | R | 0...250
96 | S19 | NOV4 | EventMaskLo | UINT32 | RW | 0...4294967295
130 | S1 | VUB1 | U1/2 >/< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
130 | V1 | VUB1 | U1/2 >/< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
130 | I1 | VUB1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
130 | I2 | VUB1 | U1/2 >/< starts | UINT32 | R | 0...4294967295
130 | I3 | VUB1 | U1/2 >/< trips | UINT32 | R | 0...4294967295
130 | I4 | VUB1 | U1/2 >/< blocks | UINT32 | R | 0...4294967295
130 | S2 | VUB1 | Clear statistics | UINT32 | W | 0=-;1=Clear
130 | S3 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S4 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S5 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S6 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S7 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S8 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S9 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S10 | VUB1 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
130 | S11 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S12 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S13 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S14 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S15 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S16 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S17 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S18 | VUB1 | Pick-up setting Uset | FLOAT | RW | 5...150
130 | S19 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S20 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S21 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S22 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S23 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S24 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S25 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S26 | VUB1 | Under block setting Ublk | FLOAT | RW | 0...80
130 | S27 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S28 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S29 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S30 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S31 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S32 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S33 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | S34 | VUB1 | Definite operating time delay | FLOAT | RW | 0...1800
130 | O1 | VUB1 | U1/2 >/< START | SIGNAL_OUT | RW | 0...4294967295
130 | O2 | VUB1 | U1/2 >/< TRIP | SIGNAL_OUT | RW | 0...4294967295
130 | O3 | VUB1 | U1/2 >/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
130 | I5 | VUB1 | Newest Register | UINT32 | R | 0...12
130 | I6 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I7 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I8 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I9 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I10 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I11 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I12 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I13 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I14 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I15 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I16 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I17 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I18 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I19 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I20 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I21 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I22 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I23 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I24 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I25 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I26 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I27 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I28 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | I29 | VUB1 | Voltage U1/U2 fault | FLOAT | R | 0...250
130 | S35 | VUB1 | EventMaskLo | UINT32 | RW | 0...4294967295
131 | S1 | VUB2 | U1/2 >>/<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
131 | V1 | VUB2 | U1/2 >>/<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
131 | I1 | VUB2 | Umeas/Uset at the moment | FLOAT | R | 0...1250
131 | I2 | VUB2 | U1/2 >>/<< starts | UINT32 | R | 0...4294967295
131 | I3 | VUB2 | U1/2 >>/<< trips | UINT32 | R | 0...4294967295
131 | I4 | VUB2 | U1/2 >>/<< blocks | UINT32 | R | 0...4294967295
131 | S2 | VUB2 | Clear statistics | UINT32 | W | 0=-;1=Clear
131 | S3 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S4 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S5 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S6 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S7 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S8 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S9 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S10 | VUB2 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
131 | S11 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S12 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S13 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S14 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S15 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S16 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S17 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S18 | VUB2 | Pick-up setting Uset | FLOAT | RW | 5...150
131 | S19 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S20 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S21 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S22 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S23 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S24 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S25 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S26 | VUB2 | Under block setting Ublk | FLOAT | RW | 0...80
131 | S27 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S28 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S29 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S30 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S31 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S32 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S33 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | S34 | VUB2 | Definite operating time delay | FLOAT | RW | 0...1800
131 | O1 | VUB2 | U1/2 >>/<< START | SIGNAL_OUT | RW | 0...4294967295
131 | O2 | VUB2 | U1/2 >>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
131 | O3 | VUB2 | U1/2 >>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
131 | I5 | VUB2 | Newest Register | UINT32 | R | 0...12
131 | I6 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I7 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I8 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I9 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I10 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I11 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I12 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I13 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I14 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I15 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I16 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I17 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I18 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I19 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I20 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I21 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I22 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I23 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I24 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I25 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I26 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I27 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I28 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | I29 | VUB2 | Voltage U1/U2 fault | FLOAT | R | 0...250
131 | S35 | VUB2 | EventMaskLo | UINT32 | RW | 0...4294967295
132 | S1 | VUB3 | U1/2 >>>/<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
132 | V1 | VUB3 | U1/2 >>>/<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
132 | I1 | VUB3 | Umeas/Uset at the moment | FLOAT | R | 0...1250
132 | I2 | VUB3 | U1/2 >>>/<<< starts | UINT32 | R | 0...4294967295
132 | I3 | VUB3 | U1/2 >>>/<<< trips | UINT32 | R | 0...4294967295
132 | I4 | VUB3 | U1/2 >>>/<<< blocks | UINT32 | R | 0...4294967295
132 | S2 | VUB3 | Clear statistics | UINT32 | W | 0=-;1=Clear
132 | S3 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S4 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S5 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S6 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S7 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S8 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S9 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S10 | VUB3 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
132 | S11 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S12 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S13 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S14 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S15 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S16 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S17 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S18 | VUB3 | Pick-up setting Uset | FLOAT | RW | 5...150
132 | S19 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S20 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S21 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S22 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S23 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S24 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S25 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S26 | VUB3 | Under block setting Ublk | FLOAT | RW | 0...80
132 | S27 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S28 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S29 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S30 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S31 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S32 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S33 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | S34 | VUB3 | Definite operating time delay | FLOAT | RW | 0...1800
132 | O1 | VUB3 | U1/2 >>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
132 | O2 | VUB3 | U1/2 >>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
132 | O3 | VUB3 | U1/2 >>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
132 | I5 | VUB3 | Newest Register | UINT32 | R | 0...12
132 | I6 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I7 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I8 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I9 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I10 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I11 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I12 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I13 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I14 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I15 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I16 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I17 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I18 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I19 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I20 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I21 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I22 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I23 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I24 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I25 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I26 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I27 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I28 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | I29 | VUB3 | Voltage U1/U2 fault | FLOAT | R | 0...250
132 | S35 | VUB3 | EventMaskLo | UINT32 | RW | 0...4294967295
133 | S1 | VUB4 | U1/2 >>>>/<<<< [47/27PN/59PN] mode | UINT32 | RW | 0=Disabled;1=Activated
133 | V1 | VUB4 | U1/2 >>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
133 | I1 | VUB4 | Umeas/Uset at the moment | FLOAT | R | 0...1250
133 | I2 | VUB4 | U1/2 >>>>/<<<< starts | UINT32 | R | 0...4294967295
133 | I3 | VUB4 | U1/2 >>>>/<<<< trips | UINT32 | R | 0...4294967295
133 | I4 | VUB4 | U1/2 >>>>/<<<< blocks | UINT32 | R | 0...4294967295
133 | S2 | VUB4 | Clear statistics | UINT32 | W | 0=-;1=Clear
133 | S3 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S4 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S5 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S6 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S7 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S8 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S9 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S10 | VUB4 | Pick-up terms | UINT32 | RW | 0=Over >;1=Under <
133 | S11 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S12 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S13 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S14 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S15 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S16 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S17 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S18 | VUB4 | Pick-up setting Uset | FLOAT | RW | 5...150
133 | S19 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S20 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S21 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S22 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S23 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S24 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S25 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S26 | VUB4 | Under block setting Ublk | FLOAT | RW | 0...80
133 | S27 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S28 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S29 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S30 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S31 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S32 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S33 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | S34 | VUB4 | Definite operating time delay | FLOAT | RW | 0...1800
133 | O1 | VUB4 | U1/2 >>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
133 | O2 | VUB4 | U1/2 >>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
133 | O3 | VUB4 | U1/2 >>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
133 | I5 | VUB4 | Newest Register | UINT32 | R | 0...12
133 | I6 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I7 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I8 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I9 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I10 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I11 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I12 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I13 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I14 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I15 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I16 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I17 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I18 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I19 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I20 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I21 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I22 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I23 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I24 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I25 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I26 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I27 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I28 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | I29 | VUB4 | Voltage U1/U2 fault | FLOAT | R | 0...250
133 | S35 | VUB4 | EventMaskLo | UINT32 | RW | 0...4294967295
99 | S1 | FRQV1 | f</> [81O/81U] mode | UINT32 | RW | 0=Disabled;1=Activated
99 | V1 | FRQV1 | f> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I1 | FRQV1 | f> fmeas / fset | FLOAT | R | 0...20
99 | S2 | FRQV1 | f>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V2 | FRQV1 | f>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I2 | FRQV1 | f>> fmeas / fset | FLOAT | R | 0...20
99 | S3 | FRQV1 | f>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V3 | FRQV1 | f>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I3 | FRQV1 | f>>> fmeas / fset | FLOAT | R | 0...20
99 | S4 | FRQV1 | f>>>> Enable | UINT32 | RW | 0=No;1=Yes
99 | V4 | FRQV1 | f>>>> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I4 | FRQV1 | f>>>> fmeas / fset | FLOAT | R | 0...20
99 | S5 | FRQV1 | f< Enable | UINT32 | RW | 0=No;1=Yes
99 | V5 | FRQV1 | f< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I5 | FRQV1 | f< fmeas / fset | FLOAT | R | 0...20
99 | S6 | FRQV1 | f<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V6 | FRQV1 | f<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I6 | FRQV1 | f<< fmeas / fset | FLOAT | R | 0...20
99 | S7 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V7 | FRQV1 | f<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I7 | FRQV1 | f<<< fmeas / fset | FLOAT | R | 0...20
99 | S8 | FRQV1 | f<<< Enable | UINT32 | RW | 0=No;1=Yes
99 | V8 | FRQV1 | f<<<< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
99 | I8 | FRQV1 | f<<<< fmeas / fset | FLOAT | R | 0...20
99 | I9 | FRQV1 | f> starts | UINT32 | R | 0...4294967295
99 | I10 | FRQV1 | f> trips | UINT32 | R | 0...4294967295
99 | I11 | FRQV1 | f> blocks | UINT32 | R | 0...4294967295
99 | I12 | FRQV1 | f>> starts | UINT32 | R | 0...4294967295
99 | I13 | FRQV1 | f>> trips | UINT32 | R | 0...4294967295
99 | I14 | FRQV1 | f>> blocks | UINT32 | R | 0...4294967295
99 | I15 | FRQV1 | f>>> starts | UINT32 | R | 0...4294967295
99 | I16 | FRQV1 | f>>> trips | UINT32 | R | 0...4294967295
99 | I17 | FRQV1 | f>>> blocks | UINT32 | R | 0...4294967295
99 | I18 | FRQV1 | f>>>> starts | UINT32 | R | 0...4294967295
99 | I19 | FRQV1 | f>>>> trips | UINT32 | R | 0...4294967295
99 | I20 | FRQV1 | f>>>> blocks | UINT32 | R | 0...4294967295
99 | I21 | FRQV1 | f< starts | UINT32 | R | 0...4294967295
99 | I22 | FRQV1 | f< trips | UINT32 | R | 0...4294967295
99 | I23 | FRQV1 | f< blocks | UINT32 | R | 0...4294967295
99 | I24 | FRQV1 | f<< starts | UINT32 | R | 0...4294967295
99 | I25 | FRQV1 | f<< trips | UINT32 | R | 0...4294967295
99 | I26 | FRQV1 | f<< blocks | UINT32 | R | 0...4294967295
99 | I27 | FRQV1 | f<<< starts | UINT32 | R | 0...4294967295
99 | I28 | FRQV1 | f<<< trips | UINT32 | R | 0...4294967295
99 | I29 | FRQV1 | f<<< blocks | UINT32 | R | 0...4294967295
99 | I30 | FRQV1 | f<<<< starts | UINT32 | R | 0...4294967295
99 | I31 | FRQV1 | f<<<< trips | UINT32 | R | 0...4294967295
99 | I32 | FRQV1 | f<<<< blocks | UINT32 | R | 0...4294967295
99 | S9 | FRQV1 | Clear statistics | UINT32 | W | 0=-;1=Clear
99 | S10 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S11 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S12 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S13 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S14 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S15 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S16 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S17 | FRQV1 | f> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S18 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S19 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S20 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S21 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S22 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S23 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S24 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S25 | FRQV1 | f> pick-up | FLOAT | RW | 10...70
99 | S26 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S27 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S28 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S29 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S30 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S31 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S32 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S33 | FRQV1 | f> Op.time | FLOAT | RW | 0...1800
99 | S34 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S35 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S36 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S37 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S38 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S39 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S40 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S41 | FRQV1 | f>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S42 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S43 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S44 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S45 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S46 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S47 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S48 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S49 | FRQV1 | f>> pick-up | FLOAT | RW | 10...70
99 | S50 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S51 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S52 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S53 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S54 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S55 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S56 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S57 | FRQV1 | f>> Op.time | FLOAT | RW | 0...1800
99 | S58 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S59 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S60 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S61 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S62 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S63 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S64 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S65 | FRQV1 | f>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S66 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S67 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S68 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S69 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S70 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S71 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S72 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S73 | FRQV1 | f>>> pick-up | FLOAT | RW | 10...70
99 | S74 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S75 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S76 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S77 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S78 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S79 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S80 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S81 | FRQV1 | f>>> Op.time | FLOAT | RW | 0...1800
99 | S82 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S83 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S84 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S85 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S86 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S87 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S88 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S89 | FRQV1 | f>>>> Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S90 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S91 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S92 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S93 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S94 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S95 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S96 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S97 | FRQV1 | f>>>> pick-up | FLOAT | RW | 10...70
99 | S98 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S99 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S100 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S101 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S102 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S103 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S104 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S105 | FRQV1 | f>>>> Op.time | FLOAT | RW | 0...1800
99 | S106 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S107 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S108 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S109 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S110 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S111 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S112 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S113 | FRQV1 | f< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S114 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S115 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S116 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S117 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S118 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S119 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S120 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S121 | FRQV1 | f< pick-up | FLOAT | RW | 7...65
99 | S122 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S123 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S124 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S125 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S126 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S127 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S128 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S129 | FRQV1 | f< Op.time | FLOAT | RW | 0...1800
99 | S130 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S131 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S132 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S133 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S134 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S135 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S136 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S137 | FRQV1 | f<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S138 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S139 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S140 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S141 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S142 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S143 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S144 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S145 | FRQV1 | f<< pick-up | FLOAT | RW | 7...65
99 | S146 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S147 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S148 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S149 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S150 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S151 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S152 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S153 | FRQV1 | f<< Op.time | FLOAT | RW | 0...1800
99 | S154 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S155 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S156 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S157 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S158 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S159 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S160 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S161 | FRQV1 | f<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S162 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S163 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S164 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S165 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S166 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S167 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S168 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S169 | FRQV1 | f<<< pick-up | FLOAT | RW | 7...65
99 | S170 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S171 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S172 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S173 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S174 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S175 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S176 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S177 | FRQV1 | f<<< Op.time | FLOAT | RW | 0...1800
99 | S178 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S179 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S180 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S181 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S182 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S183 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S184 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S185 | FRQV1 | f<<<< Used in SG | UINT32 | RW | 0=No;1=Yes
99 | S186 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S187 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S188 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S189 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S190 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S191 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S192 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S193 | FRQV1 | f<<<< pick-up | FLOAT | RW | 7...65
99 | S194 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S195 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S196 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S197 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S198 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S199 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S200 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | S201 | FRQV1 | f<<<< Op.time | FLOAT | RW | 0...1800
99 | O1 | FRQV1 | f> START | SIGNAL_OUT | RW | 0...4294967295
99 | O2 | FRQV1 | f> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O3 | FRQV1 | f> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O4 | FRQV1 | f>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O5 | FRQV1 | f>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O6 | FRQV1 | f>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O7 | FRQV1 | f>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O8 | FRQV1 | f>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O9 | FRQV1 | f>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O10 | FRQV1 | f>>>> START | SIGNAL_OUT | RW | 0...4294967295
99 | O11 | FRQV1 | f>>>> TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O12 | FRQV1 | f>>>> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O13 | FRQV1 | f< START | SIGNAL_OUT | RW | 0...4294967295
99 | O14 | FRQV1 | f< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O15 | FRQV1 | f< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O16 | FRQV1 | f<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O17 | FRQV1 | f<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O18 | FRQV1 | f<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O19 | FRQV1 | f<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O20 | FRQV1 | f<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O21 | FRQV1 | f<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | O22 | FRQV1 | f<<<< START | SIGNAL_OUT | RW | 0...4294967295
99 | O23 | FRQV1 | f<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
99 | O24 | FRQV1 | f<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
99 | I33 | FRQV1 | Newest Register | UINT32 | R | 0...12
99 | I34 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I35 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I36 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I37 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I38 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I39 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I40 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I41 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I42 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I43 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I44 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | I45 | FRQV1 | f Fault (Hz) | FLOAT | R | 0...250
99 | S202 | FRQV1 | EventMaskLo | UINT32 | RW | 0...4294967295
103 | S1 | DFT1 | df/dt >/< [81] mode | UINT32 | RW | 0=Disabled;1=Activated
103 | S2 | DFT1 | Max allowed df/dt rate | FLOAT | RW | 0.1...50
103 | I1 | DFT1 | Measured df/dt | FLOAT | R | 0...20
103 | S3 | DFT1 | df/dt >/< (1) Enable | UINT32 | RW | 0=No;1=Yes
103 | V1 | DFT1 | df/dt >/< (1) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I2 | DFT1 | df/dt >/< (1) fmeas / fset | FLOAT | R | 0...20
103 | S4 | DFT1 | df/dt >/< (2) Enable | UINT32 | RW | 0=No;1=Yes
103 | V2 | DFT1 | df/dt >/< (2) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I3 | DFT1 | df/dt >/< (2) fmeas / fset | FLOAT | R | 0...20
103 | S5 | DFT1 | df/dt >/< (3) Enable | UINT32 | RW | 0=No;1=Yes
103 | V3 | DFT1 | df/dt >/< (3) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I4 | DFT1 | df/dt >/< (3) fmeas / fset | FLOAT | R | 0...20
103 | S6 | DFT1 | df/dt >/< (4) Enable | UINT32 | RW | 0=No;1=Yes
103 | V4 | DFT1 | df/dt >/< (4) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I5 | DFT1 | df/dt >/< (4) fmeas / fset | FLOAT | R | 0...20
103 | S7 | DFT1 | df/dt >/< (5) Enable | UINT32 | RW | 0=No;1=Yes
103 | V5 | DFT1 | df/dt >/< (5) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I6 | DFT1 | df/dt >/< (5) fmeas / fset | FLOAT | R | 0...20
103 | S8 | DFT1 | df/dt >/< (6) Enable | UINT32 | RW | 0=No;1=Yes
103 | V6 | DFT1 | df/dt >/< (6) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I7 | DFT1 | df/dt >/< (6) fmeas / fset | FLOAT | R | 0...20
103 | S9 | DFT1 | df/dt >/< (7) Enable | UINT32 | RW | 0=No;1=Yes
103 | V7 | DFT1 | df/dt >/< (7) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I8 | DFT1 | df/dt >/< (7) fmeas / fset | FLOAT | R | 0...20
103 | S10 | DFT1 | df/dt >/< (8) Enable | UINT32 | RW | 0=No;1=Yes
103 | V8 | DFT1 | df/dt >/< (8) condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
103 | I9 | DFT1 | df/dt >/< (8) fmeas / fset | FLOAT | R | 0...20
103 | I10 | DFT1 | df/dt >/< (1) starts | UINT32 | R | 0...4294967295
103 | I11 | DFT1 | df/dt >/< (1) trips | UINT32 | R | 0...4294967295
103 | I12 | DFT1 | df/dt >/< (1) blocks | UINT32 | R | 0...4294967295
103 | I13 | DFT1 | df/dt >/< (2) starts | UINT32 | R | 0...4294967295
103 | I14 | DFT1 | df/dt >/< (2) trips | UINT32 | R | 0...4294967295
103 | I15 | DFT1 | df/dt >/< (2) blocks | UINT32 | R | 0...4294967295
103 | I16 | DFT1 | df/dt >/< (3) starts | UINT32 | R | 0...4294967295
103 | I17 | DFT1 | df/dt >/< (3) trips | UINT32 | R | 0...4294967295
103 | I18 | DFT1 | df/dt >/< (3) blocks | UINT32 | R | 0...4294967295
103 | I19 | DFT1 | df/dt >/< (4) starts | UINT32 | R | 0...4294967295
103 | I20 | DFT1 | df/dt >/< (4) trips | UINT32 | R | 0...4294967295
103 | I21 | DFT1 | df/dt >/< (4) blocks | UINT32 | R | 0...4294967295
103 | I22 | DFT1 | df/dt >/< (5) starts | UINT32 | R | 0...4294967295
103 | I23 | DFT1 | df/dt >/< (5) trips | UINT32 | R | 0...4294967295
103 | I24 | DFT1 | df/dt >/< (5) blocks | UINT32 | R | 0...4294967295
103 | I25 | DFT1 | df/dt >/< (6) starts | UINT32 | R | 0...4294967295
103 | I26 | DFT1 | df/dt >/< (6) trips | UINT32 | R | 0...4294967295
103 | I27 | DFT1 | df/dt >/< (6) blocks | UINT32 | R | 0...4294967295
103 | I28 | DFT1 | df/dt >/< (7) starts | UINT32 | R | 0...4294967295
103 | I29 | DFT1 | df/dt >/< (7) trips | UINT32 | R | 0...4294967295
103 | I30 | DFT1 | df/dt >/< (7) blocks | UINT32 | R | 0...4294967295
103 | I31 | DFT1 | df/dt >/< (8) starts | UINT32 | R | 0...4294967295
103 | I32 | DFT1 | df/dt >/< (8) trips | UINT32 | R | 0...4294967295
103 | I33 | DFT1 | df/dt >/< (8) blocks | UINT32 | R | 0...4294967295
103 | S11 | DFT1 | Clear statistics | UINT32 | W | 0=-;1=Clear
103 | S12 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S13 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S14 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S15 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S16 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S17 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S18 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S19 | DFT1 | df/dt >/< (1) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S20 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S21 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S22 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S23 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S24 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S25 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S26 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S27 | DFT1 | df/dt >/< (1) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S28 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S29 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S30 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S31 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S32 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S33 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S34 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S35 | DFT1 | df/dt >/< (1) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S36 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S37 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S38 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S39 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S40 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S41 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S42 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S43 | DFT1 | df/dt >/< (1) f > limit | FLOAT | RW | 10...70
103 | S44 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S45 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S46 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S47 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S48 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S49 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S50 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S51 | DFT1 | df/dt >/< (1) f < limit | FLOAT | RW | 7...65
103 | S52 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S53 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S54 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S55 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S56 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S57 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S58 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S59 | DFT1 | df/dt >/< (1) pick-up | FLOAT | RW | 0.15...10
103 | S60 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S61 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S62 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S63 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S64 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S65 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S66 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S67 | DFT1 | df/dt >/< (1) Op.time | FLOAT | RW | 0...1800
103 | S68 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S69 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S70 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S71 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S72 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S73 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S74 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S75 | DFT1 | df/dt >/< (2) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S76 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S77 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S78 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S79 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S80 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S81 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S82 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S83 | DFT1 | df/dt >/< (2) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S84 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S85 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S86 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S87 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S88 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S89 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S90 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S91 | DFT1 | df/dt >/< (2) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S92 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S93 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S94 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S95 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S96 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S97 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S98 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S99 | DFT1 | df/dt >/< (2) f > limit | FLOAT | RW | 10...70
103 | S100 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S101 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S102 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S103 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S104 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S105 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S106 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S107 | DFT1 | df/dt >/< (2) f < limit | FLOAT | RW | 7...65
103 | S108 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S109 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S110 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S111 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S112 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S113 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S114 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S115 | DFT1 | df/dt >/< (2) pick-up | FLOAT | RW | 0.15...10
103 | S116 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S117 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S118 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S119 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S120 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S121 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S122 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S123 | DFT1 | df/dt >/< (2) Op.time | FLOAT | RW | 0...1800
103 | S124 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S125 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S126 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S127 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S128 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S129 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S130 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S131 | DFT1 | df/dt >/< (3) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S132 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S133 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S134 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S135 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S136 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S137 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S138 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S139 | DFT1 | df/dt >/< (3) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S140 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S141 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S142 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S143 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S144 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S145 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S146 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S147 | DFT1 | df/dt >/< (3) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S148 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S149 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S150 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S151 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S152 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S153 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S154 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S155 | DFT1 | df/dt >/< (3) f > limit | FLOAT | RW | 10...70
103 | S156 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S157 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S158 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S159 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S160 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S161 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S162 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S163 | DFT1 | df/dt >/< (3) f < limit | FLOAT | RW | 7...65
103 | S164 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S165 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S166 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S167 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S168 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S169 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S170 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S171 | DFT1 | df/dt >/< (3) pick-up | FLOAT | RW | 0.15...10
103 | S172 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S173 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S174 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S175 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S176 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S177 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S178 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S179 | DFT1 | df/dt >/< (3) Op.time | FLOAT | RW | 0...1800
103 | S180 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S181 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S182 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S183 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S184 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S185 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S186 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S187 | DFT1 | df/dt >/< (4) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S188 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S189 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S190 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S191 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S192 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S193 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S194 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S195 | DFT1 | df/dt >/< (4) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S196 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S197 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S198 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S199 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S200 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S201 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S202 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S203 | DFT1 | df/dt >/< (4) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S204 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S205 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S206 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S207 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S208 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S209 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S210 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S211 | DFT1 | df/dt >/< (4) f > limit | FLOAT | RW | 10...70
103 | S212 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S213 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S214 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S215 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S216 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S217 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S218 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S219 | DFT1 | df/dt >/< (4) f < limit | FLOAT | RW | 7...65
103 | S220 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S221 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S222 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S223 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S224 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S225 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S226 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S227 | DFT1 | df/dt >/< (4) pick-up | FLOAT | RW | 0.15...10
103 | S228 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S229 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S230 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S231 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S232 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S233 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S234 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S235 | DFT1 | df/dt >/< (4) Op.time | FLOAT | RW | 0...1800
103 | S236 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S237 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S238 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S239 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S240 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S241 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S242 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S243 | DFT1 | df/dt >/< (5) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S244 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S245 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S246 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S247 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S248 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S249 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S250 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S251 | DFT1 | df/dt >/< (5) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S252 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S253 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S254 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S255 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S256 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S257 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S258 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S259 | DFT1 | df/dt >/< (5) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S260 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S261 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S262 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S263 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S264 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S265 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S266 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S267 | DFT1 | df/dt >/< (5) f > limit | FLOAT | RW | 10...70
103 | S268 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S269 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S270 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S271 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S272 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S273 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S274 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S275 | DFT1 | df/dt >/< (5) f < limit | FLOAT | RW | 7...65
103 | S276 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S277 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S278 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S279 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S280 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S281 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S282 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S283 | DFT1 | df/dt >/< (5) pick-up | FLOAT | RW | 0.15...10
103 | S284 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S285 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S286 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S287 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S288 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S289 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S290 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S291 | DFT1 | df/dt >/< (5) Op.time | FLOAT | RW | 0...1800
103 | S292 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S293 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S294 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S295 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S296 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S297 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S298 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S299 | DFT1 | df/dt >/< (6) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S300 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S301 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S302 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S303 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S304 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S305 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S306 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S307 | DFT1 | df/dt >/< (6) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S308 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S309 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S310 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S311 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S312 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S313 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S314 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S315 | DFT1 | df/dt >/< (6) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S316 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S317 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S318 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S319 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S320 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S321 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S322 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S323 | DFT1 | df/dt >/< (6) f > limit | FLOAT | RW | 10...70
103 | S324 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S325 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S326 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S327 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S328 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S329 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S330 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S331 | DFT1 | df/dt >/< (6) f < limit | FLOAT | RW | 7...65
103 | S332 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S333 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S334 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S335 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S336 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S337 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S338 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S339 | DFT1 | df/dt >/< (6) pick-up | FLOAT | RW | 0.15...10
103 | S340 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S341 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S342 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S343 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S344 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S345 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S346 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S347 | DFT1 | df/dt >/< (6) Op.time | FLOAT | RW | 0...1800
103 | S348 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S349 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S350 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S351 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S352 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S353 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S354 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S355 | DFT1 | df/dt >/< (7) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S356 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S357 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S358 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S359 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S360 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S361 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S362 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S363 | DFT1 | df/dt >/< (7) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S364 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S365 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S366 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S367 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S368 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S369 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S370 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S371 | DFT1 | df/dt >/< (7) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S372 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S373 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S374 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S375 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S376 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S377 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S378 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S379 | DFT1 | df/dt >/< (7) f > limit | FLOAT | RW | 10...70
103 | S380 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S381 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S382 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S383 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S384 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S385 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S386 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S387 | DFT1 | df/dt >/< (7) f < limit | FLOAT | RW | 7...65
103 | S388 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S389 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S390 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S391 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S392 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S393 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S394 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S395 | DFT1 | df/dt >/< (7) pick-up | FLOAT | RW | 0.15...10
103 | S396 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S397 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S398 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S399 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S400 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S401 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S402 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S403 | DFT1 | df/dt >/< (7) Op.time | FLOAT | RW | 0...1800
103 | S404 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S405 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S406 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S407 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S408 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S409 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S410 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S411 | DFT1 | df/dt >/< (8) Used in SG | UINT32 | RW | 0=No;1=Yes
103 | S412 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S413 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S414 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S415 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S416 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S417 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S418 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S419 | DFT1 | df/dt >/< (8) op.mode | UINT32 | RW | 0=Rising;1=Falling;2=Both
103 | S420 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S421 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S422 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S423 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S424 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S425 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S426 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S427 | DFT1 | df/dt >/< (8) Freqlimit | UINT32 | R | 0=Not used;1=Use f limit
103 | S428 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S429 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S430 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S431 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S432 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S433 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S434 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S435 | DFT1 | df/dt >/< (8) f > limit | FLOAT | RW | 10...70
103 | S436 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S437 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S438 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S439 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S440 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S441 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S442 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S443 | DFT1 | df/dt >/< (8) f < limit | FLOAT | RW | 7...65
103 | S444 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S445 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S446 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S447 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S448 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S449 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S450 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S451 | DFT1 | df/dt >/< (8) pick-up | FLOAT | RW | 0.15...10
103 | S452 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S453 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S454 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S455 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S456 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S457 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S458 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | S459 | DFT1 | df/dt >/< (8) Op.time | FLOAT | RW | 0...1800
103 | O1 | DFT1 | df/dt >/< (1) START | SIGNAL_OUT | RW | 0...4294967295
103 | O2 | DFT1 | df/dt >/< (1) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O3 | DFT1 | df/dt >/< (1) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O4 | DFT1 | df/dt >/< (2) START | SIGNAL_OUT | RW | 0...4294967295
103 | O5 | DFT1 | df/dt >/< (2) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O6 | DFT1 | df/dt >/< (2) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O7 | DFT1 | df/dt >/< (3) START | SIGNAL_OUT | RW | 0...4294967295
103 | O8 | DFT1 | df/dt >/< (3) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O9 | DFT1 | df/dt >/< (3) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O10 | DFT1 | df/dt >/< (4) START | SIGNAL_OUT | RW | 0...4294967295
103 | O11 | DFT1 | df/dt >/< (4) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O12 | DFT1 | df/dt >/< (4) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O13 | DFT1 | df/dt >/< (5) START | SIGNAL_OUT | RW | 0...4294967295
103 | O14 | DFT1 | df/dt >/< (5) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O15 | DFT1 | df/dt >/< (5) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O16 | DFT1 | df/dt >/< (6) START | SIGNAL_OUT | RW | 0...4294967295
103 | O17 | DFT1 | df/dt >/< (6) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O18 | DFT1 | df/dt >/< (6) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O19 | DFT1 | df/dt >/< (7) START | SIGNAL_OUT | RW | 0...4294967295
103 | O20 | DFT1 | df/dt >/< (7) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O21 | DFT1 | df/dt >/< (7) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | O22 | DFT1 | df/dt >/< (8) START | SIGNAL_OUT | RW | 0...4294967295
103 | O23 | DFT1 | df/dt >/< (8) TRIP | SIGNAL_OUT | RW | 0...4294967295
103 | O24 | DFT1 | df/dt >/< (8) BLOCKED | SIGNAL_OUT | RW | 0...4294967295
103 | I34 | DFT1 | Newest Register | UINT32 | R | 0...12
103 | I35 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I36 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I37 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I38 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I39 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I40 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I41 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I42 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I43 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I44 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I45 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I46 | DFT1 | df/dt Fault (Hz/s) | FLOAT | R | 0...250
103 | I47 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I48 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I49 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I50 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I51 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I52 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I53 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I54 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I55 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I56 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I57 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | I58 | DFT1 | f Fault (Hz) | FLOAT | R | 0...75
103 | S460 | DFT1 | EventMaskLo | UINT32 | RW | 0...4294967295
183 | V1 | RHC1 | Counter is now | UINT32 | R | 0=Idle;1=Counting
183 | I1 | RHC1 | Running hours | UINT32 | RW | 0...4294967295
183 | I2 | RHC1 | Start count | UINT32 | RW | 0...4294967295
183 | I3 | RHC1 | Clear Hours | UINT32 | W | 0=-;1=Clear
183 | S1 | RHC1 | EventMaskLo | UINT32 | RW | 0...4294967295
113 | V1 | GST1 | Generator is now | UINT32 | R | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
113 | I1 | GST1 | Times Overloaded | UINT32 | R | 0...4294967295
113 | I2 | GST1 | Times Heavy overloaded | UINT32 | R | 0...4294967295
113 | I3 | GST1 | Clear statistics | UINT32 | W | 0=-;1=Clear
113 | I4 | GST1 | Generating time | UINT32 | R | 0...4294967295
113 | I5 | GST1 | Overloading cumulative | UINT32 | R | 0...4294967295
113 | I6 | GST1 | Last overload duration | UINT32 | R | 0...4294967295
113 | I7 | GST1 | Heavy overloading cumulative | UINT32 | R | 0...4294967295
113 | I8 | GST1 | Last Heavy overload duration | UINT32 | R | 0...4294967295
113 | S1 | GST1 | Clear total times | UINT32 | W | 0=-;1=Clear
113 | S2 | GST1 | Generator nominal MVA (S) | FLOAT | RW | 0.1...500
113 | S3 | GST1 | Generator nominal Voltage (Vt) | FLOAT | RW | 0.1...25
113 | S4 | GST1 | Prime mover max power output (Pmax) | FLOAT | RW | 0.1...500
113 | S5 | GST1 | Block trafo in protection area | UINT32 | RW | 0=No;1=Yes
113 | S6 | GST1 | Generator voltage measurement | UINT32 | RW | 0=LV side VT (no corrections);1=HV side VT(Reduce to LV);2=HV side VT(HV measurements)
113 | S7 | GST1 | Ratio for generator nominal voltage scaling (1 p.u.) | UINT32 | RW | 0=Generator nominal voltage;1=Transformer LV nominal voltage;2=Set Un ratio by hand
113 | I9 | GST1 | Transformer ratio HV -> LV Trafo. | FLOAT | R | 0.01...100
113 | I10 | GST1 | Transformer ratio HV -> LV Gen. | FLOAT | R | 0.01...100
113 | I11 | GST1 | Voltage ratio | FLOAT | RW | 0.001...100
113 | I12 | GST1 | Voltage scaling | FLOAT | R | 0.01...100
113 | S8 | GST1 | Transformer nominal MVA | FLOAT | RW | 0.001...500
113 | S9 | GST1 | HV side nominal voltage | FLOAT | RW | 0.001...500
113 | S10 | GST1 | LV side nominal voltage | FLOAT | RW | 0.001...500
113 | S11 | GST1 | Transformer Zk % | FLOAT | RW | 0.001...25
113 | S12 | GST1 | Transformer nom freq. | FLOAT | RW | 10...75
113 | S13 | GST1 | Transf. Vect. group | UINT32 | RW | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
113 | I13 | GST1 | HV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I14 | GST1 | HV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I15 | GST1 | HV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I16 | GST1 | LV side nominal current(pri) | FLOAT | R | 0.01...50000
113 | I17 | GST1 | LV side nominal current(sec) | FLOAT | R | 0.01...250
113 | I18 | GST1 | LV CT nom to TR nom factor | FLOAT | R | 0.01...250
113 | I19 | GST1 | Transformer nom impedance | FLOAT | R | 0.01...250
113 | I20 | GST1 | Transformer nom Zk ohm | FLOAT | R | 0.01...250
113 | I21 | GST1 | Transformer nom SC inductance | FLOAT | R | 0.001...100
113 | I22 | GST1 | LV side max 3ph SC curr | FLOAT | R | 0.001...500
113 | I23 | GST1 | LV side 3ph SC to HV side | FLOAT | R | 0.001...500
113 | I24 | GST1 | LV side max 2ph SC curr | FLOAT | R | 0.001...500
113 | I25 | GST1 | LV side 2ph SC to HV side | FLOAT | R | 0.001...500
113 | I26 | GST1 | Trafo HV nominal current | FLOAT | R | 0.01...50000
113 | I27 | GST1 | Trafo LV nominal current | FLOAT | R | 0.01...50000
113 | O1 | GST1 | No/Light load | SIGNAL_OUT | RW | 0...4294967295
113 | O2 | GST1 | HV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O3 | GST1 | LV side inrush detected | SIGNAL_OUT | RW | 0...4294967295
113 | O4 | GST1 | Load normal | SIGNAL_OUT | RW | 0...4294967295
113 | O5 | GST1 | Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | O6 | GST1 | HVY Overloading | SIGNAL_OUT | RW | 0...4294967295
113 | I28 | GST1 | Newest Register | UINT32 | R | 0...12
113 | I29 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I30 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I31 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I32 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I33 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I34 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I35 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I36 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I37 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I38 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I39 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I40 | GST1 | L1 Current | FLOAT | R | 0...250
113 | I41 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I42 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I43 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I44 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I45 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I46 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I47 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I48 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I49 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I50 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I51 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I52 | GST1 | L2 Current | FLOAT | R | 0...250
113 | I53 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I54 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I55 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I56 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I57 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I58 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I59 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I60 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I61 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I62 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I63 | GST1 | L3 Current | FLOAT | R | 0...250
113 | I64 | GST1 | L3 Current | FLOAT | R | 0...250
113 | S14 | GST1 | EventMaskLo | UINT32 | RW | 0...4294967295
164 | S1 | PWR1 | PQS>/< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
164 | V1 | PWR1 | PQS>/< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
164 | I1 | PWR1 | Meas/Set at the moment | FLOAT | R | -1250...1250
164 | I2 | PWR1 | Meas/Nom at the moment | FLOAT | R | -1250...1250
164 | I3 | PWR1 | PQS>/< starts | UINT32 | R | 0...4294967295
164 | I4 | PWR1 | PQS>/< trips | UINT32 | R | 0...4294967295
164 | I5 | PWR1 | PQS>/< blocks | UINT32 | R | 0...4294967295
164 | S2 | PWR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
164 | S3 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S4 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S5 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S6 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S7 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S8 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S9 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S10 | PWR1 | Pick-up setting PQS>/< | FLOAT | RW | -500...500
164 | S11 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S12 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S13 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S14 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S15 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S16 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S17 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | S18 | PWR1 | Definite operating time delay | FLOAT | RW | 0...1800
164 | O1 | PWR1 | PQS>/< START | SIGNAL_OUT | RW | 0...4294967295
164 | O2 | PWR1 | PQS>/< TRIP | SIGNAL_OUT | RW | 0...4294967295
164 | O3 | PWR1 | PQS>/< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
164 | I6 | PWR1 | Newest Register | UINT32 | R | 0...12
164 | I7 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I8 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I9 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I10 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I11 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I12 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I13 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I14 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I15 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I16 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I17 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | I18 | PWR1 | 3PH fault power | FLOAT | R | 0...250
164 | S19 | PWR1 | EventMaskLo | UINT32 | RW | 0...4294967295
165 | S1 | PWR2 | PQS>>/<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
165 | V1 | PWR2 | PQS>>/<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
165 | I1 | PWR2 | Meas/Set at the moment | FLOAT | R | -1250...1250
165 | I2 | PWR2 | Meas/Nom at the moment | FLOAT | R | -1250...1250
165 | I3 | PWR2 | PQS>>/<< starts | UINT32 | R | 0...4294967295
165 | I4 | PWR2 | PQS>>/<< trips | UINT32 | R | 0...4294967295
165 | I5 | PWR2 | PQS>>/<< blocks | UINT32 | R | 0...4294967295
165 | S2 | PWR2 | Clear statistics | UINT32 | W | 0=-;1=Clear
165 | S3 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S4 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S5 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S6 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S7 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S8 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S9 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S10 | PWR2 | Pick-up setting PQS>>/<< | FLOAT | RW | -500...500
165 | S11 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S12 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S13 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S14 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S15 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S16 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S17 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | S18 | PWR2 | Definite operating time delay | FLOAT | RW | 0...1800
165 | O1 | PWR2 | PQS>>/<< START | SIGNAL_OUT | RW | 0...4294967295
165 | O2 | PWR2 | PQS>>/<< TRIP | SIGNAL_OUT | RW | 0...4294967295
165 | O3 | PWR2 | PQS>>/<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
165 | I6 | PWR2 | Newest Register | UINT32 | R | 0...12
165 | I7 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I8 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I9 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I10 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I11 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I12 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I13 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I14 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I15 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I16 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I17 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | I18 | PWR2 | 3PH fault power | FLOAT | R | 0...250
165 | S19 | PWR2 | EventMaskLo | UINT32 | RW | 0...4294967295
166 | S1 | PWR3 | PQS>>>/<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
166 | V1 | PWR3 | PQS>>>/<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
166 | I1 | PWR3 | Meas/Set at the moment | FLOAT | R | -1250...1250
166 | I2 | PWR3 | Meas/Nom at the moment | FLOAT | R | -1250...1250
166 | I3 | PWR3 | PQS>>>/<<< starts | UINT32 | R | 0...4294967295
166 | I4 | PWR3 | PQS>>>/<<< trips | UINT32 | R | 0...4294967295
166 | I5 | PWR3 | PQS>>>/<<< blocks | UINT32 | R | 0...4294967295
166 | S2 | PWR3 | Clear statistics | UINT32 | W | 0=-;1=Clear
166 | S3 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S4 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S5 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S6 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S7 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S8 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S9 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S10 | PWR3 | Pick-up setting PQS>>>/<<< | FLOAT | RW | -500...500
166 | S11 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S12 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S13 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S14 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S15 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S16 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S17 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | S18 | PWR3 | Definite operating time delay | FLOAT | RW | 0...1800
166 | O1 | PWR3 | PQS>>>/<<< START | SIGNAL_OUT | RW | 0...4294967295
166 | O2 | PWR3 | PQS>>>/<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
166 | O3 | PWR3 | PQS>>>/<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
166 | I6 | PWR3 | Newest Register | UINT32 | R | 0...12
166 | I7 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I8 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I9 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I10 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I11 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I12 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I13 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I14 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I15 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I16 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I17 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | I18 | PWR3 | 3PH fault power | FLOAT | R | 0...250
166 | S19 | PWR3 | EventMaskLo | UINT32 | RW | 0...4294967295
167 | S1 | PWR4 | PQS>>>>/<<<< [32] mode | UINT32 | RW | 0=Disabled; 1=Activated
167 | V1 | PWR4 | PQS>>>>/<<<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
167 | I1 | PWR4 | Meas/Set at the moment | FLOAT | R | -1250...1250
167 | I2 | PWR4 | Meas/Nom at the moment | FLOAT | R | -1250...1250
167 | I3 | PWR4 | PQS>>>>/<<<< starts | UINT32 | R | 0...4294967295
167 | I4 | PWR4 | PQS>>>>/<<<< trips | UINT32 | R | 0...4294967295
167 | I5 | PWR4 | PQS>>>>/<<<< blocks | UINT32 | R | 0...4294967295
167 | S2 | PWR4 | Clear statistics | UINT32 | W | 0=-;1=Clear
167 | S3 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S4 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S5 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S6 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S7 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S8 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S9 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S10 | PWR4 | Pick-up setting PQS>>>>/<<<< | FLOAT | RW | -500...500
167 | S11 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S12 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S13 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S14 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S15 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S16 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S17 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | S18 | PWR4 | Definite operating time delay | FLOAT | RW | 0...1800
167 | O1 | PWR4 | PQS>>>>/<<<< START | SIGNAL_OUT | RW | 0...4294967295
167 | O2 | PWR4 | PQS>>>>/<<<< TRIP | SIGNAL_OUT | RW | 0...4294967295
167 | O3 | PWR4 | PQS>>>>/<<<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
167 | I6 | PWR4 | Newest Register | UINT32 | R | 0...12
167 | I7 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I8 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I9 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I10 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I11 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I12 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I13 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I14 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I15 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I16 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I17 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | I18 | PWR4 | 3PH fault power | FLOAT | R | 0...250
167 | S19 | PWR4 | EventMaskLo | UINT32 | RW | 0...4294967295
100 | S1 | OPW1 | P> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
100 | V1 | OPW1 | P> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
100 | I1 | OPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
100 | I2 | OPW1 | P> starts | UINT32 | R | 0...4294967295
100 | I3 | OPW1 | P> trips | UINT32 | R | 0...4294967295
100 | I4 | OPW1 | P> blocks | UINT32 | R | 0...4294967295
100 | S2 | OPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
100 | S3 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S4 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S5 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S6 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S7 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S8 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S9 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S10 | OPW1 | Pick-up setting Pset> | FLOAT | RW | 0.1...150000
100 | S11 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S12 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S13 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S14 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S15 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S16 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S17 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | S18 | OPW1 | Definite operating time delay | FLOAT | RW | 0...1800
100 | O1 | OPW1 | P> START | SIGNAL_OUT | RW | 0...4294967295
100 | O2 | OPW1 | P> TRIP | SIGNAL_OUT | RW | 0...4294967295
100 | O3 | OPW1 | P> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
100 | I5 | OPW1 | Newest Register | UINT32 | R | 0...12
100 | I6 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I7 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I8 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I9 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I10 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I11 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I12 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I13 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I14 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I15 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I16 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | I17 | OPW1 | 3PH fault power | FLOAT | R | 0...250
100 | S19 | OPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
101 | S1 | UPW1 | P< [37] mode | UINT32 | RW | 0=Disabled;1=Activated
101 | V1 | UPW1 | P< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
101 | I1 | UPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
101 | I2 | UPW1 | P< starts | UINT32 | R | 0...4294967295
101 | I3 | UPW1 | P< trips | UINT32 | R | 0...4294967295
101 | I4 | UPW1 | P< blocks | UINT32 | R | 0...4294967295
101 | S2 | UPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
101 | S3 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S4 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S5 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S6 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S7 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S8 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S9 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S10 | UPW1 | Pick-up setting Pset< | FLOAT | RW | -150000...150000
101 | S11 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S12 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S13 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S14 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S15 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S16 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S17 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S18 | UPW1 | Low Power Block Pset< | FLOAT | RW | 0...100000
101 | S19 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S20 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S21 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S22 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S23 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S24 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S25 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | S26 | UPW1 | Definite operating time delay | FLOAT | RW | 0...1800
101 | O1 | UPW1 | P< START | SIGNAL_OUT | RW | 0...4294967295
101 | O2 | UPW1 | P< TRIP | SIGNAL_OUT | RW | 0...4294967295
101 | O3 | UPW1 | P< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
101 | I5 | UPW1 | Newest Register | UINT32 | R | 0...12
101 | I6 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I7 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I8 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I9 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I10 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I11 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I12 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I13 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I14 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I15 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I16 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | I17 | UPW1 | 3PH fault power | FLOAT | R | 0...250
101 | S27 | UPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
102 | S1 | RPW1 | Prev> [32] mode | UINT32 | RW | 0=Disabled;1=Activated
102 | V1 | RPW1 | Prev> condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked
102 | I1 | RPW1 | Pmeas/Pset at the moment | FLOAT | R | 0...1250
102 | I2 | RPW1 | Prev> starts | UINT32 | R | 0...4294967295
102 | I3 | RPW1 | Prev> trips | UINT32 | R | 0...4294967295
102 | I4 | RPW1 | Prev> blocks | UINT32 | R | 0...4294967295
102 | S2 | RPW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
102 | S3 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S4 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S5 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S6 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S7 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S8 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S9 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S10 | RPW1 | Pick-up setting Pset rev. | FLOAT | RW | -15000...0
102 | S11 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S12 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S13 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S14 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S15 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S16 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S17 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | S18 | RPW1 | Definite operating time delay | FLOAT | RW | 0...1800
102 | O1 | RPW1 | Prev> START | SIGNAL_OUT | RW | 0...4294967295
102 | O2 | RPW1 | Prev> TRIP | SIGNAL_OUT | RW | 0...4294967295
102 | O3 | RPW1 | Prev> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
102 | I5 | RPW1 | Newest Register | UINT32 | R | 0...12
102 | I6 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I7 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I8 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I9 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I10 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I11 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I12 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I13 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I14 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I15 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I16 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | I17 | RPW1 | 3PH fault power | FLOAT | R | 0...250
102 | S19 | RPW1 | EventMaskLo | UINT32 | RW | 0...4294967295
110 | S1 | SEF1 | U03rd< [64S] mode | UINT32 | RW | 0=Disabled; 1=Activated
110 | V1 | SEF1 | U03rd< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
110 | I1 | SEF1 | Umeas/Uset at the moment | FLOAT | R | 0...1250
110 | I2 | SEF1 | Measured U0 3rd harm (%) | FLOAT | R | 0...1250
110 | I3 | SEF1 | Measured U0 3rd harm (Pri) | FLOAT | R | 0...1250
110 | I4 | SEF1 | U03rd< starts | UINT32 | R | 0...4294967295
110 | I5 | SEF1 | U03rd< trips | UINT32 | R | 0...4294967295
110 | I6 | SEF1 | U03rd< blocks | UINT32 | R | 0...4294967295
110 | S2 | SEF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
110 | S3 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S4 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S5 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S6 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S7 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S8 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S9 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S10 | SEF1 | Pick-up setting U03h < set | FLOAT | RW | 1...95
110 | S11 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S12 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S13 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S14 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S15 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S16 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S17 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S18 | SEF1 | Low current blocking I1< set | FLOAT | RW | 0...1
110 | S19 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S20 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S21 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S22 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S23 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S24 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S25 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | S26 | SEF1 | Definite operating time delay | FLOAT | RW | 0...1800
110 | O1 | SEF1 | U03rd< START | SIGNAL_OUT | RW | 0...4294967295
110 | O2 | SEF1 | U03rd< TRIP | SIGNAL_OUT | RW | 0...4294967295
110 | O3 | SEF1 | U03rd< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
110 | I7 | SEF1 | Newest Register | UINT32 | R | 0...12
110 | I8 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I9 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I10 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I11 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I12 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I13 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I14 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I15 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I16 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I17 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I18 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I19 | SEF1 | U0 Fault (%) | FLOAT | R | 0...250
110 | I20 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I21 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I22 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I23 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I24 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I25 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I26 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I27 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I28 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I29 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I30 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | I31 | SEF1 | U0 Fault (V) | FLOAT | R | 0...250
110 | S27 | SEF1 | EventMaskLo | UINT32 | RW | 0...4294967295
109 | S1 | UEX1 | Q< [40] mode | UINT32 | RW | 0=Disabled; 1=Activated
109 | V1 | UEX1 | Q< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
109 | I1 | UEX1 | Qmeas/Qset at the moment | FLOAT | R | -1250...1250
109 | I2 | UEX1 | Q< starts | UINT32 | R | 0...4294967295
109 | I3 | UEX1 | Q< trips | UINT32 | R | 0...4294967295
109 | I4 | UEX1 | Q< blocks | UINT32 | R | 0...4294967295
109 | S2 | UEX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
109 | S3 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S4 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S5 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S6 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S7 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S8 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S9 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S10 | UEX1 | Q set mode | UINT32 | RW | 0=Fixed;1=P dependent
109 | S11 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S12 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S13 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S14 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S15 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S16 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S17 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S18 | UEX1 | Pick-up setting Qset< | FLOAT | RW | -1000000...0
109 | S19 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S20 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S21 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S22 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S23 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S24 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S25 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S26 | UEX1 | Pick-up setting P1 for Qset | FLOAT | RW | 0.1...1000000
109 | S27 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S28 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S29 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S30 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S31 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S32 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S33 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S34 | UEX1 | Pick-up setting Qset2< | FLOAT | RW | -1000000...0
109 | S35 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S36 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S37 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S38 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S39 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S40 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S41 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S42 | UEX1 | Pick-up setting P2 for Qset2 | FLOAT | RW | 0.1...1000000
109 | S43 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S44 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S45 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S46 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S47 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S48 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S49 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | S50 | UEX1 | Definite operating time delay | FLOAT | RW | 0...1800
109 | O1 | UEX1 | Q< START | SIGNAL_OUT | RW | 0...4294967295
109 | O2 | UEX1 | Q< TRIP | SIGNAL_OUT | RW | 0...4294967295
109 | O3 | UEX1 | Q< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
109 | I5 | UEX1 | Newest Register | UINT32 | R | 0...12
109 | I6 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I7 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I8 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I9 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I10 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I11 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I12 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I13 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I14 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I15 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I16 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I17 | UEX1 | 3PH fault Q | FLOAT | R | 0...250
109 | I18 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I19 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I20 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I21 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I22 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I23 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I24 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I25 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I26 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I27 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I28 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | I29 | UEX1 | 3PH fault P | FLOAT | R | 0...250
109 | S51 | UEX1 | EventMaskLo | UINT32 | RW | 0...4294967295
111 | S1 | UIM1 | Z< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
111 | V1 | UIM1 | Z< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
111 | I1 | UIM1 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
111 | I2 | UIM1 | Z< starts | UINT32 | R | 0...4294967295
111 | I3 | UIM1 | Z< trips | UINT32 | R | 0...4294967295
111 | I4 | UIM1 | Z< blocks | UINT32 | R | 0...4294967295
111 | S2 | UIM1 | Clear statistics | UINT32 | W | 0=-;1=Clear
111 | S3 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S4 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S5 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S6 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S7 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S8 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S9 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S10 | UIM1 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
111 | S11 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S12 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S13 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S14 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S15 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S16 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S17 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | S18 | UIM1 | Definite operating time delay | FLOAT | RW | 0...1800
111 | O1 | UIM1 | Z< START | SIGNAL_OUT | RW | 0...4294967295
111 | O2 | UIM1 | Z< TRIP | SIGNAL_OUT | RW | 0...4294967295
111 | O3 | UIM1 | Z< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
111 | I5 | UIM1 | Newest Register | UINT32 | R | 0...12
111 | I6 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I7 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I8 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I9 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I10 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I11 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I12 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I13 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I14 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I15 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I16 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I17 | UIM1 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
111 | I18 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I19 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I20 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I21 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I22 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I23 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I24 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I25 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I26 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I27 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I28 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I29 | UIM1 | Z2 fault impedance | FLOAT | R | 0...250
111 | I30 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I31 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I32 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I33 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I34 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I35 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I36 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I37 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I38 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I39 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I40 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | I41 | UIM1 | Z3 fault impedance | FLOAT | R | 0...250
111 | S19 | UIM1 | EventMaskLo | UINT32 | RW | 0...4294967295
149 | S1 | UIM2 | Z<< [21] mode | UINT32 | RW | 0=Disabled; 1=Activated
149 | V1 | UIM2 | Z<< condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
149 | I1 | UIM2 | Zmeas/Zset at the moment | FLOAT | R | 0...1250
149 | I2 | UIM2 | Z<< starts | UINT32 | R | 0...4294967295
149 | I3 | UIM2 | Z<< trips | UINT32 | R | 0...4294967295
149 | I4 | UIM2 | Z<< blocks | UINT32 | R | 0...4294967295
149 | S2 | UIM2 | Clear statistics | UINT32 | W | 0=-;1=Clear
149 | S3 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S4 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S5 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S6 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S7 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S8 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S9 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S10 | UIM2 | Pick-up setting Zset(pri)< | FLOAT | RW | 0.1...150
149 | S11 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S12 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S13 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S14 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S15 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S16 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S17 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | S18 | UIM2 | Definite operating time delay | FLOAT | RW | 0...1800
149 | O1 | UIM2 | Z<< START | SIGNAL_OUT | RW | 0...4294967295
149 | O2 | UIM2 | Z<< TRIP | SIGNAL_OUT | RW | 0...4294967295
149 | O3 | UIM2 | Z<< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
149 | I5 | UIM2 | Newest Register | UINT32 | R | 0...12
149 | I6 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I7 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I8 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I9 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I10 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I11 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I12 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I13 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I14 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I15 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I16 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I17 | UIM2 | Z1 (Zseq) fault impedance | FLOAT | R | 0...250
149 | I18 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I19 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I20 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I21 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I22 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I23 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I24 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I25 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I26 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I27 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I28 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I29 | UIM2 | Z2 fault impedance | FLOAT | R | 0...250
149 | I30 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I31 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I32 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I33 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I34 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I35 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I36 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I37 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I38 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I39 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I40 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | I41 | UIM2 | Z3 fault impedance | FLOAT | R | 0...250
149 | S19 | UIM2 | EventMaskLo | UINT32 | RW | 0...4294967295
112 | S1 | VOC1 | Iv> [51V] mode | UINT32 | RW | 0=Disabled; 1=Activated
112 | V1 | VOC1 | Iv> condition | UINT32 | R | 0=Normal;1=Start; 2=Trip; 3=Blocked
112 | I1 | VOC1 | Imeas/Iset at the moment | FLOAT | R | 0...1250
112 | I2 | VOC1 | Iv> starts | UINT32 | R | 0...4294967295
112 | I3 | VOC1 | Iv> trips | UINT32 | R | 0...4294967295
112 | I4 | VOC1 | Iv> blocks | UINT32 | R | 0...4294967295
112 | S2 | VOC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
112 | S3 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S4 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S5 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S6 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S7 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S8 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S9 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S10 | VOC1 | Pick-up setting IvSet 1st knee point | FLOAT | RW | 0.1...40
112 | S11 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S12 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S13 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S14 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S15 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S16 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S17 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S18 | VOC1 | Pick-up setting IvSet 2nd knee point | FLOAT | RW | 0.1...40
112 | S19 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S20 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S21 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S22 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S23 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S24 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S25 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S26 | VOC1 | 1st knee point voltage | FLOAT | RW | 0...150
112 | S27 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S28 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S29 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S30 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S31 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S32 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S33 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S34 | VOC1 | 2nd knee point voltage | FLOAT | RW | 0...150
112 | S35 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S36 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S37 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S38 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S39 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S40 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S41 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | S42 | VOC1 | Definite operating time delay | FLOAT | RW | 0...1800
112 | O1 | VOC1 | Iv> START | SIGNAL_OUT | RW | 0...4294967295
112 | O2 | VOC1 | Iv> TRIP | SIGNAL_OUT | RW | 0...4294967295
112 | O3 | VOC1 | Iv> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
112 | I5 | VOC1 | Newest Register | UINT32 | R | 0...12
112 | I6 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I7 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I8 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I9 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I10 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I11 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I12 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I13 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I14 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I15 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I16 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I17 | VOC1 | Phase A fault current | FLOAT | R | 0...250
112 | I18 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I19 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I20 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I21 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I22 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I23 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I24 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I25 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I26 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I27 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I28 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I29 | VOC1 | Phase B fault current | FLOAT | R | 0...250
112 | I30 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I31 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I32 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I33 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I34 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I35 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I36 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I37 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I38 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I39 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I40 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I41 | VOC1 | Phase C fault current | FLOAT | R | 0...250
112 | I42 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I43 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I44 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I45 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I46 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I47 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I48 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I49 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I50 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I51 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I52 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I53 | VOC1 | U1 Voltage | FLOAT | R | 0...250
112 | I54 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I55 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I56 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I57 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I58 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I59 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I60 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I61 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I62 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I63 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I64 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | I65 | VOC1 | Current pick-up | FLOAT | R | 0...250
112 | S43 | VOC1 | EventMaskLo | UINT32 | RW | 0...4294967295
128 | S1 | VHZ1 | V/Hz > [24] mode | UINT32 | RW | 0=Disabled;1=Activated
128 | S2 | VHZ1 | V/Hz(1) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V1 | VHZ1 | V/Hz(1) > condition | UINT32 | R | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
128 | I1 | VHZ1 | V/Hz(1) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | S3 | VHZ1 | V/Hz(2) > mode | UINT32 | RW | 0=Disabled;1=Activated
128 | V2 | VHZ1 | V/Hz(2) > condition | UINT32 | R | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
128 | I2 | VHZ1 | V/Hz(2) > U/f atm to pick-up U/f ratio | FLOAT | R | -100...100
128 | I3 | VHZ1 | U/f at the moment | FLOAT | R | -100...100
128 | I4 | VHZ1 | U/f atm to nominal U/f ratio | FLOAT | R | -100...100
128 | I5 | VHZ1 | V/Hz(1) > Starts | UINT32 | R | 0...4294967295
128 | I6 | VHZ1 | V/Hz(1) > Alarms | UINT32 | R | 0...4294967295
128 | I7 | VHZ1 | V/Hz(1) > Trips | UINT32 | R | 0...4294967295
128 | I8 | VHZ1 | V/Hz(1) > Blocks | UINT32 | R | 0...4294967295
128 | I9 | VHZ1 | V/Hz(2) > Starts | UINT32 | R | 0...4294967295
128 | I10 | VHZ1 | V/Hz(2) > Alarms | UINT32 | R | 0...4294967295
128 | I11 | VHZ1 | V/Hz(2) > Trips | UINT32 | R | 0...4294967295
128 | I12 | VHZ1 | V/Hz(2) > Blocks | UINT32 | R | 0...4294967295
128 | S4 | VHZ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
128 | S5 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S6 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S7 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S8 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S9 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S10 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S11 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S12 | VHZ1 | V/Hz(1) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S13 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S14 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S15 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S16 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S17 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S18 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S19 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S20 | VHZ1 | V/Hz(1) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S21 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S22 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S23 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S24 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S25 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S26 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S27 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S28 | VHZ1 | V/Hz(1) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S29 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S30 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S31 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S32 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S33 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S34 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S35 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S36 | VHZ1 | V/Hz(2) > Pick-up (% of nominal) | FLOAT | RW | 0.01...75
128 | S37 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S38 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S39 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S40 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S41 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S42 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S43 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S44 | VHZ1 | V/Hz(2) > Alarm delay (DT) | FLOAT | RW | 0...1800
128 | S45 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S46 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S47 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S48 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S49 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S50 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S51 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | S52 | VHZ1 | V/Hz(2) > Definite operating time delay | FLOAT | RW | 0...1800
128 | O1 | VHZ1 | V/Hz(1) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O2 | VHZ1 | V/Hz(1) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O3 | VHZ1 | V/Hz(1) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O4 | VHZ1 | V/Hz(1) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | O5 | VHZ1 | V/Hz(2) > START | SIGNAL_OUT | RW | 0...4294967295
128 | O6 | VHZ1 | V/Hz(2) > ALARM | SIGNAL_OUT | RW | 0...4294967295
128 | O7 | VHZ1 | V/Hz(2) > TRIP | SIGNAL_OUT | RW | 0...4294967295
128 | O8 | VHZ1 | V/Hz(2) > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
128 | I13 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I14 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I15 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I16 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I17 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I18 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I19 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I20 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I21 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I22 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I23 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I24 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I25 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I26 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I27 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I28 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I29 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I30 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I31 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I32 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I33 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I34 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I35 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I36 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I37 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I38 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I39 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I40 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I41 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I42 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I43 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I44 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I45 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I46 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I47 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I48 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I49 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I50 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I51 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I52 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I53 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I54 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I55 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I56 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I57 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I58 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I59 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I60 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I61 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I62 | VHZ1 | Newest Register | UINT32 | R | 0...12
128 | I63 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I64 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I65 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I66 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I67 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I68 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I69 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I70 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I71 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I72 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I73 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I74 | VHZ1 | Voltage AB fault volt | FLOAT | R | 0...250
128 | I75 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I76 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I77 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I78 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I79 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I80 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I81 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I82 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I83 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I84 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I85 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I86 | VHZ1 | Voltage BC fault volt | FLOAT | R | 0...250
128 | I87 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I88 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I89 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I90 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I91 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I92 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I93 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I94 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I95 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I96 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I97 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I98 | VHZ1 | Voltage CA fault volt | FLOAT | R | 0...250
128 | I99 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I100 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I101 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I102 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I103 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I104 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I105 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I106 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I107 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I108 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I109 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | I110 | VHZ1 | Fault frequency | FLOAT | R | 0...75
128 | S53 | VHZ1 | EventMaskLo | UINT32 | RW | 0...4294967295
129 | S1 | UPF1 | PF< [55] mode | UINT32 | RW | 0=Disabled; 1=Activated
129 | V1 | UPF1 | PF< condition | UINT32 | R | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
129 | S2 | UPF1 | Available modes | UINT32 | RW | 0=Trip;1=Trip and Alarm
129 | I1 | UPF1 | PFmeas/PFalarm at the moment | FLOAT | R | 0...1250
129 | I2 | UPF1 | PFmeas/PFtrip at the moment | FLOAT | R | 0...1250
129 | I3 | UPF1 | PF< Alarm Starts | UINT32 | R | 0...4294967295
129 | I4 | UPF1 | PF< Alarms | UINT32 | R | 0...4294967295
129 | I5 | UPF1 | PF< Starts | UINT32 | R | 0...4294967295
129 | I6 | UPF1 | PF< Trips | UINT32 | R | 0...4294967295
129 | I7 | UPF1 | PF< Blocks | UINT32 | R | 0...4294967295
129 | S3 | UPF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
129 | S4 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S5 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S6 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S7 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S8 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S9 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S10 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S11 | UPF1 | Pick-up setting PF< (lead or lag) Trip | FLOAT | RW | 0.05...0.99
129 | S12 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S13 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S14 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S15 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S16 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S17 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S18 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S19 | UPF1 | Definite operating time delay Trip | FLOAT | RW | 0...1800
129 | S20 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S21 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S22 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S23 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S24 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S25 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S26 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S27 | UPF1 | Pick-up setting PF< (lead or lag) Alarm | FLOAT | RW | 0.05...0.99
129 | S28 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S29 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S30 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S31 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S32 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S33 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S34 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | S35 | UPF1 | Definite operating time delay Alarm | FLOAT | RW | 0...1800
129 | O1 | UPF1 | PF< START | SIGNAL_OUT | RW | 0...4294967295
129 | O2 | UPF1 | PF< TRIP | SIGNAL_OUT | RW | 0...4294967295
129 | O3 | UPF1 | PF< BLOCKED | SIGNAL_OUT | RW | 0...4294967295
129 | I8 | UPF1 | Newest Register | UINT32 | R | 0...12
129 | I9 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I10 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I11 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I12 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I13 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I14 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I15 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I16 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I17 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I18 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I19 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | I20 | UPF1 | Fault PF | FLOAT | R | 0...250
129 | S36 | UPF1 | EventMaskLo | UINT32 | RW | 0...4294967295
141 | I1 | RTDIN | S1 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I2 | RTDIN | S1 Resistance | FLOAT | R | 0...4000.000
141 | I3 | RTDIN | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I4 | RTDIN | S1 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I5 | RTDIN | S2 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I6 | RTDIN | S2 Resistance | FLOAT | R | 0...4000.000
141 | I7 | RTDIN | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I8 | RTDIN | S2 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I9 | RTDIN | S3 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I10 | RTDIN | S3 Resistance | FLOAT | R | 0...4000.000
141 | I11 | RTDIN | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I12 | RTDIN | S3 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I13 | RTDIN | S4 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I14 | RTDIN | S4 Resistance | FLOAT | R | 0...4000.000
141 | I15 | RTDIN | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I16 | RTDIN | S4 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I17 | RTDIN | S5 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I18 | RTDIN | S5 Resistance | FLOAT | R | 0...4000.000
141 | I19 | RTDIN | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I20 | RTDIN | S5 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I21 | RTDIN | S6 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I22 | RTDIN | S6 Resistance | FLOAT | R | 0...4000.000
141 | I23 | RTDIN | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I24 | RTDIN | S6 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I25 | RTDIN | S7 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I26 | RTDIN | S7 Resistance | FLOAT | R | 0...4000.000
141 | I27 | RTDIN | S7 Measurement mA | FLOAT | R | 0.000...20.000
141 | I28 | RTDIN | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I29 | RTDIN | S7 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I30 | RTDIN | S8 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I31 | RTDIN | S8 Resistance | FLOAT | R | 0...4000.000
141 | I32 | RTDIN | S8 Measurement mA | FLOAT | R | 0.000...20.000
141 | I33 | RTDIN | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I34 | RTDIN | S8 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I35 | RTDIN | S9 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I36 | RTDIN | S9 Resistance | FLOAT | R | 0...4000.000
141 | I37 | RTDIN | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I38 | RTDIN | S9 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I39 | RTDIN | S10 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I40 | RTDIN | S10 Resistance | FLOAT | R | 0...4000.000
141 | I41 | RTDIN | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I42 | RTDIN | S10 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I43 | RTDIN | S11 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I44 | RTDIN | S11 Resistance | FLOAT | R | 0...4000.000
141 | I45 | RTDIN | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I46 | RTDIN | S11 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I47 | RTDIN | S12 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I48 | RTDIN | S12 Resistance | FLOAT | R | 0...4000.000
141 | I49 | RTDIN | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I50 | RTDIN | S12 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I51 | RTDIN | S13 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I52 | RTDIN | S13 Resistance | FLOAT | R | 0...4000.000
141 | I53 | RTDIN | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I54 | RTDIN | S13 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I55 | RTDIN | S14 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I56 | RTDIN | S14 Resistance | FLOAT | R | 0...4000.000
141 | I57 | RTDIN | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I58 | RTDIN | S14 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I59 | RTDIN | S15 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I60 | RTDIN | S15 Resistance | FLOAT | R | 0...4000.000
141 | I61 | RTDIN | S15 Measurement mA | FLOAT | R | 0.000...20.000
141 | I62 | RTDIN | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I63 | RTDIN | S15 Filtered measurement | FLOAT | R | -200.0...2000.0
141 | I64 | RTDIN | S16 Measurement(Raw) | FLOAT | R | -200.0...2000.0
141 | I65 | RTDIN | S16 Resistance | FLOAT | R | 0...4000.000
141 | I66 | RTDIN | S16 Measurement mA | FLOAT | R | 0.000...20.000
141 | I67 | RTDIN | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
141 | I68 | RTDIN | S16 Filtered measurement | FLOAT | R | -200.0...2000.0
69 | S1 | RTD1 | RTD mode | UINT32 | RW | 0=Disabled;1=Activated
69 | S2 | RTD1 | S1 enable | UINT32 | RW | 0=No;1=Yes
69 | I1 | RTD1 | S1 Measurement (Protection) | FLOAT | R | -200...2000
69 | V1 | RTD1 | S1 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S3 | RTD1 | S1 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I2 | RTD1 | S1 Alarm1 act | UINT32 | R | 0...4294967295
69 | S4 | RTD1 | S1 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S5 | RTD1 | S1 Alarm1 | FLOAT | RW | -200...2000
69 | S6 | RTD1 | S1 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I3 | RTD1 | S1 Alarm2 act | UINT32 | R | 0...4294967295
69 | S7 | RTD1 | S1 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S8 | RTD1 | S1 Alarm2 | FLOAT | RW | -200...2000
69 | I4 | RTD1 | S2 Measurement (Protection) | FLOAT | R | -200...2000
69 | V2 | RTD1 | S2 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S9 | RTD1 | S2 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I5 | RTD1 | S2 Alarm1 act | UINT32 | R | 0...4294967295
69 | S10 | RTD1 | S2 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S11 | RTD1 | S2 Alarm1 | FLOAT | RW | -200...2000
69 | S12 | RTD1 | S2 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I6 | RTD1 | S2 Alarm2 act | UINT32 | R | 0...4294967295
69 | S13 | RTD1 | S2 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S14 | RTD1 | S2 Alarm2 | FLOAT | RW | -200...2000
69 | I7 | RTD1 | S3 Measurement (Protection) | FLOAT | R | -200...2000
69 | V3 | RTD1 | S3 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S15 | RTD1 | S3 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I8 | RTD1 | S3 Alarm1 act | UINT32 | R | 0...4294967295
69 | S16 | RTD1 | S3 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S17 | RTD1 | S3 Alarm1 | FLOAT | RW | -200...2000
69 | S18 | RTD1 | S3 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I9 | RTD1 | S3 Alarm2 act | UINT32 | R | 0...4294967295
69 | S19 | RTD1 | S3 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S20 | RTD1 | S3 Alarm2 | FLOAT | RW | -200...2000
69 | I10 | RTD1 | S4 Measurement (Protection) | FLOAT | R | -200...2000
69 | V4 | RTD1 | S4 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S21 | RTD1 | S4 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I11 | RTD1 | S4 Alarm1 act | UINT32 | R | 0...4294967295
69 | S22 | RTD1 | S4 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S23 | RTD1 | S4 Alarm1 | FLOAT | RW | -200...2000
69 | S24 | RTD1 | S4 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I12 | RTD1 | S4 Alarm2 act | UINT32 | R | 0...4294967295
69 | S25 | RTD1 | S4 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S26 | RTD1 | S4 Alarm2 | FLOAT | RW | -200...2000
69 | I13 | RTD1 | S5 Measurement (Protection) | FLOAT | R | -200...2000
69 | V5 | RTD1 | S5 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S27 | RTD1 | S5 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I14 | RTD1 | S5 Alarm1 act | UINT32 | R | 0...4294967295
69 | S28 | RTD1 | S5 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S29 | RTD1 | S5 Alarm1 | FLOAT | RW | -200...2000
69 | S30 | RTD1 | S5 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I15 | RTD1 | S5 Alarm2 act | UINT32 | R | 0...4294967295
69 | S31 | RTD1 | S5 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S32 | RTD1 | S5 Alarm2 | FLOAT | RW | -200...2000
69 | I16 | RTD1 | S6 Measurement (Protection) | FLOAT | R | -200...2000
69 | V6 | RTD1 | S6 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S33 | RTD1 | S6 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I17 | RTD1 | S6 Alarm1 act | UINT32 | R | 0...4294967295
69 | S34 | RTD1 | S6 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S35 | RTD1 | S6 Alarm1 | FLOAT | RW | -200...2000
69 | S36 | RTD1 | S6 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I18 | RTD1 | S6 Alarm2 act | UINT32 | R | 0...4294967295
69 | S37 | RTD1 | S6 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S38 | RTD1 | S6 Alarm2 | FLOAT | RW | -200...2000
69 | I19 | RTD1 | S7 Measurement (Protection) | FLOAT | R | -200...2000
69 | V7 | RTD1 | S7 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S39 | RTD1 | S7 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I20 | RTD1 | S7 Alarm1 act | UINT32 | R | 0...4294967295
69 | S40 | RTD1 | S7 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S41 | RTD1 | S7 Alarm1 | FLOAT | RW | -200...2000
69 | S42 | RTD1 | S7 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I21 | RTD1 | S7 Alarm2 act | UINT32 | R | 0...4294967295
69 | S43 | RTD1 | S7 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S44 | RTD1 | S7 Alarm2 | FLOAT | RW | -200...2000
69 | I22 | RTD1 | S8 Measurement (Protection) | FLOAT | R | -200...2000
69 | V8 | RTD1 | S8 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S45 | RTD1 | S8 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I23 | RTD1 | S8 Alarm1 act | UINT32 | R | 0...4294967295
69 | S46 | RTD1 | S8 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S47 | RTD1 | S8 Alarm1 | FLOAT | RW | -200...2000
69 | S48 | RTD1 | S8 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I24 | RTD1 | S8 Alarm2 act | UINT32 | R | 0...4294967295
69 | S49 | RTD1 | S8 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S50 | RTD1 | S8 Alarm2 | FLOAT | RW | -200...2000
69 | I25 | RTD1 | S9 Measurement (Protection) | FLOAT | R | -200...2000
69 | V9 | RTD1 | S9 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S51 | RTD1 | S9 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I26 | RTD1 | S9 Alarm1 act | UINT32 | R | 0...4294967295
69 | S52 | RTD1 | S9 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S53 | RTD1 | S9 Alarm1 | FLOAT | RW | -200...2000
69 | S54 | RTD1 | S9 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I27 | RTD1 | S9 Alarm2 act | UINT32 | R | 0...4294967295
69 | S55 | RTD1 | S9 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S56 | RTD1 | S9 Alarm2 | FLOAT | RW | -200...2000
69 | I28 | RTD1 | S10 Measurement (Protection) | FLOAT | R | -200...2000
69 | V10 | RTD1 | S10 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S57 | RTD1 | S10 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I29 | RTD1 | S10 Alarm1 act | UINT32 | R | 0...4294967295
69 | S58 | RTD1 | S10 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S59 | RTD1 | S10 Alarm1 | FLOAT | RW | -200...2000
69 | S60 | RTD1 | S10 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I30 | RTD1 | S10 Alarm2 act | UINT32 | R | 0...4294967295
69 | S61 | RTD1 | S10 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S62 | RTD1 | S10 Alarm2 | FLOAT | RW | -200...2000
69 | I31 | RTD1 | S11 Measurement (Protection) | FLOAT | R | -200...2000
69 | V11 | RTD1 | S11 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S63 | RTD1 | S11 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I32 | RTD1 | S11 Alarm1 act | UINT32 | R | 0...4294967295
69 | S64 | RTD1 | S11 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S65 | RTD1 | S11 Alarm1 | FLOAT | RW | -200...2000
69 | S66 | RTD1 | S11 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I33 | RTD1 | S11 Alarm2 act | UINT32 | R | 0...4294967295
69 | S67 | RTD1 | S11 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S68 | RTD1 | S11 Alarm2 | FLOAT | RW | -200...2000
69 | I34 | RTD1 | S12 Measurement (Protection) | FLOAT | R | -200...2000
69 | V12 | RTD1 | S12 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S69 | RTD1 | S12 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I35 | RTD1 | S12 Alarm1 act | UINT32 | R | 0...4294967295
69 | S70 | RTD1 | S12 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S71 | RTD1 | S12 Alarm1 | FLOAT | RW | -200...2000
69 | S72 | RTD1 | S12 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I36 | RTD1 | S12 Alarm2 act | UINT32 | R | 0...4294967295
69 | S73 | RTD1 | S12 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S74 | RTD1 | S12 Alarm2 | FLOAT | RW | -200...2000
69 | I37 | RTD1 | S13 Measurement (Protection) | FLOAT | R | -200...2000
69 | V13 | RTD1 | S13 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S75 | RTD1 | S13 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I38 | RTD1 | S13 Alarm1 act | UINT32 | R | 0...4294967295
69 | S76 | RTD1 | S13 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S77 | RTD1 | S13 Alarm1 | FLOAT | RW | -200...2000
69 | S78 | RTD1 | S13 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I39 | RTD1 | S13 Alarm2 act | UINT32 | R | 0...4294967295
69 | S79 | RTD1 | S13 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S80 | RTD1 | S13 Alarm2 | FLOAT | RW | -200...2000
69 | I40 | RTD1 | S14 Measurement (Protection) | FLOAT | R | -200...2000
69 | V14 | RTD1 | S14 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S81 | RTD1 | S14 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I41 | RTD1 | S14 Alarm1 act | UINT32 | R | 0...4294967295
69 | S82 | RTD1 | S14 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S83 | RTD1 | S14 Alarm1 | FLOAT | RW | -200...2000
69 | S84 | RTD1 | S14 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I42 | RTD1 | S14 Alarm2 act | UINT32 | R | 0...4294967295
69 | S85 | RTD1 | S14 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S86 | RTD1 | S14 Alarm2 | FLOAT | RW | -200...2000
69 | I43 | RTD1 | S15 Measurement (Protection) | FLOAT | R | -200...2000
69 | V15 | RTD1 | S15 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S87 | RTD1 | S15 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I44 | RTD1 | S15 Alarm1 act | UINT32 | R | 0...4294967295
69 | S88 | RTD1 | S15 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S89 | RTD1 | S15 Alarm1 | FLOAT | RW | -200...2000
69 | S90 | RTD1 | S15 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I45 | RTD1 | S15 Alarm2 act | UINT32 | R | 0...4294967295
69 | S91 | RTD1 | S15 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S92 | RTD1 | S15 Alarm2 | FLOAT | RW | -200...2000
69 | I46 | RTD1 | S16 Measurement (Protection) | FLOAT | R | -200...2000
69 | V16 | RTD1 | S16 Sensor | UINT32 | R | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
69 | S93 | RTD1 | S16 Enable Alarm1 | UINT32 | RW | 0=Disable;1=Enable
69 | I47 | RTD1 | S16 Alarm1 act | UINT32 | R | 0...4294967295
69 | S94 | RTD1 | S16 Alarm1 > / < | UINT32 | RW | 0=>;1=<
69 | S95 | RTD1 | S16 Alarm1 | FLOAT | RW | -200...2000
69 | S96 | RTD1 | S16 Enable Alarm2 | UINT32 | RW | 0=Disable;1=Enable
69 | I48 | RTD1 | S16 Alarm2 act | UINT32 | R | 0...4294967295
69 | S97 | RTD1 | S16 Alarm2 > / < | UINT32 | RW | 0=>;1=<
69 | S98 | RTD1 | S16 Alarm2 | FLOAT | RW | -200...2000
69 | O1 | RTD1 | S1 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O2 | RTD1 | S1 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O3 | RTD1 | S1 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O4 | RTD1 | S2 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O5 | RTD1 | S2 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O6 | RTD1 | S2 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O7 | RTD1 | S3 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O8 | RTD1 | S3 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O9 | RTD1 | S3 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O10 | RTD1 | S4 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O11 | RTD1 | S4 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O12 | RTD1 | S4 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O13 | RTD1 | S5 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O14 | RTD1 | S5 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O15 | RTD1 | S5 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O16 | RTD1 | S6 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O17 | RTD1 | S6 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O18 | RTD1 | S6 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O19 | RTD1 | S7 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O20 | RTD1 | S7 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O21 | RTD1 | S7 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O22 | RTD1 | S8 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O23 | RTD1 | S8 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O24 | RTD1 | S8 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O25 | RTD1 | S9 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O26 | RTD1 | S9 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O27 | RTD1 | S9 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O28 | RTD1 | S10 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O29 | RTD1 | S10 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O30 | RTD1 | S10 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O31 | RTD1 | S11 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O32 | RTD1 | S11 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O33 | RTD1 | S11 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O34 | RTD1 | S12 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O35 | RTD1 | S12 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O36 | RTD1 | S12 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O37 | RTD1 | S13 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O38 | RTD1 | S13 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O39 | RTD1 | S13 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O40 | RTD1 | S14 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O41 | RTD1 | S14 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O42 | RTD1 | S14 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O43 | RTD1 | S15 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O44 | RTD1 | S15 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O45 | RTD1 | S15 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | O46 | RTD1 | S16 ALARM1 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O47 | RTD1 | S16 ALARM2 ON | SIGNAL_OUT | RW | 0...4294967295
69 | O48 | RTD1 | S16 MEAS INVALID | SIGNAL_OUT | RW | 0...4294967295
69 | S99 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
69 | S100 | RTD1 | Alarm event mask | UINT32 | RW | 0...4294967295
70 | S1 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
70 | S2 | RTD2 | Meas quality mask | UINT32 | RW | 0...4294967295
74 | S1 | ARC1 | I/I0 Arc> [50ARC/50NARC] mode | UINT32 | RW | 0=Disabled;1=Activated
74 | S2 | ARC1 | I/I0 Arc> Self supervision test pulse | UINT32 | RW | 0=Disabled;1=On
74 | V1 | ARC1 | I/I0 Arc> condition | UINT32 | R | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
74 | V2 | ARC1 | Sensor status | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I1 | ARC1 | I/I0 Arc> Zone1 Trips | UINT32 | R | 0...4294967295
74 | I2 | ARC1 | I/I0 Arc> Zone1 Blocks | UINT32 | R | 0...4294967295
74 | I3 | ARC1 | I/I0 Arc> Zone2 Trips | UINT32 | R | 0...4294967295
74 | I4 | ARC1 | I/I0 Arc> Zone2 Blocks | UINT32 | R | 0...4294967295
74 | I5 | ARC1 | I/I0 Arc> Zone3 Trips | UINT32 | R | 0...4294967295
74 | I6 | ARC1 | I/I0 Arc> Zone3 Blocks | UINT32 | R | 0...4294967295
74 | I7 | ARC1 | I/I0 Arc> Zone4 Trips | UINT32 | R | 0...4294967295
74 | I8 | ARC1 | I/I0 Arc> Zone4 Blocks | UINT32 | R | 0...4294967295
74 | S3 | ARC1 | Clear statistics | UINT32 | W | 0=-;1=Clear
74 | I9 | ARC1 | Channel 1 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I10 | ARC1 | Channel 1 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I11 | ARC1 | Channel 2 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I12 | ARC1 | Channel 2 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I13 | ARC1 | Channel 3 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I14 | ARC1 | Channel 3 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | I15 | ARC1 | Channel 4 sensors | UINT32 | RW | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
74 | I16 | ARC1 | Channel 4 sensor status | UINT32 | R | 0=Sensors Ok;1=Configuration fault
74 | S4 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S5 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S6 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S7 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S8 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S9 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S10 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S11 | ARC1 | Phase current pick-up | FLOAT | RW | 0.05...40
74 | S12 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S13 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S14 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S15 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S16 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S17 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S18 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S19 | ARC1 | I0 input selection | UINT32 | RW | 0=None;1=I01;2=I02
74 | S20 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S21 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S22 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S23 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S24 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S25 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S26 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S27 | ARC1 | Res. current pick-up | FLOAT | RW | 0.05...40
74 | S28 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S29 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S30 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S31 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S32 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S33 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S34 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S35 | ARC1 | Zone1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S36 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S37 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S38 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S39 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S40 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S41 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S42 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S43 | ARC1 | Zone1 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S44 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S45 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S46 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S47 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S48 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S49 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S50 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S51 | ARC1 | Zone1 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S52 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S53 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S54 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S55 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S56 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S57 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S58 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S59 | ARC1 | Zone1 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S60 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S61 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S62 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S63 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S64 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S65 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S66 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S67 | ARC1 | Zone1 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S68 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S69 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S70 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S71 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S72 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S73 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S74 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S75 | ARC1 | Zone1 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S76 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S77 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S78 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S79 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S80 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S81 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S82 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S83 | ARC1 | Zone1 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S84 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S85 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S86 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S87 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S88 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S89 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S90 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S91 | ARC1 | Zone1 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S92 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S93 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S94 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S95 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S96 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S97 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S98 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S99 | ARC1 | Zone1 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S100 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S101 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S102 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S103 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S104 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S105 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S106 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S107 | ARC1 | Zone1 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S108 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S109 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S110 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S111 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S112 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S113 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S114 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S115 | ARC1 | Zone1 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S116 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S117 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S118 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S119 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S120 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S121 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S122 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S123 | ARC1 | Zone1 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S124 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S125 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S126 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S127 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S128 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S129 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S130 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S131 | ARC1 | Zone2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S132 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S133 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S134 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S135 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S136 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S137 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S138 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S139 | ARC1 | Zone2 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S140 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S141 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S142 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S143 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S144 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S145 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S146 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S147 | ARC1 | Zone2 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S148 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S149 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S150 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S151 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S152 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S153 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S154 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S155 | ARC1 | Zone2 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S156 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S157 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S158 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S159 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S160 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S161 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S162 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S163 | ARC1 | Zone2 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S164 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S165 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S166 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S167 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S168 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S169 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S170 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S171 | ARC1 | Zone2 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S172 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S173 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S174 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S175 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S176 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S177 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S178 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S179 | ARC1 | Zone2 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S180 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S181 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S182 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S183 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S184 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S185 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S186 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S187 | ARC1 | Zone2 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S188 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S189 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S190 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S191 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S192 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S193 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S194 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S195 | ARC1 | Zone2 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S196 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S197 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S198 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S199 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S200 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S201 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S202 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S203 | ARC1 | Zone2 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S204 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S205 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S206 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S207 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S208 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S209 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S210 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S211 | ARC1 | Zone2 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S212 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S213 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S214 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S215 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S216 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S217 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S218 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S219 | ARC1 | Zone2 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S220 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S221 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S222 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S223 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S224 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S225 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S226 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S227 | ARC1 | Zone3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S228 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S229 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S230 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S231 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S232 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S233 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S234 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S235 | ARC1 | Zone3 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S236 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S237 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S238 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S239 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S240 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S241 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S242 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S243 | ARC1 | Zone3 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S244 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S245 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S246 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S247 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S248 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S249 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S250 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S251 | ARC1 | Zone3 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S252 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S253 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S254 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S255 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S256 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S257 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S258 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S259 | ARC1 | Zone3 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S260 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S261 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S262 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S263 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S264 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S265 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S266 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S267 | ARC1 | Zone3 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S268 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S269 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S270 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S271 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S272 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S273 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S274 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S275 | ARC1 | Zone3 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S276 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S277 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S278 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S279 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S280 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S281 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S282 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S283 | ARC1 | Zone3 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S284 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S285 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S286 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S287 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S288 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S289 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S290 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S291 | ARC1 | Zone3 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S292 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S293 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S294 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S295 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S296 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S297 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S298 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S299 | ARC1 | Zone3 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S300 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S301 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S302 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S303 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S304 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S305 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S306 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S307 | ARC1 | Zone3 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S308 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S309 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S310 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S311 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S312 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S313 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S314 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S315 | ARC1 | Zone3 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S316 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S317 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S318 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S319 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S320 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S321 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S322 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S323 | ARC1 | Zone4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S324 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S325 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S326 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S327 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S328 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S329 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S330 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S331 | ARC1 | Zone4 Ph.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S332 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S333 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S334 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S335 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S336 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S337 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S338 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S339 | ARC1 | Zone4 Res.Curr Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S340 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S341 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S342 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S343 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S344 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S345 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S346 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S347 | ARC1 | Zone4 Light 1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S348 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S349 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S350 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S351 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S352 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S353 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S354 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S355 | ARC1 | Zone4 Light 2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S356 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S357 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S358 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S359 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S360 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S361 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S362 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S363 | ARC1 | Zone4 Light 3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S364 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S365 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S366 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S367 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S368 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S369 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S370 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S371 | ARC1 | Zone4 Light 4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S372 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S373 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S374 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S375 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S376 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S377 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S378 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S379 | ARC1 | Zone4 Pres.1 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S380 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S381 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S382 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S383 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S384 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S385 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S386 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S387 | ARC1 | Zone4 Pres.2 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S388 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S389 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S390 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S391 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S392 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S393 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S394 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S395 | ARC1 | Zone4 Pres.3 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S396 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S397 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S398 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S399 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S400 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S401 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S402 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S403 | ARC1 | Zone4 Pres.4 Enabled | UINT32 | RW | 0=Disabled;1=Enabled
74 | S404 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S405 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S406 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S407 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S408 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S409 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S410 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | S411 | ARC1 | Zone4 DI Enabled | UINT32 | RW | 0=Disabled;1=Light In;2=Current In
74 | O1 | ARC1 | I/I0 Arc> Ph.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O2 | ARC1 | I/I0 Arc> Res.Curr.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O3 | ARC1 | I/I0 Arc> Zone1.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O4 | ARC1 | I/I0 Arc> Zone2.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O5 | ARC1 | I/I0 Arc> Zone3.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O6 | ARC1 | I/I0 Arc> Zone4.BLOCK | SIGNAL_IN | RW | 0...4294967295
74 | O7 | ARC1 | I/I0 Arc> Ph.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O8 | ARC1 | I/I0 Arc> Res.Curr.START | SIGNAL_OUT | RW | 0...4294967295
74 | O9 | ARC1 | I/I0 Arc> Ph.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O10 | ARC1 | I/I0 Arc> Res.Curr.BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O11 | ARC1 | I/I0 Arc> Zone1 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O12 | ARC1 | I/I0 Arc> Zone1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O13 | ARC1 | I/I0 Arc> Zone2 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O14 | ARC1 | I/I0 Arc> Zone2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O15 | ARC1 | I/I0 Arc> Zone3 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O16 | ARC1 | I/I0 Arc> Zone3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O17 | ARC1 | I/I0 Arc> Zone4 TRIP | SIGNAL_OUT | RW | 0...4294967295
74 | O18 | ARC1 | I/I0 Arc> Zone4 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
74 | O19 | ARC1 | I/I0 Arc> S1 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O20 | ARC1 | I/I0 Arc> S2 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O21 | ARC1 | I/I0 Arc> S3 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O22 | ARC1 | I/I0 Arc> S4 Sensor fault | SIGNAL_OUT | RW | 0...4294967295
74 | O23 | ARC1 | I/I0 Arc> IO unit fault | SIGNAL_OUT | RW | 0...4294967295
74 | I17 | ARC1 | Newest Register | UINT32 | R | 0...12
74 | I18 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I19 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I20 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I21 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I22 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I23 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I24 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I25 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I26 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I27 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I28 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I29 | ARC1 | Phase A Current | FLOAT | R | 0...250
74 | I30 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I31 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I32 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I33 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I34 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I35 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I36 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I37 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I38 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I39 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I40 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I41 | ARC1 | Phase B Current | FLOAT | R | 0...250
74 | I42 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I43 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I44 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I45 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I46 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I47 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I48 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I49 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I50 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I51 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I52 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I53 | ARC1 | Phase C Current | FLOAT | R | 0...250
74 | I54 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I55 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I56 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I57 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I58 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I59 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I60 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I61 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I62 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I63 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I64 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I65 | ARC1 | Residual Current | FLOAT | R | 0...250
74 | I66 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I67 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I68 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I69 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I70 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I71 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I72 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I73 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I74 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I75 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I76 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | I77 | ARC1 | Active sensors | UINT32 | R | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault
74 | S412 | ARC1 | EventMaskLo | UINT32 | RW | 0...4294967295
74 | S413 | ARC1 | EventMaskHi | UINT32 | RW | 0...4294967295
52 | S1 | CTS1 | CTS1 mode | UINT32 | RW | 0=Disabled;1=Activated
52 | V1 | CTS1 | CTS1 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
52 | I1 | CTS1 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
52 | I2 | CTS1 | Natural unbalance ang | FLOAT | R | -360...360
52 | I3 | CTS1 | Measured current difference Isum, I0 | FLOAT | R | 0...50
52 | I4 | CTS1 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
52 | I5 | CTS1 | CTS1 alarms | UINT32 | R | 0...4294967295
52 | I6 | CTS1 | CTS1 blocks | UINT32 | R | 0...4294967295
52 | S2 | CTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
52 | S3 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S4 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S5 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S6 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S7 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S8 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S9 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S10 | CTS1 | Iset Highlimit | FLOAT | RW | 0.01...40
52 | S11 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S12 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S13 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S14 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S15 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S16 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S17 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S18 | CTS1 | Iset Lowlimit | FLOAT | RW | 0.01...40
52 | S19 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S20 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S21 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S22 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S23 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S24 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S25 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S26 | CTS1 | Iset ratio | FLOAT | RW | 0.01...100
52 | S27 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S28 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S29 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S30 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S31 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S32 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S33 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S34 | CTS1 | I2/I1 ratio | FLOAT | RW | 0.01...100
52 | S35 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S36 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S37 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S38 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S39 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S40 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S41 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S42 | CTS1 | Isum difference | FLOAT | RW | 0.01...40
52 | S43 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S44 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S45 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S46 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S47 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S48 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S49 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | S50 | CTS1 | Time delay for alarm | FLOAT | RW | 0...1800
52 | O1 | CTS1 | CTS1 ALARM | SIGNAL_OUT | RW | 0...4294967295
52 | O2 | CTS1 | CTS1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
52 | I7 | CTS1 | Newest Register | UINT32 | R | 0...12
52 | I8 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I9 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I10 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I11 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I12 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I13 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I14 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I15 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I16 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I17 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I18 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I19 | CTS1 | L1 Current | FLOAT | R | 0...250
52 | I20 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I21 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I22 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I23 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I24 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I25 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I26 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I27 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I28 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I29 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I30 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I31 | CTS1 | L2 Current | FLOAT | R | 0...250
52 | I32 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I33 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I34 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I35 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I36 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I37 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I38 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I39 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I40 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I41 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I42 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I43 | CTS1 | L3 Current | FLOAT | R | 0...250
52 | I44 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I45 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I46 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I47 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I48 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I49 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I50 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I51 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I52 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I53 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I54 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I55 | CTS1 | I2 Current | FLOAT | R | 0...250
52 | I56 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I57 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I58 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I59 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I60 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I61 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I62 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I63 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I64 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I65 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I66 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I67 | CTS1 | I1 Current | FLOAT | R | 0...250
52 | I68 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I69 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I70 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I71 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I72 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I73 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I74 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I75 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I76 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I77 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I78 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | I79 | CTS1 | I0 Current | FLOAT | R | 0...250
52 | S51 | CTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
52 | S52 | CTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
54 | S1 | CTS2 | CTS2 mode | UINT32 | RW | 0=Disabled;1=Activated
54 | V1 | CTS2 | CTS2 condition | UINT32 | R | 0=Normal;1=Alarm;2=Blocked
54 | I1 | CTS2 | Uncompensated residual unbalance Pri | FLOAT | R | 0...50
54 | I2 | CTS2 | Natural unbalance ang | FLOAT | R | -360...360
54 | I3 | CTS2 | Measured current difference Isum, I0 | FLOAT | R | 0...50
54 | I4 | CTS2 | Measured angle difference Isum, I0 | FLOAT | R | -360...360
54 | I5 | CTS2 | CTS2 alarms | UINT32 | R | 0...4294967295
54 | I6 | CTS2 | CTS2 blocks | UINT32 | R | 0...4294967295
54 | S2 | CTS2 | Clear statistics | UINT32 | W | 0=-;1=Clear
54 | S3 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S4 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S5 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S6 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S7 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S8 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S9 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S10 | CTS2 | Iset Highlimit | FLOAT | RW | 0.01...40
54 | S11 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S12 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S13 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S14 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S15 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S16 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S17 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S18 | CTS2 | Iset Lowlimit | FLOAT | RW | 0.01...40
54 | S19 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S20 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S21 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S22 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S23 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S24 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S25 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S26 | CTS2 | Iset ratio | FLOAT | RW | 0.01...100
54 | S27 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S28 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S29 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S30 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S31 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S32 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S33 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S34 | CTS2 | I2/I1 ratio | FLOAT | RW | 0.01...100
54 | S35 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S36 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S37 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S38 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S39 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S40 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S41 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S42 | CTS2 | Isum difference | FLOAT | RW | 0.01...40
54 | S43 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S44 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S45 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S46 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S47 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S48 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S49 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | S50 | CTS2 | Time delay for alarm | FLOAT | RW | 0...1800
54 | O1 | CTS2 | CTS2 ALARM | SIGNAL_OUT | RW | 0...4294967295
54 | O2 | CTS2 | CTS2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
54 | I7 | CTS2 | Newest Register | UINT32 | R | 0...12
54 | I8 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I9 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I10 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I11 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I12 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I13 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I14 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I15 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I16 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I17 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I18 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I19 | CTS2 | L1 Current | FLOAT | R | 0...250
54 | I20 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I21 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I22 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I23 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I24 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I25 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I26 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I27 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I28 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I29 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I30 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I31 | CTS2 | L2 Current | FLOAT | R | 0...250
54 | I32 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I33 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I34 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I35 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I36 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I37 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I38 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I39 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I40 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I41 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I42 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I43 | CTS2 | L3 Current | FLOAT | R | 0...250
54 | I44 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I45 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I46 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I47 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I48 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I49 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I50 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I51 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I52 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I53 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I54 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I55 | CTS2 | I2 Current | FLOAT | R | 0...250
54 | I56 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I57 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I58 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I59 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I60 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I61 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I62 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I63 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I64 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I65 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I66 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I67 | CTS2 | I1 Current | FLOAT | R | 0...250
54 | I68 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I69 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I70 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I71 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I72 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I73 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I74 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I75 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I76 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I77 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I78 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | I79 | CTS2 | I0 Current | FLOAT | R | 0...250
54 | S51 | CTS2 | EventMaskLo | UINT32 | RW | 0...4294967295
54 | S52 | CTS2 | EventMaskHi | UINT32 | RW | 0...4294967295
53 | S1 | VTS1 | VTS [60] mode | UINT32 | RW | 0=Disabled;1=Activated
53 | V1 | VTS1 | VTS condition | UINT32 | R | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
53 | V2 | VTS1 | Bus voltages | UINT32 | R | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
53 | I1 | VTS1 | VTS Starts | UINT32 | R | 0...4294967295
53 | I2 | VTS1 | Line fuse fails | UINT32 | R | 0...4294967295
53 | I3 | VTS1 | Bus fuse fails | UINT32 | R | 0...4294967295
53 | I4 | VTS1 | VTS Blocks | UINT32 | R | 0...4294967295
53 | S2 | VTS1 | Clear statistics | UINT32 | W | 0=-;1=Clear
53 | S3 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S4 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S5 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S6 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S7 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S8 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S9 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S10 | VTS1 | Voltage low pickup | FLOAT | RW | 0.05...0.5
53 | S11 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S12 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S13 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S14 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S15 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S16 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S17 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S18 | VTS1 | Voltage high detect | FLOAT | RW | 0.5...1.1
53 | S19 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S20 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S21 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S22 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S23 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S24 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S25 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S26 | VTS1 | Angle shift limit | FLOAT | RW | 2...90
53 | S27 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S28 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S29 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S30 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S31 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S32 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S33 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S34 | VTS1 | Bus Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S35 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S36 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S37 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S38 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S39 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S40 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S41 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S42 | VTS1 | Line Fuse fail check | UINT32 | RW | 0=No;1=Yes
53 | S43 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S44 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S45 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S46 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S47 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S48 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S49 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | S50 | VTS1 | Definite operating time delay | FLOAT | RW | 0...1800
53 | O1 | VTS1 | VTS Start | SIGNAL_OUT | RW | 0...4294967295
53 | O2 | VTS1 | VTS Fail Alarm Bus | SIGNAL_OUT | RW | 0...4294967295
53 | O3 | VTS1 | VTS Fail Alarm Line | SIGNAL_OUT | RW | 0...4294967295
53 | O4 | VTS1 | VTS Blocked(time delay) | SIGNAL_OUT | RW | 0...4294967295
53 | I5 | VTS1 | Newest Register | UINT32 | R | 0...12
53 | I6 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I7 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I8 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I9 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I10 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I11 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I12 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I13 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I14 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I15 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I16 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I17 | VTS1 | Volt In 1 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I18 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I19 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I20 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I21 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I22 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I23 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I24 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I25 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I26 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I27 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I28 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I29 | VTS1 | Volt In 2 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I30 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I31 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I32 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I33 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I34 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I35 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I36 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I37 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I38 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I39 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I40 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I41 | VTS1 | Volt In 3 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I42 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I43 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I44 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I45 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I46 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I47 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I48 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I49 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I50 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I51 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I52 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I53 | VTS1 | Volt In 4 status | UINT32 | R | 0b=No Voltage;1b=Voltage Ok;2b=Low Voltage;3b=;
53 | I54 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I55 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I56 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I57 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I58 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I59 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I60 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I61 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I62 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I63 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I64 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | I65 | VTS1 | System status | UINT32 | R | 0=BusDead;1=BusLive VTSok SeqOk;2=BusLive VTSok SeqRev;3=BusLive VTSok SeqUndef;4=BusLive VTS fault;
53 | S51 | VTS1 | EventMaskLo | UINT32 | RW | 0...4294967295
53 | S52 | VTS1 | EventMaskHi | UINT32 | RW | 0...4294967295
43 | S1 | FLX1 | Fault locator mode | UINT32 | RW | 0=Disabled;1=Activated
43 | V1 | FLX1 | Fault locator condition | UINT32 | R | 0=Idle;1=Triggered;2=Calc ready
43 | I1 | FLX1 | Times Flocator triggered | UINT32 | R | 0...4294967295
43 | I2 | FLX1 | Last fault reactance | FLOAT | R | -1800...1800
43 | I3 | FLX1 | Last fault distance | FLOAT | R | -1800...1800
43 | V2 | FLX1 | Last fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I4 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I5 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I6 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | I7 | FLX1 | Last fault IL1 | FLOAT | R | 0...1800
43 | I8 | FLX1 | Last fault IL2 | FLOAT | R | 0...1800
43 | I9 | FLX1 | Last fault IL3 | FLOAT | R | 0...1800
43 | V3 | FLX1 | Last fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | S2 | FLX1 | Clear statistics | UINT32 | W | 0=-;1=Clear
43 | S3 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S4 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S5 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S6 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S7 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S8 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S9 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S10 | FLX1 | Trigger current > | FLOAT | RW | 0...40
43 | S11 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S12 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S13 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S14 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S15 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S16 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S17 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | S18 | FLX1 | Reactance per km | FLOAT | RW | 0...5
43 | I10 | FLX1 | Newest Register | UINT32 | R | 0...12
43 | I11 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I12 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I13 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I14 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I15 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I16 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I17 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I18 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I19 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I20 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I21 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I22 | FLX1 | Fault type | UINT32 | R | 0=No trigs;1=L1-L2;2=L2-L3;3=L3-L1;4=L1-N;5=L2-N;6=L3-N;7=L1-L2-L3;8=No idea..
43 | I23 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I24 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I25 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I26 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I27 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I28 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I29 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I30 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I31 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I32 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I33 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I34 | FLX1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
43 | I35 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I36 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I37 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I38 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I39 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I40 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I41 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I42 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I43 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I44 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I45 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I46 | FLX1 | Fault reactance | FLOAT | R | 0...500
43 | I47 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I48 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I49 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I50 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I51 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I52 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I53 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I54 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I55 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I56 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I57 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I58 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I59 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I60 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I61 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I62 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I63 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I64 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I65 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I66 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I67 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I68 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I69 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I70 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I71 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I72 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I73 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I74 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I75 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I76 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I77 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I78 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I79 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I80 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I81 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I82 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I83 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I84 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I85 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I86 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I87 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I88 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I89 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I90 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I91 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I92 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I93 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I94 | FLX1 | IL1 Fault current | FLOAT | R | 0...500
43 | I95 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I96 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I97 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I98 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I99 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I100 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I101 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I102 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I103 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I104 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I105 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I106 | FLX1 | IL2 Fault current | FLOAT | R | 0...500
43 | I107 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I108 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I109 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I110 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I111 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I112 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I113 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I114 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I115 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I116 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I117 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I118 | FLX1 | IL3 Fault current | FLOAT | R | 0...500
43 | I119 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I120 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I121 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I122 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I123 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I124 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I125 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I126 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I127 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I128 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I129 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | I130 | FLX1 | Fault distance | FLOAT | R | 0...360
43 | S19 | FLX1 | EventMaskLo | UINT32 | RW | 0...4294967295
55 | S1 | THD1 | THD mode | UINT32 | RW | 0=Disabled;1=Activated
55 | V1 | THD1 | THD condition | UINT32 | R | 0=Normal;1=Start;2=Alarm;3=Blocked
55 | S2 | THD1 | Measurement magnitude | UINT32 | RW | 0=Amplitude;1=Power
55 | I1 | THD1 | THD starts | UINT32 | R | 0...4294967295
55 | I2 | THD1 | THD alarms | UINT32 | R | 0...4294967295
55 | I3 | THD1 | THD blocks | UINT32 | R | 0...4294967295
55 | S3 | THD1 | Clear statistics | UINT32 | W | 0=-;1=Clear
55 | S4 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S5 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S6 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S7 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S8 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S9 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S10 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S11 | THD1 | Enable Phase THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S12 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S13 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S14 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S15 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S16 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S17 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S18 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S19 | THD1 | Enable I01 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S20 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S21 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S22 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S23 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S24 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S25 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S26 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S27 | THD1 | Enable I02 THD Alarm | UINT32 | RW | 0=Disabled;1=Enabled
55 | S28 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S29 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S30 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S31 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S32 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S33 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S34 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S35 | THD1 | Phase THD pick up | FLOAT | RW | 0.1...100
55 | S36 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S37 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S38 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S39 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S40 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S41 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S42 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S43 | THD1 | I01THD pick up | FLOAT | RW | 0.1...100
55 | S44 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S45 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S46 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S47 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S48 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S49 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S50 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S51 | THD1 | I02 THD pick up | FLOAT | RW | 0.1...100
55 | S52 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S53 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S54 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S55 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S56 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S57 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S58 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S59 | THD1 | Phase THD alarm delay | FLOAT | RW | 0...1800
55 | S60 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S61 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S62 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S63 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S64 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S65 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S66 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S67 | THD1 | I01 THD alarm delay | FLOAT | RW | 0...1800
55 | S68 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S69 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S70 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S71 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S72 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S73 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S74 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | S75 | THD1 | I02 THD alarm delay | FLOAT | RW | 0...1800
55 | O1 | THD1 | THDPH> START | SIGNAL_OUT | RW | 0...4294967295
55 | O2 | THD1 | THDPH> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O3 | THD1 | THDI01> START | SIGNAL_OUT | RW | 0...4294967295
55 | O4 | THD1 | THDI01> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O5 | THD1 | THDI02> START | SIGNAL_OUT | RW | 0...4294967295
55 | O6 | THD1 | THDI02> ALARM | SIGNAL_OUT | RW | 0...4294967295
55 | O7 | THD1 | THD> BLOCKED | SIGNAL_OUT | RW | 0...4294967295
55 | I4 | THD1 | Newest Register | UINT32 | R | 0...12
55 | I5 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I6 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I7 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I8 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I9 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I10 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I11 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I12 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I13 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I14 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I15 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I16 | THD1 | I01 THD | FLOAT | R | 0...250
55 | I17 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I18 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I19 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I20 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I21 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I22 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I23 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I24 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I25 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I26 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I27 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I28 | THD1 | I02 THD | FLOAT | R | 0...250
55 | I29 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I30 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I31 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I32 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I33 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I34 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I35 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I36 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I37 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I38 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I39 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | I40 | THD1 | Ph THD Time remaining | FLOAT | R | 0...250
55 | S76 | THD1 | EventMaskLo | UINT32 | RW | 0...4294967295
58 | S1 | CBW1 | CBW mode | UINT32 | RW | 0=Disabled;1=Activated
58 | V1 | CBW1 | CBW condition | UINT32 | R | 0=Normal;1=Alarm1 On;2=Alarm2 On
58 | I1 | CBW1 | Breaker operations | UINT32 | R | 0...4294967295
58 | I2 | CBW1 | Alarm 1 counter | UINT32 | R | 0...4294967295
58 | I3 | CBW1 | Alarm 2 counter | UINT32 | R | 0...4294967295
58 | I4 | CBW1 | L1 Operations Left | FLOAT | R | 0...4294967295
58 | I5 | CBW1 | L2 Operations Left | FLOAT | R | 0...4294967295
58 | I6 | CBW1 | L3 Operations Left | FLOAT | R | 0...4294967295
58 | S2 | CBW1 | Clear statistics | UINT32 | W | 0=-;1=Clear
58 | S3 | CBW1 | Alarm 1 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S4 | CBW1 | Alarm 2 Enable | UINT32 | RW | 0=Disabled;1=Enabled
58 | S5 | CBW1 | Alarm 1 Set | UINT32 | RW | 0...200000
58 | S6 | CBW1 | Alarm 2 Set | UINT32 | RW | 0...200000
58 | S7 | CBW1 | Operations 1 | FLOAT | RW | 0...200000
58 | S8 | CBW1 | Operations 2 | FLOAT | RW | 0...200000
58 | S9 | CBW1 | Current 1 | FLOAT | RW | 0...100
58 | S10 | CBW1 | Current 2 | FLOAT | RW | 0...100
58 | O1 | CBW1 | CBW Alarm 1 act | SIGNAL_OUT | RW | 0...4294967295
58 | I7 | CBW1 | Newest Register | UINT32 | R | 0...12
58 | I8 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I9 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I10 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I11 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I12 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I13 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I14 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I15 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I16 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I17 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I18 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I19 | CBW1 | L1 operations left | FLOAT | R | 0...600000
58 | I20 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I21 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I22 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I23 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I24 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I25 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I26 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I27 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I28 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I29 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I30 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I31 | CBW1 | L2 operations left | FLOAT | R | 0...600000
58 | I32 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I33 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I34 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I35 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I36 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I37 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I38 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I39 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I40 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I41 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I42 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | I43 | CBW1 | L3 operations left | FLOAT | R | 0...600000
58 | S11 | CBW1 | EventMaskLo | UINT32 | RW | 0...4294967295
97 | S1 | NJK1 | U0> RECL [79] mode | UINT32 | RW | 0=Disabled;1=Activated
97 | V1 | NJK1 | U0> RECL condition | UINT32 | R | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
97 | I1 | NJK1 | Requests | UINT32 | R | 0...4294967295
97 | I2 | NJK1 | Blocks | UINT32 | R | 0...4294967295
97 | I3 | NJK1 | Starts | UINT32 | R | 0...4294967295
97 | I4 | NJK1 | Breaker closes | UINT32 | R | 0...4294967295
97 | S2 | NJK1 | Clear statistics | UINT32 | W | 0=-;1=Clear
97 | S3 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S4 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S5 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S6 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S7 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S8 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S9 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | S10 | NJK1 | Reclose time for U0> RECL | FLOAT | RW | 0...1800
97 | O1 | NJK1 | U0> RECL Blocked | SIGNAL_OUT | RW | 0...4294967295
97 | O2 | NJK1 | U0> RECL Active | SIGNAL_OUT | RW | 0...4294967295
97 | O3 | NJK1 | U0> RECL CLOSE | SIGNAL_OUT | RW | 0...4294967295
97 | O4 | NJK1 | U0> RECL BLKU0 | SIGNAL_OUT | RW | 0...4294967295
97 | I5 | NJK1 | Newest Register | UINT32 | R | 0...12
97 | I6 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I7 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I8 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I9 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I10 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I11 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I12 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I13 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I14 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I15 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I16 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I17 | NJK1 | U0> RECL time before close | FLOAT | R | 0...1800
97 | I18 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I19 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I20 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I21 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I22 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I23 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I24 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I25 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I26 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I27 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I28 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | I29 | NJK1 | U0> RECL been active | FLOAT | R | 0...1800
97 | S11 | NJK1 | EventMaskLo | UINT32 | RW | 0...4294967295
61 | S1 | SOF1 | SOTF mode | UINT32 | RW | 0=Disabled;1=Activated
61 | V1 | SOF1 | SOTF condition | UINT32 | R | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
61 | I1 | SOF1 | Inits | UINT32 | R | 0...4294967295
61 | I2 | SOF1 | Starts | UINT32 | R | 0...4294967295
61 | I3 | SOF1 | Trips | UINT32 | R | 0...4294967295
61 | I4 | SOF1 | Blocks | UINT32 | R | 0...4294967295
61 | S2 | SOF1 | Clear statistics | UINT32 | W | 0=-;1=Clear
61 | S3 | SOF1 | SG in use | UINT32 | RW | 0...255
61 | S4 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S5 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S6 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S7 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S8 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S9 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S10 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | S11 | SOF1 | Release time for SOTF | FLOAT | RW | 0...1800
61 | O1 | SOF1 | SOTF Blocked | SIGNAL_OUT | RW | 0...4294967295
61 | O2 | SOF1 | SOTF Active | SIGNAL_OUT | RW | 0...4294967295
61 | O3 | SOF1 | SOTF Trip | SIGNAL_OUT | RW | 0...4294967295
61 | I5 | SOF1 | Newest Register | UINT32 | R | 0...12
61 | I6 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I7 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I8 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I9 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I10 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I11 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I12 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I13 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I14 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I15 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I16 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I17 | SOF1 | SOTF remaining time | FLOAT | R | 0...1800
61 | I18 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I19 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I20 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I21 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I22 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I23 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I24 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I25 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I26 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I27 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I28 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | I29 | SOF1 | SOTF been active | FLOAT | R | 0...1800
61 | S12 | SOF1 | EventMaskLo | UINT32 | RW | 0...4294967295
142 | S1 | DOS1 | Energy dose counter mode | UINT32 | RW | 0=Disabled;1=Activated
142 | S2 | DOS1 | Clear pulsecounters | UINT32 | W | 0=-;1=Clear
142 | S3 | DOS1 | DC 1 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S4 | DOS1 | DC 1 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I1 | DOS1 | DC 1 Input signal | FLOAT | R | -1000000...1000000
142 | S5 | DOS1 | DC 1 Pulse magnitude | FLOAT | RW | 0...1800
142 | S6 | DOS1 | DC 1 Pulse Lenght | FLOAT | RW | 0...1800
142 | I2 | DOS1 | DC 1 Pulses sent | UINT32 | R | 0...4294967295
142 | S7 | DOS1 | DC 2 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S8 | DOS1 | DC 2 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I3 | DOS1 | DC 2 Input signal | FLOAT | R | -1000000...1000000
142 | S9 | DOS1 | DC 2 Pulse magnitude | FLOAT | RW | 0...1800
142 | S10 | DOS1 | DC 2 Pulse Lenght | FLOAT | RW | 0...1800
142 | I4 | DOS1 | DC 2 Pulses sent | UINT32 | R | 0...4294967295
142 | S11 | DOS1 | DC 3 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S12 | DOS1 | DC 3 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I5 | DOS1 | DC 3 Input signal | FLOAT | R | -1000000...1000000
142 | S13 | DOS1 | DC 3 Pulse magnitude | FLOAT | RW | 0...1800
142 | S14 | DOS1 | DC 3 Pulse Lenght | FLOAT | RW | 0...1800
142 | I6 | DOS1 | DC 3 Pulses sent | UINT32 | R | 0...4294967295
142 | S15 | DOS1 | DC 4 enable | UINT32 | RW | 0=Disabled;1=Enabled
142 | S16 | DOS1 | DC 4 Input signal select | UINT32 | RW | 0=3PH.Fwd.Act.EP;1=3PH.Rev.Act.EP;2=3PH.Fwd.React.EQ.CAP;3=3PH.Fwd.React.EQ.IND;4=3PH.Rev.React.EQ.CAP;5=3PH.Rev.React.EQ.IND
142 | I7 | DOS1 | DC 4 Input signal | FLOAT | R | -1000000...1000000
142 | S17 | DOS1 | DC 4 Pulse magnitude | FLOAT | RW | 0...1800
142 | S18 | DOS1 | DC 4 Pulse Lenght | FLOAT | RW | 0...1800
142 | I8 | DOS1 | DC 4 Pulses sent | UINT32 | R | 0...4294967295
142 | O1 | DOS1 | DC 1 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O2 | DOS1 | DC 2 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O3 | DOS1 | DC 3 Pulse out | SIGNAL_OUT | RW | 0...4294967295
142 | O4 | DOS1 | DC 4 Pulse out | SIGNAL_OUT | RW | 0...4294967295
144 | V1 | PCS1 | PCS1 Switch Status | SIGNAL_OUT | RW | 0...4294967295
145 | V1 | PCS2 | PCS2 Switch Status | SIGNAL_OUT | RW | 0...4294967295
146 | V1 | PCS3 | PCS3 Switch Status | SIGNAL_OUT | RW | 0...4294967295
147 | V1 | PCS4 | PCS4 Switch Status | SIGNAL_OUT | RW | 0...4294967295
148 | V1 | PCS5 | PCS5 Switch Status | SIGNAL_OUT | RW | 0...4294967295
45 | S1 | SYN1 | Synchrocheck (SYN1,2,3) [25] mode | UINT32 | RW | 0=Disabled;1=Activated
45 | V1 | SYN1 | SYN1 Condition | UINT32 | R | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok
45 | V2 | SYN1 | SYN2 Condition | UINT32 | R | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok
45 | V3 | SYN1 | SYN3 Condition | UINT32 | R | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok
45 | I1 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I2 | SYN1 | SYN1 Mag diff | FLOAT | R | -120...120
45 | I3 | SYN1 | SYN1 Ang diff | FLOAT | R | -360...360
45 | I4 | SYN1 | SYN1 freq diff | FLOAT | R | -75...75
45 | I5 | SYN1 | SYN1 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S2 | SYN1 | Estimated BRK Closing time | FLOAT | R | 0...360
45 | S3 | SYN1 | Networks rotating time | FLOAT | R | 0...360
45 | S4 | SYN1 | Networks placement atm | FLOAT | R | -360...360
45 | I6 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I7 | SYN1 | SYN2 Mag diff | FLOAT | R | -120...120
45 | I8 | SYN1 | SYN2 Ang diff | FLOAT | R | -360...360
45 | I9 | SYN1 | SYN2 freq diff | FLOAT | R | -75...75
45 | I10 | SYN1 | SYN2 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S5 | SYN1 | SYN2 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S6 | SYN1 | SYN2 Networks rotating time | FLOAT | R | 0...360.000
45 | S7 | SYN1 | SYN2 Networks placement atm | FLOAT | R | -360.000...360.000
45 | I11 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I12 | SYN1 | SYN3 Mag diff | FLOAT | R | -120...120
45 | I13 | SYN1 | SYN3 Ang diff | FLOAT | R | -360...360
45 | I14 | SYN1 | SYN3 freq diff | FLOAT | R | -75...75
45 | I15 | SYN1 | SYN3 Switch status | UINT32 | R | 0=Still;1=Departing;2=Enclosing
45 | S8 | SYN1 | SYN3 Estimated BRK Closing time | FLOAT | R | 0...360.000
45 | S9 | SYN1 | SYN3 Networks rotating time | FLOAT | R | 0...360.000
45 | S10 | SYN1 | SYN3 Networks placement atm | FLOAT | R | -360.000...360.000
45 | S11 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S12 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S13 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S14 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S15 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S16 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S17 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S18 | SYN1 | SYN1 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S19 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S20 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S21 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S22 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S23 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S24 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S25 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S26 | SYN1 | SYN1 U Gen > | FLOAT | RW | 20...105
45 | S27 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S28 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S29 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S30 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S31 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S32 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S33 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S34 | SYN1 | SYN1 U Gen < | FLOAT | RW | 0.1...50
45 | S35 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S36 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S37 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S38 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S39 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S40 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S41 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S42 | SYN1 | SYN1 U Bus < | FLOAT | RW | 0.1...50
45 | S43 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S44 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S45 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S46 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S47 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S48 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S49 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S50 | SYN1 | SYN1 f Gen > | FLOAT | RW | 98...102
45 | S51 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S52 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S53 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S54 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S55 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S56 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S57 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S58 | SYN1 | SYN1 Synchro check start time | FLOAT | RW | 0...1800
45 | S59 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S60 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S61 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S62 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S63 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S64 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S65 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S66 | SYN1 | SYN1 U live > | FLOAT | RW | 0.1...100
45 | S67 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S68 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S69 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S70 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S71 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S72 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S73 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S74 | SYN1 | SYN1 U dead < | FLOAT | RW | 0...100
45 | S75 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S76 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S77 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S78 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S79 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S80 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S81 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S82 | SYN1 | SYN1 U diff < | FLOAT | RW | 2...50
45 | S83 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S84 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S85 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S86 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S87 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S88 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S89 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S90 | SYN1 | SYN1 angle diff < | FLOAT | RW | 3...90
45 | S91 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S92 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S93 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S94 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S95 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S96 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S97 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S98 | SYN1 | SYN1 freq diff < | FLOAT | RW | 0.05...0.5
45 | S99 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S100 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S101 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S102 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S103 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S104 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S105 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S106 | SYN1 | SYN2 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S107 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S108 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S109 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S110 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S111 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S112 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S113 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S114 | SYN1 | SYN2 U Gen > | FLOAT | RW | 20...105
45 | S115 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S116 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S117 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S118 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S119 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S120 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S121 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S122 | SYN1 | SYN2 U Gen < | FLOAT | RW | 0.1...50
45 | S123 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S124 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S125 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S126 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S127 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S128 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S129 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S130 | SYN1 | SYN2 U Bus < | FLOAT | RW | 0.1...50
45 | S131 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S132 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S133 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S134 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S135 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S136 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S137 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S138 | SYN1 | SYN2 f Gen > | FLOAT | RW | 98...102
45 | S139 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S140 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S141 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S142 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S143 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S144 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S145 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S146 | SYN1 | SYN2 Synchro check start time | FLOAT | RW | 0...1800
45 | S147 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S148 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S149 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S150 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S151 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S152 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S153 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S154 | SYN1 | SYN2 U live > | FLOAT | RW | 0.1...100
45 | S155 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S156 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S157 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S158 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S159 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S160 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S161 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S162 | SYN1 | SYN2 U dead < | FLOAT | RW | 0...100
45 | S163 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S164 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S165 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S166 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S167 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S168 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S169 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S170 | SYN1 | SYN2 U diff < | FLOAT | RW | 2...50
45 | S171 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S172 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S173 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S174 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S175 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S176 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S177 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S178 | SYN1 | SYN2 angle diff < | FLOAT | RW | 3...90
45 | S179 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S180 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S181 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S182 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S183 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S184 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S185 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S186 | SYN1 | SYN2 freq diff < | FLOAT | RW | 0.05...0.5
45 | S187 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S188 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S189 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S190 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S191 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S192 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S193 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S194 | SYN1 | SYN3 U conditions | UINT32 | RW | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
45 | S195 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S196 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S197 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S198 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S199 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S200 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S201 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S202 | SYN1 | SYN3 U Gen > | FLOAT | RW | 20...105
45 | S203 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S204 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S205 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S206 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S207 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S208 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S209 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S210 | SYN1 | SYN3 U Gen < | FLOAT | RW | 0.1...50
45 | S211 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S212 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S213 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S214 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S215 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S216 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S217 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S218 | SYN1 | SYN3 U Bus < | FLOAT | RW | 0.1...50
45 | S219 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S220 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S221 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S222 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S223 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S224 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S225 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S226 | SYN1 | SYN3 f Gen > | FLOAT | RW | 98...102
45 | S227 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S228 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S229 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S230 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S231 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S232 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S233 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S234 | SYN1 | SYN3 Synchro check start time | FLOAT | RW | 0...1800
45 | S235 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S236 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S237 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S238 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S239 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S240 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S241 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S242 | SYN1 | SYN3 U live > | FLOAT | RW | 0.1...100
45 | S243 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S244 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S245 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S246 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S247 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S248 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S249 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S250 | SYN1 | SYN3 U dead < | FLOAT | RW | 0...100
45 | S251 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S252 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S253 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S254 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S255 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S256 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S257 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S258 | SYN1 | SYN3 U diff < | FLOAT | RW | 2...50
45 | S259 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S260 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S261 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S262 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S263 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S264 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S265 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S266 | SYN1 | SYN3 angle diff < | FLOAT | RW | 3...90
45 | S267 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S268 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S269 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S270 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S271 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S272 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S273 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | S274 | SYN1 | SYN3 freq diff < | FLOAT | RW | 0.05...0.5
45 | O1 | SYN1 | SYN1 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O2 | SYN1 | SYN1 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O3 | SYN1 | SYN1 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O4 | SYN1 | SYN1 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O5 | SYN1 | SYN1 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O6 | SYN1 | SYN1 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O7 | SYN1 | SYN1 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O8 | SYN1 | SYN1 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O9 | SYN1 | SYN1 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O10 | SYN1 | SYN1 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O11 | SYN1 | SYN1 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O12 | SYN1 | SYN1 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O13 | SYN1 | SYN1 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O14 | SYN1 | SYN1 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O15 | SYN1 | SYN1 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O16 | SYN1 | SYN1 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O17 | SYN1 | SYN1 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O18 | SYN1 | SYN1 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O19 | SYN1 | SYN1 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O20 | SYN1 | SYN1 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O21 | SYN1 | SYN2 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O22 | SYN1 | SYN2 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O23 | SYN1 | SYN2 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O24 | SYN1 | SYN2 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O25 | SYN1 | SYN2 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O26 | SYN1 | SYN2 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O27 | SYN1 | SYN2 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O28 | SYN1 | SYN2 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O29 | SYN1 | SYN2 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O30 | SYN1 | SYN2 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O31 | SYN1 | SYN2 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O32 | SYN1 | SYN2 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O33 | SYN1 | SYN2 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O34 | SYN1 | SYN2 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O35 | SYN1 | SYN2 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O36 | SYN1 | SYN2 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O37 | SYN1 | SYN2 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O38 | SYN1 | SYN2 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O39 | SYN1 | SYN2 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O40 | SYN1 | SYN2 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | O41 | SYN1 | SYN3 OK | SIGNAL_OUT | RW | 0...4294967295
45 | O42 | SYN1 | SYN3 Voltage Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O43 | SYN1 | SYN3 Angle Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O44 | SYN1 | SYN3 Frequency Difference OK | SIGNAL_OUT | RW | 0...4294967295
45 | O45 | SYN1 | SYN3 Live Live | SIGNAL_OUT | RW | 0...4294967295
45 | O46 | SYN1 | SYN3 Live Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O47 | SYN1 | SYN3 Dead Live | SIGNAL_OUT | RW | 0...4294967295
45 | O48 | SYN1 | SYN3 Dead Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O49 | SYN1 | SYN3 Voltage Difference too high Vbus > Vline | SIGNAL_OUT | RW | 0...4294967295
45 | O50 | SYN1 | SYN3 Voltage Difference too high Vline > Vbus | SIGNAL_OUT | RW | 0...4294967295
45 | O51 | SYN1 | SYN3 Frequency Difference too high fbus > fline | SIGNAL_OUT | RW | 0...4294967295
45 | O52 | SYN1 | SYN3 Frequency Difference too high fline > fbus | SIGNAL_OUT | RW | 0...4294967295
45 | O53 | SYN1 | SYN3 Angle Difference too high <alpha> bus leads <alpha> line | SIGNAL_OUT | RW | 0...4294967295
45 | O54 | SYN1 | SYN3 Angle Difference too high <alpha> line leads <alpha> bus | SIGNAL_OUT | RW | 0...4294967295
45 | O55 | SYN1 | SYN3 Bus voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O56 | SYN1 | SYN3 Bus voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O57 | SYN1 | SYN3 Line voltage Live | SIGNAL_OUT | RW | 0...4294967295
45 | O58 | SYN1 | SYN3 Line voltage Dead | SIGNAL_OUT | RW | 0...4294967295
45 | O59 | SYN1 | SYN3 SWITCH OK | SIGNAL_OUT | RW | 0...4294967295
45 | O60 | SYN1 | SYN3 BLOCKED | SIGNAL_OUT | RW | 0...4294967295
45 | I16 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I17 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I18 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I19 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I20 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I21 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I22 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I23 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I24 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I25 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I26 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I27 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I28 | SYN1 | SYN1 Ref1 Voltage | FLOAT | R | 0...150
45 | I29 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I30 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I31 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I32 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I33 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I34 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I35 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I36 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I37 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I38 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I39 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I40 | SYN1 | SYN1 Ref2 Voltage | FLOAT | R | 0...150
45 | I41 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I42 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I43 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I44 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I45 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I46 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I47 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I48 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I49 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I50 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I51 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I52 | SYN1 | SYN1 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I53 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I54 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I55 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I56 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I57 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I58 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I59 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I60 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I61 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I62 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I63 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I64 | SYN1 | SYN1 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I65 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I66 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I67 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I68 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I69 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I70 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I71 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I72 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I73 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I74 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I75 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I76 | SYN1 | SYN1 Vdiff | FLOAT | R | 0...150
45 | I77 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I78 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I79 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I80 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I81 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I82 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I83 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I84 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I85 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I86 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I87 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I88 | SYN1 | SYN1 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I89 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I90 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I91 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I92 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I93 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I94 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I95 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I96 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I97 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I98 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I99 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I100 | SYN1 | SYN1 Adiff | FLOAT | R | -360...360
45 | I101 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I102 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I103 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I104 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I105 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I106 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I107 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I108 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I109 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I110 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I111 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I112 | SYN1 | SYN1 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I113 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I114 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I115 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I116 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I117 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I118 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I119 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I120 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I121 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I122 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I123 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I124 | SYN1 | SYN1 fdiff | FLOAT | R | 0...75
45 | I125 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I126 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I127 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I128 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I129 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I130 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I131 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I132 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I133 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I134 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I135 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I136 | SYN1 | SYN1 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I137 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I138 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I139 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I140 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I141 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I142 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I143 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I144 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I145 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I146 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I147 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I148 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I149 | SYN1 | SYN2 Ref1 Voltage | FLOAT | R | 0...150
45 | I150 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I151 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I152 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I153 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I154 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I155 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I156 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I157 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I158 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I159 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I160 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I161 | SYN1 | SYN2 Ref2 Voltage | FLOAT | R | 0...150
45 | I162 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I163 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I164 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I165 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I166 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I167 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I168 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I169 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I170 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I171 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I172 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I173 | SYN1 | SYN2 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I174 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I175 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I176 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I177 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I178 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I179 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I180 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I181 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I182 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I183 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I184 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I185 | SYN1 | SYN2 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I186 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I187 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I188 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I189 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I190 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I191 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I192 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I193 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I194 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I195 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I196 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I197 | SYN1 | SYN2 Vdiff | FLOAT | R | 0...150
45 | I198 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I199 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I200 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I201 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I202 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I203 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I204 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I205 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I206 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I207 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I208 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I209 | SYN1 | SYN2 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I210 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I211 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I212 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I213 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I214 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I215 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I216 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I217 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I218 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I219 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I220 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I221 | SYN1 | SYN2 Adiff | FLOAT | R | -360...360
45 | I222 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I223 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I224 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I225 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I226 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I227 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I228 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I229 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I230 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I231 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I232 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I233 | SYN1 | SYN2 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I234 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I235 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I236 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I237 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I238 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I239 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I240 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I241 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I242 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I243 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I244 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I245 | SYN1 | SYN2 fdiff | FLOAT | R | 0...75
45 | I246 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I247 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I248 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I249 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I250 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I251 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I252 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I253 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I254 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I255 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I256 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I257 | SYN1 | SYN2 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I258 | SYN1 | Newest Register | UINT32 | R | 0...12
45 | I259 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I260 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I261 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I262 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I263 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I264 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I265 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I266 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I267 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I268 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I269 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I270 | SYN1 | SYN3 Ref1 Voltage | FLOAT | R | 0...150
45 | I271 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I272 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I273 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I274 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I275 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I276 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I277 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I278 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I279 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I280 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I281 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I282 | SYN1 | SYN3 Ref2 Voltage | FLOAT | R | 0...150
45 | I283 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I284 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I285 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I286 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I287 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I288 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I289 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I290 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I291 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I292 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I293 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I294 | SYN1 | SYN3 Volt Cond | UINT32 | R | 0=Dead Dead;1=Live Dead;2=Dead Live;3=Live Live;4=Undefined;5=Not monitored
45 | I295 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I296 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I297 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I298 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I299 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I300 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I301 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I302 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I303 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I304 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I305 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I306 | SYN1 | SYN3 Volt status | UINT32 | R | 0=Not Ok;1=Ok
45 | I307 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I308 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I309 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I310 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I311 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I312 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I313 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I314 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I315 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I316 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I317 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I318 | SYN1 | SYN3 Vdiff | FLOAT | R | 0...150
45 | I319 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I320 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I321 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I322 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I323 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I324 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I325 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I326 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I327 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I328 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I329 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I330 | SYN1 | SYN3 Vdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I331 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I332 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I333 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I334 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I335 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I336 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I337 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I338 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I339 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I340 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I341 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I342 | SYN1 | SYN3 Adiff | FLOAT | R | -360...360
45 | I343 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I344 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I345 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I346 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I347 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I348 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I349 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I350 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I351 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I352 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I353 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I354 | SYN1 | SYN3 Adiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I355 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I356 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I357 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I358 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I359 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I360 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I361 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I362 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I363 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I364 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I365 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I366 | SYN1 | SYN3 fdiff | FLOAT | R | 0...75
45 | I367 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I368 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I369 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I370 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I371 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I372 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I373 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I374 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I375 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I376 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I377 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | I378 | SYN1 | SYN3 fdiff cond | UINT32 | R | 0=Not Ok;1=Ok
45 | S275 | SYN1 | EventMaskLo | UINT32 | RW | 0...4294967295
45 | S276 | SYN1 | EventMaskHi | UINT32 | RW | 0...4294967295
219 | S1 | SYNX1 | SYN1 Extra EventMaskLo | UINT32 | RW | 0...4294967295
219 | S2 | SYNX1 | SYN1 Extra EventMaskHi | UINT32 | RW | 0...4294967295
220 | S1 | SYNX2 | SYN2 Extra EventMaskLo | UINT32 | RW | 0...4294967295
220 | S2 | SYNX2 | SYN2 Extra EventMaskHi | UINT32 | RW | 0...4294967295
221 | S1 | SYNX3 | SYN3 Extra EventMaskLo | UINT32 | RW | 0...4294967295
221 | S2 | SYNX3 | SYN3 Extra EventMaskHi | UINT32 | RW | 0...4294967295
155 | S1 | VJP1 | <DELTA><alpha> > mode | UINT32 | RW | 0=Disabled;1=Activated
155 | V1 | VJP1 | <DELTA><alpha> > condition | UINT32 | R | 0=Normal;1=Blocked:2=Trip;3=Alarm
155 | S2 | VJP1 | Available stages | UINT32 | RW | 0=Trip;1=Trip and Alarm
155 | S3 | VJP1 | Monitored voltages | UINT32 | RW | 0=System all P-P Voltages;1=System any P-P Voltage;2=System L12 Voltage;3=System L23 Voltage;4=System L31 Voltage;5=System all P-E voltages;6=System any P-E voltage;7=System L1 Voltage;8=System L2 Voltage;9=System L3 Voltage;10=U3 Voltage;11=U4 Voltage
155 | V2 | VJP1 | Voltage meas selected | UINT32 | R | 0=Selection Ok;1=Selection not available
155 | I1 | VJP1 | <DELTA><alpha> > U1 Angle difference | FLOAT | R | -360...360
155 | I2 | VJP1 | <DELTA><alpha> U1meas/Set | FLOAT | R | -360...360
155 | I3 | VJP1 | <DELTA><alpha> U2 Angle difference | FLOAT | R | -360...360
155 | I4 | VJP1 | <DELTA><alpha> U2meas/Set | FLOAT | R | -360...360
155 | I5 | VJP1 | <DELTA><alpha> U3 Angle difference | FLOAT | R | -360...360
155 | I6 | VJP1 | <DELTA><alpha> U3meas/Set | FLOAT | R | -360...360
155 | I7 | VJP1 | <DELTA><alpha> > Alarms | UINT32 | R | 0...4294967295
155 | I8 | VJP1 | <DELTA><alpha> > Trips | UINT32 | R | 0...4294967295
155 | I9 | VJP1 | <DELTA><alpha> > Blocks | UINT32 | R | 0...4294967295
155 | S4 | VJP1 | Clear statistics | UINT32 | W | 0=-;1=Clear
155 | S5 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S6 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S7 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S8 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S9 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S10 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S11 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S12 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Trip | FLOAT | RW | 0.05...30
155 | S13 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S14 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S15 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S16 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S17 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S18 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S19 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S20 | VJP1 | Pick-up setting <DELTA><alpha> > (lead or lag) Alarm | FLOAT | RW | 0.05...30
155 | S21 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S22 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S23 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S24 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S25 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S26 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S27 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | S28 | VJP1 | Undervoltage block limit % < Un | FLOAT | RW | 0.01...100
155 | O1 | VJP1 | <DELTA><alpha> > TRIP | SIGNAL_OUT | RW | 0...4294967295
155 | O2 | VJP1 | <DELTA><alpha> > BLOCKED | SIGNAL_OUT | RW | 0...4294967295
155 | I10 | VJP1 | Newest Register | UINT32 | R | 0...12
155 | I11 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I12 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I13 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I14 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I15 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I16 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I17 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I18 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I19 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I20 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I21 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I22 | VJP1 | L2(3) ang diff fault | FLOAT | R | -360...360
155 | I23 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I24 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I25 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I26 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I27 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I28 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I29 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I30 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I31 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I32 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I33 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I34 | VJP1 | Trip dameas / daset | FLOAT | R | -250...250
155 | I35 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I36 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I37 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I38 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I39 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I40 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I41 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I42 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I43 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I44 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I45 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | I46 | VJP1 | Alarm dameas / daset | FLOAT | R | -250...250
155 | S29 | VJP1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S1 | OBJ1 | Object1 mode | UINT32 | RW | 0=Disabled;1=Activated
46 | I1 | OBJ1 | Object1 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I2 | OBJ1 | Object1 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
46 | I3 | OBJ1 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | S2 | OBJ1 | Breaker traverse time | FLOAT | RW | 0.02...500
46 | S3 | OBJ1 | WD Cart traverse time | FLOAT | RW | 0.02...500
46 | S4 | OBJ1 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
46 | S5 | OBJ1 | Sync wait timeout | FLOAT | RW | 0.02...500
46 | S6 | OBJ1 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
46 | S7 | OBJ1 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
46 | S8 | OBJ1 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
46 | S9 | OBJ1 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
46 | S10 | OBJ1 | Control Termination Timeout | FLOAT | RW | 0.02...500
46 | O1 | OBJ1 | Object1 Status Open | SIGNAL_OUT | RW | 0...4294967295
46 | O2 | OBJ1 | Object1 Status Closed | SIGNAL_OUT | RW | 0...4294967295
46 | O3 | OBJ1 | Object1 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
46 | O4 | OBJ1 | Object1 Status Bad | SIGNAL_OUT | RW | 0...4294967295
46 | O5 | OBJ1 | Object1 Open Command | SIGNAL_OUT | RW | 0...4294967295
46 | O6 | OBJ1 | Object1 Close Command | SIGNAL_OUT | RW | 0...4294967295
46 | O7 | OBJ1 | Object1 Open Request | SIGNAL_OUT | RW | 0...4294967295
46 | O8 | OBJ1 | Object1 Close Request | SIGNAL_OUT | RW | 0...4294967295
46 | O9 | OBJ1 | Object1 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
46 | O10 | OBJ1 | Object1 No sync wait | SIGNAL_OUT | RW | 0...4294967295
46 | O11 | OBJ1 | Object1 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
46 | O12 | OBJ1 | Object1 No sync fail | SIGNAL_OUT | RW | 0...4294967295
46 | O13 | OBJ1 | Object1 Open timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O14 | OBJ1 | Object1 Close timeout | SIGNAL_OUT | RW | 0...4294967295
46 | O15 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O16 | OBJ1 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
46 | O17 | OBJ1 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
46 | S11 | OBJ1 | EventMaskLo | UINT32 | RW | 0...4294967295
46 | S12 | OBJ1 | EventMaskHi | UINT32 | RW | 0...4294967295
46 | I4 | OBJ1 | Newest Register | UINT32 | R | 0...12
46 | I5 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I6 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I7 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I8 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I9 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I10 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I11 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I12 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I13 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I14 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I15 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I16 | OBJ1 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
46 | I17 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I18 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I19 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I20 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I21 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I22 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I23 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I24 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I25 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I26 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I27 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I28 | OBJ1 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
46 | I29 | OBJ1 | Open requests | UINT32 | R | 0...4294967295
46 | I30 | OBJ1 | Close requests | UINT32 | R | 0...4294967295
46 | I31 | OBJ1 | Open requests failed | UINT32 | R | 0...4294967295
46 | I32 | OBJ1 | Close requests failed | UINT32 | R | 0...4294967295
46 | S13 | OBJ1 | Clear statistics | UINT32 | W | 0=-;1=Clear
47 | S1 | OBJ2 | Object2 mode | UINT32 | RW | 0=Disabled;1=Activated
47 | I1 | OBJ2 | Object2 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I2 | OBJ2 | Object2 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
47 | I3 | OBJ2 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | S2 | OBJ2 | Breaker traverse time | FLOAT | RW | 0.02...500
47 | S3 | OBJ2 | WD Cart traverse time | FLOAT | RW | 0.02...500
47 | S4 | OBJ2 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
47 | S5 | OBJ2 | Sync wait timeout | FLOAT | RW | 0.02...500
47 | S6 | OBJ2 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
47 | S7 | OBJ2 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
47 | S8 | OBJ2 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
47 | S9 | OBJ2 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
47 | S10 | OBJ2 | Control Termination Timeout | FLOAT | RW | 0.02...500
47 | O1 | OBJ2 | Object2 Status Open | SIGNAL_OUT | RW | 0...4294967295
47 | O2 | OBJ2 | Object2 Status Closed | SIGNAL_OUT | RW | 0...4294967295
47 | O3 | OBJ2 | Object2 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
47 | O4 | OBJ2 | Object2 Status Bad | SIGNAL_OUT | RW | 0...4294967295
47 | O5 | OBJ2 | Object2 Open Command | SIGNAL_OUT | RW | 0...4294967295
47 | O6 | OBJ2 | Object2 Close Command | SIGNAL_OUT | RW | 0...4294967295
47 | O7 | OBJ2 | Object2 Open Request | SIGNAL_OUT | RW | 0...4294967295
47 | O8 | OBJ2 | Object2 Close Request | SIGNAL_OUT | RW | 0...4294967295
47 | O9 | OBJ2 | Object2 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
47 | O10 | OBJ2 | Object2 No sync wait | SIGNAL_OUT | RW | 0...4294967295
47 | O11 | OBJ2 | Object2 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
47 | O12 | OBJ2 | Object2 No sync fail | SIGNAL_OUT | RW | 0...4294967295
47 | O13 | OBJ2 | Object2 Open timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O14 | OBJ2 | Object2 Close timeout | SIGNAL_OUT | RW | 0...4294967295
47 | O15 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O16 | OBJ2 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
47 | O17 | OBJ2 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
47 | S11 | OBJ2 | EventMaskLo | UINT32 | RW | 0...4294967295
47 | S12 | OBJ2 | EventMaskHi | UINT32 | RW | 0...4294967295
47 | I4 | OBJ2 | Newest Register | UINT32 | R | 0...12
47 | I5 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I6 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I7 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I8 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I9 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I10 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I11 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I12 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I13 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I14 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I15 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I16 | OBJ2 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
47 | I17 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I18 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I19 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I20 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I21 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I22 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I23 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I24 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I25 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I26 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I27 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I28 | OBJ2 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
47 | I29 | OBJ2 | Open requests | UINT32 | R | 0...4294967295
47 | I30 | OBJ2 | Close requests | UINT32 | R | 0...4294967295
47 | I31 | OBJ2 | Open requests failed | UINT32 | R | 0...4294967295
47 | I32 | OBJ2 | Close requests failed | UINT32 | R | 0...4294967295
47 | S13 | OBJ2 | Clear statistics | UINT32 | W | 0=-;1=Clear
48 | S1 | OBJ3 | Object3 mode | UINT32 | RW | 0=Disabled;1=Activated
48 | I1 | OBJ3 | Object3 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I2 | OBJ3 | Object3 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
48 | I3 | OBJ3 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | S2 | OBJ3 | Breaker traverse time | FLOAT | RW | 0.02...500
48 | S3 | OBJ3 | WD Cart traverse time | FLOAT | RW | 0.02...500
48 | S4 | OBJ3 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
48 | S5 | OBJ3 | Sync wait timeout | FLOAT | RW | 0.02...500
48 | S6 | OBJ3 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
48 | S7 | OBJ3 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
48 | S8 | OBJ3 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
48 | S9 | OBJ3 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
48 | S10 | OBJ3 | Control Termination Timeout | FLOAT | RW | 0.02...500
48 | O1 | OBJ3 | Object3 Status Open | SIGNAL_OUT | RW | 0...4294967295
48 | O2 | OBJ3 | Object3 Status Closed | SIGNAL_OUT | RW | 0...4294967295
48 | O3 | OBJ3 | Object3 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
48 | O4 | OBJ3 | Object3 Status Bad | SIGNAL_OUT | RW | 0...4294967295
48 | O5 | OBJ3 | Object3 Open Command | SIGNAL_OUT | RW | 0...4294967295
48 | O6 | OBJ3 | Object3 Close Command | SIGNAL_OUT | RW | 0...4294967295
48 | O7 | OBJ3 | Object3 Open Request | SIGNAL_OUT | RW | 0...4294967295
48 | O8 | OBJ3 | Object3 Close Request | SIGNAL_OUT | RW | 0...4294967295
48 | O9 | OBJ3 | Object3 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
48 | O10 | OBJ3 | Object3 No sync wait | SIGNAL_OUT | RW | 0...4294967295
48 | O11 | OBJ3 | Object3 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
48 | O12 | OBJ3 | Object3 No sync fail | SIGNAL_OUT | RW | 0...4294967295
48 | O13 | OBJ3 | Object3 Open timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O14 | OBJ3 | Object3 Close timeout | SIGNAL_OUT | RW | 0...4294967295
48 | O15 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O16 | OBJ3 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
48 | O17 | OBJ3 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
48 | S11 | OBJ3 | EventMaskLo | UINT32 | RW | 0...4294967295
48 | S12 | OBJ3 | EventMaskHi | UINT32 | RW | 0...4294967295
48 | I4 | OBJ3 | Newest Register | UINT32 | R | 0...12
48 | I5 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I6 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I7 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I8 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I9 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I10 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I11 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I12 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I13 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I14 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I15 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I16 | OBJ3 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
48 | I17 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I18 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I19 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I20 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I21 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I22 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I23 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I24 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I25 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I26 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I27 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I28 | OBJ3 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
48 | I29 | OBJ3 | Open requests | UINT32 | R | 0...4294967295
48 | I30 | OBJ3 | Close requests | UINT32 | R | 0...4294967295
48 | I31 | OBJ3 | Open requests failed | UINT32 | R | 0...4294967295
48 | I32 | OBJ3 | Close requests failed | UINT32 | R | 0...4294967295
48 | S13 | OBJ3 | Clear statistics | UINT32 | W | 0=-;1=Clear
49 | S1 | OBJ4 | Object4 mode | UINT32 | RW | 0=Disabled;1=Activated
49 | I1 | OBJ4 | Object4 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I2 | OBJ4 | Object4 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
49 | I3 | OBJ4 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | S2 | OBJ4 | Breaker traverse time | FLOAT | RW | 0.02...500
49 | S3 | OBJ4 | WD Cart traverse time | FLOAT | RW | 0.02...500
49 | S4 | OBJ4 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
49 | S5 | OBJ4 | Sync wait timeout | FLOAT | RW | 0.02...500
49 | S6 | OBJ4 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
49 | S7 | OBJ4 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
49 | S8 | OBJ4 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
49 | S9 | OBJ4 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
49 | S10 | OBJ4 | Control Termination Timeout | FLOAT | RW | 0.02...500
49 | O1 | OBJ4 | Object4 Status Open | SIGNAL_OUT | RW | 0...4294967295
49 | O2 | OBJ4 | Object4 Status Closed | SIGNAL_OUT | RW | 0...4294967295
49 | O3 | OBJ4 | Object4 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
49 | O4 | OBJ4 | Object4 Status Bad | SIGNAL_OUT | RW | 0...4294967295
49 | O5 | OBJ4 | Object4 Open Command | SIGNAL_OUT | RW | 0...4294967295
49 | O6 | OBJ4 | Object4 Close Command | SIGNAL_OUT | RW | 0...4294967295
49 | O7 | OBJ4 | Object4 Open Request | SIGNAL_OUT | RW | 0...4294967295
49 | O8 | OBJ4 | Object4 Close Request | SIGNAL_OUT | RW | 0...4294967295
49 | O9 | OBJ4 | Object4 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
49 | O10 | OBJ4 | Object4 No sync wait | SIGNAL_OUT | RW | 0...4294967295
49 | O11 | OBJ4 | Object4 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
49 | O12 | OBJ4 | Object4 No sync fail | SIGNAL_OUT | RW | 0...4294967295
49 | O13 | OBJ4 | Object4 Open timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O14 | OBJ4 | Object4 Close timeout | SIGNAL_OUT | RW | 0...4294967295
49 | O15 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O16 | OBJ4 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
49 | O17 | OBJ4 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
49 | S11 | OBJ4 | EventMaskLo | UINT32 | RW | 0...4294967295
49 | S12 | OBJ4 | EventMaskHi | UINT32 | RW | 0...4294967295
49 | I4 | OBJ4 | Newest Register | UINT32 | R | 0...12
49 | I5 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I6 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I7 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I8 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I9 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I10 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I11 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I12 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I13 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I14 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I15 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I16 | OBJ4 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
49 | I17 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I18 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I19 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I20 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I21 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I22 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I23 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I24 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I25 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I26 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I27 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I28 | OBJ4 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
49 | I29 | OBJ4 | Open requests | UINT32 | R | 0...4294967295
49 | I30 | OBJ4 | Close requests | UINT32 | R | 0...4294967295
49 | I31 | OBJ4 | Open requests failed | UINT32 | R | 0...4294967295
49 | I32 | OBJ4 | Close requests failed | UINT32 | R | 0...4294967295
49 | S13 | OBJ4 | Clear statistics | UINT32 | W | 0=-;1=Clear
50 | S1 | OBJ5 | Object5 mode | UINT32 | RW | 0=Disabled;1=Activated
50 | I1 | OBJ5 | Object5 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I2 | OBJ5 | Object5 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
50 | I3 | OBJ5 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | S2 | OBJ5 | Breaker traverse time | FLOAT | RW | 0.02...500
50 | S3 | OBJ5 | WD Cart traverse time | FLOAT | RW | 0.02...500
50 | S4 | OBJ5 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
50 | S5 | OBJ5 | Sync wait timeout | FLOAT | RW | 0.02...500
50 | S6 | OBJ5 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
50 | S7 | OBJ5 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
50 | S8 | OBJ5 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
50 | S9 | OBJ5 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
50 | S10 | OBJ5 | Control Termination Timeout | FLOAT | RW | 0.02...500
50 | O1 | OBJ5 | Object5 Status Open | SIGNAL_OUT | RW | 0...4294967295
50 | O2 | OBJ5 | Object5 Status Closed | SIGNAL_OUT | RW | 0...4294967295
50 | O3 | OBJ5 | Object5 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
50 | O4 | OBJ5 | Object5 Status Bad | SIGNAL_OUT | RW | 0...4294967295
50 | O5 | OBJ5 | Object5 Open Command | SIGNAL_OUT | RW | 0...4294967295
50 | O6 | OBJ5 | Object5 Close Command | SIGNAL_OUT | RW | 0...4294967295
50 | O7 | OBJ5 | Object5 Open Request | SIGNAL_OUT | RW | 0...4294967295
50 | O8 | OBJ5 | Object5 Close Request | SIGNAL_OUT | RW | 0...4294967295
50 | O9 | OBJ5 | Object5 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
50 | O10 | OBJ5 | Object5 No sync wait | SIGNAL_OUT | RW | 0...4294967295
50 | O11 | OBJ5 | Object5 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
50 | O12 | OBJ5 | Object5 No sync fail | SIGNAL_OUT | RW | 0...4294967295
50 | O13 | OBJ5 | Object5 Open timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O14 | OBJ5 | Object5 Close timeout | SIGNAL_OUT | RW | 0...4294967295
50 | O15 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O16 | OBJ5 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
50 | O17 | OBJ5 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
50 | S11 | OBJ5 | EventMaskLo | UINT32 | RW | 0...4294967295
50 | S12 | OBJ5 | EventMaskHi | UINT32 | RW | 0...4294967295
50 | I4 | OBJ5 | Newest Register | UINT32 | R | 0...12
50 | I5 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I6 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I7 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I8 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I9 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I10 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I11 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I12 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I13 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I14 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I15 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I16 | OBJ5 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
50 | I17 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I18 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I19 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I20 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I21 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I22 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I23 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I24 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I25 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I26 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I27 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I28 | OBJ5 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
50 | I29 | OBJ5 | Open requests | UINT32 | R | 0...4294967295
50 | I30 | OBJ5 | Close requests | UINT32 | R | 0...4294967295
50 | I31 | OBJ5 | Open requests failed | UINT32 | R | 0...4294967295
50 | I32 | OBJ5 | Close requests failed | UINT32 | R | 0...4294967295
50 | S13 | OBJ5 | Clear statistics | UINT32 | W | 0=-;1=Clear
150 | S1 | OBJ6 | Object6 mode | UINT32 | RW | 0=Disabled;1=Activated
150 | I1 | OBJ6 | Object6 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I2 | OBJ6 | Object6 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
150 | I3 | OBJ6 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | S2 | OBJ6 | Breaker traverse time | FLOAT | RW | 0.02...500
150 | S3 | OBJ6 | WD Cart traverse time | FLOAT | RW | 0.02...500
150 | S4 | OBJ6 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
150 | S5 | OBJ6 | Sync wait timeout | FLOAT | RW | 0.02...500
150 | S6 | OBJ6 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
150 | S7 | OBJ6 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
150 | S8 | OBJ6 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
150 | S9 | OBJ6 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
150 | S10 | OBJ6 | Control Termination Timeout | FLOAT | RW | 0.02...500
150 | O1 | OBJ6 | Object6 Status Open | SIGNAL_OUT | RW | 0...4294967295
150 | O2 | OBJ6 | Object6 Status Closed | SIGNAL_OUT | RW | 0...4294967295
150 | O3 | OBJ6 | Object6 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
150 | O4 | OBJ6 | Object6 Status Bad | SIGNAL_OUT | RW | 0...4294967295
150 | O5 | OBJ6 | Object6 Open Command | SIGNAL_OUT | RW | 0...4294967295
150 | O6 | OBJ6 | Object6 Close Command | SIGNAL_OUT | RW | 0...4294967295
150 | O7 | OBJ6 | Object6 Open Request | SIGNAL_OUT | RW | 0...4294967295
150 | O8 | OBJ6 | Object6 Close Request | SIGNAL_OUT | RW | 0...4294967295
150 | O9 | OBJ6 | Object6 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
150 | O10 | OBJ6 | Object6 No sync wait | SIGNAL_OUT | RW | 0...4294967295
150 | O11 | OBJ6 | Object6 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
150 | O12 | OBJ6 | Object6 No sync fail | SIGNAL_OUT | RW | 0...4294967295
150 | O13 | OBJ6 | Object6 Open timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O14 | OBJ6 | Object6 Close timeout | SIGNAL_OUT | RW | 0...4294967295
150 | O15 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O16 | OBJ6 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
150 | O17 | OBJ6 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
150 | S11 | OBJ6 | EventMaskLo | UINT32 | RW | 0...4294967295
150 | S12 | OBJ6 | EventMaskHi | UINT32 | RW | 0...4294967295
150 | I4 | OBJ6 | Newest Register | UINT32 | R | 0...12
150 | I5 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I6 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I7 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I8 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I9 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I10 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I11 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I12 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I13 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I14 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I15 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I16 | OBJ6 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
150 | I17 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I18 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I19 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I20 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I21 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I22 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I23 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I24 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I25 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I26 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I27 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I28 | OBJ6 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
150 | I29 | OBJ6 | Open requests | UINT32 | R | 0...4294967295
150 | I30 | OBJ6 | Close requests | UINT32 | R | 0...4294967295
150 | I31 | OBJ6 | Open requests failed | UINT32 | R | 0...4294967295
150 | I32 | OBJ6 | Close requests failed | UINT32 | R | 0...4294967295
150 | S13 | OBJ6 | Clear statistics | UINT32 | W | 0=-;1=Clear
151 | S1 | OBJ7 | Object7 mode | UINT32 | RW | 0=Disabled;1=Activated
151 | I1 | OBJ7 | Object7 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I2 | OBJ7 | Object7 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
151 | I3 | OBJ7 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | S2 | OBJ7 | Breaker traverse time | FLOAT | RW | 0.02...500
151 | S3 | OBJ7 | WD Cart traverse time | FLOAT | RW | 0.02...500
151 | S4 | OBJ7 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
151 | S5 | OBJ7 | Sync wait timeout | FLOAT | RW | 0.02...500
151 | S6 | OBJ7 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
151 | S7 | OBJ7 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
151 | S8 | OBJ7 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
151 | S9 | OBJ7 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
151 | S10 | OBJ7 | Control Termination Timeout | FLOAT | RW | 0.02...500
151 | O1 | OBJ7 | Object7 Status Open | SIGNAL_OUT | RW | 0...4294967295
151 | O2 | OBJ7 | Object7 Status Closed | SIGNAL_OUT | RW | 0...4294967295
151 | O3 | OBJ7 | Object7 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
151 | O4 | OBJ7 | Object7 Status Bad | SIGNAL_OUT | RW | 0...4294967295
151 | O5 | OBJ7 | Object7 Open Command | SIGNAL_OUT | RW | 0...4294967295
151 | O6 | OBJ7 | Object7 Close Command | SIGNAL_OUT | RW | 0...4294967295
151 | O7 | OBJ7 | Object7 Open Request | SIGNAL_OUT | RW | 0...4294967295
151 | O8 | OBJ7 | Object7 Close Request | SIGNAL_OUT | RW | 0...4294967295
151 | O9 | OBJ7 | Object7 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
151 | O10 | OBJ7 | Object7 No sync wait | SIGNAL_OUT | RW | 0...4294967295
151 | O11 | OBJ7 | Object7 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
151 | O12 | OBJ7 | Object7 No sync fail | SIGNAL_OUT | RW | 0...4294967295
151 | O13 | OBJ7 | Object7 Open timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O14 | OBJ7 | Object7 Close timeout | SIGNAL_OUT | RW | 0...4294967295
151 | O15 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O16 | OBJ7 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
151 | O17 | OBJ7 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
151 | S11 | OBJ7 | EventMaskLo | UINT32 | RW | 0...4294967295
151 | S12 | OBJ7 | EventMaskHi | UINT32 | RW | 0...4294967295
151 | I4 | OBJ7 | Newest Register | UINT32 | R | 0...12
151 | I5 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I6 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I7 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I8 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I9 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I10 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I11 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I12 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I13 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I14 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I15 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I16 | OBJ7 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
151 | I17 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I18 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I19 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I20 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I21 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I22 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I23 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I24 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I25 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I26 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I27 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I28 | OBJ7 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
151 | I29 | OBJ7 | Open requests | UINT32 | R | 0...4294967295
151 | I30 | OBJ7 | Close requests | UINT32 | R | 0...4294967295
151 | I31 | OBJ7 | Open requests failed | UINT32 | R | 0...4294967295
151 | I32 | OBJ7 | Close requests failed | UINT32 | R | 0...4294967295
151 | S13 | OBJ7 | Clear statistics | UINT32 | W | 0=-;1=Clear
152 | S1 | OBJ8 | Object8 mode | UINT32 | RW | 0=Disabled;1=Activated
152 | I1 | OBJ8 | Object8 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I2 | OBJ8 | Object8 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
152 | I3 | OBJ8 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | S2 | OBJ8 | Breaker traverse time | FLOAT | RW | 0.02...500
152 | S3 | OBJ8 | WD Cart traverse time | FLOAT | RW | 0.02...500
152 | S4 | OBJ8 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
152 | S5 | OBJ8 | Sync wait timeout | FLOAT | RW | 0.02...500
152 | S6 | OBJ8 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
152 | S7 | OBJ8 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
152 | S8 | OBJ8 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
152 | S9 | OBJ8 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
152 | S10 | OBJ8 | Control Termination Timeout | FLOAT | RW | 0.02...500
152 | O1 | OBJ8 | Object8 Status Open | SIGNAL_OUT | RW | 0...4294967295
152 | O2 | OBJ8 | Object8 Status Closed | SIGNAL_OUT | RW | 0...4294967295
152 | O3 | OBJ8 | Object8 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
152 | O4 | OBJ8 | Object8 Status Bad | SIGNAL_OUT | RW | 0...4294967295
152 | O5 | OBJ8 | Object8 Open Command | SIGNAL_OUT | RW | 0...4294967295
152 | O6 | OBJ8 | Object8 Close Command | SIGNAL_OUT | RW | 0...4294967295
152 | O7 | OBJ8 | Object8 Open Request | SIGNAL_OUT | RW | 0...4294967295
152 | O8 | OBJ8 | Object8 Close Request | SIGNAL_OUT | RW | 0...4294967295
152 | O9 | OBJ8 | Object8 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
152 | O10 | OBJ8 | Object8 No sync wait | SIGNAL_OUT | RW | 0...4294967295
152 | O11 | OBJ8 | Object8 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
152 | O12 | OBJ8 | Object8 No sync fail | SIGNAL_OUT | RW | 0...4294967295
152 | O13 | OBJ8 | Object8 Open timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O14 | OBJ8 | Object8 Close timeout | SIGNAL_OUT | RW | 0...4294967295
152 | O15 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O16 | OBJ8 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
152 | O17 | OBJ8 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
152 | S11 | OBJ8 | EventMaskLo | UINT32 | RW | 0...4294967295
152 | S12 | OBJ8 | EventMaskHi | UINT32 | RW | 0...4294967295
152 | I4 | OBJ8 | Newest Register | UINT32 | R | 0...12
152 | I5 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I6 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I7 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I8 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I9 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I10 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I11 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I12 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I13 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I14 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I15 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I16 | OBJ8 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
152 | I17 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I18 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I19 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I20 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I21 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I22 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I23 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I24 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I25 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I26 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I27 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I28 | OBJ8 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
152 | I29 | OBJ8 | Open requests | UINT32 | R | 0...4294967295
152 | I30 | OBJ8 | Close requests | UINT32 | R | 0...4294967295
152 | I31 | OBJ8 | Open requests failed | UINT32 | R | 0...4294967295
152 | I32 | OBJ8 | Close requests failed | UINT32 | R | 0...4294967295
152 | S13 | OBJ8 | Clear statistics | UINT32 | W | 0=-;1=Clear
153 | S1 | OBJ9 | Object9 mode | UINT32 | RW | 0=Disabled;1=Activated
153 | I1 | OBJ9 | Object9 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I2 | OBJ9 | Object9 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
153 | I3 | OBJ9 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | S2 | OBJ9 | Breaker traverse time | FLOAT | RW | 0.02...500
153 | S3 | OBJ9 | WD Cart traverse time | FLOAT | RW | 0.02...500
153 | S4 | OBJ9 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
153 | S5 | OBJ9 | Sync wait timeout | FLOAT | RW | 0.02...500
153 | S6 | OBJ9 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
153 | S7 | OBJ9 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
153 | S8 | OBJ9 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
153 | S9 | OBJ9 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
153 | S10 | OBJ9 | Control Termination Timeout | FLOAT | RW | 0.02...500
153 | O1 | OBJ9 | Object9 Status Open | SIGNAL_OUT | RW | 0...4294967295
153 | O2 | OBJ9 | Object9 Status Closed | SIGNAL_OUT | RW | 0...4294967295
153 | O3 | OBJ9 | Object9 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
153 | O4 | OBJ9 | Object9 Status Bad | SIGNAL_OUT | RW | 0...4294967295
153 | O5 | OBJ9 | Object9 Open Command | SIGNAL_OUT | RW | 0...4294967295
153 | O6 | OBJ9 | Object9 Close Command | SIGNAL_OUT | RW | 0...4294967295
153 | O7 | OBJ9 | Object9 Open Request | SIGNAL_OUT | RW | 0...4294967295
153 | O8 | OBJ9 | Object9 Close Request | SIGNAL_OUT | RW | 0...4294967295
153 | O9 | OBJ9 | Object9 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
153 | O10 | OBJ9 | Object9 No sync wait | SIGNAL_OUT | RW | 0...4294967295
153 | O11 | OBJ9 | Object9 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
153 | O12 | OBJ9 | Object9 No sync fail | SIGNAL_OUT | RW | 0...4294967295
153 | O13 | OBJ9 | Object9 Open timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O14 | OBJ9 | Object9 Close timeout | SIGNAL_OUT | RW | 0...4294967295
153 | O15 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O16 | OBJ9 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
153 | O17 | OBJ9 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
153 | S11 | OBJ9 | EventMaskLo | UINT32 | RW | 0...4294967295
153 | S12 | OBJ9 | EventMaskHi | UINT32 | RW | 0...4294967295
153 | I4 | OBJ9 | Newest Register | UINT32 | R | 0...12
153 | I5 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I6 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I7 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I8 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I9 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I10 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I11 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I12 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I13 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I14 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I15 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I16 | OBJ9 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
153 | I17 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I18 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I19 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I20 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I21 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I22 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I23 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I24 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I25 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I26 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I27 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I28 | OBJ9 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
153 | I29 | OBJ9 | Open requests | UINT32 | R | 0...4294967295
153 | I30 | OBJ9 | Close requests | UINT32 | R | 0...4294967295
153 | I31 | OBJ9 | Open requests failed | UINT32 | R | 0...4294967295
153 | I32 | OBJ9 | Close requests failed | UINT32 | R | 0...4294967295
153 | S13 | OBJ9 | Clear statistics | UINT32 | W | 0=-;1=Clear
154 | S1 | OBJ10 | Object10 mode | UINT32 | RW | 0=Disabled;1=Activated
154 | I1 | OBJ10 | Object10 Breaker Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I2 | OBJ10 | Object10 Withdraw Status | UINT32 | R | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
154 | I3 | OBJ10 | Additional Status Information | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | S2 | OBJ10 | Breaker traverse time | FLOAT | RW | 0.02...500
154 | S3 | OBJ10 | WD Cart traverse time | FLOAT | RW | 0.02...500
154 | S4 | OBJ10 | Use Synchrocheck | UINT32 | RW | 0=Not in use;1=Synchrocheck in use
154 | S5 | OBJ10 | Sync wait timeout | FLOAT | RW | 0.02...500
154 | S6 | OBJ10 | Obj Ready wait timeout | FLOAT | RW | 0.02...500
154 | S7 | OBJ10 | Use Object Ready | UINT32 | RW | 0=ReadyHigh;1=ReadyLow;2 =Not in use
154 | S8 | OBJ10 | Max Close Command Pulse Length | FLOAT | RW | 0.02...500
154 | S9 | OBJ10 | Max Open Command Pulse Length | FLOAT | RW | 0.02...500
154 | S10 | OBJ10 | Control Termination Timeout | FLOAT | RW | 0.02...500
154 | O1 | OBJ10 | Object10 Status Open | SIGNAL_OUT | RW | 0...4294967295
154 | O2 | OBJ10 | Object10 Status Closed | SIGNAL_OUT | RW | 0...4294967295
154 | O3 | OBJ10 | Object10 Status Interm. | SIGNAL_OUT | RW | 0...4294967295
154 | O4 | OBJ10 | Object10 Status Bad | SIGNAL_OUT | RW | 0...4294967295
154 | O5 | OBJ10 | Object10 Open Command | SIGNAL_OUT | RW | 0...4294967295
154 | O6 | OBJ10 | Object10 Close Command | SIGNAL_OUT | RW | 0...4294967295
154 | O7 | OBJ10 | Object10 Open Request | SIGNAL_OUT | RW | 0...4294967295
154 | O8 | OBJ10 | Object10 Close Request | SIGNAL_OUT | RW | 0...4294967295
154 | O9 | OBJ10 | Object10 Not ready wait | SIGNAL_OUT | RW | 0...4294967295
154 | O10 | OBJ10 | Object10 No sync wait | SIGNAL_OUT | RW | 0...4294967295
154 | O11 | OBJ10 | Object10 Not ready fail | SIGNAL_OUT | RW | 0...4294967295
154 | O12 | OBJ10 | Object10 No sync fail | SIGNAL_OUT | RW | 0...4294967295
154 | O13 | OBJ10 | Object10 Open timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O14 | OBJ10 | Object10 Close timeout | SIGNAL_OUT | RW | 0...4294967295
154 | O15 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O16 | OBJ10 | Open Requested by user | SIGNAL_OUT | RW | 0...4294967295
154 | O17 | OBJ10 | Synchroswitch request | SIGNAL_OUT | RW | 0...4294967295
154 | S11 | OBJ10 | EventMaskLo | UINT32 | RW | 0...4294967295
154 | S12 | OBJ10 | EventMaskHi | UINT32 | RW | 0...4294967295
154 | I4 | OBJ10 | Newest Register | UINT32 | R | 0...12
154 | I5 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I6 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I7 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I8 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I9 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I10 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I11 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I12 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I13 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I14 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I15 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I16 | OBJ10 | Object status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
154 | I17 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I18 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I19 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I20 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I21 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I22 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I23 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I24 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I25 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I26 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I27 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I28 | OBJ10 | General status | UINT32 | R | 0b=Open Blocked;1b=Open Allowed;2b=Close Blocked;3b=Close Allowed;4b=Object Ready;5b=Object Not Ready;6b=Sync Ok;7b=Sync Not Ok
154 | I29 | OBJ10 | Open requests | UINT32 | R | 0...4294967295
154 | I30 | OBJ10 | Close requests | UINT32 | R | 0...4294967295
154 | I31 | OBJ10 | Open requests failed | UINT32 | R | 0...4294967295
154 | I32 | OBJ10 | Close requests failed | UINT32 | R | 0...4294967295
154 | S13 | OBJ10 | Clear statistics | UINT32 | W | 0=-;1=Clear
104 | S1 | CIN1 | Indicator 1 mode | UINT32 | RW | 0=Disabled;1=Activated
104 | S2 | CIN1 | Ind.1 traverse time | FLOAT | RW | 0.02...500
104 | I1 | CIN1 | Ind.1 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
105 | S1 | CIN2 | Indicator 2 mode | UINT32 | RW | 0=Disabled;1=Activated
105 | S2 | CIN2 | Ind.2 traverse time | FLOAT | RW | 0.02...500
105 | I1 | CIN2 | Ind.2 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
106 | S1 | CIN3 | Indicator 3 mode | UINT32 | RW | 0=Disabled;1=Activated
106 | S2 | CIN3 | Ind.3 traverse time | FLOAT | RW | 0.02...500
106 | I1 | CIN3 | Ind.3 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
107 | S1 | CIN4 | Indicator 4 mode | UINT32 | RW | 0=Disabled;1=Activated
107 | S2 | CIN4 | Ind.4 traverse time | FLOAT | RW | 0.02...500
107 | I1 | CIN4 | Ind.4 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
108 | S1 | CIN5 | Indicator 5 mode | UINT32 | RW | 0=Disabled;1=Activated
108 | S2 | CIN5 | Ind.5 traverse time | FLOAT | RW | 0.02...500
108 | I1 | CIN5 | Ind.5 Object Status | UINT32 | R | 0=Intermediate;1=Open;2=Closed;3=Bad
63 | S1 | AR1 | Auto-recloser [79] Mode | UINT32 | RW | 0=Disabled;1=Activated
63 | V1 | AR1 | AR Status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear
63 | V2 | AR1 | Timer active | UINT32 | R | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
63 | I1 | AR1 | AR Timer value | FLOAT | R | 0...1800
63 | I2 | AR1 | AR Started | UINT32 | R | 0...4294967295
63 | I3 | AR1 | Shot 1 Started | UINT32 | R | 0...4294967295
63 | I4 | AR1 | Shot 2 Started | UINT32 | R | 0...4294967295
63 | I5 | AR1 | Shot 3 Started | UINT32 | R | 0...4294967295
63 | I6 | AR1 | Shot 4 Started | UINT32 | R | 0...4294967295
63 | I7 | AR1 | Shot 5 Started | UINT32 | R | 0...4294967295
63 | I8 | AR1 | Shot 1 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I9 | AR1 | Shot 2 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I10 | AR1 | Shot 3 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I11 | AR1 | Shot 4 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I12 | AR1 | Shot 5 Started by REQ1 | UINT32 | R | 0...4294967295
63 | I13 | AR1 | Shot 1 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I14 | AR1 | Shot 2 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I15 | AR1 | Shot 3 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I16 | AR1 | Shot 4 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I17 | AR1 | Shot 5 Started by REQ2 | UINT32 | R | 0...4294967295
63 | I18 | AR1 | Shot 1 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I19 | AR1 | Shot 2 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I20 | AR1 | Shot 3 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I21 | AR1 | Shot 4 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I22 | AR1 | Shot 5 Started by REQ3 | UINT32 | R | 0...4294967295
63 | I23 | AR1 | Shot 1 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I24 | AR1 | Shot 2 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I25 | AR1 | Shot 3 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I26 | AR1 | Shot 4 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I27 | AR1 | Shot 5 Started by REQ4 | UINT32 | R | 0...4294967295
63 | I28 | AR1 | Shot 1 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I29 | AR1 | Shot 2 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I30 | AR1 | Shot 3 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I31 | AR1 | Shot 4 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I32 | AR1 | Shot 5 Started by REQ5 | UINT32 | R | 0...4294967295
63 | I33 | AR1 | Shots failed | UINT32 | R | 0...4294967295
63 | I34 | AR1 | Shots cleared | UINT32 | R | 0...4294967295
63 | I35 | AR1 | Final trips | UINT32 | R | 0...4294967295
63 | S2 | AR1 | Clear statistics | UINT32 | W | 0=-;1=Clear
63 | S3 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S4 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S5 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S6 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S7 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S8 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S9 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S10 | AR1 | Object for AR | UINT32 | RW | 0=Object 1;1=Object 2;2=Object 3;3=Object 4;4=Object 5
63 | S11 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S12 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S13 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S14 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S15 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S16 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S17 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S18 | AR1 | AR Enabled in SG | UINT32 | RW | 0=Disabled;1=Enabled
63 | S19 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S20 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S21 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S22 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S23 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S24 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S25 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S26 | AR1 | Require manual resetting | UINT32 | RW | 0=Required;1=OBJ Close CMD resets
63 | S27 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S28 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S29 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S30 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S31 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S32 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S33 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S34 | AR1 | Successfull reclose start gen recl | UINT32 | RW | 0=Only shot reclaim;1=Shot reclaim and Gen reclaim
63 | S35 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S36 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S37 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S38 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S39 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S40 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S41 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S42 | AR1 | Lockout after successfull AR | FLOAT | RW | 0...1800
63 | S43 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S44 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S45 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S46 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S47 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S48 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S49 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S50 | AR1 | Obj clo reclaim time | FLOAT | RW | 0...1800
63 | S51 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S52 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S53 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S54 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S55 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S56 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S57 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S58 | AR1 | AR1 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S59 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S60 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S61 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S62 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S63 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S64 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S65 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S66 | AR1 | AR1 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S67 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S68 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S69 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S70 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S71 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S72 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S73 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S74 | AR1 | AR1 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S75 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S76 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S77 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S78 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S79 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S80 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S81 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S82 | AR1 | AR1 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S83 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S84 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S85 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S86 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S87 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S88 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S89 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S90 | AR1 | AR1 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S91 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S92 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S93 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S94 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S95 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S96 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S97 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S98 | AR1 | AR2 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S99 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S100 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S101 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S102 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S103 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S104 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S105 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S106 | AR1 | AR2 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S107 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S108 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S109 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S110 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S111 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S112 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S113 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S114 | AR1 | AR2 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S115 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S116 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S117 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S118 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S119 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S120 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S121 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S122 | AR1 | AR2 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S123 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S124 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S125 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S126 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S127 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S128 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S129 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S130 | AR1 | AR2 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S131 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S132 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S133 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S134 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S135 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S136 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S137 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S138 | AR1 | AR3 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S139 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S140 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S141 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S142 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S143 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S144 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S145 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S146 | AR1 | AR3 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S147 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S148 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S149 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S150 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S151 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S152 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S153 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S154 | AR1 | AR3 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S155 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S156 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S157 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S158 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S159 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S160 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S161 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S162 | AR1 | AR3 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S163 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S164 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S165 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S166 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S167 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S168 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S169 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S170 | AR1 | AR3 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S171 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S172 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S173 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S174 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S175 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S176 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S177 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S178 | AR1 | AR4 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S179 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S180 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S181 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S182 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S183 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S184 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S185 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S186 | AR1 | AR4 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S187 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S188 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S189 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S190 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S191 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S192 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S193 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S194 | AR1 | AR4 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S195 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S196 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S197 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S198 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S199 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S200 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S201 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S202 | AR1 | AR4 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S203 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S204 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S205 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S206 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S207 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S208 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S209 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S210 | AR1 | AR4 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S211 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S212 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S213 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S214 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S215 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S216 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S217 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S218 | AR1 | AR5 Shot 1 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S219 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S220 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S221 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S222 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S223 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S224 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S225 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S226 | AR1 | AR5 Shot 2 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S227 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S228 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S229 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S230 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S231 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S232 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S233 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S234 | AR1 | AR5 Shot 3 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S235 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S236 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S237 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S238 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S239 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S240 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S241 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S242 | AR1 | AR5 Shot 4 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S243 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S244 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S245 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S246 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S247 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S248 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S249 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S250 | AR1 | AR5 Shot 5 | UINT32 | RW | 0=Disabled;1=Enabled
63 | S251 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S252 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S253 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S254 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S255 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S256 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S257 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S258 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S259 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S260 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S261 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S262 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S263 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S264 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S265 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S266 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S267 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S268 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S269 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S270 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S271 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S272 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S273 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S274 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S275 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S276 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S277 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S278 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S279 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S280 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S281 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S282 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S283 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S284 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S285 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S286 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S287 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S288 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S289 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S290 | AR1 | AR1 Shot Starting delay | FLOAT | RW | 0...1800
63 | S291 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S292 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S293 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S294 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S295 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S296 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S297 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S298 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S299 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S300 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S301 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S302 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S303 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S304 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S305 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S306 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S307 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S308 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S309 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S310 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S311 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S312 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S313 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S314 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S315 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S316 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S317 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S318 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S319 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S320 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S321 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S322 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S323 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S324 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S325 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S326 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S327 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S328 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S329 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S330 | AR1 | AR2 Shot Starting delay | FLOAT | RW | 0...1800
63 | S331 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S332 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S333 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S334 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S335 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S336 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S337 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S338 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S339 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S340 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S341 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S342 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S343 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S344 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S345 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S346 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S347 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S348 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S349 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S350 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S351 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S352 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S353 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S354 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S355 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S356 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S357 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S358 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S359 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S360 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S361 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S362 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S363 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S364 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S365 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S366 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S367 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S368 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S369 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S370 | AR1 | AR3 Shot Starting delay | FLOAT | RW | 0...1800
63 | S371 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S372 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S373 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S374 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S375 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S376 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S377 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S378 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S379 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S380 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S381 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S382 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S383 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S384 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S385 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S386 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S387 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S388 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S389 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S390 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S391 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S392 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S393 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S394 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S395 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S396 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S397 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S398 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S399 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S400 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S401 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S402 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S403 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S404 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S405 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S406 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S407 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S408 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S409 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S410 | AR1 | AR4 Shot Starting delay | FLOAT | RW | 0...1800
63 | S411 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S412 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S413 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S414 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S415 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S416 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S417 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S418 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S419 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S420 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S421 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S422 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S423 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S424 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S425 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S426 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S427 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S428 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S429 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S430 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S431 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S432 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S433 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S434 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S435 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S436 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S437 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S438 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S439 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S440 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S441 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S442 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S443 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S444 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S445 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S446 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S447 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S448 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S449 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S450 | AR1 | AR5 Shot Starting delay | FLOAT | RW | 0...1800
63 | S451 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S452 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S453 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S454 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S455 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S456 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S457 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S458 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S459 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S460 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S461 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S462 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S463 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S464 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S465 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S466 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S467 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S468 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S469 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S470 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S471 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S472 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S473 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S474 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S475 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S476 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S477 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S478 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S479 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S480 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S481 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S482 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S483 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S484 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S485 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S486 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S487 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S488 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S489 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S490 | AR1 | AR1 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S491 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S492 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S493 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S494 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S495 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S496 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S497 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S498 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S499 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S500 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S501 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S502 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S503 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S504 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S505 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S506 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S507 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S508 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S509 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S510 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S511 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S512 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S513 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S514 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S515 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S516 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S517 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S518 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S519 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S520 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S521 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S522 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S523 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S524 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S525 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S526 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S527 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S528 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S529 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S530 | AR1 | AR2 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S531 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S532 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S533 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S534 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S535 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S536 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S537 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S538 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S539 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S540 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S541 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S542 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S543 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S544 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S545 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S546 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S547 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S548 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S549 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S550 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S551 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S552 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S553 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S554 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S555 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S556 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S557 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S558 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S559 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S560 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S561 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S562 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S563 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S564 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S565 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S566 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S567 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S568 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S569 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S570 | AR1 | AR3 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S571 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S572 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S573 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S574 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S575 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S576 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S577 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S578 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S579 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S580 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S581 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S582 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S583 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S584 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S585 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S586 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S587 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S588 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S589 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S590 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S591 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S592 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S593 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S594 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S595 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S596 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S597 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S598 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S599 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S600 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S601 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S602 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S603 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S604 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S605 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S606 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S607 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S608 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S609 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S610 | AR1 | AR4 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S611 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S612 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S613 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S614 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S615 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S616 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S617 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S618 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S619 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S620 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S621 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S622 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S623 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S624 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S625 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S626 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S627 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S628 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S629 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S630 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S631 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S632 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S633 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S634 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S635 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S636 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S637 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S638 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S639 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S640 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S641 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S642 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S643 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S644 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S645 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S646 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S647 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S648 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S649 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S650 | AR1 | AR5 Shot DeadTime delay | FLOAT | RW | 0...1800
63 | S651 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S652 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S653 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S654 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S655 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S656 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S657 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S658 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S659 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S660 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S661 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S662 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S663 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S664 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S665 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S666 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S667 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S668 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S669 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S670 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S671 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S672 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S673 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S674 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S675 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S676 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S677 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S678 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S679 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S680 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S681 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S682 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S683 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S684 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S685 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S686 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S687 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S688 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S689 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S690 | AR1 | AR1 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S691 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S692 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S693 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S694 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S695 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S696 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S697 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S698 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S699 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S700 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S701 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S702 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S703 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S704 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S705 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S706 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S707 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S708 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S709 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S710 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S711 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S712 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S713 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S714 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S715 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S716 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S717 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S718 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S719 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S720 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S721 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S722 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S723 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S724 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S725 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S726 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S727 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S728 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S729 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S730 | AR1 | AR2 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S731 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S732 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S733 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S734 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S735 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S736 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S737 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S738 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S739 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S740 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S741 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S742 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S743 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S744 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S745 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S746 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S747 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S748 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S749 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S750 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S751 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S752 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S753 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S754 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S755 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S756 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S757 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S758 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S759 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S760 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S761 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S762 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S763 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S764 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S765 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S766 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S767 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S768 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S769 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S770 | AR1 | AR3 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S771 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S772 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S773 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S774 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S775 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S776 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S777 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S778 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S779 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S780 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S781 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S782 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S783 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S784 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S785 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S786 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S787 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S788 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S789 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S790 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S791 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S792 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S793 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S794 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S795 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S796 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S797 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S798 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S799 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S800 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S801 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S802 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S803 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S804 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S805 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S806 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S807 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S808 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S809 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S810 | AR1 | AR4 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S811 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S812 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S813 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S814 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S815 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S816 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S817 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S818 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S819 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S820 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S821 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S822 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S823 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S824 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S825 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S826 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S827 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S828 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S829 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S830 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S831 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S832 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S833 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S834 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S835 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S836 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S837 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S838 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S839 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S840 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S841 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S842 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S843 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S844 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S845 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S846 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S847 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S848 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S849 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S850 | AR1 | AR5 Shot Arc or Discr. | UINT32 | RW | 0=Arcing;1=Discrimination
63 | S851 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S852 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S853 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S854 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S855 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S856 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S857 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S858 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S859 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S860 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S861 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S862 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S863 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S864 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S865 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S866 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S867 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S868 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S869 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S870 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S871 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S872 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S873 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S874 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S875 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S876 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S877 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S878 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S879 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S880 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S881 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S882 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S883 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S884 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S885 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S886 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S887 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S888 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S889 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S890 | AR1 | AR1 Shot Action time | FLOAT | RW | 0...1800
63 | S891 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S892 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S893 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S894 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S895 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S896 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S897 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S898 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S899 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S900 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S901 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S902 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S903 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S904 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S905 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S906 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S907 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S908 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S909 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S910 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S911 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S912 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S913 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S914 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S915 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S916 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S917 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S918 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S919 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S920 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S921 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S922 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S923 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S924 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S925 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S926 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S927 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S928 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S929 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S930 | AR1 | AR2 Shot Action time | FLOAT | RW | 0...1800
63 | S931 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S932 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S933 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S934 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S935 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S936 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S937 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S938 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S939 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S940 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S941 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S942 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S943 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S944 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S945 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S946 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S947 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S948 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S949 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S950 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S951 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S952 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S953 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S954 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S955 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S956 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S957 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S958 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S959 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S960 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S961 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S962 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S963 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S964 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S965 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S966 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S967 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S968 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S969 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S970 | AR1 | AR3 Shot Action time | FLOAT | RW | 0...1800
63 | S971 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S972 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S973 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S974 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S975 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S976 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S977 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S978 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S979 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S980 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S981 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S982 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S983 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S984 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S985 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S986 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S987 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S988 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S989 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S990 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S991 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S992 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S993 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S994 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S995 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S996 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S997 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S998 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S999 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1000 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1001 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1002 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1003 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1004 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1005 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1006 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1007 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1008 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1009 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1010 | AR1 | AR4 Shot Action time | FLOAT | RW | 0...1800
63 | S1011 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1012 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1013 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1014 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1015 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1016 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1017 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1018 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1019 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1020 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1021 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1022 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1023 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1024 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1025 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1026 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1027 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1028 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1029 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1030 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1031 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1032 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1033 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1034 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1035 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1036 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1037 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1038 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1039 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1040 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1041 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1042 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1043 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1044 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1045 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1046 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1047 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1048 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1049 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1050 | AR1 | AR5 Shot Action time | FLOAT | RW | 0...1800
63 | S1051 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1052 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1053 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1054 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1055 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1056 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1057 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1058 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1059 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1060 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1061 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1062 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1063 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1064 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1065 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1066 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1067 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1068 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1069 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1070 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1071 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1072 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1073 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1074 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1075 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1076 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1077 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1078 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1079 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1080 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1081 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1082 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1083 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1084 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1085 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1086 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1087 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1088 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1089 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1090 | AR1 | AR1 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1091 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1092 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1093 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1094 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1095 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1096 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1097 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1098 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1099 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1100 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1101 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1102 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1103 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1104 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1105 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1106 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1107 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1108 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1109 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1110 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1111 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1112 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1113 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1114 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1115 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1116 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1117 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1118 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1119 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1120 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1121 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1122 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1123 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1124 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1125 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1126 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1127 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1128 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1129 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1130 | AR1 | AR2 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1131 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1132 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1133 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1134 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1135 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1136 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1137 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1138 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1139 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1140 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1141 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1142 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1143 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1144 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1145 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1146 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1147 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1148 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1149 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1150 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1151 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1152 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1153 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1154 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1155 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1156 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1157 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1158 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1159 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1160 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1161 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1162 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1163 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1164 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1165 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1166 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1167 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1168 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1169 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1170 | AR1 | AR3 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1171 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1172 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1173 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1174 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1175 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1176 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1177 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1178 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1179 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1180 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1181 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1182 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1183 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1184 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1185 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1186 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1187 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1188 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1189 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1190 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1191 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1192 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1193 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1194 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1195 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1196 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1197 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1198 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1199 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1200 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1201 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1202 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1203 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1204 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1205 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1206 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1207 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1208 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1209 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1210 | AR1 | AR4 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1211 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1212 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1213 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1214 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1215 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1216 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1217 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1218 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1219 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1220 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1221 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1222 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1223 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1224 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1225 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1226 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1227 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1228 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1229 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1230 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1231 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1232 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1233 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1234 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1235 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1236 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1237 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1238 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1239 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1240 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1241 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1242 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1243 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1244 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1245 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1246 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1247 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1248 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1249 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | S1250 | AR1 | AR5 Shot Reclaim time | FLOAT | RW | 0...1800
63 | O1 | AR1 | AR On | SIGNAL_OUT | RW | 0...4294967295
63 | O2 | AR1 | AR Off | SIGNAL_OUT | RW | 0...4294967295
63 | O3 | AR1 | AR In Progress | SIGNAL_OUT | RW | 0...4294967295
63 | O4 | AR1 | AR1 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O5 | AR1 | AR2 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O6 | AR1 | AR3 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O7 | AR1 | AR4 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O8 | AR1 | AR5 Request on | SIGNAL_OUT | RW | 0...4294967295
63 | O9 | AR1 | AR Running | SIGNAL_OUT | RW | 0...4294967295
63 | O10 | AR1 | AR Shot 1 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O11 | AR1 | AR Shot 2 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O12 | AR1 | AR Shot 3 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O13 | AR1 | AR Shot 4 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O14 | AR1 | AR Shot 5 Running | SIGNAL_OUT | RW | 0...4294967295
63 | O15 | AR1 | AR Sequence finished | SIGNAL_OUT | RW | 0...4294967295
63 | O16 | AR1 | AR Final Trip | SIGNAL_OUT | RW | 0...4294967295
63 | O17 | AR1 | Dead time on | SIGNAL_OUT | RW | 0...4294967295
63 | O18 | AR1 | ARC time on | SIGNAL_OUT | RW | 0...4294967295
63 | O19 | AR1 | Reclaim time on | SIGNAL_OUT | RW | 0...4294967295
63 | O20 | AR1 | AR Ready | SIGNAL_OUT | RW | 0...4294967295
63 | O21 | AR1 | AR Lockout after successfull sequence | SIGNAL_OUT | RW | 0...4294967295
63 | O22 | AR1 | AR Operation Inhibit | SIGNAL_OUT | RW | 0...4294967295
63 | O23 | AR1 | AR Locked | SIGNAL_OUT | RW | 0...4294967295
63 | I36 | AR1 | Newest Register | UINT32 | R | 0...12
63 | I37 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I38 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I39 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I40 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I41 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I42 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I43 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I44 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I45 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I46 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I47 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I48 | AR1 | AR status | UINT32 | R | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5
63 | I49 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I50 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I51 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I52 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I53 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I54 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I55 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I56 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I57 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I58 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I59 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I60 | AR1 | Active timer | UINT32 | R | 0=None;1=Lockout delay;2=Obj Close reclaim;3=Start delay;4=Dead Time;5=Arc/Discr Time;6=Shot Reclaim
63 | I61 | AR1 | Active time | FLOAT | R | 0...1800
63 | I62 | AR1 | Active time | FLOAT | R | 0...1800
63 | I63 | AR1 | Active time | FLOAT | R | 0...1800
63 | I64 | AR1 | Active time | FLOAT | R | 0...1800
63 | I65 | AR1 | Active time | FLOAT | R | 0...1800
63 | I66 | AR1 | Active time | FLOAT | R | 0...1800
63 | I67 | AR1 | Active time | FLOAT | R | 0...1800
63 | I68 | AR1 | Active time | FLOAT | R | 0...1800
63 | I69 | AR1 | Active time | FLOAT | R | 0...1800
63 | I70 | AR1 | Active time | FLOAT | R | 0...1800
63 | I71 | AR1 | Active time | FLOAT | R | 0...1800
63 | I72 | AR1 | Active time | FLOAT | R | 0...1800
63 | S1251 | AR1 | EventMaskLo | UINT32 | RW | 0...4294967295
63 | S1252 | AR1 | EventMaskHi | UINT32 | RW | 0...4294967295
115 | S1 | VRG1 | Vreg [AVR/90] mode | UINT32 | RW | 0=Disabled;1=Activated
115 | V1 | VRG1 | Vreg settings condition | UINT32 | R | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok
115 | V2 | VRG1 | Vreg condition | UINT32 | R | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on
115 | V3 | VRG1 | Vreg timer active | UINT32 | R | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
115 | I1 | VRG1 | Time left to operation | FLOAT | R | 0...1800
115 | I2 | VRG1 | Voltage now | FLOAT | R | 0...140
115 | I3 | VRG1 | Voltage difference to set target | FLOAT | R | -140...140
115 | I4 | VRG1 | Voltage set now to | FLOAT | R | -50000...50000
115 | I5 | VRG1 | Tap location now (- 0 +) | FLOAT | R | -30...30
115 | I6 | VRG1 | Absolute tap location | FLOAT | R | 0...50
115 | V4 | VRG1 | Tap changer on high border | UINT32 | R | 0=No;1=Yes
115 | V5 | VRG1 | Tap changer on low border | UINT32 | R | 0=No;1=Yes
115 | I7 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual (loc&rem)
115 | V6 | VRG1 | Remote tap control input | UINT32 | RW | 0=Stop;1=Lower;2=Higher
115 | S2 | VRG1 | Control pulselength max | FLOAT | RW | 0...1800
115 | S3 | VRG1 | Control pulselength min | FLOAT | RW | 0...1800
115 | S4 | VRG1 | Min time between pulses | FLOAT | RW | 0...1800
115 | V7 | VRG1 | Tap position ind. Setting | UINT32 | R | 0=Not selected;1=Set Ok;2=Wrong setting;3=Meas.Quality Fault.
115 | I8 | VRG1 | AVR rised voltage | UINT32 | R | 0...4294967295
115 | I9 | VRG1 | AVR reduced voltage | UINT32 | R | 0...4294967295
115 | I10 | VRG1 | AVR control blocked | UINT32 | R | 0...4294967295
115 | I11 | VRG1 | AVR Undervoltage blocked | UINT32 | R | 0...4294967295
115 | I12 | VRG1 | AVR Overcurrent blocked | UINT32 | R | 0...4294967295
115 | S5 | VRG1 | Clear statistics | UINT32 | W | 0=-;1=Clear
115 | S6 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S7 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S8 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S9 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S10 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S11 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S12 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S13 | VRG1 | Target Voltage (UTGT) | FLOAT | RW | 70...140
115 | S14 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S15 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S16 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S17 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S18 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S19 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S20 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S21 | VRG1 | Track optimum voltage | UINT32 | RW | 0=Not in use;1=In use
115 | S22 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S23 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S24 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S25 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S26 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S27 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S28 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S29 | VRG1 | U>/< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S30 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S31 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S32 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S33 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S34 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S35 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S36 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S37 | VRG1 | U> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S38 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S39 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S40 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S41 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S42 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S43 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S44 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S45 | VRG1 | U< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S46 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S47 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S48 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S49 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S50 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S51 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S52 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S53 | VRG1 | U>/< time delay (DT) | FLOAT | RW | 0...1800
115 | S54 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S55 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S56 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S57 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S58 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S59 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S60 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S61 | VRG1 | U>>/<< window in use | UINT32 | RW | 0=Not in use;1=In use
115 | S62 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S63 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S64 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S65 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S66 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S67 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S68 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S69 | VRG1 | U>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S70 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S71 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S72 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S73 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S74 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S75 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S76 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S77 | VRG1 | U<< setting (-UTGT) | FLOAT | RW | 0.1...30
115 | S78 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S79 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S80 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S81 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S82 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S83 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S84 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S85 | VRG1 | U>>/<< time delay mode | UINT32 | RW | 0=Definite;1=Integral
115 | S86 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S87 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S88 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S89 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S90 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S91 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S92 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S93 | VRG1 | U>>/<< time delay (DT / Multiplier) | FLOAT | RW | 0...1800
115 | S94 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S95 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S96 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S97 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S98 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S99 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S100 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S101 | VRG1 | U>>> instant in use | UINT32 | RW | 0=Not in use;1=In use
115 | S102 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S103 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S104 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S105 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S106 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S107 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S108 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S109 | VRG1 | U>>> setting (+UTGT) | FLOAT | RW | 0.1...30
115 | S110 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S111 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S112 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S113 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S114 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S115 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S116 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S117 | VRG1 | U<<< Block stting (-UTGT) | FLOAT | RW | 0...80
115 | S118 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S119 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S120 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S121 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S122 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S123 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S124 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S125 | VRG1 | Internal OC blocking | UINT32 | RW | 0=Not in use;1=In use
115 | S126 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S127 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S128 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S129 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S130 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S131 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S132 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | S133 | VRG1 | Internal OC pick-up > | FLOAT | RW | 0...40
115 | I13 | VRG1 | AVR to Manual control | SIGNAL_IN | RW | 0...4294967295
115 | O1 | VRG1 | AVR Raise Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O2 | VRG1 | AVR Lower Tap CMD | SIGNAL_OUT | RW | 0...4294967295
115 | O3 | VRG1 | AVR In manual control | SIGNAL_OUT | RW | 0...4294967295
115 | O4 | VRG1 | AVR U>/< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O5 | VRG1 | AVR U>>/<< STARTED | SIGNAL_OUT | RW | 0...4294967295
115 | O6 | VRG1 | AVR Outputs blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O7 | VRG1 | AVR Operation blocked | SIGNAL_OUT | RW | 0...4294967295
115 | O8 | VRG1 | AVR Control wait on | SIGNAL_OUT | RW | 0...4294967295
115 | O9 | VRG1 | AVR U< block active | SIGNAL_OUT | RW | 0...4294967295
115 | O10 | VRG1 | AVR I> block active | SIGNAL_OUT | RW | 0...4294967295
115 | O11 | VRG1 | AVR Tap in highlimit | SIGNAL_OUT | RW | 0...4294967295
115 | O12 | VRG1 | AVR Tap in lowlimit | SIGNAL_OUT | RW | 0...4294967295
115 | I14 | VRG1 | Newest Register | UINT32 | R | 0...12
115 | I15 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I16 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I17 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I18 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I19 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I20 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I21 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I22 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I23 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I24 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I25 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I26 | VRG1 | Voltage now | FLOAT | R | 0...250
115 | I27 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I28 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I29 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I30 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I31 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I32 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I33 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I34 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I35 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I36 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I37 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I38 | VRG1 | Tap now | FLOAT | R | 0...250
115 | I39 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I40 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I41 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I42 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I43 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I44 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I45 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I46 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I47 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I48 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I49 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I50 | VRG1 | Target volt | FLOAT | R | 0...250
115 | I51 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I52 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I53 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I54 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I55 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I56 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I57 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I58 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I59 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I60 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I61 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | I62 | VRG1 | Control mode | UINT32 | R | 0=Auto;1=Manual
115 | S134 | VRG1 | EventMaskLo | UINT32 | RW | 0...4294967295
115 | S135 | VRG1 | EventMaskHi | UINT32 | RW | 0...4294967295
135 | S1 | EMON1 | Monitor mode | UINT32 | RW | 0=Disabled;1=Activated
135 | S2 | EMON1 | I> (50) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V1 | EMON1 | I> (50) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S3 | EMON1 | I0> (50N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S4 | EMON1 | I0> (50N) I0input | UINT32 | RW | 0=I01;1=I02;2=I0Calc
135 | V2 | EMON1 | I0> (50N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S5 | EMON1 | Idir> (67) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V3 | EMON1 | Idir> (67) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S6 | EMON1 | I0dir> (67N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S7 | EMON1 | I0dir> (67N) I0input | UINT32 | RW | 0=I01;1=I02
135 | S8 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=select
135 | S9 | EMON1 | I0dir> (67N) U0 Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V4 | EMON1 | I0dir> (67N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S10 | EMON1 | I0Int> (67NT) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S11 | EMON1 | I0Int> (67NT) I0input | UINT32 | RW | 0=I01;1=I02
135 | V5 | EMON1 | I0Int> (67NT) Monitor condition | UINT32 | R | 0=Normal;1=FLT FW;2=FLT REV
135 | S12 | EMON1 | U< (27) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S13 | EMON1 | U< (27) Measured magnitude | UINT32 | RW | 0=P-P Voltages;1=P-E Voltages
135 | S14 | EMON1 | U< (27) Pick-up terms | UINT32 | RW | 0=1 voltage;1=2 voltages;2=3 voltages
135 | V6 | EMON1 | U< (27) Monitor condition | UINT32 | R | 0=Normal;1=Undervoltage;2=No voltage
135 | S15 | EMON1 | U0> (59N) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | S16 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U3 Input;1=U4 Input;2=Select
135 | S17 | EMON1 | U0> (59N) Meas input select | UINT32 | RW | 0=U0Calc;1=U4 Input;2=Select
135 | V7 | EMON1 | U0> (59N) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | S18 | EMON1 | FL (21FL) Monitor enable | UINT32 | RW | 0=Disabled;1=Enabled
135 | V8 | EMON1 | FL (21FL) Monitor condition | UINT32 | R | 0=Normal;1=FLT detected
135 | I1 | EMON1 | I> (50) Alarms | UINT32 | R | 0...4294967295
135 | I2 | EMON1 | I0> (50N) Alarms | UINT32 | R | 0...4294967295
135 | I3 | EMON1 | Idir> (67) Alarms | UINT32 | R | 0...4294967295
135 | I4 | EMON1 | I0dir> (67N) Alarms | UINT32 | R | 0...4294967295
135 | I5 | EMON1 | I0Int> (67) Alarms FWD | UINT32 | R | 0...4294967295
135 | I6 | EMON1 | I0Int> (67) Alarms REV | UINT32 | R | 0...4294967295
135 | I7 | EMON1 | U< (27) Undervoltage Alarms | UINT32 | R | 0...4294967295
135 | I8 | EMON1 | U< (27) No voltage Alarms | UINT32 | R | 0...4294967295
135 | I9 | EMON1 | U0> (59N) Alarms | UINT32 | R | 0...4294967295
135 | I10 | EMON1 | FL (21FL) Triggered | UINT32 | R | 0...4294967295
135 | S19 | EMON1 | Clear statistics | UINT32 | W | 0=-;1=Clear
135 | S20 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S21 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S22 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S23 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S24 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S25 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S26 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S27 | EMON1 | I> (50) I pick-up > | FLOAT | RW | 0.1...40
135 | S28 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S29 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S30 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S31 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S32 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S33 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S34 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S35 | EMON1 | I0> (50N) I0 pick-up > | FLOAT | RW | 0.1...40
135 | S36 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S37 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S38 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S39 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S40 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S41 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S42 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S43 | EMON1 | Idir> (67) characteristic direction | UINT32 | RW | 0=Forward;1=Reverse;2=NonDir
135 | S44 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S45 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S46 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S47 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S48 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S49 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S50 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S51 | EMON1 | Idir> (67) operating sector size (+/-) | FLOAT | RW | 1...170
135 | S52 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S53 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S54 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S55 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S56 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S57 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S58 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S59 | EMON1 | Idir> (67) operating sector center | FLOAT | RW | -180...180
135 | S60 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S61 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S62 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S63 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S64 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S65 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S66 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S67 | EMON1 | Idir> (67) pick-up > | FLOAT | RW | 0.1...40
135 | S68 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S69 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S70 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S71 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S72 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S73 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S74 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S75 | EMON1 | I0dir> (67N) Grounding type | UINT32 | RW | 0=Unearthed;1=Petersen coil GND;2=Grounded;3=I0Cos&I0Sin Broadrange with MCD
135 | S76 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S77 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S78 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S79 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S80 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S81 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S82 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S83 | EMON1 | I0dir> (67N) Pick-up setting I0set> | FLOAT | RW | 0.005...40
135 | S84 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S85 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S86 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S87 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S88 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S89 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S90 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S91 | EMON1 | I0dir> (67N) Pick-up setting U0set> | FLOAT | RW | 1...75
135 | S92 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S93 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S94 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S95 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S96 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S97 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S98 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S99 | EMON1 | I0dir> (67N) Comp. Pick-up setting I0set (I0Cosfi)> | FLOAT | RW | 0.005...40
135 | S100 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S101 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S102 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S103 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S104 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S105 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S106 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S107 | EMON1 | I0dir> (67N) Comp. Pick-up setting U0set(I0Cosfi)> | FLOAT | RW | 1...75
135 | S108 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S109 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S110 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S111 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S112 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S113 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S114 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S115 | EMON1 | I0dir> (67N) Resistive (I0Cosfi) mode I0 angle blinder | FLOAT | RW | -90...0
135 | S116 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S117 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S118 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S119 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S120 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S121 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S122 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S123 | EMON1 | I0dir> (67N) Unearth. Pick-up setting I0set (I0Sinfi)> | FLOAT | RW | 0.005...40
135 | S124 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S125 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S126 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S127 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S128 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S129 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S130 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S131 | EMON1 | I0dir> (67N) Unearth. Pick-up setting U0set(I0Sinfi)> | FLOAT | RW | 1...75
135 | S132 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S133 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S134 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S135 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S136 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S137 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S138 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S139 | EMON1 | I0dir> (67N) Trip area size (+/-) | FLOAT | RW | 45...135
135 | S140 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S141 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S142 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S143 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S144 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S145 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S146 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S147 | EMON1 | I0dir> (67N) Trip area center | FLOAT | RW | 0...360
135 | S148 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S149 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S150 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S151 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S152 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S153 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S154 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S155 | EMON1 | I0Int> (67NT) U0 Detect spike > | FLOAT | RW | 1...100
135 | S156 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S157 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S158 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S159 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S160 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S161 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S162 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S163 | EMON1 | I0Int> (67NT) I0 Detect spike > | FLOAT | RW | 0.05...40
135 | S164 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S165 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S166 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S167 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S168 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S169 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S170 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S171 | EMON1 | I0Int> (67NT) FWD reset time | FLOAT | RW | 0...1800
135 | S172 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S173 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S174 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S175 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S176 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S177 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S178 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S179 | EMON1 | I0Int> (67NT) REV reset time | FLOAT | RW | 0...1800
135 | S180 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S181 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S182 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S183 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S184 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S185 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S186 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S187 | EMON1 | I0Int> (67NT) Spikes to Indicate > | UINT32 | RW | 1...50
135 | S188 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S189 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S190 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S191 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S192 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S193 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S194 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S195 | EMON1 | U< (27) Undervoltage set< | FLOAT | RW | 0...120
135 | S196 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S197 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S198 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S199 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S200 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S201 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S202 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S203 | EMON1 | U< (27) No voltage set< | FLOAT | RW | 0...80
135 | S204 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S205 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S206 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S207 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S208 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S209 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S210 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S211 | EMON1 | U0V> (59N) Overvoltage set > | FLOAT | RW | 1...99
135 | S212 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S213 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S214 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S215 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S216 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S217 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S218 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S219 | EMON1 | FL (21FL) Trigger current > | FLOAT | RW | 0...40
135 | S220 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S221 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S222 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S223 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S224 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S225 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S226 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | S227 | EMON1 | FL (21FL) Reactance per km | FLOAT | RW | 0.001...5
135 | O1 | EMON1 | I> (50) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O2 | EMON1 | I0> (50N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O3 | EMON1 | Idir> (67) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O4 | EMON1 | I0dir> (67N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O5 | EMON1 | I0int> (67NT) Alarm FWD | SIGNAL_OUT | RW | 0...4294967295
135 | O6 | EMON1 | I0int> (67NT) Alarm REV | SIGNAL_OUT | RW | 0...4294967295
135 | O7 | EMON1 | U< (27) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O8 | EMON1 | U< (27) No voltage | SIGNAL_OUT | RW | 0...4294967295
135 | O9 | EMON1 | U0> (59N) Alarm | SIGNAL_OUT | RW | 0...4294967295
135 | O10 | EMON1 | FL (21FL) Triggered | SIGNAL_OUT | RW | 0...4294967295
135 | I11 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I12 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I13 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I14 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I15 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I16 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I17 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I18 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I19 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I20 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I21 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I22 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I23 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
135 | I24 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I25 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I26 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I27 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I28 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I29 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I30 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I31 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I32 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I33 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I34 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I35 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I36 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I37 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I38 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I39 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I40 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I41 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I42 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I43 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I44 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I45 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I46 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I47 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I48 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I49 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I50 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I51 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I52 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I53 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I54 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I55 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I56 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I57 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I58 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I59 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I60 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I61 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I62 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I63 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I64 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I65 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I66 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I67 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I68 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I69 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I70 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I71 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I72 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I73 | EMON1 | Fault type | UINT32 | R | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
135 | I74 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I75 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I76 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I77 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I78 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I79 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I80 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I81 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I82 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I83 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I84 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I85 | EMON1 | Max Im/Iset | FLOAT | R | 0...250
135 | I86 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I87 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I88 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I89 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I90 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I91 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I92 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I93 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I94 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I95 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I96 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I97 | EMON1 | Operating angle | FLOAT | R | 0...250
135 | I98 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I99 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I100 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I101 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I102 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I103 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I104 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I105 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I106 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I107 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I108 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I109 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I110 | EMON1 | Max I0m/I0set | FLOAT | R | 0...250
135 | I111 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I112 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I113 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I114 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I115 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I116 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I117 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I118 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I119 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I120 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I121 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I122 | EMON1 | Fault U0(%) | FLOAT | R | 0...500
135 | I123 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I124 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I125 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I126 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I127 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I128 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I129 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I130 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I131 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I132 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I133 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I134 | EMON1 | I0 Fault angle | FLOAT | R | -360...360
135 | I135 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I136 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I137 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I138 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I139 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I140 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I141 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I142 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I143 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I144 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I145 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I146 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I147 | EMON1 | Start FWD | UINT32 | R | 0=No;1=Yes
135 | I148 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I149 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I150 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I151 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I152 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I153 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I154 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I155 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I156 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I157 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I158 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I159 | EMON1 | Start REV | UINT32 | R | 0=No;1=Yes
135 | I160 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I161 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I162 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I163 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I164 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I165 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I166 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I167 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I168 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I169 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I170 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I171 | EMON1 | Pulses | UINT32 | R | 0...500
135 | I172 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I173 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I174 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I175 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I176 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I177 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I178 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I179 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I180 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I181 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I182 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I183 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I184 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I185 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I186 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I187 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I188 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I189 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I190 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I191 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I192 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I193 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I194 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I195 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I196 | EMON1 | Umeas/Uset | FLOAT | R | 0...250
135 | I197 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I198 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I199 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I200 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I201 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I202 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I203 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I204 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I205 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I206 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I207 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I208 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I209 | EMON1 | U0meas/U0set | FLOAT | R | 0...250
135 | I210 | EMON1 | Newest Register | UINT32 | R | 0...12
135 | I211 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I212 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I213 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I214 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I215 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I216 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I217 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I218 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I219 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I220 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I221 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I222 | EMON1 | Fault direction | UINT32 | R | 0=Not detected;1=Forward;2=Reverse
135 | I223 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I224 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I225 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I226 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I227 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I228 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I229 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I230 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I231 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I232 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I233 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I234 | EMON1 | Fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C
135 | I235 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I236 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I237 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I238 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I239 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I240 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I241 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I242 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I243 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I244 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I245 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I246 | EMON1 | km to fault | FLOAT | R | 0...250
135 | I247 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I248 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I249 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I250 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I251 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I252 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I253 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I254 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I255 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I256 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I257 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | I258 | EMON1 | React (X) to fault | FLOAT | R | 0...250
135 | S228 | EMON1 | EventMaskLo | UINT32 | RW | 0...4294967295
135 | S229 | EMON1 | EventMaskHi | UINT32 | RW | 0...4294967295
143 | O1 | ALARM | ALARM 1 | SIGNAL_IN | RW | 0...4294967295
143 | O2 | ALARM | ALARM 2 | SIGNAL_IN | RW | 0...4294967295
143 | O3 | ALARM | ALARM 3 | SIGNAL_IN | RW | 0...4294967295
143 | O4 | ALARM | ALARM 4 | SIGNAL_IN | RW | 0...4294967295
143 | O5 | ALARM | ALARM 5 | SIGNAL_IN | RW | 0...4294967295
143 | O6 | ALARM | ALARM 6 | SIGNAL_IN | RW | 0...4294967295
143 | O7 | ALARM | ALARM 7 | SIGNAL_IN | RW | 0...4294967295
143 | O8 | ALARM | ALARM 8 | SIGNAL_IN | RW | 0...4294967295
143 | O9 | ALARM | ALARM 9 | SIGNAL_IN | RW | 0...4294967295
143 | O10 | ALARM | ALARM 10 | SIGNAL_IN | RW | 0...4294967295
143 | O11 | ALARM | ALARM 11 | SIGNAL_IN | RW | 0...4294967295
143 | O12 | ALARM | ALARM 12 | SIGNAL_IN | RW | 0...4294967295
143 | O13 | ALARM | ALARM 13 | SIGNAL_IN | RW | 0...4294967295
143 | O14 | ALARM | ALARM 14 | SIGNAL_IN | RW | 0...4294967295
143 | O15 | ALARM | ALARM 15 | SIGNAL_IN | RW | 0...4294967295
143 | O16 | ALARM | ALARM 16 | SIGNAL_IN | RW | 0...4294967295
143 | O17 | ALARM | ALARM 17 | SIGNAL_IN | RW | 0...4294967295
143 | O18 | ALARM | ALARM 18 | SIGNAL_IN | RW | 0...4294967295
143 | O19 | ALARM | ALARM 19 | SIGNAL_IN | RW | 0...4294967295
143 | O20 | ALARM | ALARM 20 | SIGNAL_IN | RW | 0...4294967295
143 | O21 | ALARM | ALARM 21 | SIGNAL_IN | RW | 0...4294967295
143 | O22 | ALARM | ALARM 22 | SIGNAL_IN | RW | 0...4294967295
143 | O23 | ALARM | ALARM 23 | SIGNAL_IN | RW | 0...4294967295
143 | O24 | ALARM | ALARM 24 | SIGNAL_IN | RW | 0...4294967295
143 | O25 | ALARM | ALARM 25 | SIGNAL_IN | RW | 0...4294967295
143 | O26 | ALARM | ALARM 26 | SIGNAL_IN | RW | 0...4294967295
143 | O27 | ALARM | ALARM 27 | SIGNAL_IN | RW | 0...4294967295
143 | O28 | ALARM | ALARM 28 | SIGNAL_IN | RW | 0...4294967295
143 | O29 | ALARM | ALARM 29 | SIGNAL_IN | RW | 0...4294967295
143 | O30 | ALARM | ALARM 30 | SIGNAL_IN | RW | 0...4294967295
143 | O31 | ALARM | ALARM 31 | SIGNAL_IN | RW | 0...4294967295
143 | O32 | ALARM | ALARM 32 | SIGNAL_IN | RW | 0...4294967295
143 | O33 | ALARM | ALARM 33 | SIGNAL_IN | RW | 0...4294967295
143 | O34 | ALARM | ALARM 34 | SIGNAL_IN | RW | 0...4294967295
143 | O35 | ALARM | ALARM 35 | SIGNAL_IN | RW | 0...4294967295
143 | O36 | ALARM | ALARM 36 | SIGNAL_IN | RW | 0...4294967295
143 | O37 | ALARM | ALARM 37 | SIGNAL_IN | RW | 0...4294967295
143 | O38 | ALARM | ALARM 38 | SIGNAL_IN | RW | 0...4294967295
143 | O39 | ALARM | ALARM 39 | SIGNAL_IN | RW | 0...4294967295
143 | O40 | ALARM | ALARM 40 | SIGNAL_IN | RW | 0...4294967295
143 | O41 | ALARM | ALARM 41 | SIGNAL_IN | RW | 0...4294967295
143 | O42 | ALARM | ALARM 42 | SIGNAL_IN | RW | 0...4294967295
143 | O43 | ALARM | ALARM 43 | SIGNAL_IN | RW | 0...4294967295
143 | O44 | ALARM | ALARM 44 | SIGNAL_IN | RW | 0...4294967295
143 | O45 | ALARM | ALARM 45 | SIGNAL_IN | RW | 0...4294967295
143 | O46 | ALARM | ALARM 46 | SIGNAL_IN | RW | 0...4294967295
143 | O47 | ALARM | ALARM 47 | SIGNAL_IN | RW | 0...4294967295
143 | O48 | ALARM | ALARM 48 | SIGNAL_IN | RW | 0...4294967295
143 | O49 | ALARM | ALARM 49 | SIGNAL_IN | RW | 0...4294967295
143 | O50 | ALARM | ALARM 50 | SIGNAL_IN | RW | 0...4294967295
143 | O51 | ALARM | ALARM 51 | SIGNAL_IN | RW | 0...4294967295
143 | O52 | ALARM | ALARM 52 | SIGNAL_IN | RW | 0...4294967295
143 | O53 | ALARM | ALARM 53 | SIGNAL_IN | RW | 0...4294967295
143 | O54 | ALARM | ALARM 54 | SIGNAL_IN | RW | 0...4294967295
143 | O55 | ALARM | ALARM 55 | SIGNAL_IN | RW | 0...4294967295
143 | O56 | ALARM | ALARM 56 | SIGNAL_IN | RW | 0...4294967295
143 | O57 | ALARM | ALARM 57 | SIGNAL_IN | RW | 0...4294967295
143 | O58 | ALARM | ALARM 58 | SIGNAL_IN | RW | 0...4294967295
143 | O59 | ALARM | ALARM 59 | SIGNAL_IN | RW | 0...4294967295
143 | O60 | ALARM | ALARM 60 | SIGNAL_IN | RW | 0...4294967295
143 | O61 | ALARM | ALARM 61 | SIGNAL_IN | RW | 0...4294967295
143 | O62 | ALARM | ALARM 62 | SIGNAL_IN | RW | 0...4294967295
143 | O63 | ALARM | ALARM 63 | SIGNAL_IN | RW | 0...4294967295
143 | O64 | ALARM | ALARM 64 | SIGNAL_IN | RW | 0...4294967295
159 | S1 | ALARM1 | EventMaskLo | UINT32 | RW | 0...4294967295
159 | S2 | ALARM1 | EventMaskHi | UINT32 | RW | 0...4294967295
160 | S1 | ALARM2 | EventMaskLo | UINT32 | RW | 0...4294967295
160 | S2 | ALARM2 | EventMaskHi | UINT32 | RW | 0...4294967295
162 | S1 | GSYN | Synchronizer mode | UINT32 | RW | 0=Disabled;1=Activated
162 | S2 | GSYN | Synchronizer reference voltage input | UINT32 | RW | 0=U4 Input;1=U3 Input
162 | S3 | GSYN | Voltage difference calculation mode | UINT32 | RW | 0=System is reference;1=U3/U4 Input is reference
162 | S4 | GSYN | Synchronizer voltage reference | UINT32 | RW | 0=UL12;1=UL23;2=UL31;3=UL1;4=UL2;5=UL3
162 | S5 | GSYN | Synchronizer measurement settings | UINT32 | R | 0=Meas.Conf.Incorrect;1=PP and PE voltages;2=PP Voltages;
162 | S6 | GSYN | Synchronizer status | UINT32 | R | 0=Conf.Error;1=Idle Ready;2=Synchronizing;3=Blocked
162 | S7 | GSYN | Force control signals on | UINT32 | RW | 0=None;1=Blocked On;2=Running On;3=Increase U On;4=Decrease U On;5=Increase F On;6=Decrease F On;7=CB Close On;8=LongSyncTime On
162 | S8 | GSYN | Synchronizing by | UINT32 | RW | 0=Autosynchronizer;1=Manual commands
162 | S9 | GSYN | Manual switching mode | UINT32 | RW | 0=Assisted synchroswitch;1=I know what I am doing
162 | S10 | GSYN | Synchroswitch status | UINT32 | R | 0=Standstill;1=Departing;2=Enclosing
162 | S11 | GSYN | Magnitude side A | FLOAT | R | 0.000...200.000
162 | S12 | GSYN | Magnitude side B | FLOAT | R | 0.000...200.000
162 | S13 | GSYN | Frequency side A | FLOAT | R | 0.000...75.000
162 | S14 | GSYN | Frequency side B | FLOAT | R | 0.000...75.000
162 | S15 | GSYN | Magnitude difference | FLOAT | R | -200...200
162 | S16 | GSYN | Frequency difference | FLOAT | R | -100...100
162 | S17 | GSYN | Angle difference | FLOAT | R | -360...360
162 | S18 | GSYN | Magnitude difference on closing BRK | FLOAT | R | -200...200
162 | S19 | GSYN | Frequency difference on closing BRK | FLOAT | R | -100...100
162 | S20 | GSYN | Angle difference on closing BRK | FLOAT | R | -360...360
162 | S21 | GSYN | Estimated BRK Closing time | FLOAT | R | 0...360
162 | S22 | GSYN | Networks rotating time | FLOAT | R | 0...360
162 | S23 | GSYN | Networks placement atm | FLOAT | R | -360...360
162 | S24 | GSYN | Synchronizing time left | FLOAT | R | 0...1800
162 | S25 | GSYN | Get measurement errors for fine tuning | UINT32 | RW | 0=-;1=Get errors
162 | S26 | GSYN | Magnitude difference fine tune | FLOAT | RW | -200...200
162 | S27 | GSYN | Frequency difference fine tune | FLOAT | RW | -100...100
162 | S28 | GSYN | Angle difference fine tune | FLOAT | RW | -360...360
162 | S29 | GSYN | Minimum voltage allowed for synchronizing | FLOAT | RW | 0...105
162 | S30 | GSYN | Maximum voltage allowed for synchronizing | FLOAT | RW | 0...200
162 | S31 | GSYN | Maximum zero voltage allowed for synchronizing (100% disabled) | FLOAT | RW | 0...100
162 | S32 | GSYN | Maximum allowed voltage difference | FLOAT | RW | 0.1...50
162 | S33 | GSYN | Maximum allowed overfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S34 | GSYN | Maximum allowed underfrequency difference to allow synchronizing | FLOAT | RW | 0...2
162 | S35 | GSYN | Max.Time for synchronizing | FLOAT | RW | 0...1800
162 | S36 | GSYN | Maximum allowed angular disposition to allow synchronizing | FLOAT | RW | 0.01...25
162 | S37 | GSYN | Adjustment for measurement inaccuracy or set of desired volt. offset | FLOAT | RW | -95...95
162 | S38 | GSYN | Adjustment for measurement inaccuracy or set of desired angular offset | FLOAT | RW | -60...60
162 | S39 | GSYN | Adjustment for measurement inaccuracy or set of desired freq. offset | FLOAT | RW | -0.5...2
162 | S40 | GSYN | Voltage adjustment slope | FLOAT | RW | 0...25
162 | S41 | GSYN | Volt. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S42 | GSYN | Volt. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S43 | GSYN | Volt. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S44 | GSYN | Freq. Max. adjustment pulse length | FLOAT | RW | 0...1800
162 | S45 | GSYN | Freq. Min. adjustment pulse length | FLOAT | RW | 0...1800
162 | S46 | GSYN | Freq. Min. Resting time between pulses | FLOAT | RW | 0...1800
162 | S47 | GSYN | Maximum allowed voltage difference to start synchronizing | FLOAT | RW | 0...50
162 | S48 | GSYN | Integrator sum when voltage adjustment pulse is generated | FLOAT | RW | 0...50
162 | S49 | GSYN | Voltage adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S50 | GSYN | Frequency adjustment slope when increasing | FLOAT | RW | 0...10
162 | S51 | GSYN | Frequency adjustment slope when decreasing | FLOAT | RW | -10...0
162 | S52 | GSYN | Maximum allowed frequency difference to start synchronizing | FLOAT | RW | 0...25
162 | S53 | GSYN | Integrator sum when frequency adjustment pulse is generated | FLOAT | RW | 0...50
162 | S54 | GSYN | Frequency adjustment pulse length constant | FLOAT | RW | 0...5000
162 | S55 | GSYN | Filter time for angle derivative | FLOAT | RW | 0...1800
162 | S56 | GSYN | Circuit breaker pre-closing adjustment constant | FLOAT | RW | 0...10
162 | S57 | GSYN | Circuit breaker pre-closing time incl auxiliary relays | FLOAT | RW | 0...1800
162 | S58 | GSYN | Lenght of circuit breaker closing pulse | FLOAT | RW | 0...1800
162 | I1 | GSYN | Start Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I2 | GSYN | Stop Synchronizer | SIGNAL_IN | RW | 0...4294967295
162 | I3 | GSYN | Block and Interrupt Synchronizing | SIGNAL_IN | RW | 0...4294967295
162 | I4 | GSYN | Breaker Closed | SIGNAL_IN | RW | 0...4294967295
162 | I5 | GSYN | Manual increase voltage | SIGNAL_IN | RW | 0...4294967295
162 | I6 | GSYN | Manual decrease voltage | SIGNAL_IN | RW | 0...4294967295
162 | I7 | GSYN | Manual increase frequency | SIGNAL_IN | RW | 0...4294967295
162 | I8 | GSYN | Manual decrease frequency | SIGNAL_IN | RW | 0...4294967295
162 | I9 | GSYN | Manual Close Breaker | SIGNAL_IN | RW | 0...4294967295
162 | O1 | GSYN | GSYN Voltage Mag.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O2 | GSYN | GSYN Voltage Freq.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O3 | GSYN | GSYN Voltage Ang.Difference Ok | SIGNAL_OUT | RW | 0...4294967295
162 | O4 | GSYN | GSYN Blocked | SIGNAL_OUT | RW | 0...4294967295
162 | O5 | GSYN | GSYN Running | SIGNAL_OUT | RW | 0...4294967295
162 | O6 | GSYN | GSYN Increase Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O7 | GSYN | GSYN Decrease Voltage | SIGNAL_OUT | RW | 0...4294967295
162 | O8 | GSYN | GSYN Increase Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O9 | GSYN | GSYN Decrease Frequency | SIGNAL_OUT | RW | 0...4294967295
162 | O10 | GSYN | GSYN Breaker Close Pulse | SIGNAL_OUT | RW | 0...4294967295
162 | O11 | GSYN | GSYN Long Sync Time | SIGNAL_OUT | RW | 0...4294967295
162 | O12 | GSYN | GSYN Nets Standstill | SIGNAL_OUT | RW | 0...4294967295
162 | O13 | GSYN | GSYN Nets Departing | SIGNAL_OUT | RW | 0...4294967295
162 | O14 | GSYN | GSYN Nets Enclosing | SIGNAL_OUT | RW | 0...4294967295
162 | S59 | GSYN | Control EventMaskLo | UINT32 | RW | 0...4294967295
162 | S60 | GSYN | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | S1 | VREC | Measurement value recorder mode | UINT32 | RW | 0=Disabled;1=Activated
163 | S2 | VREC | Scale current values to primary | UINT32 | RW | 0=No;1=Yes
163 | S3 | VREC | Record fault types (Overcurrrent & Voltage Over/Under) faults | UINT32 | RW | 0=No;1=Yes
163 | I1 | VREC | Trigger register to memory | SIGNAL_IN | RW | 0...4294967295
163 | I2 | VREC | Tripped stage | UINT32 | R | 0=-;1=I> Trip;2=I>> Trip;3=I>>> Trip;4=I>>>> Trip;5=IDir> Trip;6=IDir>> Trip;7=IDir>>> Trip;8=IDir>>>> Trip;9=U> Trip;10=U>> Trip;11=U>>> Trip;12=U>>>> Trip;13=U< Trip;14=U<< Trip;15=U<<< Trip;16=U<<<< Trip;17=I0> TRIP;18=I0>> Trip;19=I0>>> Trip;20=I0>>>> Trip;21=I0Dir> Trip;22=I0Dir>> Trip;23=I0Dir>>> Trip;24=I0Dir>>>> Trip;25=f> Trip;26=f>> Trip;27=f>>> Trip;28=f>>>> Trip;29=f< Trip;30=f<< Trip;31=f<<< Trip;32=f<<<< Trip;33=P> Trip;34=P< Trip;35=Prev> Trip;36=T> Trip;37=I2> Trip;38=I2>> Trip;39=I2>>> Trip;40=I2>>>> Trip;41=U1/2 > Trip;42=U1/2 >> Trip;43=U1/2 >>> Trip;44=U1/2 >>>> Trip;45=U0> Trip;46=U0>> Trip;47=U0>>> Trip;48=U0>>>> Trip
163 | I3 | VREC | Overcurrent fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;
163 | I4 | VREC | Voltage fault type | UINT32 | R | 0=-;1=A(AB);2=B(BC);3=A-B(AB-BC);4=C(CA);5=A-C(AB-CA);6=B-C(BC-CA);7=A-B-C;8=-;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I5 | VREC | VREC Magnitude 1 | FLOAT | R | 0...1800
163 | I6 | VREC | VREC Magnitude 2 | FLOAT | R | 0...1800
163 | I7 | VREC | VREC Magnitude 3 | FLOAT | R | 0...1800
163 | I8 | VREC | VREC Magnitude 4 | FLOAT | R | 0...1800
163 | I9 | VREC | VREC Magnitude 5 | FLOAT | R | 0...1800
163 | I10 | VREC | VREC Magnitude 6 | FLOAT | R | 0...1800
163 | I11 | VREC | VREC Magnitude 7 | FLOAT | R | 0...1800
163 | I12 | VREC | VREC Magnitude 8 | FLOAT | R | 0...1800
163 | I13 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I14 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I15 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I16 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I17 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I18 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I19 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I20 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I21 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I22 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I23 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I24 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295
163 | I22 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I23 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | I24 | VREC | Fault type | UINT32 | R | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C;8=Groundfault;9=Overfrequency;10=Underfrequency;11=Overpower;12=Underpower;13=Reversepower;14=Thermal overload;15=Unbalance;16=Harmonic overcurrent;17=Residual overvoltage
163 | S4 | VREC | Control EventMaskLo | UINT32 | RW | 0...4294967295
163 | S5 | VREC | Control EventMaskHi | UINT32 | RW | 0...4294967295