## AQ 210 v2.1.1.3-233
AQ-200 IED IEC101/IEC104 IOA LIST
NOTE: THIS MAP CAN BE DIFFERENT FROM THE ONE USED BY YOUR DEVICE! TO MAKE SURE YOU HAVE A MAP THAT MATCHES WITH YOUR DEVICE, GET IT FROM THE AQS CONFIGURATION FILE (TOOLS -> COMMUNICATION -> IEC101 / 104 MAP)
Single points
IOA | Description
65537 | Local/Remote switch
65538 | DI1
65539 | DI2
65540 | DI3
65541 | DI4
65542 | DI5
65543 | DI6
65544 | DI7
65545 | DI8
65546 | DI9
65547 | DI10
65548 | DI11
65549 | DI12
65550 | DI13
65551 | DI14
65552 | DI15
65553 | DI16
65554 | DI17
65555 | DI18
65556 | DI19
65557 | DI20
65558 | DI21
65559 | DI22
65560 | DI23
65561 | DI24
65562 | DI25
65563 | DI26
65564 | DI27
65565 | DI28
65566 | DI29
65567 | DI30
65568 | DI31
65569 | DI32
65570 | DI33
65571 | DI34
65572 | DI35
65573 | DI36
65574 | DI37
65575 | DI38
65576 | DI39
65577 | DI40
65578 | DI41
65579 | DI42
65580 | DI43
65581 | DI44
65582 | DI45
65583 | DI46
65584 | DI47
65585 | DI48
65586 | DI49
65587 | DI50
65588 | DI51
65589 | I> START (General)
65590 | I> TRIP (General)
65591 | I>> START (General)
65592 | I>> TRIP (General)
65593 | I>>> START (General)
65594 | I>>> TRIP (General)
65595 | I>>>> START (General)
65596 | I>>>> TRIP (General)
65597 | I0> START
65598 | I0> TRIP
65599 | I0>> START
65600 | I0>> TRIP
65601 | I0>>> START
65602 | I0>>> TRIP
65603 | I0>>>> START
65604 | I0>>>> TRIP
65605 | Ih> START
65606 | Ih>> START
65607 | Ih>>> START
65608 | Ih>>>> START
65609 | I2> START
65610 | I2> TRIP
65611 | I2>> START
65612 | I2>> TRIP
65613 | I2>>> START
65614 | I2>>> TRIP
65615 | I2>>>> START
65616 | I2>>>> TRIP
65617 | CLP condition
65618 | CLP condition
65619 | CBFP condition
65620 | CBFP condition
65621 | Operate for IEC61850
65622 | AR1 Request on
65623 | AR2 Request on
65624 | AR3 Request on
65625 | AR4 Request on
65626 | AR5 Request on
65627 | AR Shot 1 Running
65628 | AR Shot 2 Running
65629 | AR Shot 3 Running
65630 | AR Shot 4 Running
65631 | AR Shot 5 Running
65632 | AR Sequence finished
65633 | AR Final Trip
65634 | ARC time on
65635 | Reclaim time on
65636 | NTP quality for events
65637 | AR Lockout after successfull sequence
65638 | AR Operation Inhibit
65639 | AR Locked
65640 | TF> Alarm1
65641 | TF> Trip
65642 | Internal Relay Fault active
65643 | I0d> TRIP
65644 | CBW Alarm 1 act
65645 | CBW Alarm 2 act
65646 | CTS1 ALARM
65647 | Logical Output 1
65648 | Logical Output 2
65649 | Logical Output 3
65650 | Logical Output 4
65651 | Logical Output 5
65652 | Logical Output 6
65653 | Logical Output 7
65654 | Logical Output 8
65655 | Logical Output 9
65656 | Logical Output 10
65657 | Logical Output 11
65658 | Logical Output 12
65659 | Logical Output 13
65660 | Logical Output 14
65661 | Logical Output 15
65662 | Logical Output 16
65663 | Logical Output 17
65664 | Logical Output 18
65665 | Logical Output 19
65666 | Logical Output 20
65667 | Logical Output 21
65668 | Logical Output 22
65669 | Logical Output 23
65670 | Logical Output 24
65671 | Logical Output 25
65672 | Logical Output 26
65673 | Logical Output 27
65674 | Logical Output 28
65675 | Logical Output 29
65676 | Logical Output 30
65677 | Logical Output 31
65678 | Logical Output 32
65679 | Logical Input 1
65680 | Logical Input 2
65681 | Logical Input 3
65682 | Logical Input 4
65683 | Logical Input 5
65684 | Logical Input 6
65685 | Logical Input 7
65686 | Logical Input 8
65687 | Logical Input 9
65688 | Logical Input 10
65689 | Logical Input 11
65690 | Logical Input 12
65691 | Logical Input 13
65692 | Logical Input 14
65693 | Logical Input 15
65694 | Logical Input 16
65695 | Logical Input 17
65696 | Logical Input 18
65697 | Logical Input 19
65698 | Logical Input 20
65699 | Logical Input 21
65700 | Logical Input 22
65701 | Logical Input 23
65702 | Logical Input 24
65703 | Logical Input 25
65704 | Logical Input 26
65705 | Logical Input 27
65706 | Logical Input 28
65707 | Logical Input 29
65708 | Logical Input 30
65709 | Logical Input 31
65710 | Logical Input 32
65711 | Object1 Open Block Input
65712 | Object1 Close Block Input
65713 | Object2 Open Block Input
65714 | Object2 Close Block Input
65715 | Object3 Open Block Input
65716 | Object3 Close Block Input
65717 | Object4 Open Block Input
65718 | Object4 Close Block Input
65719 | Object5 Open Block Input
65720 | Object5 Close Block Input
65721 | Object6 Open Block Input
65722 | Object6 Close Block Input
65723 | Object7 Open Block Input
65724 | Object7 Close Block Input
65725 | Object8 Open Block Input
65726 | Object8 Close Block Input
65727 | Object9 Open Block Input
65728 | Object9 Close Block Input
65729 | Object10 Open Block Input
65730 | Object10 Close Block Input
65731 | Idir> START
65732 | Idir> TRIP
65733 | Idir>> START
65734 | Idir>> TRIP
65735 | Idir>>> START
65736 | Idir>>> TRIP
65737 | Idir>>>> START
65738 | Idir>>>> TRIP
65739 | N> One start remaining (Alarm)
65740 | N> INHIBIT ON (General)
65741 | TM> Trip
65742 | TM> Restart Inh.
65743 | ISt> START
65744 | ISt> Set time TRIP
65745 | Motor stopped
65746 | Motor starting
65747 | Motor running
65748 | Motor stalled
65749 | Missing phase
65750 | Load Normal
65751 | Overloading
65752 | High overcurrent
65753 | I< START
65754 | I< TRIP
65755 | Im> START
65756 | Im> TRIP
65757 | U> START
65758 | U> TRIP
65759 | U>> START
65760 | U>>> START
65761 | U>>> TRIP
65762 | U>>>> START
65763 | U>>>> TRIP
65764 | U>> TRIP
65765 | U0> START
65766 | U0> TRIP
65767 | U0>> START
65768 | U0>> TRIP
65769 | U0>>> START
65770 | U0>>> TRIP
65771 | U0>>>> START
65772 | U0>>>> TRIP
65773 | U< START
65774 | U< TRIP
65775 | U<< START
65776 | U<< TRIP
65777 | U<<< START
65778 | U<<< TRIP
65779 | U<<<< START
65780 | U<<<< TRIP
65781 | VTS Start
65782 | VTS Fail Alarm Bus
65783 | VTS Fail Alarm Line
65784 | SOTF Active
65785 | SOTF Trip
65786 | I0dir> START (General)
65787 | I0dir> TRIP (General)
65788 | I0dir>> START (General)
65789 | I0dir>> TRIP (General)
65790 | I0dir>>> START (General)
65791 | I0dir>>> TRIP (General)
65792 | I0dir>>>> START (General)
65793 | I0dir>>>> TRIP (General)
65794 | P> START
65795 | P> TRIP
65796 | Prev> START
65797 | Prev> TRIP
65798 | P< START
65799 | P< TRIP
65800 | f> START
65801 | f> TRIP
65802 | f>> START
65803 | f>> TRIP
65804 | f>>> START
65805 | f>>> TRIP
65806 | f>>>> START
65807 | f>>>> TRIP
65808 | f< START
65809 | f< TRIP
65810 | f<< START
65811 | f<< TRIP
65812 | f<<< START
65813 | f<<< TRIP
65814 | f<<<< START
65815 | f<<<< TRIP
65816 | I/I0 Arc> Zone1 TRIP
65817 | I/I0 Arc> Zone2 TRIP
65818 | I/I0 Arc> Zone3 TRIP
65819 | I/I0 Arc> Zone4 TRIP
65820 | PCS1 Switch Status
65821 | PCS2 Switch Status
65822 | PCS3 Switch Status
65823 | PCS4 Switch Status
65824 | PCS5 Switch Status
65825 | GOOSE IN 1
65826 | GOOSE IN 2
65827 | GOOSE IN 3
65828 | GOOSE IN 4
65829 | GOOSE IN 5
65830 | GOOSE IN 6
65831 | GOOSE IN 7
65832 | GOOSE IN 8
65833 | GOOSE IN 9
65834 | GOOSE IN 10
65835 | GOOSE IN 11
65836 | GOOSE IN 12
65837 | GOOSE IN 13
65838 | GOOSE IN 14
65839 | GOOSE IN 15
65840 | GOOSE IN 16
65841 | GOOSE IN 17
65842 | GOOSE IN 18
65843 | GOOSE IN 19
65844 | GOOSE IN 20
65845 | GOOSE IN 21
65846 | GOOSE IN 22
65847 | GOOSE IN 23
65848 | GOOSE IN 24
65849 | GOOSE IN 25
65850 | GOOSE IN 26
65851 | GOOSE IN 27
65852 | GOOSE IN 28
65853 | GOOSE IN 29
65854 | GOOSE IN 30
65855 | GOOSE IN 31
65856 | GOOSE IN 32
65857 | GOOSE IN 33
65858 | GOOSE IN 34
65859 | GOOSE IN 35
65860 | GOOSE IN 36
65861 | GOOSE IN 37
65862 | GOOSE IN 38
65863 | GOOSE IN 39
65864 | GOOSE IN 40
65865 | GOOSE IN 41
65866 | GOOSE IN 42
65867 | GOOSE IN 43
65868 | GOOSE IN 44
65869 | GOOSE IN 45
65870 | GOOSE IN 46
65871 | GOOSE IN 47
65872 | GOOSE IN 48
65873 | GOOSE IN 49
65874 | GOOSE IN 50
65875 | GOOSE IN 51
65876 | GOOSE IN 52
65877 | GOOSE IN 53
65878 | GOOSE IN 54
65879 | GOOSE IN 55
65880 | GOOSE IN 56
65881 | GOOSE IN 57
65882 | GOOSE IN 58
65883 | GOOSE IN 59
65884 | GOOSE IN 60
65885 | GOOSE IN 61
65886 | GOOSE IN 62
65887 | GOOSE IN 63
65888 | GOOSE IN 64
65889 | SYN1 Condition
65890 | SYN2 Condition
65891 | SYN3 Condition
65892 | I0Int> IEF DETECTED
65893 | I0Int> TRIP
65894 | Final Trip Object1
65895 | Final Trip Object2
65896 | Final Trip Object3
65897 | Final Trip Object4
65898 | Final Trip Object5
65899 | Recordings in memory
65900 | Fault locator condition
65901 | AR On
65902 | U1/2 >/< START
65903 | U1/2 >/< TRIP
65904 | U1/2 >>/<< START
65905 | U1/2 >>/<< TRIP
65906 | U1/2 >>>/<<< START
65907 | U1/2 >>>/<<< TRIP
65908 | U1/2 >>>>/<<<< START
65909 | U1/2 >>>>/<<<< TRIP
65910 | PF< START
65911 | PF< TRIP
65912 | V/Hz(1) > START
65913 | V/Hz(1) > TRIP
65914 | I> (50) Alarm
65915 | I0> (50N) Alarm
65916 | Idir> (67) Alarm
65917 | I0dir> (67N) Alarm
65918 | I0int> (67NT) Alarm FWD
65919 | I0int> (67NT) Alarm REV
65920 | U< (27) Alarm
65921 | U< (27) No voltage
65922 | U0> (59N) Alarm
65923 | FL (21FL) Triggered
65924 | AR In Progress
65925 | Force SG change
65926 | Idb> BIAS TRIP
65927 | ALARM 1
65928 | ALARM 2
65929 | ALARM 3
65930 | ALARM 4
65931 | ALARM 5
65932 | ALARM 6
65933 | ALARM 7
65934 | ALARM 8
65935 | ALARM 9
65936 | ALARM 10
65937 | ALARM 11
65938 | ALARM 12
65939 | ALARM 13
65940 | ALARM 14
65941 | ALARM 15
65942 | ALARM 16
65943 | ALARM 17
65944 | ALARM 18
65945 | ALARM 19
65946 | ALARM 20
65947 | ALARM 21
65948 | ALARM 22
65949 | ALARM 23
65950 | ALARM 24
65951 | ALARM 25
65952 | ALARM 26
65953 | ALARM 27
65954 | ALARM 28
65955 | ALARM 29
65956 | ALARM 30
65957 | ALARM 31
65958 | ALARM 32
65959 | ALARM 33
65960 | ALARM 34
65961 | ALARM 35
65962 | ALARM 36
65963 | ALARM 37
65964 | ALARM 38
65965 | ALARM 39
65966 | ALARM 40
65967 | ALARM 41
65968 | ALARM 42
65969 | ALARM 43
65970 | ALARM 44
65971 | ALARM 45
65972 | ALARM 46
65973 | ALARM 47
65974 | ALARM 48
65975 | ALARM 49
65976 | ALARM 50
65977 | ALARM 51
65978 | ALARM 52
65979 | ALARM 53
65980 | ALARM 54
65981 | ALARM 55
65982 | ALARM 56
65983 | ALARM 57
65984 | ALARM 58
65985 | ALARM 59
65986 | ALARM 60
65987 | ALARM 61
65988 | ALARM 62
65989 | ALARM 63
65990 | ALARM 64
65991 | Configuration changed
65992 | Control mode
65993 | Enable input
65994 | U0> RECL Active
65995 | U0> RECL CLOSE
65996 | U0> RECL BLKU0
65997 | AVR Tap in highlimit
65998 | AVR Tap in lowlimit
Double points
IOA | Description
196609 | Object1 Breaker Status
196610 | Object2 Breaker Status
196611 | Object3 Breaker Status
196612 | Object4 Breaker Status
196613 | Object5 Breaker Status
196614 | Object6 Breaker Status
196615 | Object7 Breaker Status
196616 | Object8 Breaker Status
196617 | Object9 Breaker Status
196618 | Object10 Breaker Status
196619 | Ind.1 Object Status
196620 | Ind.2 Object Status
196621 | Ind.3 Object Status
196622 | Ind.4 Object Status
196623 | Ind.5 Object Status
196624 | Object1 Withdraw Status
196625 | Object2 Withdraw Status
196626 | Object3 Withdraw Status
196627 | Object4 Withdraw Status
196628 | Object5 Withdraw Status
196629 | Object6 Withdraw Status
196630 | Object7 Withdraw Status
196631 | Object8 Withdraw Status
196632 | Object9 Withdraw Status
196633 | Object10 Withdraw Status
Measured values
IOA | Description
851969 | Pri.Pha.curr.IL1
851970 | Pha.angle IL1
851971 | Pri.Pha.curr.IL2
851972 | Pha.angle IL2
851973 | Pri.Pha.curr.IL3
851974 | Pha.angle IL3
851975 | Alg f avg
851976 | Pri.Res.curr.I01
851977 | Pri.Res.curr.I02
851978 | System volt UL1 mag
851979 | System volt UL1 ang
851980 | System volt UL2 mag
851981 | System volt UL2 ang
851982 | System volt UL3 mag
851983 | System volt UL3 ang
851984 | System volt UL12 mag
851985 | System volt UL12 ang
851986 | System volt UL23 mag
851987 | System volt UL23 ang
851988 | System volt UL31 mag
851989 | System volt UL31 ang
851990 | System volt U0 mag
851991 | System volt U0 ang
851992 | POW1 3PH Active power (P)
851993 | POW1 3PH Reactive power (Q)
851994 | POW1 3PH Apparent power (S)
851995 | POW1 3PH Cos(phi)
851996 | Recorded fault value
851997 | Recorded fault value
851998 | Recorded fault value
851999 | Recorded fault value
852000 | Recorded fault value
852001 | Recorded fault value
852002 | Recorded fault value
852003 | Recorded fault value
852004 | Recorded fault value
852005 | Recorded fault value
852006 | Recorded fault value
852007 | Recorded fault value
852008 | Last fault reactance
852009 | Last fault distance
852010 | System volt U3 mag
852011 | System volt U4 mag
852012 | Pri.Pha.curr.I''L1
852013 | Pha.angle I''L1
852014 | Pri.Pha.curr.I''L2
852015 | Pha.angle I''L2
852016 | Pri.Pha.curr.I''L3
852017 | Pha.angle I''L3
852018 | S1 Measurement(Raw)
852019 | S2 Measurement(Raw)
852020 | S3 Measurement(Raw)
852021 | S4 Measurement(Raw)
852022 | S5 Measurement(Raw)
852023 | S6 Measurement(Raw)
852024 | S7 Measurement(Raw)
852025 | S8 Measurement(Raw)
852026 | S9 Measurement(Raw)
852027 | S10 Measurement(Raw)
852028 | S11 Measurement(Raw)
852029 | S12 Measurement(Raw)
852030 | S13 Measurement(Raw)
852031 | S14 Measurement(Raw)
852032 | S15 Measurement(Raw)
852033 | S16 Measurement(Raw)
852034 | S7 Measurement mA
852035 | S8 Measurement mA
852036 | S15 Measurement mA
852037 | S16 Measurement mA
852038 | Voltage now
852039 | Voltage difference to set target
852040 | POW1 3PH Tan(phi)
852041 | POW1 L1 Active power (P)
852042 | POW1 L1 Reactive power (Q)
852043 | POW1 L1 Apparent power (S)
852044 | POW1 L1 Cos(phi)
852045 | POW1 L1 Tan(phi)
852046 | POW1 L2 Active power (P)
852047 | POW1 L2 Reactive power (Q)
852048 | POW1 L2 Apparent power (S)
852049 | POW1 L2 Cos(phi)
852050 | POW1 L2 Tan(phi)
852051 | POW1 L3 Active power (P)
852052 | POW1 L3 Reactive power (Q)
852053 | POW1 L3 Apparent power (S)
852054 | POW1 L3 Cos(phi)
852055 | POW1 L3 Tan(phi)
852056 | MBIO ModA Ch0 Input value
852057 | MBIO ModA Ch1 Input value
852058 | MBIO ModA Ch2 Input value
852059 | MBIO ModA Ch3 Input value
852060 | MBIO ModA Ch4 Input value
852061 | MBIO ModA Ch5 Input value
852062 | MBIO ModA Ch6 Input value
852063 | MBIO ModA Ch7 Input value
852064 | MBIO ModB Ch0 Input value
852065 | MBIO ModB Ch1 Input value
852066 | MBIO ModB Ch2 Input value
852067 | MBIO ModB Ch3 Input value
852068 | MBIO ModB Ch4 Input value
852069 | MBIO ModB Ch5 Input value
852070 | MBIO ModB Ch6 Input value
852071 | MBIO ModB Ch7 Input value
852072 | MBIO ModC Ch0 Input value
852073 | MBIO ModC Ch1 Input value
852074 | MBIO ModC Ch2 Input value
852075 | MBIO ModC Ch3 Input value
852076 | MBIO ModC Ch4 Input value
852077 | MBIO ModC Ch5 Input value
852078 | MBIO ModC Ch6 Input value
852079 | MBIO ModC Ch7 Input value
852080 | System volt U0 mag(%)
852081 | Curve1 Output
852082 | Curve2 Output
852083 | Curve3 Output
852084 | Curve4 Output
Integrated totals
IOA | Description
983041 | Internal Relay Fault status
983042 | Export Active Energy (P) kWh
983043 | Import Active Energy (P) kWh
983044 | Imported (Q) while Export (P) kVarh
983045 | Imported (Q) while Import (P) kVarh
983046 | Recordings in memory
983047 | Max amount of recordings
983048 | Active setting group
983049 | Tap location now (- 0 +)
983050 | Absolute tap location
983051 | DI1 Counter
983052 | DI2 Counter
983053 | DI3 Counter
983054 | DI4 Counter
983055 | DI5 Counter
983056 | DI6 Counter
983057 | DI7 Counter
983058 | DI8 Counter
983059 | DI9 Counter
983060 | DI10 Counter
983061 | DI11 Counter
983062 | DI12 Counter
983063 | DI13 Counter
983064 | DI14 Counter
983065 | DI15 Counter
983066 | DI16 Counter
983067 | DI17 Counter
983068 | DI18 Counter
983069 | DI19 Counter
983070 | DI20 Counter
983071 | DI21 Counter
983072 | DI22 Counter
983073 | DI23 Counter
983074 | DI24 Counter
983075 | DI25 Counter
983076 | DI26 Counter
983077 | DI27 Counter
983078 | DI28 Counter
983079 | DI29 Counter
983080 | DI30 Counter
983081 | DI31 Counter
983082 | DI32 Counter
983083 | DI33 Counter
983084 | DI34 Counter
983085 | DI35 Counter
983086 | DI36 Counter
983087 | DI37 Counter
983088 | DI38 Counter
983089 | DI39 Counter
983090 | DI40 Counter
983091 | DI41 Counter
983092 | DI42 Counter
983093 | DI43 Counter
983094 | DI44 Counter
983095 | DI45 Counter
983096 | DI46 Counter
983097 | DI47 Counter
983098 | DI48 Counter
983099 | DI49 Counter
983100 | DI50 Counter
983101 | DI51 Counter
Single commands
IOA | Description
2949121 | Reset Latches
2949122 | Logical Input 1
2949123 | Logical Input 2
2949124 | Logical Input 3
2949125 | Logical Input 4
2949126 | Logical Input 5
2949127 | Logical Input 6
2949128 | Logical Input 7
2949129 | Logical Input 8
2949130 | Logical Input 9
2949131 | Logical Input 10
2949132 | Logical Input 11
2949133 | Logical Input 12
2949134 | Logical Input 13
2949135 | Logical Input 14
2949136 | Logical Input 15
2949137 | Logical Input 16
2949138 | Logical Input 17
2949139 | Logical Input 18
2949140 | Logical Input 19
2949141 | Logical Input 20
2949142 | Logical Input 21
2949143 | Logical Input 22
2949144 | Logical Input 23
2949145 | Logical Input 24
2949146 | Logical Input 25
2949147 | Logical Input 26
2949148 | Logical Input 27
2949149 | Logical Input 28
2949150 | Logical Input 29
2949151 | Logical Input 30
2949152 | Logical Input 31
2949153 | Logical Input 32
2949154 | PCS1 Switch Status
2949155 | PCS2 Switch Status
2949156 | PCS3 Switch Status
2949157 | PCS4 Switch Status
2949158 | PCS5 Switch Status
2949159 | AVR to Manual control
Double commands
IOA | Description
3014657 | OBJECT1 CTRL
3014658 | OBJECT2 CTRL
3014659 | OBJECT3 CTRL
3014660 | OBJECT4 CTRL
3014661 | OBJECT5 CTRL
3014662 | OBJECT6 CTRL
3014663 | OBJECT7 CTRL
3014664 | OBJECT8 CTRL
3014665 | OBJECT9 CTRL
3014666 | OBJECT10 CTRL

## AQ 250 v.2.5.7.1-400 AP3
Single points
IOA | Description
65537 | Local/Remote switch
65538 | DI1
65539 | DI2
65540 | DI3
65541 | DI4
65542 | DI5
65543 | DI6
65544 | DI7
65545 | DI8
65546 | DI9
65547 | DI10
65548 | DI11
65549 | DI12
65550 | DI13
65551 | DI14
65552 | DI15
65553 | DI16
65554 | DI17
65555 | DI18
65556 | DI19
65557 | DI20
65558 | DI21
65559 | DI22
65560 | DI23
65561 | DI24
65562 | DI25
65563 | DI26
65564 | DI27
65565 | DI28
65566 | DI29
65567 | DI30
65568 | DI31
65569 | DI32
65570 | DI33
65571 | DI34
65572 | DI35
65573 | DI36
65574 | DI37
65575 | DI38
65576 | DI39
65577 | DI40
65578 | DI41
65579 | DI42
65580 | DI43
65581 | DI44
65582 | DI45
65583 | DI46
65584 | DI47
65585 | DI48
65586 | DI49
65587 | DI50
65588 | DI51
65589 | I> START (General)
65590 | I> TRIP (General)
65591 | I>> START (General)
65592 | I>> TRIP (General)
65593 | I>>> START (General)
65594 | I>>> TRIP (General)
65595 | I>>>> START (General)
65596 | I>>>> TRIP (General)
65597 | I0> START
65598 | I0> TRIP
65599 | I0>> START
65600 | I0>> TRIP
65601 | I0>>> START
65602 | I0>>> TRIP
65603 | I0>>>> START
65604 | I0>>>> TRIP
65605 | Ih> START
65606 | Ih>> START
65607 | Ih>>> START
65608 | Ih>>>> START
65609 | I2> START
65610 | I2> TRIP
65611 | I2>> START
65612 | I2>> TRIP
65613 | I2>>> START
65614 | I2>>> TRIP
65615 | I2>>>> START
65616 | I2>>>> TRIP
65617 | CLP condition (Curr Low)
65618 | CLP condition (Overcurrent)
65619 | CBFP condition (Start)
65620 | CBFP condition (CBFP On)
65621 | Operate for IEC61850
65622 | AR1 Request On
65623 | AR2 Request On
65624 | AR3 Request On
65625 | AR4 Request On
65626 | AR5 Request On
65627 | AR Shot 1 Running
65628 | AR Shot 2 Running
65629 | AR Shot 3 Running
65630 | AR Shot 4 Running
65631 | AR Shot 5 Running
65632 | AR Sequence finished
65633 | AR Final Trip
65634 | ARC time on
65635 | Gen. reclaim time on
65636 | NTP quality
65637 | AR Lockout after successfull sequence
65638 | AR Operation Inhibit
65639 | AR Locked
65640 | TF> Alarm1
65641 | TF> Trip
65642 | Internal Relay Fault active
65643 | I0d> TRIP
65644 | CBW Alarm 1 act
65645 | CBW Alarm 2 act
65646 | CTS1 ALARM
65647 | Logical Output 1
65648 | Logical Output 2
65649 | Logical Output 3
65650 | Logical Output 4
65651 | Logical Output 5
65652 | Logical Output 6
65653 | Logical Output 7
65654 | Logical Output 8
65655 | Logical Output 9
65656 | Logical Output 10
65657 | Logical Output 11
65658 | Logical Output 12
65659 | Logical Output 13
65660 | Logical Output 14
65661 | Logical Output 15
65662 | Logical Output 16
65663 | Logical Output 17
65664 | Logical Output 18
65665 | Logical Output 19
65666 | Logical Output 20
65667 | Logical Output 21
65668 | Logical Output 22
65669 | Logical Output 23
65670 | Logical Output 24
65671 | Logical Output 25
65672 | Logical Output 26
65673 | Logical Output 27
65674 | Logical Output 28
65675 | Logical Output 29
65676 | Logical Output 30
65677 | Logical Output 31
65678 | Logical Output 32
65679 | Logical Input 1
65680 | Logical Input 2
65681 | Logical Input 3
65682 | Logical Input 4
65683 | Logical Input 5
65684 | Logical Input 6
65685 | Logical Input 7
65686 | Logical Input 8
65687 | Logical Input 9
65688 | Logical Input 10
65689 | Logical Input 11
65690 | Logical Input 12
65691 | Logical Input 13
65692 | Logical Input 14
65693 | Logical Input 15
65694 | Logical Input 16
65695 | Logical Input 17
65696 | Logical Input 18
65697 | Logical Input 19
65698 | Logical Input 20
65699 | Logical Input 21
65700 | Logical Input 22
65701 | Logical Input 23
65702 | Logical Input 24
65703 | Logical Input 25
65704 | Logical Input 26
65705 | Logical Input 27
65706 | Logical Input 28
65707 | Logical Input 29
65708 | Logical Input 30
65709 | Logical Input 31
65710 | Logical Input 32
65711 | Object1 Open Enabled
65712 | Object1 Close Enabled
65713 | Object2 Open Enabled
65714 | Object2 Close Enabled
65715 | Object3 Open Enabled
65716 | Object3 Close Enabled
65717 | Object4 Open Enabled
65718 | Object4 Close Enabled
65719 | Object5 Open Enabled
65720 | Object5 Close Enabled
65721 | Object6 Open Enabled
65722 | Object6 Close Enabled
65723 | Object7 Open Enabled
65724 | Object7 Close Enabled
65725 | Object8 Open Enabled
65726 | Object8 Close Enabled
65727 | Object9 Open Enabled
65728 | Object9 Close Enabled
65729 | Object10 Open Enabled
65730 | Object10 Close Enabled
65731 | Idir> START
65732 | Idir> TRIP
65733 | Idir>> START
65734 | Idir>> TRIP
65735 | Idir>>> START
65736 | Idir>>> TRIP
65737 | Idir>>>> START
65738 | Idir>>>> TRIP
65739 | N> One start remaining (Alarm)
65740 | N> INHIBIT ON (General)
65741 | TM> Trip
65742 | TM> Restart Inh.
65743 | ISt> START
65744 | ISt> Set time TRIP
65745 | Motor stopped
65746 | Motor starting
65747 | Motor running
65748 | Motor stalled
65749 | Missing phase
65750 | Load normal
65751 | Overloading
65752 | High overcurrent
65753 | I< START
65754 | I< TRIP
65755 | Im> START
65756 | Im> TRIP
65757 | U> START
65758 | U> TRIP
65759 | U>> START
65760 | U>>> START
65761 | U>>> TRIP
65762 | U>>>> START
65763 | U>>>> TRIP
65764 | U>> TRIP
65765 | U0> START
65766 | U0> TRIP
65767 | U0>> START
65768 | U0>> TRIP
65769 | U0>>> START
65770 | U0>>> TRIP
65771 | U0>>>> START
65772 | U0>>>> TRIP
65773 | U< START
65774 | U< TRIP
65775 | U<< START
65776 | U<< TRIP
65777 | U<<< START
65778 | U<<< TRIP
65779 | U<<<< START
65780 | U<<<< TRIP
65781 | VTS Start
65782 | VTS Fail Alarm Line
65783 | VTS Fail Alarm Bus
65784 | SOTF Active
65785 | SOTF Trip
65786 | I0dir> START (General)
65787 | I0dir> TRIP (General)
65788 | I0dir>> START (General)
65789 | I0dir>> TRIP (General)
65790 | I0dir>>> START (General)
65791 | I0dir>>> TRIP (General)
65792 | I0dir>>>> START (General)
65793 | I0dir>>>> TRIP (General)
65794 | P> START (OBSOLETE)
65795 | P> TRIP (OBSOLETE)
65796 | Prev> START (OBSOLETE)
65797 | Prev> TRIP (OBSOLETE)
65798 | P< START (OBSOLETE)
65799 | P< TRIP (OBSOLETE)
65800 | f> START
65801 | f> TRIP
65802 | f>> START
65803 | f>> TRIP
65804 | f>>> START
65805 | f>>> TRIP
65806 | f>>>> START
65807 | f>>>> TRIP
65808 | f< START
65809 | f< TRIP
65810 | f<< START
65811 | f<< TRIP
65812 | f<<< START
65813 | f<<< TRIP
65814 | f<<<< START
65815 | f<<<< TRIP
65816 | I/I0 Arc> Zone1 TRIP
65817 | I/I0 Arc> Zone2 TRIP
65818 | I/I0 Arc> Zone3 TRIP
65819 | I/I0 Arc> Zone4 TRIP
65820 | PCS1 Switch Status
65821 | PCS2 Switch Status
65822 | PCS3 Switch Status
65823 | PCS4 Switch Status
65824 | PCS5 Switch Status
65825 | GOOSE IN 1 boolean value
65826 | GOOSE IN 2 boolean value
65827 | GOOSE IN 3 boolean value
65828 | GOOSE IN 4 boolean value
65829 | GOOSE IN 5 boolean value
65830 | GOOSE IN 6 boolean value
65831 | GOOSE IN 7 boolean value
65832 | GOOSE IN 8 boolean value
65833 | GOOSE IN 9 boolean value
65834 | GOOSE IN 10 boolean value
65835 | GOOSE IN 11 boolean value
65836 | GOOSE IN 12 boolean value
65837 | GOOSE IN 13 boolean value
65838 | GOOSE IN 14 boolean value
65839 | GOOSE IN 15 boolean value
65840 | GOOSE IN 16 boolean value
65841 | GOOSE IN 17 boolean value
65842 | GOOSE IN 18 boolean value
65843 | GOOSE IN 19 boolean value
65844 | GOOSE IN 20 boolean value
65845 | GOOSE IN 21 boolean value
65846 | GOOSE IN 22 boolean value
65847 | GOOSE IN 23 boolean value
65848 | GOOSE IN 24 boolean value
65849 | GOOSE IN 25 boolean value
65850 | GOOSE IN 26 boolean value
65851 | GOOSE IN 27 boolean value
65852 | GOOSE IN 28 boolean value
65853 | GOOSE IN 29 boolean value
65854 | GOOSE IN 30 boolean value
65855 | GOOSE IN 31 boolean value
65856 | GOOSE IN 32 boolean value
65857 | GOOSE IN 33 boolean value
65858 | GOOSE IN 34 boolean value
65859 | GOOSE IN 35 boolean value
65860 | GOOSE IN 36 boolean value
65861 | GOOSE IN 37 boolean value
65862 | GOOSE IN 38 boolean value
65863 | GOOSE IN 39 boolean value
65864 | GOOSE IN 40 boolean value
65865 | GOOSE IN 41 boolean value
65866 | GOOSE IN 42 boolean value
65867 | GOOSE IN 43 boolean value
65868 | GOOSE IN 44 boolean value
65869 | GOOSE IN 45 boolean value
65870 | GOOSE IN 46 boolean value
65871 | GOOSE IN 47 boolean value
65872 | GOOSE IN 48 boolean value
65873 | GOOSE IN 49 boolean value
65874 | GOOSE IN 50 boolean value
65875 | GOOSE IN 51 boolean value
65876 | GOOSE IN 52 boolean value
65877 | GOOSE IN 53 boolean value
65878 | GOOSE IN 54 boolean value
65879 | GOOSE IN 55 boolean value
65880 | GOOSE IN 56 boolean value
65881 | GOOSE IN 57 boolean value
65882 | GOOSE IN 58 boolean value
65883 | GOOSE IN 59 boolean value
65884 | GOOSE IN 60 boolean value
65885 | GOOSE IN 61 boolean value
65886 | GOOSE IN 62 boolean value
65887 | GOOSE IN 63 boolean value
65888 | GOOSE IN 64 boolean value
65889 | SYN1 Condition
65890 | SYN2 Condition
65891 | SYN3 Condition
65892 | I0Int> IEF DETECTED
65893 | I0Int> TRIP
65894 | Final Trip Object1
65895 | Final Trip Object2
65896 | Final Trip Object3
65897 | Final Trip Object4
65898 | Final Trip Object5
65899 | Recordings in memory
65900 | Fault locator condition
65901 | AR On
65902 | U1/2 >/< START
65903 | U1/2 >/< TRIP
65904 | U1/2 >>/<< START
65905 | U1/2 >>/<< TRIP
65906 | U1/2 >>>/<<< START
65907 | U1/2 >>>/<<< TRIP
65908 | U1/2 >>>>/<<<< START
65909 | U1/2 >>>>/<<<< TRIP
65910 | PF< START
65911 | PF< TRIP
65912 | V/Hz(1) > START
65913 | V/Hz(1) > TRIP
65914 | I> (50) Alarm
65915 | I0> (50N) Alarm
65916 | Idir> (67) Alarm
65917 | I0dir> (67N) Alarm
65918 | I0int> (67NT) Alarm FWD
65919 | I0int> (67NT) Alarm REV
65920 | U< (27) Alarm
65921 | U< (27) No voltage
65922 | U0> (59N) Alarm
65923 | FL (21FL) Triggered
65924 | AR In Progress
65925 | Force setting group change
65926 | Idb> BIAS TRIP
65927 | ALARM 1
65928 | ALARM 2
65929 | ALARM 3
65930 | ALARM 4
65931 | ALARM 5
65932 | ALARM 6
65933 | ALARM 7
65934 | ALARM 8
65935 | ALARM 9
65936 | ALARM 10
65937 | ALARM 11
65938 | ALARM 12
65939 | ALARM 13
65940 | ALARM 14
65941 | ALARM 15
65942 | ALARM 16
65943 | ALARM 17
65944 | ALARM 18
65945 | ALARM 19
65946 | ALARM 20
65947 | ALARM 21
65948 | ALARM 22
65949 | ALARM 23
65950 | ALARM 24
65951 | ALARM 25
65952 | ALARM 26
65953 | ALARM 27
65954 | ALARM 28
65955 | ALARM 29
65956 | ALARM 30
65957 | ALARM 31
65958 | ALARM 32
65959 | ALARM 33
65960 | ALARM 34
65961 | ALARM 35
65962 | ALARM 36
65963 | ALARM 37
65964 | ALARM 38
65965 | ALARM 39
65966 | ALARM 40
65967 | ALARM 41
65968 | ALARM 42
65969 | ALARM 43
65970 | ALARM 44
65971 | ALARM 45
65972 | ALARM 46
65973 | ALARM 47
65974 | ALARM 48
65975 | ALARM 49
65976 | ALARM 50
65977 | ALARM 51
65978 | ALARM 52
65979 | ALARM 53
65980 | ALARM 54
65981 | ALARM 55
65982 | ALARM 56
65983 | ALARM 57
65984 | ALARM 58
65985 | ALARM 59
65986 | ALARM 60
65987 | ALARM 61
65988 | ALARM 62
65989 | ALARM 63
65990 | ALARM 64
65991 | Configuration changed
65992 | Control mode
65993 | U0> RECL Blocked
65994 | U0> RECL Active
65995 | U0> RECL CLOSE
65996 | U0> RECL BLKU0
65997 | AVR Tap in highlimit
65998 | AVR Tap in lowlimit
65999 | Idi> NOBIAS TRIP
66000 | Q< START
66001 | Q< TRIP
66002 | TM> Alarm1
66003 | TM> Alarm2
66004 | GSYN Blocked
66005 | GSYN Running
66006 | GSYN Increase Voltage
66007 | GSYN Decrease Voltage
66008 | GSYN Increase Frequency
66009 | GSYN Decrease Frequency
66010 | GSYN Breaker Close Pulse
66011 | GSYN Long Sync Time
66012 | GMAG AVR Mode
66013 | GMAG FCR Mode
66014 | GMAG MVAR Mode
66015 | GMAG PF Mode
66016 | GMAG Field Breaker is closed
66017 | GMAG Excitation Off
66018 | GMAG Field Breaker is open
66019 | GMAG Synchronised
66020 | GMAG Islandmode
66021 | GMAG Test mode on
66022 | GMAG Reset On
66023 | GMAG Excitation run order
66024 | GMAG Overriding control
66025 | GMAG Increase MVar PF
66026 | GMAG Decrease MVar PF
66027 | GMAG New reference start
66028 | GMAG GB is closed
66029 | GMAG Field breaker is open Gen breaker is Closed
66030 | GMAG Following line volt
66031 | GMAG Test square enabled
66032 | GMAG Reactive power unloaded
66033 | GMAG AVR Start Ref
66034 | GMAG FCR Start Ref
66035 | GMAG Excitation On
66036 | GMAG Field current limiter active
66037 | GMAG VHZ limit active
66038 | GMAG Under excitation limiter active
66039 | GMAG Stator current limiter overexcited active
66040 | GMAG Stator current limiter underexcited active
66041 | GMAG High active current
66042 | GMAG Instantaneous field current limiter
66043 | GMAG Overcurrent
66044 | GMAG Low measured voltage
66045 | GMAG Phase retard
66046 | GMAG Field flashing
66047 | GMAG Long field flashing
66048 | GMAG Low Q Error
66049 | GMAG Field breaker does not open
66050 | GMAG Disturbed mode
66051 | GMAG Disturbed mode pulse
66052 | GMAG AVR ref on low limit
66053 | GMAG AVR ref on high limit
66054 | GMAG FCR ref on low limit
66055 | GMAG FCR ref on high limit
66056 | GMAG Mvar ref on highlimit
66057 | GMAG Mvar ref on lowlimit
66058 | GMAG PF ref on highlimit
66059 | GMAG PF ref on lowlimit
66060 | GMAG Reset and excitation off
66061 | GMAG Low supply voltage
66062 | GMAG IGBT shorted
66063 | GMAG PWM Enabled
66064 | GMAG PWM AC1 On
66065 | GMAG PWM DC1 On
66066 | GMAG Rectifier trip
66067 | GMAG Bridge1 temperature high
66068 | GMAG Bridge2 temperature high
66069 | GMAG Diode fault
66070 | GMAG Bridge 1 DI1 Signal
66071 | GMAG Bridge 1 DI2 Signal
66072 | GMAG Bridge 1 DI3 Signal
66073 | GMAG Bridge 1 DI4 Signal
66074 | GMAG Bridge 1 DI5 Signal
66075 | GMAG Bridge 1 DI6 Signal
66076 | GMAG Bridge 1 DI7 Signal
66077 | GMAG Bridge 1 DI8 Signal
66078 | IPW> START (General)
66079 | IPW> START (Phase A)
66080 | IPW> START (Phase B)
66081 | IPW> START (Phase C)
66082 | IPW> TRIP (General)
66083 | IPW> TRIP (Phase A)
66084 | IPW> TRIP (Phase B)
66085 | IPW> TRIP (Phase C)
66086 | IPW>> START (General)
66087 | IPW>> START (Phase A)
66088 | IPW>> START (Phase B)
66089 | IPW>> START (Phase C)
66090 | IPW>> TRIP (General)
66091 | IPW>> TRIP (Phase A)
66092 | IPW>> TRIP (Phase B)
66093 | IPW>> TRIP (Phase C)
66094 | DI52
66095 | DI53
66096 | DI54
66097 | DI55
66098 | DI56
66099 | DI57
66100 | DI58
66101 | DI59
66102 | DI60
66103 | DI61
66104 | DI62
66105 | DI63
66106 | DI64
66107 | DI65
66108 | DI66
66109 | DI67
66110 | DI68
66111 | DI69
66112 | DI70
66113 | DI71
66114 | DI72
66115 | DI73
66116 | DI74
66117 | DI75
66118 | DI76
66119 | DI77
66120 | DI78
66121 | DI79
66122 | DI80
66123 | DI81
66124 | DI82
66125 | DI83
66126 | DI84
66127 | DI85
66128 | DI86
66129 | DI87
66130 | DI88
66131 | DI89
66132 | DI90
66133 | DI91
66134 | DI92
66135 | DI93
66136 | DI94
66137 | DI95
66138 | DI96
66139 | DI97
66140 | DI98
66141 | DI99
66142 | DI100
66143 | DI101
66144 | DI102
66145 | DI103
66146 | DI104
66147 | DI105
66148 | DI106
66149 | DI107
66150 | DI108
66151 | DI109
66152 | DI110
66153 | DI111
66154 | DI112
66155 | DI113
66156 | DI114
66157 | DI115
66158 | Logical Output 33
66159 | Logical Output 34
66160 | Logical Output 35
66161 | Logical Output 36
66162 | Logical Output 37
66163 | Logical Output 38
66164 | Logical Output 39
66165 | Logical Output 40
66166 | Logical Output 41
66167 | Logical Output 42
66168 | Logical Output 43
66169 | Logical Output 44
66170 | Logical Output 45
66171 | Logical Output 46
66172 | Logical Output 47
66173 | Logical Output 48
66174 | Logical Output 49
66175 | Logical Output 50
66176 | Logical Output 51
66177 | Logical Output 52
66178 | Logical Output 53
66179 | Logical Output 54
66180 | Logical Output 55
66181 | Logical Output 56
66182 | Logical Output 57
66183 | Logical Output 58
66184 | Logical Output 59
66185 | Logical Output 60
66186 | Logical Output 61
66187 | Logical Output 62
66188 | Logical Output 63
66189 | Logical Output 64
66190 | ALARM 65
66191 | ALARM 66
66192 | ALARM 67
66193 | ALARM 68
66194 | ALARM 69
66195 | ALARM 70
66196 | ALARM 71
66197 | ALARM 72
66198 | ALARM 73
66199 | ALARM 74
66200 | ALARM 75
66201 | ALARM 76
66202 | ALARM 77
66203 | ALARM 78
66204 | ALARM 79
66205 | ALARM 80
66206 | ALARM 81
66207 | ALARM 82
66208 | ALARM 83
66209 | ALARM 84
66210 | ALARM 85
66211 | ALARM 86
66212 | ALARM 87
66213 | ALARM 88
66214 | ALARM 89
66215 | ALARM 90
66216 | ALARM 91
66217 | ALARM 92
66218 | ALARM 93
66219 | ALARM 94
66220 | ALARM 95
66221 | ALARM 96
66222 | ALARM 97
66223 | ALARM 98
66224 | ALARM 99
66225 | ALARM 100
66226 | ALARM 101
66227 | ALARM 102
66228 | ALARM 103
66229 | ALARM 104
66230 | ALARM 105
66231 | ALARM 106
66232 | ALARM 107
66233 | ALARM 108
66234 | ALARM 109
66235 | ALARM 110
66236 | ALARM 111
66237 | ALARM 112
66238 | ALARM 113
66239 | ALARM 114
66240 | ALARM 115
66241 | ALARM 116
66242 | ALARM 117
66243 | ALARM 118
66244 | ALARM 119
66245 | ALARM 120
66246 | ALARM 121
66247 | ALARM 122
66248 | ALARM 123
66249 | ALARM 124
66250 | ALARM 125
66251 | ALARM 126
66252 | ALARM 127
66253 | ALARM 128
66254 | I0x> START (forward)
66255 | I0x> TRIP (forward)
66256 | I0x> START (reverse)
66257 | I0x> TRIP (reverse)
66258 | I0x> BLOCKED
66259 | PFC switching on condition
66260 | Control mode
66261 | PFC> BLOCKED
66262 | Bank 1 discharging
66263 | Bank 2 discharging
66264 | Bank 3 discharging
66265 | Bank 4 discharging
66266 | Bank 5 discharging
66267 | Bank 1 switching failure
66268 | CTS2 ALARM
66269 | Cap+ starting
66270 | Cap+ request pulse
66271 | Cap- starting
66272 | Cap- request pulse
66273 | Auto/Manual status to mimic
66274 | AVR tap control status
66275 | AVR/block: Tap differential failure
66276 | AVR/block: Parallel communication failure
66277 | ICOL> [49OL] START (General)
66278 | ICOL> [49OL] TRIP (General)
66279 | ICOL> [49OL] BLOCKED
66280 | ICOL>> [49OL] START (General)
66281 | ICOL>> [49OL] TRIP (General)
66282 | ICOL>> [49OL] BLOCKED
66283 | CNU> [50UB] ALARM START
66284 | CNU> [50UB] ALARM ON
66285 | CNU> [50UB] START
66286 | CNU> [50UB] TRIP
66287 | CNU> [50UB] BLOCKED
66288 | IdLi> NOBIAS TRIP
66289 | IdLi> NOBIAS BLOCKED
66290 | IdLb> BIAS TRIP
66291 | IdLb> BIAS BLOCKED
66292 | HSO1 TCS input
66293 | HSO2 TCS input
66294 | HSO3 TCS input
66295 | HSO4 TCS input
66296 | HSO5 TCS input
66297 | HSO6 TCS input
66298 | HSO7 TCS input
66299 | HSO8 TCS input
66300 | HSO9 TCS input
66301 | LVRT START
66302 | LVRT TRIP
66303 | LVRT BLOCKED
66304 | PVPS Any line protection failure
66305 | PVPS Line comm failure
66306 | PVPS Synchronization lost
66307 | Demand blocked
66308 | Fault register trigger
66309 | Z< Z1PP Zone START
66310 | Z< Z1PP Zone TRIP
66311 | Z< Z1PP Zone BLOCKED
66312 | Z< Z2PP Zone START
66313 | Z< Z2PP Zone TRIP
66314 | Z< Z2PP Zone BLOCKED
66315 | Z< Z3PP Zone START
66316 | Z< Z3PP Zone TRIP
66317 | Z< Z3PP Zone BLOCKED
66318 | Z< Z4PP Zone START
66319 | Z< Z4PP Zone TRIP
66320 | Z< Z4PP Zone BLOCKED
66321 | Z< Z5PP Zone START
66322 | Z< Z5PP Zone TRIP
66323 | Z< Z5PP Zone BLOCKED
66324 | Z< Z6PP Zone START
66325 | Z< Z6PP Zone TRIP
66326 | Z< Z6PP Zone BLOCKED
66327 | Z< Z7PP Zone START
66328 | Z< Z7PP Zone TRIP
66329 | Z< Z7PP Zone BLOCKED
66330 | Z< Z8PP Zone START
66331 | Z< Z8PP Zone TRIP
66332 | Z< Z8PP Zone BLOCKED
66333 | Z< Z9PP Zone START
66334 | Z< Z9PP Zone TRIP
66335 | Z< Z9PP Zone BLOCKED
66336 | Z< Z10PP Zone START
66337 | Z< Z10PP Zone TRIP
66338 | Z< Z10PP Zone BLOCKED
66339 | Z< Z1PE Zone START
66340 | Z< Z1PE Zone TRIP
66341 | Z< Z1PE Zone BLOCKED
66342 | Z< Z2PE Zone START
66343 | Z< Z2PE Zone TRIP
66344 | Z< Z2PE Zone BLOCKED
66345 | Z< Z3PE Zone START
66346 | Z< Z3PE Zone TRIP
66347 | Z< Z3PE Zone BLOCKED
66348 | Z< Z4PE Zone START
66349 | Z< Z4PE Zone TRIP
66350 | Z< Z4PE Zone BLOCKED
66351 | Z< Z5PE Zone START
66352 | Z< Z5PE Zone TRIP
66353 | Z< Z5PE Zone BLOCKED
66354 | Z< Z6PE Zone START
66355 | Z< Z6PE Zone TRIP
66356 | Z< Z6PE Zone BLOCKED
66357 | Z< Z7PE Zone START
66358 | Z< Z7PE Zone TRIP
66359 | Z< Z7PE Zone BLOCKED
66360 | Z< Z8PE Zone START
66361 | Z< Z8PE Zone TRIP
66362 | Z< Z8PE Zone BLOCKED
66363 | Z< Z9PE Zone START
66364 | Z< Z9PE Zone TRIP
66365 | Z< Z9PE Zone BLOCKED
66366 | Z< Z10PE Zone START
66367 | Z< Z10PE Zone TRIP
66368 | Z< Z10PE Zone BLOCKED
66369 | Iv> START
66370 | Iv> TRIP
66371 | Iv> BLOCKED
66372 | PS1 >/< START
66373 | PS1 >/< TRIP
66374 | PS1 >/< BLOCKED
66375 | PS2 >/< START
66376 | PS2 >/< TRIP
66377 | PS2 >/< BLOCKED
66378 | PS3 >/< START
66379 | PS3 >/< TRIP
66380 | PS3 >/< BLOCKED
66381 | PS4 >/< START
66382 | PS4 >/< TRIP
66383 | PS4 >/< BLOCKED
66384 | PS5 >/< START
66385 | PS5 >/< TRIP
66386 | PS5 >/< BLOCKED
66387 | PS6 >/< START
66388 | PS6 >/< TRIP
66389 | PS6 >/< BLOCKED
66390 | PS7 >/< START
66391 | PS7 >/< TRIP
66392 | PS7 >/< BLOCKED
66393 | PS8 >/< START
66394 | PS8 >/< TRIP
66395 | PS8 >/< BLOCKED
66396 | PS9 >/< START
66397 | PS9 >/< TRIP
66398 | PS9 >/< BLOCKED
66399 | PS10 >/< START
66400 | PS10 >/< TRIP
66401 | PS10 >/< BLOCKED
66402 | PQS>/< START
66403 | PQS>/< TRIP
66404 | PQS>/< BLOCKED
66405 | PQS>>/<< START
66406 | PQS>>/<< TRIP
66407 | PQS>>/<< BLOCKED
66408 | PQS>>>/<<< START
66409 | PQS>>>/<<< TRIP
66410 | PQS>>>/<<< BLOCKED
66411 | PQS>>>>/<<<< START
66412 | PQS>>>>/<<<< TRIP
66413 | PQS>>>>/<<<< BLOCKED
66414 | df/dt >/< (1) START
66415 | df/dt >/< (1) TRIP
66416 | df/dt >/< (1) BLOCKED
66417 | df/dt >/< (2) START
66418 | df/dt >/< (2) TRIP
66419 | df/dt >/< (2) BLOCKED
66420 | df/dt >/< (3) START
66421 | df/dt >/< (3) TRIP
66422 | df/dt >/< (3) BLOCKED
66423 | df/dt >/< (4) START
66424 | df/dt >/< (4) TRIP
66425 | df/dt >/< (4) BLOCKED
66426 | df/dt >/< (5) START
66427 | df/dt >/< (5) TRIP
66428 | df/dt >/< (5) BLOCKED
66429 | df/dt >/< (6) START
66430 | df/dt >/< (6) TRIP
66431 | df/dt >/< (6) BLOCKED
66432 | df/dt >/< (7) START
66433 | df/dt >/< (7) TRIP
66434 | df/dt >/< (7) BLOCKED
66435 | df/dt >/< (8) START
66436 | df/dt >/< (8) TRIP
66437 | df/dt >/< (8) BLOCKED
66438 | Z< START
66439 | Z< TRIP
66440 | Z< BLOCKED
66441 | Z<< START
66442 | Z<< TRIP
66443 | Z<< BLOCKED
66444 | Q< BLOCKED
66445 | X< START
66446 | X< TRIP
66447 | X< BLOCKED
66448 | X<< START
66449 | X<< TRIP
66450 | X<< BLOCKED
66451 | I>U< I.A.E. START
66452 | I>U< I.A.E. TRIP
66453 | I>U< I.A.E. BLOCKED
66454 | U1/2 >/< BLOCKED
66455 | U1/2 >>/<< BLOCKED
66456 | U1/2 >>>/<<< BLOCKED
66457 | U1/2 >>>>/<<<< BLOCKED
Double points
IOA | Description
196609 | Object1 Breaker Status
196610 | Object2 Breaker Status
196611 | Object3 Breaker Status
196612 | Object4 Breaker Status
196613 | Object5 Breaker Status
196614 | Object6 Breaker Status
196615 | Object7 Breaker Status
196616 | Object8 Breaker Status
196617 | Object9 Breaker Status
196618 | Object10 Breaker Status
196619 | Ind.1 Object Status
196620 | Ind.2 Object Status
196621 | Ind.3 Object Status
196622 | Ind.4 Object Status
196623 | Ind.5 Object Status
196624 | Object1 Withdraw Status
196625 | Object2 Withdraw Status
196626 | Object3 Withdraw Status
196627 | Object4 Withdraw Status
196628 | Object5 Withdraw Status
196629 | Object6 Withdraw Status
196630 | Object7 Withdraw Status
196631 | Object8 Withdraw Status
196632 | Object9 Withdraw Status
196633 | Object10 Withdraw Status
196634 | Ind.6 Object Status
196635 | Ind.7 Object Status
196636 | Ind.8 Object Status
196637 | Ind.9 Object Status
196638 | Ind.10 Object Status
196639 | Ind.11 Object Status
196640 | Ind.12 Object Status
196641 | Ind.13 Object Status
196642 | Ind.14 Object Status
196643 | Ind.15 Object Status
196644 | Ind.16 Object Status
196645 | Ind.17 Object Status
196646 | Ind.18 Object Status
196647 | Ind.19 Object Status
196648 | Ind.20 Object Status
196649 | Phase-wise object Breaker Status A(L1)
196650 | Phase-wise object Breaker Status B(L2)
196651 | Phase-wise object Breaker Status C(L3)
196652 | Phase-wise object Withdraw Status
Measured values
IOA | Description
851969 | Pri.Pha.curr.IL1
851970 | Pha.angle IL1
851971 | Pri.Pha.curr.IL2
851972 | Pha.angle IL2
851973 | Pri.Pha.curr.IL3
851974 | Pha.angle IL3
851975 | f atm. Display (when not measurable is 0Hz)
851976 | Pri.Res.curr.I01
851977 | Pri.Res.curr.I02
851978 | System volt UL1 mag
851979 | System volt UL1 ang
851980 | System volt UL2 mag
851981 | System volt UL2 ang
851982 | System volt UL3 mag
851983 | System volt UL3 ang
851984 | System volt UL12 mag
851985 | System volt UL12 ang
851986 | System volt UL23 mag
851987 | System volt UL23 ang
851988 | System volt UL31 mag
851989 | System volt UL31 ang
851990 | System volt U0 mag
851991 | System volt U0 ang
851992 | POW1 3PH Active power (P)
851993 | POW1 3PH Reactive power (Q)
851994 | POW1 3PH Apparent power (S)
851995 | POW1 3PH Cos(phi)
851996 | Recorded fault value
851997 | Recorded fault value
851998 | Recorded fault value
851999 | Recorded fault value
852000 | Recorded fault value
852001 | Recorded fault value
852002 | Recorded fault value
852003 | Recorded fault value
852004 | Recorded fault value
852005 | Recorded fault value
852006 | Recorded fault value
852007 | Recorded fault value
852008 | Latest fault reactance
852009 | Latest fault distance
852010 | System volt U3 mag
852011 | System volt U4 mag
852012 | Pri.Pha.curr.I''L1
852013 | Pha.angle I''L1
852014 | Pri.Pha.curr.I''L2
852015 | Pha.angle I''L2
852016 | Pri.Pha.curr.I''L3
852017 | Pha.angle I''L3
852018 | S1 Measurement(Raw)
852019 | S2 Measurement(Raw)
852020 | S3 Measurement(Raw)
852021 | S4 Measurement(Raw)
852022 | S5 Measurement(Raw)
852023 | S6 Measurement(Raw)
852024 | S7 Measurement(Raw)
852025 | S8 Measurement(Raw)
852026 | S9 Measurement(Raw)
852027 | S10 Measurement(Raw)
852028 | S11 Measurement(Raw)
852029 | S12 Measurement(Raw)
852030 | S13 Measurement(Raw)
852031 | S14 Measurement(Raw)
852032 | S15 Measurement(Raw)
852033 | S16 Measurement(Raw)
852034 | S7 Measurement mA
852035 | S8 Measurement mA
852036 | S15 Measurement mA
852037 | S16 Measurement mA
852038 | Voltage now
852039 | Voltage difference to set target
852040 | POW1 3PH Tan(phi)
852041 | POW1 L1 Active power (P)
852042 | POW1 L1 Reactive power (Q)
852043 | POW1 L1 Apparent power (S)
852044 | POW1 L1 Cos(phi)
852045 | POW1 L1 Tan(phi)
852046 | POW1 L2 Active power (P)
852047 | POW1 L2 Reactive power (Q)
852048 | POW1 L2 Apparent power (S)
852049 | POW1 L2 Cos(phi)
852050 | POW1 L2 Tan(phi)
852051 | POW1 L3 Active power (P)
852052 | POW1 L3 Reactive power (Q)
852053 | POW1 L3 Apparent power (S)
852054 | POW1 L3 Cos(phi)
852055 | POW1 L3 Tan(phi)
852056 | Curve1 Output
852057 | Curve2 Output
852058 | Curve3 Output
852059 | Curve4 Output
852060 | Curve5 Output
852061 | Curve6 Output
852062 | Curve7 Output
852063 | Curve8 Output
852064 | Curve9 Output
852065 | Curve10 Output
852066 | IL1 harmonic demand
852067 | IL2 harmonic demand
852068 | IL3 harmonic demand
852069 | Tripped stage
852070 | Overcurrent fault type
852071 | Voltage fault type
852072 | VREC Magnitude 1
852073 | VREC Magnitude 2
852074 | VREC Magnitude 3
852075 | VREC Magnitude 4
852076 | VREC Magnitude 5
852077 | VREC Magnitude 6
852078 | VREC Magnitude 7
852079 | VREC Magnitude 8
852080 | Z< Z1PP Last fault location
852081 | Z< Z2PP Last fault location
852082 | Z< Z3PP Last fault location
852083 | Z< Z4PP Last fault location
852084 | Z< Z5PP Last fault location
852085 | Z< Z6PP Last fault location
852086 | Z< Z7PP Last fault location
852087 | Z< Z8PP Last fault location
852088 | Z< Z9PP Last fault location
852089 | Z< Z10PP Last fault location
852090 | Z< Z1PE Last fault location
852091 | Z< Z2PE Last fault location
852092 | Z< Z3PE Last fault location
852093 | Z< Z4PE Last fault location
852094 | Z< Z5PE Last fault location
852095 | Z< Z6PE Last fault location
852096 | Z< Z7PE Last fault location
852097 | Z< Z8PE Last fault location
852098 | Z< Z9PE Last fault location
852099 | Z< Z10PE Last fault location
852100 | mA In (I option 1)
852101 | mA In (I option 2)
852102 | Pri.Res.curr.I''01
852103 | Pri.Res.curr.I''02
852104 | POW2 3PH Active power (P)
852105 | POW2 3PH Reactive power (Q)
852106 | POW2 3PH Apparent power (S)
852107 | POW2 3PH Cos(phi)
852108 | POW2 3PH Tan(phi)
852109 | POW2 L1 Active power (P)
852110 | POW2 L1 Reactive power (Q)
852111 | POW2 L1 Apparent power (S)
852112 | POW2 L1 Cos(phi)
852113 | POW2 L1 Tan(phi)
852114 | POW2 L2 Active power (P)
852115 | POW2 L2 Reactive power (Q)
852116 | POW2 L2 Apparent power (S)
852117 | POW2 L2 Cos(phi)
852118 | POW2 L2 Tan(phi)
852119 | POW2 L3 Active power (P)
852120 | POW2 L3 Reactive power (Q)
852121 | POW2 L3 Apparent power (S)
852122 | POW2 L3 Cos(phi)
852123 | POW2 L3 Tan(phi)
852124 | mA In (T card) 1 mA In 1
852125 | mA In (T card) 1 mA In 2
852126 | mA In (T card) 1 mA In 3
852127 | mA In (T card) 1 mA In 4
852128 | mA In (T card) 2 mA In 1
852129 | mA In (T card) 2 mA In 2
852130 | mA In (T card) 2 mA In 3
852131 | mA In (T card) 2 mA In 4
Integrated totals
IOA | Description
983041 | Internal Relay Fault status
983042 | Export Active Energy (P) kWh
983043 | Import Active Energy (P) kWh
983044 | Imported (Q) while Export (P) kVarh
983045 | Imported (Q) while Import (P) kVarh
983046 | Recordings in memory
983047 | Max amount of recordings
983048 | Active setting group
983049 | Tap location now (- 0 +)
983050 | Absolute tap location
983051 | DI1 Counter
983052 | DI2 Counter
983053 | DI3 Counter
983054 | DI4 Counter
983055 | DI5 Counter
983056 | DI6 Counter
983057 | DI7 Counter
983058 | DI8 Counter
983059 | DI9 Counter
983060 | DI10 Counter
983061 | DI11 Counter
983062 | DI12 Counter
983063 | DI13 Counter
983064 | DI14 Counter
983065 | DI15 Counter
983066 | DI16 Counter
983067 | DI17 Counter
983068 | DI18 Counter
983069 | DI19 Counter
983070 | DI20 Counter
983071 | DI21 Counter
983072 | DI22 Counter
983073 | DI23 Counter
983074 | DI24 Counter
983075 | DI25 Counter
983076 | DI26 Counter
983077 | DI27 Counter
983078 | DI28 Counter
983079 | DI29 Counter
983080 | DI30 Counter
983081 | DI31 Counter
983082 | DI32 Counter
983083 | DI33 Counter
983084 | DI34 Counter
983085 | DI35 Counter
983086 | DI36 Counter
983087 | DI37 Counter
983088 | DI38 Counter
983089 | DI39 Counter
983090 | DI40 Counter
983091 | DI41 Counter
983092 | DI42 Counter
983093 | DI43 Counter
983094 | DI44 Counter
983095 | DI45 Counter
983096 | DI46 Counter
983097 | DI47 Counter
983098 | DI48 Counter
983099 | DI49 Counter
983100 | DI50 Counter
983101 | DI51 Counter
983102 | DI52 Counter
983103 | DI53 Counter
983104 | DI54 Counter
983105 | DI55 Counter
983106 | DI56 Counter
983107 | DI57 Counter
983108 | DI58 Counter
983109 | DI59 Counter
983110 | DI60 Counter
983111 | DI61 Counter
983112 | DI62 Counter
983113 | DI63 Counter
983114 | DI64 Counter
983115 | DI65 Counter
983116 | DI66 Counter
983117 | DI67 Counter
983118 | DI68 Counter
983119 | DI69 Counter
983120 | DI70 Counter
983121 | DI71 Counter
983122 | DI72 Counter
983123 | DI73 Counter
983124 | DI74 Counter
983125 | DI75 Counter
983126 | DI76 Counter
983127 | DI77 Counter
983128 | DI78 Counter
983129 | DI79 Counter
983130 | DI80 Counter
983131 | DI81 Counter
983132 | DI82 Counter
983133 | DI83 Counter
983134 | DI84 Counter
983135 | DI85 Counter
983136 | DI86 Counter
983137 | DI87 Counter
983138 | DI88 Counter
983139 | DI89 Counter
983140 | DI90 Counter
983141 | DI91 Counter
983142 | DI92 Counter
983143 | DI93 Counter
983144 | DI94 Counter
983145 | DI95 Counter
983146 | DI96 Counter
983147 | DI97 Counter
983148 | DI98 Counter
983149 | DI99 Counter
983150 | DI100 Counter
983151 | DI101 Counter
983152 | DI102 Counter
983153 | DI103 Counter
983154 | DI104 Counter
983155 | DI105 Counter
983156 | DI106 Counter
983157 | DI107 Counter
983158 | DI108 Counter
983159 | DI109 Counter
983160 | DI110 Counter
983161 | DI111 Counter
983162 | DI112 Counter
983163 | DI113 Counter
983164 | DI114 Counter
983165 | DI115 Counter
983166 | ParallelTransfModeKind
Single commands
IOA | Description
2949121 | Reset Latches
2949122 | Logical Input 1
2949123 | Logical Input 2
2949124 | Logical Input 3
2949125 | Logical Input 4
2949126 | Logical Input 5
2949127 | Logical Input 6
2949128 | Logical Input 7
2949129 | Logical Input 8
2949130 | Logical Input 9
2949131 | Logical Input 10
2949132 | Logical Input 11
2949133 | Logical Input 12
2949134 | Logical Input 13
2949135 | Logical Input 14
2949136 | Logical Input 15
2949137 | Logical Input 16
2949138 | Logical Input 17
2949139 | Logical Input 18
2949140 | Logical Input 19
2949141 | Logical Input 20
2949142 | Logical Input 21
2949143 | Logical Input 22
2949144 | Logical Input 23
2949145 | Logical Input 24
2949146 | Logical Input 25
2949147 | Logical Input 26
2949148 | Logical Input 27
2949149 | Logical Input 28
2949150 | Logical Input 29
2949151 | Logical Input 30
2949152 | Logical Input 31
2949153 | Logical Input 32
2949154 | PCS1 Switch Status
2949155 | PCS2 Switch Status
2949156 | PCS3 Switch Status
2949157 | PCS4 Switch Status
2949158 | PCS5 Switch Status
2949159 | Control mode
Double commands
IOA | Description
3014657 | OBJECT1 CTRL
3014658 | OBJECT2 CTRL
3014659 | OBJECT3 CTRL
3014660 | OBJECT4 CTRL
3014661 | OBJECT5 CTRL
3014662 | OBJECT6 CTRL
3014663 | OBJECT7 CTRL
3014664 | OBJECT8 CTRL
3014665 | OBJECT9 CTRL
3014666 | OBJECT10 CTRL
3014667 | OBJECT S1 CTRL